## 2018 Summary Grades
2018-07-19 |  | 2018 Standard Grading Summary
Hover over cell |  | Content Questions | [5 empty] | Quality Questions
Standard | Req. | OC | PC | RE | NERC | Avg | Delta | OC | PC | RE | NERC | Avg | Delta
CIP-014-2 | R1. | 3 | 3 | 1 | 2 | 2.25 | 2 | 13 | 13 | 12 | 11 | 12.25 | 2
CIP-014-2 | R2. | 3 | 3 | 2 | 3 | 2.75 | 1 | 13 | 13 | 13 | 12 | 12.75 | 1
CIP-014-2 | R3. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 13 | 12 | 11 | 12.25 | 2
CIP-014-2 | R4. | 3 | 3 | 2 | 3 | 2.75 | 1 | 13 | 13 | 13 | 13 | 13 | 0
CIP-014-2 | R5. | 3 | 3 | 2 | 3 | 2.75 | 1 | 13 | 13 | 11 | 13 | 12.5 | 2
CIP-014-2 | R6. | 3 | 3 | 2 | 3 | 2.75 | 1 | 13 | 13 | 12 | 11 | 12.25 | 2
COM-002-4 | R1. | 3 | 2 | 3 | 3 | 2.75 | 1 | 13 | 12 | 13 | 11 | 12.25 | 2
COM-002-4 | R2. | 3 | 3 | 2 | 3 | 2.75 | 1 | 11 | 13 | 13 | 13 | 12.5 | 2
COM-002-4 | R3. | 3 | 3 | 1 | 2 | 2.25 | 2 | 11 | 13 | 11 | 13 | 12 | 2
COM-002-4 | R4. | 3 | 2 | 3 | 3 | 2.75 | 1 | 11 | 13 | 12 | 13 | 12.25 | 2
COM-002-4 | R5. | 3 | 3 | 3 | 3 | 3 | 0 | 11 | 13 | 13 | 13 | 12.5 | 2
COM-002-4 | R6. | 3 | 3 | 2 | 3 | 2.75 | 1 | 11 | 13 | 13 | 13 | 12.5 | 2
COM-002-4 | R7. | 3 | 3 | 3 | 3 | 3 | 0 | 11 | 13 | 13 | 13 | 12.5 | 2
FAC-003-4 | R1. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 13 | 13 | 12 | 12.75 | 1
FAC-003-4 | R2. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 12 | 12 | 11 | 12 | 2
FAC-003-4 | R3. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 13 | 12 | 13 | 12.75 | 1
FAC-003-4 | R4. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 13 | 10 | 13 | 12.25 | 3
FAC-003-4 | R5. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 13 | 12 | 13 | 12.75 | 1
FAC-003-4 | R6. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 13 | 11 | 13 | 12.5 | 2
FAC-003-4 | R7. | 3 | 3 | 3 | 2 | 2.75 | 1 | 13 | 13 | 12 | 13 | 12.75 | 1
FAC-013-2 | R1. | 3 | 3 | 3 | 2 | 2.75 | 1 | 11 | 13 | 12 | 13 | 12.25 | 2
FAC-013-2 | R2. | 3 | 3 | 3 | 2 | 2.75 | 1 | 11 | 13 | 12 | 13 | 12.25 | 2
FAC-013-2 | R3. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 13 | 13 | 13 | 13 | 0
FAC-013-2 | R4. | 3 | 3 | 2 | 2 | 2.5 | 1 | 11 | 13 | 13 | 12 | 12.25 | 2
FAC-013-2 | R5. | 3 | 3 | 3 | 2 | 2.75 | 1 | 11 | 13 | 12 | 13 | 12.25 | 2
FAC-013-2 | R6. | 3 | 3 | 3 | 3 | 3 | 0 | 11 | 13 | 12 | 13 | 12.25 | 2
IRO-006-5 | R1. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 12 | 13 | 13 | 12.75 | 1
MOD-020-0 | R1. | 3 | 3 | 2 | 3 | 2.75 | 1 | 13 | 12 | 12 | 13 | 12.5 | 1
MOD-025-2 | R1. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 13 | 12 | 11 | 12.25 | 2
MOD-025-2 | R2. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 12 | 12 | 13 | 12.5 | 1
MOD-025-2 | R3. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 12 | 12 | 13 | 12.5 | 1
MOD-026-1 | R1. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 13 | 13 | 13 | 13 | 0
MOD-026-1 | R2. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 11 | 13 | 12 | 12.25 | 2
MOD-026-1 | R3. | 3 | 3 | 2 | 3 | 2.75 | 1 | 13 | 12 | 12 | 13 | 12.5 | 1
MOD-026-1 | R4. | 3 | 3 | 2 | 3 | 2.75 | 1 | 13 | 13 | 12 | 13 | 12.75 | 1
MOD-026-1 | R5. | 3 | 3 | 2 | 3 | 2.75 | 1 | 13 | 13 | 13 | 13 | 13 | 0
MOD-026-1 | R6. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 13 | 13 | 13 | 13 | 0
MOD-027-1 | R1. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 12 | 13 | 13 | 12.75 | 1
MOD-027-1 | R2. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 11 | 13 | 12 | 12.25 | 2
MOD-027-1 | R3. | 3 | 3 | 2 | 3 | 2.75 | 1 | 13 | 11 | 13 | 13 | 12.5 | 2
MOD-027-1 | R4. | 3 | 3 | 2 | 3 | 2.75 | 1 | 13 | 12 | 13 | 13 | 12.75 | 1
MOD-027-1 | R5. | 3 | 3 | 1 | 2 | 2.25 | 2 | 13 | 12 | 13 | 13 | 12.75 | 1
MOD-028-2 | R1. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 12 | 12 | 13 | 12.5 | 1
MOD-028-2 | R10. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 12 | 12 | 13 | 12.5 | 1
MOD-028-2 | R11. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 12 | 12 | 13 | 12.5 | 1
MOD-028-2 | R2. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 12 | 12 | 13 | 12.5 | 1
MOD-028-2 | R3. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 12 | 12 | 13 | 12.5 | 1
MOD-028-2 | R4. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 12 | 12 | 13 | 12.5 | 1
MOD-028-2 | R5. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 12 | 12 | 13 | 12.5 | 1
MOD-028-2 | R6. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 12 | 12 | 13 | 12.5 | 1
MOD-028-2 | R7. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 12 | 12 | 13 | 12.5 | 1
MOD-028-2 | R8. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 12 | 12 | 13 | 12.5 | 1
MOD-028-2 | R9. | 3 | 3 | 3 | 3 | 3 | 0 | 13 | 12 | 12 | 13 | 12.5 | 1
Note on A2: Color coding is not percentileor range based. It is configured to bring attention to the lower scores.
Note on B26: (Inactive)

## 2018 Summary Comments
Note* | [8 empty] | Content Questions from the Standards Independent Experts Report |  |  | Quality Questions from the Standards Independent Experts Report
Standard Number | Requirement Number | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Content Score (0-3) | Quality Score (0-13) | Combined (OC/PC/RE/NERC) Comment/Rationale | Supports a Reliability Objective (as defined by the Reliability Principles) | Meets the Paragraph 81 criteria? | Appropriate as a guide rather than a standard? | C1. Is the content of the requirement technically correct, including identifying who does what and when? | C2. Are the correct functional entities identified? | C3. Are the appropriate actions, for which there should be accountability, included or is there a gap? | Q1. Should the requirement stand alone as is (or should it be consolidated with other standards)? | Q2. Is it drafted as a results-based standard (RBS) requirement (performance, risk (prevention) or capability) and does it follow the RBS format (e.g., sub-requirement structure)? | Q3. Is it technologically neutral? | Q4. Are the expectations for each function clear? | Q5. Does the requirement align with the purpose? | Q6. Is it a higher solution than the lowest common denominator? | Q7. Is it measureable? | Q8. Does it have a technical basis in engineering and operations? | Q9. Is it complete and self-contained? | Q10. Is the language clear and does not contain ambiguous or outdated terms? | Q11. Can it be practically implemented? | Q12. Does it use consistent terminology? | Q13. Is the Standard cost effective in achieving the reliability purpose or objective of the Standard and mitigating the risk to the BES? | Content Score (0-3) | Quality Score (0-13) | Combined (OC/PC/RE/NERC) Comment/Rationale | Operating Committee Comment/Rationale | Planning Committee Comment/Rationale | Regional Entities Comment/Rationale | NERC Comment/Rationale
CIP-014-2 | R1. | R1. Each Transmission Owner shall perform an initial risk assessment and subsequent risk assessments of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria specified in Applicability Section 4.1.1. The initial and subsequent risk assessments shall consist of a transmission analysis or transmission analyses designed to identify the Transmission station(s) and Transmission substation(s) that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection. 1.1. Subsequent risk assessments shall be performed: • At least once every 30 calendar months for a Transmission Owner that hasidentified in its previous risk assessment (as verified according to Requirement R2) one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection; or • At least once every 60 calendar months for a Transmission Owner that has not identified in its previous risk assessment (as verified according to Requirement R2) any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. 1.2. The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. | Delta:2 OC:3 PC:3 RE:1 NERC:2 | Delta:2 OC:13 PC:13 RE:12 NERC:11 | OC: No comment PC: No comment RE: This requirement needs additional clarity. Additional clarity necessary in regards to subsequent risk assessments under R1.1. (The concern is that if your initial risk assessment is satisfied you do not have to do another risk assessment until 5 years later, 5 years is a long time frame.) Does the TO have the expertise to do the assessment? If the TO is also TP then yes however if the TO is not a TP then they might need to hire a third party contractor to do the assessment. How long does the TO have to be compliant for a new facility. Unclear how co-owned facilities risk assessments should be done, the entire facility should be looked at regardless of ownership. NERC: 1st Question & Q8: The standard is open-ended and does not specify a specific assessment methodology. Two entities could have differing approaches for the same identified facilities and result in differing conclusions. C1. Not clear on adjacent stations/substations. What happens during topology changes? Q11. Lack of methodology does not make it practical/duplicate over time. | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:Yes | OC:Yes PC:Yes RE:No NERC:No | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:2 OC:3 PC:3 RE:1 NERC:2 | Delta:2 OC:13 PC:13 RE:12 NERC:11 | OC: No comment PC: No comment RE: This requirement needs additional clarity. Additional clarity necessary in regards to subsequent risk assessments under R1.1. (The concern is that if your initial risk assessment is satisfied you do not have to do another risk assessment until 5 years later, 5 years is a long time frame.) Does the TO have the expertise to do the assessment? If the TO is also TP then yes however if the TO is not a TP then they might need to hire a third party contractor to do the assessment. How long does the TO have to be compliant for a new facility. Unclear how co-owned facilities risk assessments should be done, the entire facility should be looked at regardless of ownership. NERC: 1st Question & Q8: The standard is open-ended and does not specify a specific assessment methodology. Two entities could have differing approaches for the same identified facilities and result in differing conclusions. C1. Not clear on adjacent stations/substations. What happens during topology changes? Q11. Lack of methodology does not make it practical/duplicate over time. | 0 | 0 | This requirement needs additional clarity. Additional clarity necessary in regards to subsequent risk assessments under R1.1. (The concern is that if your initial risk assessment is satisfied you do not have to do another risk assessment until 5 years later, 5 years is a long time frame.) Does the TO have the expertise to do the assessment? If the TO is also TP then yes however if the TO is not a TP then they might need to hire a third party contractor to do the assessment. How long does the TO have to be compliant for a new facility. Unclear how co-owned facilities risk assessments should be done, the entire facility should be looked at regardless of ownership. | 1st Question & Q8: The standard is open-ended and does not specify a specific assessment methodology. Two entities could have differing approaches for the same identified facilities and result in differing conclusions. C1. Not clear on adjacent stations/substations. What happens during topology changes? Q11. Lack of methodology does not make it practical/duplicate over time.
CIP-014-2 | R2. | R2. Each Transmission Owner shall have an unaffiliated third party verify the risk assessment performed under Requirement R1. The verification may occur concurrent with or after the risk assessment performed under Requirement R1. 2.1. Each Transmission Owner shall select an unaffiliated verifying entity that is either: • A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or • An entity that has transmission planning or analysis experience. 2.2. The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment. 2.3. If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station(s) or Transmission substation(s) from, its identification under Requirement R1, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation: • Modify its identification under Requirement R1 consistent with the recommendation; or • Document the technical basis for not modifying the identification in accordance with the recommendation. 2.4. Each Transmission Owner shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:1 OC:13 PC:13 RE:13 NERC:12 | OC: No comment PC: No comment RE: The concern is the requirement does not have any way to ensure the quality of the unaffiliated third party's review. The entity conducting the verification required by R2 should not be the same entity that conducted R1. NERC: C1. The lack of a defined methodology could prohibit the third-party from appropriately measuring the entity's risk assessment. | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:1 OC:13 PC:13 RE:13 NERC:12 | OC: No comment PC: No comment RE: The concern is the requirement does not have any way to ensure the quality of the unaffiliated third party's review. The entity conducting the verification required by R2 should not be the same entity that conducted R1. NERC: C1. The lack of a defined methodology could prohibit the third-party from appropriately measuring the entity's risk assessment. | 0 | 0 | The concern is the requirement does not have any way to ensure the quality of the unaffiliated third party's review. The entity conducting the verification required by R2 should not be the same entity that conducted R1. | C1. The lack of a defined methodology could prohibit the third-party from appropriately measuring the entity's risk assessment.
CIP-014-2 | R3. | R3. For a primary control center(s) identified by the Transmission Owner according to Requirement R1, Part 1.2 that a) operationally controls an identified Transmission station or Transmission substation verified according to Requirement R2, and b) is not under the operational control of the Transmission Owner: the Transmission Owner shall, within seven calendar days following completion of Requirement R2, notify the Transmission Operator that has operational control of the primary control center of such identification and the date of completion of Requirement R2. 3.1. If a Transmission station or Transmission substation previously identified under Requirement R1 and verified according to Requirement R2 is removed from the identification during a subsequent risk assessment performed according to Requirement R1 or a verification according to Requirement R2, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:2 OC:13 PC:13 RE:12 NERC:11 | OC: No comment PC: No comment RE: This is strictly a notification requirement and could be combined with a different requirement. R1.2 is a candidate that potentially could be reviewed to include this requirement "prior" to the verification process. This would enable the entity owning or TOP controlling the primary control center to provide input to the decision made by the TO. NERC: Q1 & Q6: There could be opportunities to prevent potential duplication and overlap with other standards (e.g., CIP-006). | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:2 OC:13 PC:13 RE:12 NERC:11 | OC: No comment PC: No comment RE: This is strictly a notification requirement and could be combined with a different requirement. R1.2 is a candidate that potentially could be reviewed to include this requirement "prior" to the verification process. This would enable the entity owning or TOP controlling the primary control center to provide input to the decision made by the TO. NERC: Q1 & Q6: There could be opportunities to prevent potential duplication and overlap with other standards (e.g., CIP-006). | 0 | 0 | This is strictly a notification requirement and could be combined with a different requirement. R1.2 is a candidate that potentially could be reviewed to include this requirement "prior" to the verification process. This would enable the entity owning or TOP controlling the primary control center to provide input to the decision made by the TO. | Q1 & Q6: There could be opportunities to prevent potential duplication and overlap with other standards (e.g., CIP-006).
CIP-014-2 | R4. | R4. Each Transmission Owner that identified a Transmission station, Transmission substation, or a primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall conduct an evaluation of the potential threats and vulnerabilities of a physical attack to each of their respective Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2. The evaluation shall consider the following: 4.1. Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); 4.2. Prior history of attack on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events; and 4.3. Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: It is possible that the threat evaluation could not be comprehensive enough if only 4.1 through 4.3 are considered. Additional resources could be provided in a guidance document. NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:Yes NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: It is possible that the threat evaluation could not be comprehensive enough if only 4.1 through 4.3 are considered. Additional resources could be provided in a guidance document. NERC: No comment | 0 | 0 | It is possible that the threat evaluation could not be comprehensive enough if only 4.1 through 4.3 are considered. Additional resources could be provided in a guidance document. | 0
CIP-014-2 | R5. | R5. Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall develop and implement a documented physical security plan(s) that covers their respective Transmission station(s), Transmission substation(s), and primary control center(s). The physical security plan(s) shall be developed within 120 calendar days following the completion of Requirement R2 and executed according to the timeline specified in the physical security plan(s). The physical security plan(s) shall include the following attributes: 5.1. Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R4. 5.2. Law enforcement contact and coordination information. 5.3. A timeline for executing the physical security enhancements and modifications specified in the physical security plan. 5.4. Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:2 OC:13 PC:13 RE:11 NERC:13 | OC: No comment PC: No comment RE: The term resiliency is also undefined and concepts of what constitutes resilience is under discussion. There are also no specific industry standards on what would represent adequate deterrence or detection as well as response. No specified time frame in which to implement physical security plan(s). In a perfect world, the entity would implement as quickly as possible, but the language of the standard allows them to set their own timeline. NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC: PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:2 OC:13 PC:13 RE:11 NERC:13 | OC: No comment PC: No comment RE: The term resiliency is also undefined and concepts of what constitutes resilience is under discussion. There are also no specific industry standards on what would represent adequate deterrence or detection as well as response. No specified time frame in which to implement physical security plan(s). In a perfect world, the entity would implement as quickly as possible, but the language of the standard allows them to set their own timeline. NERC: No comment | 0 | 0 | The term resiliency is also undefined and concepts of what constitutes resilience is under discussion. There are also no specific industry standards on what would represent adequate deterrence or detection as well as response. No specified time frame in which to implement physical security plan(s). In a perfect world, the entity would implement as quickly as possible, but the language of the standard allows them to set their own timeline. | 0
CIP-014-2 | R6. | R6. Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall have an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5. The review may occur concurrently with or after completion of the evaluation performed under Requirement R4 and the security plan development under Requirement R5. 6.1. Each Transmission Owner and Transmission Operator shall select an unaffiliated third party reviewer from the following: • An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification. • An entity or organization approved by the ERO. • A governmental agency with physical security expertise. • An entity or organization with demonstrated law enforcement, government, or military physical security expertise. 6.2. The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. 6.3. If the unaffiliated third party reviewer recommends changes to the evaluation performed under Requirement R4 or security plan(s) developed under Requirement R5, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation: • Modify its evaluation or security plan(s) consistent with the recommendation; or • Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. 6.4. Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:2 OC:13 PC:13 RE:12 NERC:11 | OC: No comment PC: No comment RE: The entity conducting the verification required by R6 should not be the same entity that conducted R4 and R5. The GTB did a good job in explaining everything but it is unclear in the requirement language. NERC: Q1 & Q6: There could be opportunities to prevent potential duplication and overlap with other standards (e.g., CIP-006). | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:2 OC:13 PC:13 RE:12 NERC:11 | OC: No comment PC: No comment RE: The entity conducting the verification required by R6 should not be the same entity that conducted R4 and R5. The GTB did a good job in explaining everything but it is unclear in the requirement language. NERC: Q1 & Q6: There could be opportunities to prevent potential duplication and overlap with other standards (e.g., CIP-006). | 0 | 0 | The entity conducting the verification required by R6 should not be the same entity that conducted R4 and R5. The GTB did a good job in explaining everything but it is unclear in the requirement language. | Q1 & Q6: There could be opportunities to prevent potential duplication and overlap with other standards (e.g., CIP-006).
COM-002-4 | R1. | R1. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall develop documented communications protocols for its operating personnel that issue and receive Operating Instructions. The protocols shall, at a minimum: 1.1. Require its operating personnel that issue and receive an oral or written Operating Instruction to use the English language, unless agreed to otherwise. An alternate language may be used for internal operations. 1.2. Require its operating personnel that issue an oral two-party, person-to-person Operating Instruction to take one of the following actions: • Confirm the receiver’s response if the repeated information is correct. • Reissue the Operating Instruction if the repeated information is incorrect or if requested by the receiver. • Take an alternative action if a response is not received or if the Operating Instruction was not understood by the receiver. 1.3. Require its operating personnel that receive an oral two-party, person-to-person Operating Instruction to take one of the following actions: • Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct. • Request that the issuer reissue the Operating Instruction. 1.4. Require its operating personnel that issue a written or oral single-party to multiple-party burst Operating Instruction to confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. 1.5. Specify the instances that require time identification when issuing an oral or written Operating Instruction and the format for that time identification. 1.6. Specify the nomenclature for Transmission interface Elements and Transmission interface Facilities when issuing an oral or written Operating Instruction. | Delta:1 OC:3 PC:2 RE:3 NERC:3 | Delta:2 OC:13 PC:12 RE:13 NERC:11 | OC: No comment PC: C2: DP and GOP should be included and required to develop documented communication protocols for receiving Operating Instructions. Q6: Assuming Operating Instructions are the lowest common denominator, we believe that the term Directive should be reintroduced into the standard to distinguish between common every day Operating Instructions (ex: switching orders) and critical reliability related instructions (i.e. Directives). RE: No comment NERC: Q1: Generally speaking, R2-R7 create the protocol, so why does it need to be listed? R4 requires assessment with the standard. Q10: 1.1 "unless agreed to otherwise" is unclear - doesn't it mean between the parties or agreed on by a specific entity. Q10: 1.6 "Specify the nomenclature for Transmission interface Elements and Transmission interface Facilities" is unclear - is this common line identifiers? | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:Yes NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:1 OC:3 PC:2 RE:3 NERC:3 | Delta:2 OC:13 PC:12 RE:13 NERC:11 | OC: No comment PC: C2: DP and GOP should be included and required to develop documented communication protocols for receiving Operating Instructions. Q6: Assuming Operating Instructions are the lowest common denominator, we believe that the term Directive should be reintroduced into the standard to distinguish between common every day Operating Instructions (ex: switching orders) and critical reliability related instructions (i.e. Directives). RE: No comment NERC: Q1: Generally speaking, R2-R7 create the protocol, so why does it need to be listed? R4 requires assessment with the standard. Q10: 1.1 "unless agreed to otherwise" is unclear - doesn't it mean between the parties or agreed on by a specific entity. Q10: 1.6 "Specify the nomenclature for Transmission interface Elements and Transmission interface Facilities" is unclear - is this common line identifiers? | 0 | C2: DP and GOP should be included and required to develop documented communication protocols for receiving Operating Instructions. Q6: Assuming Operating Instructions are the lowest common denominator, we believe that the term Directive should be reintroduced into the standard to distinguish between common every day Operating Instructions (ex: switching orders) and critical reliability related instructions (i.e. Directives). | 0 | Q1: Generally speaking, R2-R7 create the protocol, so why does it need to be listed? R4 requires assessment with the standard. Q10: 1.1 "unless agreed to otherwise" is unclear - doesn't it mean between the parties or agreed on by a specific entity. Q10: 1.6 "Specify the nomenclature for Transmission interface Elements and Transmission interface Facilities" is unclear - is this common line identifiers?
COM-002-4 | R2. | R2. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall conduct initial training for each of its operating personnel responsible for the Real-time operation of the interconnected Bulk Electric System on the documented communications protocols developed in Requirement R1 prior to that individual operator issuing an Operating Instruction. | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:2 OC:11 PC:13 RE:13 NERC:13 | OC: Move to PER-005 (training) or remove. All training requirements should be in one place and need to decide whether we need to list every subject that needs training. PC: No comment RE: Personnel should be trained more than just initially. At a minimum, the operating personnel should be trained annually, or when an issue arises and when getting re-certified as a System Operator (or other appropriate licensing/certification). NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:2 OC:11 PC:13 RE:13 NERC:13 | OC: Move to PER-005 (training) or remove. All training requirements should be in one place and need to decide whether we need to list every subject that needs training. PC: No comment RE: Personnel should be trained more than just initially. At a minimum, the operating personnel should be trained annually, or when an issue arises and when getting re-certified as a System Operator (or other appropriate licensing/certification). NERC: No comment | Move to PER-005 (training) or remove. All training requirements should be in one place and need to decide whether we need to list every subject that needs training. | 0 | Personnel should be trained more than just initially. At a minimum, the operating personnel should be trained annually, or when an issue arises and when getting re-certified as a System Operator (or other appropriate licensing/certification). | 0
COM-002-4 | R3. | R3. Each Distribution Provider and Generator Operator shall conduct initial training for each of its operating personnel who can receive an oral two-party, person-to-person Operating Instruction prior to that individual operator receiving an oral two-party, person-to-person Operating Instruction to either: • Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or • Request that the issuer reissue the Operating Instruction. | Delta:2 OC:3 PC:3 RE:1 NERC:2 | Delta:2 OC:11 PC:13 RE:11 NERC:13 | OC: Move to PER-005 (training) or remove. All training requirements should be in one place and need to decide whether we need to list every subject that needs training. PC: No comment RE: UFLS-only DP should be added to the applicability of the requirement. If UFLS-only DP is not added to the applicability, that entity may not do the training required by COM-002-4 Requirement R3 or three-part communication as required by COM-002-4 Requirement R6. A UFLS-only DP may receive Operating Instructions to coordinate the re-energization of underfrequency relay equipped load. That would indicate the need for proper communications between the appropriate parties. Furthermore, during a Blackstart scenario the UFLS-only DP may be required to not re-energize load (through an Operating Instruction) to help coordinate the stabilization of the grid during restoration. Personnel should be trained more than just initially. At a minimum, the operating personnel should be trained annually, or when an issue arises and when getting re-certified as a System Operator (or other appropriate licensing/certification). NERC: C2: Should the GO and TO be included in the realm of "operating personnel". | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:No | OC:Yes PC:Yes RE:No NERC:Yes | OC:No PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | Delta:2 OC:3 PC:3 RE:1 NERC:2 | Delta:2 OC:11 PC:13 RE:11 NERC:13 | OC: Move to PER-005 (training) or remove. All training requirements should be in one place and need to decide whether we need to list every subject that needs training. PC: No comment RE: UFLS-only DP should be added to the applicability of the requirement. If UFLS-only DP is not added to the applicability, that entity may not do the training required by COM-002-4 Requirement R3 or three-part communication as required by COM-002-4 Requirement R6. A UFLS-only DP may receive Operating Instructions to coordinate the re-energization of underfrequency relay equipped load. That would indicate the need for proper communications between the appropriate parties. Furthermore, during a Blackstart scenario the UFLS-only DP may be required to not re-energize load (through an Operating Instruction) to help coordinate the stabilization of the grid during restoration. Personnel should be trained more than just initially. At a minimum, the operating personnel should be trained annually, or when an issue arises and when getting re-certified as a System Operator (or other appropriate licensing/certification). NERC: C2: Should the GO and TO be included in the realm of "operating personnel". | Move to PER-005 (training) or remove. All training requirements should be in one place and need to decide whether we need to list every subject that needs training. | 0 | UFLS-only DP should be added to the applicability of the requirement. If UFLS-only DP is not added to the applicability, that entity may not do the training required by COM-002-4 Requirement R3 or three-part communication as required by COM-002-4 Requirement R6. A UFLS-only DP may receive Operating Instructions to coordinate the re-energization of underfrequency relay equipped load. That would indicate the need for proper communications between the appropriate parties. Furthermore, during a Blackstart scenario the UFLS-only DP may be required to not re-energize load (through an Operating Instruction) to help coordinate the stabilization of the grid during restoration. Personnel should be trained more than just initially. At a minimum, the operating personnel should be trained annually, or when an issue arises and when getting re-certified as a System Operator (or other appropriate licensing/certification). | C2: Should the GO and TO be included in the realm of "operating personnel".
COM-002-4 | R4. | R4. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall at least once every twelve (12) calendar months: 4.1. Assess adherence to the documented communications protocols in Requirement R1 by its operating personnel that issue and receive Operating Instructions, provide feedback to those operating personnel and take corrective action, as deemed appropriate by the entity, to address deviations from the documented protocols. 4.2. Assess the effectiveness of its documented communications protocols in Requirement R1 for its operating personnel that issue and receive Operating Instructions and modify its documented communication protocols, as necessary. | Delta:1 OC:3 PC:2 RE:3 NERC:3 | Delta:2 OC:11 PC:13 RE:12 NERC:13 | OC: R4 should move to R1 and align with M1. PC: We believe R1-R3 satisfy the purpose of this standard, while R4 should be a guide. C2: GOP should be included since they are the receiving party in three part communication. RE: The concern is "deemed appropriate" language is vague. NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:Yes NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | Delta:1 OC:3 PC:2 RE:3 NERC:3 | Delta:2 OC:11 PC:13 RE:12 NERC:13 | OC: R4 should move to R1 and align with M1. PC: We believe R1-R3 satisfy the purpose of this standard, while R4 should be a guide. C2: GOP should be included since they are the receiving party in three part communication. RE: The concern is "deemed appropriate" language is vague. NERC: No comment | R4 should move to R1 and align with M1. | We believe R1-R3 satisfy the purpose of this standard, while R4 should be a guide. C2: GOP should be included since they are the receiving party in three part communication. | The concern is "deemed appropriate" language is vague. | 0
COM-002-4 | R5. | R5. Each Balancing Authority, Reliability Coordinator, and Transmission Operator that issues an oral two-party, person-to-person Operating Instruction during an Emergency, excluding written or oral single-party to multiple-party burst Operating Instructions, shall either: • Confirm the receiver’s response if the repeated information is correct (in accordance with Requirement R6). • Reissue the Operating Instruction if the repeated information is incorrect or if requested by the receiver, or • Take an alternative action if a response is not received or if the Operating Instruction was not understood by the receiver. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:2 OC:11 PC:13 RE:13 NERC:13 | OC: Combine with R1 to simplify. PC: No comment RE: No comment NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:2 OC:11 PC:13 RE:13 NERC:13 | OC: Combine with R1 to simplify. PC: No comment RE: No comment NERC: No comment | Combine with R1 to simplify. | 0 | 0 | 0
COM-002-4 | R6. | R6. Each Balancing Authority, Distribution Provider, Generator Operator, and Transmission Operator that receives an oral two-party, person-to-person Operating Instruction during an Emergency, excluding written or oral single-party to multiple-party burst Operating Instructions, shall either: • Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or • Request that the issuer reissue the Operating Instruction. | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:2 OC:11 PC:13 RE:13 NERC:13 | OC: Combine with R1 to simplify. PC: No comment RE: UFLS-only DP should be added to the applicability of the requirement. If UFLS-only DP is not added to the applicability, that entity may not do the training required by COM-002-4 Requirement R3 or three-part communication as required by COM-002-4 Requirement R6. A UFLS-only DP may receive Operating Instructions to coordinate the re-energization of underfrequency relay equipped load. That would indicate the need for proper communications between the appropriate parties. Furthermore, during a Blackstart scenario the UFLS-only DP may be required to not re-energize load (through an Operating Instruction) to help coordinate the stabilization of the grid during restoration. NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:2 OC:11 PC:13 RE:13 NERC:13 | OC: Combine with R1 to simplify. PC: No comment RE: UFLS-only DP should be added to the applicability of the requirement. If UFLS-only DP is not added to the applicability, that entity may not do the training required by COM-002-4 Requirement R3 or three-part communication as required by COM-002-4 Requirement R6. A UFLS-only DP may receive Operating Instructions to coordinate the re-energization of underfrequency relay equipped load. That would indicate the need for proper communications between the appropriate parties. Furthermore, during a Blackstart scenario the UFLS-only DP may be required to not re-energize load (through an Operating Instruction) to help coordinate the stabilization of the grid during restoration. NERC: No comment | Combine with R1 to simplify. | 0 | UFLS-only DP should be added to the applicability of the requirement. If UFLS-only DP is not added to the applicability, that entity may not do the training required by COM-002-4 Requirement R3 or three-part communication as required by COM-002-4 Requirement R6. A UFLS-only DP may receive Operating Instructions to coordinate the re-energization of underfrequency relay equipped load. That would indicate the need for proper communications between the appropriate parties. Furthermore, during a Blackstart scenario the UFLS-only DP may be required to not re-energize load (through an Operating Instruction) to help coordinate the stabilization of the grid during restoration. | 0
COM-002-4 | R7. | R7. Each Balancing Authority, Reliability Coordinator, and Transmission Operator that issues a written or oral single-party to multiple-party burst Operating Instruction during an Emergency shall confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:2 OC:11 PC:13 RE:13 NERC:13 | OC: Combine with R1 to simplify. PC: No comment RE: No comment NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:2 OC:11 PC:13 RE:13 NERC:13 | OC: Combine with R1 to simplify. PC: No comment RE: No comment NERC: No comment | Combine with R1 to simplify. | 0 | 0 | 0
FAC-003-4 | R1. | R1. Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the Minimum Vegetation Clearance Distance (MVCD) of its applicable line(s) which are either an element of an IROL, or an element of a Major WECC Transfer Path; operating within their Rating and all Rated Electrical Operating Conditions of the types shown below: 1.1. An encroachment into the MVCD as shown in FAC-003-Table 2, observed in Real-time, absent a Sustained Outage, 1.2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, 1.3. An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, 1.4. An encroachment due to vegetation growth into the MVCD that caused a vegetation-related Sustained Outage. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:13 RE:13 NERC:12 | OC: No comment PC: No comment RE: In the Applicability section there is reference to PCs identifying IROLs for lines less than 200 kV. This needs to be revisited. The FAC project team is moving forward with recommending retirement of FAC-010 because PC's don't develop IROLs. All references to PCs identifying IROLs will have to be revisited. Specifically in this standard and the CIP-002 standard. NERC: Q7: WECC is moving away from Major WECC Transfer Path. | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:13 RE:13 NERC:12 | OC: No comment PC: No comment RE: In the Applicability section there is reference to PCs identifying IROLs for lines less than 200 kV. This needs to be revisited. The FAC project team is moving forward with recommending retirement of FAC-010 because PC's don't develop IROLs. All references to PCs identifying IROLs will have to be revisited. Specifically in this standard and the CIP-002 standard. NERC: Q7: WECC is moving away from Major WECC Transfer Path. | 0 | 0 | In the Applicability section there is reference to PCs identifying IROLs for lines less than 200 kV. This needs to be revisited. The FAC project team is moving forward with recommending retirement of FAC-010 because PC's don't develop IROLs. All references to PCs identifying IROLs will have to be revisited. Specifically in this standard and the CIP-002 standard. | Q7: WECC is moving away from Major WECC Transfer Path.
FAC-003-4 | R2. | R2. Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are not either an element of an IROL, or an element of a Major WECC Transfer Path; operating within its Rating and all Rated Electrical Operating Conditions of the types shown below: 2.1. An encroachment into the MVCD, observed in Real-time, absent a Sustained Outage, 2.2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, 2.3. An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, 2.4. An encroachment due to vegetation growth into the line MVCD that caused a vegetation-related Sustained Outage. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:2 OC:13 PC:12 RE:12 NERC:11 | OC: No comment PC: Clear definition of Sustained Outage. RE: Requirement 2.1 is missing "as shown in FAC-003-Table 2". The language is not consistent however it is referenced in the VSLs. NERC: Q7: WECC is moving away from Major WECC Transfer Path. Q12: Table 2 for MVCD is not referenced in 2.1 like it is in 1.1. | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:2 OC:13 PC:12 RE:12 NERC:11 | OC: No comment PC: Clear definition of Sustained Outage. RE: Requirement 2.1 is missing "as shown in FAC-003-Table 2". The language is not consistent however it is referenced in the VSLs. NERC: Q7: WECC is moving away from Major WECC Transfer Path. Q12: Table 2 for MVCD is not referenced in 2.1 like it is in 1.1. | 0 | Clear definition of Sustained Outage. | Requirement 2.1 is missing "as shown in FAC-003-Table 2". The language is not consistent however it is referenced in the VSLs. | Q7: WECC is moving away from Major WECC Transfer Path. Q12: Table 2 for MVCD is not referenced in 2.1 like it is in 1.1.
FAC-003-4 | R3. | R3. Each applicable Transmission Owner and applicable Generator Owner shall have documented maintenance strategies or procedures or processes or specifications it uses to prevent the encroachment of vegetation into the MVCD of its applicable lines that accounts for the following: 3.1. Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; 3.2. Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:13 RE:12 NERC:13 | OC: No comment PC: This Requirement acts as a control to support compliance with R1 and R2. R1 and R2 are the ultimate goal - no vegetation encroachment within the MVCD and no faults. This Requirement deals with how NERC expects the Transmission Owner to achieve compliance with R1 and R2. RE: The reliability objective of the standard is not necessarily contingent to a specific method or strategy or even having one. The objective is to have no vegetation related outages and specificity of how that is achieved is a detail appropriate for a guideline. NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:Yes NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:13 RE:12 NERC:13 | OC: No comment PC: This Requirement acts as a control to support compliance with R1 and R2. R1 and R2 are the ultimate goal - no vegetation encroachment within the MVCD and no faults. This Requirement deals with how NERC expects the Transmission Owner to achieve compliance with R1 and R2. RE: The reliability objective of the standard is not necessarily contingent to a specific method or strategy or even having one. The objective is to have no vegetation related outages and specificity of how that is achieved is a detail appropriate for a guideline. NERC: No comment | 0 | This Requirement acts as a control to support compliance with R1 and R2. R1 and R2 are the ultimate goal - no vegetation encroachment within the MVCD and no faults. This Requirement deals with how NERC expects the Transmission Owner to achieve compliance with R1 and R2. | The reliability objective of the standard is not necessarily contingent to a specific method or strategy or even having one. The objective is to have no vegetation related outages and specificity of how that is achieved is a detail appropriate for a guideline. | 0
FAC-003-4 | R4. | R4. Each applicable Transmission Owner and applicable Generator Owner, without any intentional time delay, shall notify the control center holding switching authority for the associated applicable line when the applicable Transmission Owner and applicable Generator Owner has confirmed the existence of a vegetation condition that is likely to cause a Fault at any moment. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:3 OC:13 PC:13 RE:10 NERC:13 | OC: No comment PC: No comment RE: The phrase "without any intentional time delay" has questionable value in this context and from a compliance point is difficult to measure. Can be consolidated with R1. NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:3 OC:13 PC:13 RE:10 NERC:13 | OC: No comment PC: No comment RE: The phrase "without any intentional time delay" has questionable value in this context and from a compliance point is difficult to measure. Can be consolidated with R1. NERC: No comment | 0 | 0 | The phrase "without any intentional time delay" has questionable value in this context and from a compliance point is difficult to measure. Can be consolidated with R1. | 0
FAC-003-4 | R5. | R5. When an applicable Transmission Owner and an applicable Generator Owner are constrained from performing vegetation work on an applicable line operating within its Rating and all Rated Electrical Operating Conditions, and the constraint may lead to a vegetation encroachment into the MVCD prior to the implementation of the next annual work plan, then the applicable Transmission Owner or applicable Generator Owner shall take corrective action to ensure continued vegetation management to prevent encroachments. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:13 RE:12 NERC:13 | OC: No comment PC: This Requirement acts as a control to support compliance with R1 and R2. R1 and R2 are the ultimate goal - no vegetation encroachment within the MVCD and no faults. This Requirement deals with how NERC expects the Transmission Owner to achieve compliance with R1 and R2. RE: Can be consolidated with Requirements. NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:13 RE:12 NERC:13 | OC: No comment PC: This Requirement acts as a control to support compliance with R1 and R2. R1 and R2 are the ultimate goal - no vegetation encroachment within the MVCD and no faults. This Requirement deals with how NERC expects the Transmission Owner to achieve compliance with R1 and R2. RE: Can be consolidated with Requirements. NERC: No comment | 0 | This Requirement acts as a control to support compliance with R1 and R2. R1 and R2 are the ultimate goal - no vegetation encroachment within the MVCD and no faults. This Requirement deals with how NERC expects the Transmission Owner to achieve compliance with R1 and R2. | Can be consolidated with Requirements. | 0
FAC-003-4 | R6. | R6. Each applicable Transmission Owner and applicable Generator Owner shall perform a Vegetation Inspection of 100% of its applicable transmission lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) at least once per calendar year and with no more than 18 calendar months between inspections on the same ROW. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:2 OC:13 PC:13 RE:11 NERC:13 | OC: No comment PC: This Requirement acts as a control to support compliance with R1 and R2. R1 and R2 are the ultimate goal - no vegetation encroachment within the MVCD and no faults. This Requirement deals with how NERC expects the Transmission Owner to achieve compliance with R1 and R2. RE: The applicability section refers to "applicable line", whereas the requirement uses the term "applicable transmission line". These terms should be the same if they are intending to refer to the same thing. Can be consolidated with other Requirements. NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:2 OC:13 PC:13 RE:11 NERC:13 | OC: No comment PC: This Requirement acts as a control to support compliance with R1 and R2. R1 and R2 are the ultimate goal - no vegetation encroachment within the MVCD and no faults. This Requirement deals with how NERC expects the Transmission Owner to achieve compliance with R1 and R2. RE: The applicability section refers to "applicable line", whereas the requirement uses the term "applicable transmission line". These terms should be the same if they are intending to refer to the same thing. Can be consolidated with other Requirements. NERC: No comment | 0 | This Requirement acts as a control to support compliance with R1 and R2. R1 and R2 are the ultimate goal - no vegetation encroachment within the MVCD and no faults. This Requirement deals with how NERC expects the Transmission Owner to achieve compliance with R1 and R2. | The applicability section refers to "applicable line", whereas the requirement uses the term "applicable transmission line". These terms should be the same if they are intending to refer to the same thing. Can be consolidated with other Requirements. | 0
FAC-003-4 | R7. | R7. Each applicable Transmission Owner and applicable Generator Owner shall complete 100% of its annual vegetation work plan of applicable lines to ensure no vegetation encroachments occur within the MVCD. Modifications to the work plan in response to changing conditions or to findings from vegetation inspections may be made (provided they do not allow encroachment of vegetation into the MVCD) and must be documented. The percent completed calculation is based on the number of units actually completed divided by the number of units in the final amended plan (measured in units of choice - circuit, pole line, line miles or kilometers, etc.). Examples of reasons for modification to annual plan may include. 7.1. Change in expected growth rate/environmental factors 7.2. Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner 7.3. Rescheduling work between growing seasons 7.4. Crew or contractor availability/Mutual assistance agreements 7.5. Identified unanticipated high priority work 7.6. Weather conditions/Accessibility 7.7. Permitting delays 7.8. Land ownership changes/Change in land use by the landowner 7.9. Emerging technologies | Delta:1 OC:3 PC:3 RE:3 NERC:2 | Delta:1 OC:13 PC:13 RE:12 NERC:13 | OC: No comment PC: This Requirement acts as a control to support compliance with R1 and R2. R1 and R2 are the ultimate goal - no vegetation encroachment within the MVCD and no faults. This Requirement deals with how NERC expects the Transmission Owner to achieve compliance with R1 and R2. RE: Can be consolidated with Requirements. NERC: Q1: Examples given in 7.1-7.9 are only examples and perhaps should be removed or moved to the GTB or measure. | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:Yes NERC:No | OC:Yes PC:Yes RE:Yes NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:1 OC:3 PC:3 RE:3 NERC:2 | Delta:1 OC:13 PC:13 RE:12 NERC:13 | OC: No comment PC: This Requirement acts as a control to support compliance with R1 and R2. R1 and R2 are the ultimate goal - no vegetation encroachment within the MVCD and no faults. This Requirement deals with how NERC expects the Transmission Owner to achieve compliance with R1 and R2. RE: Can be consolidated with Requirements. NERC: Q1: Examples given in 7.1-7.9 are only examples and perhaps should be removed or moved to the GTB or measure. | 0 | This Requirement acts as a control to support compliance with R1 and R2. R1 and R2 are the ultimate goal - no vegetation encroachment within the MVCD and no faults. This Requirement deals with how NERC expects the Transmission Owner to achieve compliance with R1 and R2. | Can be consolidated with Requirements. | Q1: Examples given in 7.1-7.9 are only examples and perhaps should be removed or moved to the GTB or measure.
FAC-013-2 | R1. | R1. Each Planning Coordinator shall have a documented methodology it uses to perform an annual assessment of Transfer Capability in the Near-Term Transmission Planning Horizon (Transfer Capability methodology). The Transfer Capability methodology shall include, at a minimum, the following information: [See standard pdf for requirements of the Transfer Capability methodology] 1.1. Criteria for the selection of the transfers to be assessed. 1.2. A statement that the assessment shall respect known System Operating Limits (SOLs). 1.3. A statement that the assumptions and criteria used to perform the assessment are consistent with the Planning Coordinator’s planning practices. 1.4. A description of how each of the following assumptions and criteria used in performing the assessment are addressed: 1.4.1. Generation dispatch, including but not limited to long term planned outages, additions and retirements. 1.4.2. Transmission system topology, including but not limited to long term planned Transmission outages, additions, and retirements. 1.4.3. System demand. 1.4.4. Current approved and projected Transmission uses. 1.4.5. Parallel path (loop flow) adjustments. 1.4.6. Contingencies 1.4.7. Monitored Facilities. 1.5. A description of how simulations of transfers are performed through the adjustment of generation, Load or both. | Delta:1 OC:3 PC:3 RE:3 NERC:2 | Delta:2 OC:11 PC:13 RE:12 NERC:13 | OC: Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard. PC: No comment RE: Doesn't seem to be RBS, but I see the need for such methodology. NERC: C3: In reference to R1, 1.4.6 and 1.4.7 should neighboring systems be considered and coordinated. C3: Should be aware of possible simultaneous transfers. | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:Yes PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:No | OC:No PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | Delta:1 OC:3 PC:3 RE:3 NERC:2 | Delta:2 OC:11 PC:13 RE:12 NERC:13 | OC: Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard. PC: No comment RE: Doesn't seem to be RBS, but I see the need for such methodology. NERC: C3: In reference to R1, 1.4.6 and 1.4.7 should neighboring systems be considered and coordinated. C3: Should be aware of possible simultaneous transfers. | Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard. | 0 | Doesn't seem to be RBS, but I see the need for such methodology. | C3: In reference to R1, 1.4.6 and 1.4.7 should neighboring systems be considered and coordinated. C3: Should be aware of possible simultaneous transfers.
FAC-013-2 | R2. | R2. Each Planning Coordinator shall issue its Transfer Capability methodology, and any revisions to the Transfer Capability methodology, to the following entities subject to the following: [See standard pdf for requirements of issuing the Transfer Capability Methodology] 2.1. Distribute to the following prior to the effectiveness of such revisions: 2.1.1. Each Planning Coordinator adjacent to the Planning Coordinator’s Planning Coordinator area or overlapping the Planning Coordinator’s area. 2.1.2. Each Transmission Planner within the Planning Coordinator’s Planning Coordinator area. 2.2. Distribute to each functional entity that has a reliability-related need for the Transfer Capability methodology and submits a request for that methodology within 30 calendar days of receiving that written request. | Delta:1 OC:3 PC:3 RE:3 NERC:2 | Delta:2 OC:11 PC:13 RE:12 NERC:13 | OC: Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard. PC: No comment RE: Doesn't seem to be RBS, but I see the need for such methodology. NERC: C3: Should the Reliability Coordinator be included to receive the Transfer Capability methodology? | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:Yes PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:No | OC:No PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | Delta:1 OC:3 PC:3 RE:3 NERC:2 | Delta:2 OC:11 PC:13 RE:12 NERC:13 | OC: Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard. PC: No comment RE: Doesn't seem to be RBS, but I see the need for such methodology. NERC: C3: Should the Reliability Coordinator be included to receive the Transfer Capability methodology? | Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard. | 0 | Doesn't seem to be RBS, but I see the need for such methodology. | C3: Should the Reliability Coordinator be included to receive the Transfer Capability methodology?
FAC-013-2 | R3. | R3. (INACTIVE) If a recipient of the Transfer Capability methodology provides documented concerns with the methodology, the Planning Coordinator shall provide a documented response to that recipient within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Transfer Capability methodology and, if no change will be made to that Transfer Capability methodology, the reason why. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard. PC: No comment RE: Inactive. NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:Yes PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard. PC: No comment RE: Inactive. NERC: No comment | Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard. | 0 | Inactive. | 0
FAC-013-2 | R4. | R4. During each calendar year, each Planning Coordinator shall conduct simulations and document an assessment based on those simulations in accordance with its Transfer Capability methodology for at least one year in the Near-Term Transmission Planning Horizon. | Delta:1 OC:3 PC:3 RE:2 NERC:2 | Delta:2 OC:11 PC:13 RE:13 NERC:12 | OC: Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard. PC: No comment RE: The Near-Term Planning Horizon is five years. Why does only one year need to be assessed? Is that enough for reliability? NERC: C3: Requirement only mandates simulating and documenting at least one year of the Near-Term Transmission Planning Horizon when this horizon includes years 1 through 5. Q6: See above, only requires one of five years. | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:Yes PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:No | OC:No PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | Delta:1 OC:3 PC:3 RE:2 NERC:2 | Delta:2 OC:11 PC:13 RE:13 NERC:12 | OC: Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard. PC: No comment RE: The Near-Term Planning Horizon is five years. Why does only one year need to be assessed? Is that enough for reliability? NERC: C3: Requirement only mandates simulating and documenting at least one year of the Near-Term Transmission Planning Horizon when this horizon includes years 1 through 5. Q6: See above, only requires one of five years. | Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard. | 0 | The Near-Term Planning Horizon is five years. Why does only one year need to be assessed? Is that enough for reliability? | C3: Requirement only mandates simulating and documenting at least one year of the Near-Term Transmission Planning Horizon when this horizon includes years 1 through 5. Q6: See above, only requires one of five years.
FAC-013-2 | R5. | R5. Each Planning Coordinator shall make the documented Transfer Capability assessment results available within 45 calendar days of the completion of the assessment to the recipients of its Transfer Capability methodology pursuant to Requirement R2, Parts 2.1 and Part 2.2. However, if a functional entity that has a reliability related need for the results of the annual assessment of the Transfer Capabilities makes a written request for such an assessment after the completion of the assessment, the Planning Coordinator shall make the documented Transfer Capability assessment results available to that entity within 45 calendar days of receipt of the request | Delta:1 OC:3 PC:3 RE:3 NERC:2 | Delta:2 OC:11 PC:13 RE:12 NERC:13 | OC: Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard. PC: No comment RE: Reliability related need is undefined. Ambiguous term. NERC: C3: Should the Reliability Coordinator be included to receive the Transfer Capability results? | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:Yes PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:No | OC:No PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | Delta:1 OC:3 PC:3 RE:3 NERC:2 | Delta:2 OC:11 PC:13 RE:12 NERC:13 | OC: Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard. PC: No comment RE: Reliability related need is undefined. Ambiguous term. NERC: C3: Should the Reliability Coordinator be included to receive the Transfer Capability results? | Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard. | 0 | Reliability related need is undefined. Ambiguous term. | C3: Should the Reliability Coordinator be included to receive the Transfer Capability results?
FAC-013-2 | R6. | R6. If a recipient of a documented Transfer Capability assessment requests data to support the assessment results, the Planning Coordinator shall provide such data to that entity within 45 calendar days of receipt of the request. The provision of such data shall be subject to the legal and regulatory obligations of the Planning Coordinator’s area regarding the disclosure of confidential and/or sensitive information. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:2 OC:11 PC:13 RE:12 NERC:13 | OC: Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard. PC: No comment RE: Potential combining this requirement with R5. NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:Yes NERC:No | OC:Yes PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:Yes RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:2 OC:11 PC:13 RE:12 NERC:13 | OC: Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard. PC: No comment RE: Potential combining this requirement with R5. NERC: No comment | Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard. | 0 | Potential combining this requirement with R5. | 0
IRO-006-5 | R1. | R1. Each Reliability Coordinator and Balancing Authority that receives a request pursuant to an Interconnection-wide transmission loading relief procedure (such as Eastern Interconnection TLR, WECC Unscheduled Flow Mitigation, or congestion management procedures from the ERCOT Protocols) from any Reliability Coordinator, Balancing Authority, or Transmission Operator in another Interconnection to curtail an Interchange Transaction that crosses an Interconnection boundary shall comply with the request, unless it provides a reliability reason to the requestor why it cannot comply with the request. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:13 NERC:13 | OC: No comment PC: Q10: We believe that "in another interconnection" should be removed. The wording of the requirement could lead one to believe that the standard only applies to TLRs across interconnections. However, we believe this should apply to all TLRs regardless of interconnection boundaries. RE: No comment NERC: Note: The phrase "Interconnection-wide transmission loading relief procedure" is generic and could use more specific terminology. | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:13 NERC:13 | OC: No comment PC: Q10: We believe that "in another interconnection" should be removed. The wording of the requirement could lead one to believe that the standard only applies to TLRs across interconnections. However, we believe this should apply to all TLRs regardless of interconnection boundaries. RE: No comment NERC: Note: The phrase "Interconnection-wide transmission loading relief procedure" is generic and could use more specific terminology. | 0 | Q10: We believe that "in another interconnection" should be removed. The wording of the requirement could lead one to believe that the standard only applies to TLRs across interconnections. However, we believe this should apply to all TLRs regardless of interconnection boundaries. | 0 | Note: The phrase "Interconnection-wide transmission loading relief procedure" is generic and could use more specific terminology.
MOD-020-0 | R1. | R1. The Load-Serving Entity, Transmission Planner, and Resource Planner shall each make known its amount of interruptible demands and Direct Control Load Management (DCLM) to Transmission Operators, Balancing Authorities, and Reliability Coordinators on request within 30 calendar days. | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: No comment PC: The Load-Serving Entity function has been removed by NERC. Consequently, the LES be removed as an applicable function. From our perspective, this is more appropriate as a guideline. However, we recognize the need may be different in regions where TOPs, BAs, and RCs may have trouble getting this type of information from their TPs, LSEs, etc. RE: The LSE is included in the applicability section. "make known" is vague. NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: No comment PC: The Load-Serving Entity function has been removed by NERC. Consequently, the LES be removed as an applicable function. From our perspective, this is more appropriate as a guideline. However, we recognize the need may be different in regions where TOPs, BAs, and RCs may have trouble getting this type of information from their TPs, LSEs, etc. RE: The LSE is included in the applicability section. "make known" is vague. NERC: No comment | 0 | The Load-Serving Entity function has been removed by NERC. Consequently, the LES be removed as an applicable function. From our perspective, this is more appropriate as a guideline. However, we recognize the need may be different in regions where TOPs, BAs, and RCs may have trouble getting this type of information from their TPs, LSEs, etc. | The LSE is included in the applicability section. "make known" is vague. | 0
MOD-025-2 | R1. | R1. Each Generator Owner shall provide its Transmission Planner with verification of the Real Power capability of its applicable Facilities as follows: 1.1. Verify the Real Power capability of its generating units in accordance with Attachment 1. 1.2. Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:2 OC:13 PC:13 RE:12 NERC:11 | OC: No comment PC: No comment RE: The term "historical operational data" is undefined. We are concern that the entity might use out dated information. NERC: Q9: Battery storage systems are not identified. Q10: Attachment - the use of "normally expected to operate" (2.1.1 At the minimum Real Power output at which they are normally expected to operate collect maximum leading and lagging reactive values as soon as a limit is reached.) is not clear. The expected normal operation can refer to minimum operation dictated by the market or the system operator, or it can refer to minimum power that the generator can normally operate at without changing any alarms or protection (e.g. reverse power). | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:No | OC:Yes PC:Yes RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:2 OC:13 PC:13 RE:12 NERC:11 | OC: No comment PC: No comment RE: The term "historical operational data" is undefined. We are concern that the entity might use out dated information. NERC: Q9: Battery storage systems are not identified. Q10: Attachment - the use of "normally expected to operate" (2.1.1 At the minimum Real Power output at which they are normally expected to operate collect maximum leading and lagging reactive values as soon as a limit is reached.) is not clear. The expected normal operation can refer to minimum operation dictated by the market or the system operator, or it can refer to minimum power that the generator can normally operate at without changing any alarms or protection (e.g. reverse power). | 0 | 0 | The term "historical operational data" is undefined. We are concern that the entity might use out dated information. | Q9: Battery storage systems are not identified. Q10: Attachment - the use of "normally expected to operate" (2.1.1 At the minimum Real Power output at which they are normally expected to operate collect maximum leading and lagging reactive values as soon as a limit is reached.) is not clear. The expected normal operation can refer to minimum operation dictated by the market or the system operator, or it can refer to minimum power that the generator can normally operate at without changing any alarms or protection (e.g. reverse power).
MOD-025-2 | R2. | R2. Each Generator Owner shall provide its Transmission Planner with verification of the Reactive Power capability of its applicable Facilities as follows: 2.1. Verify, in accordance with Attachment 1, (i) the Reactive Power capability of its generating units and (ii) the Reactive Power capability of its synchronous condenser units. 2.2. Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: No comment PC: The requirement only requiring GOs to perform a reactive power capability test without considering system conditions which would likely limit the demonstration of FULL reactive power capability. RE: The term "historical operational data" is undefined. We are concern that the entity might use out dated information. NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: No comment PC: The requirement only requiring GOs to perform a reactive power capability test without considering system conditions which would likely limit the demonstration of FULL reactive power capability. RE: The term "historical operational data" is undefined. We are concern that the entity might use out dated information. NERC: No comment | 0 | The requirement only requiring GOs to perform a reactive power capability test without considering system conditions which would likely limit the demonstration of FULL reactive power capability. | The term "historical operational data" is undefined. We are concern that the entity might use out dated information. | 0
MOD-025-2 | R3. | R3. Each Transmission Owner shall provide its Transmission Planner with verification of the Reactive Power capability of its applicable Facilities as follows: 3.1. Verify, in accordance with Attachment 1, the Reactive Power capability of its synchronous condenser units. 3.2. Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: No comment PC: The requirement only requiring GOs to perform a reactive power capability test without considering system conditions which would likely limit the demonstration of FULL reactive power capability. RE: The term "historical operational data" is undefined. We are concern that the entity might use out dated information. NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: No comment PC: The requirement only requiring GOs to perform a reactive power capability test without considering system conditions which would likely limit the demonstration of FULL reactive power capability. RE: The term "historical operational data" is undefined. We are concern that the entity might use out dated information. NERC: No comment | 0 | The requirement only requiring GOs to perform a reactive power capability test without considering system conditions which would likely limit the demonstration of FULL reactive power capability. | The term "historical operational data" is undefined. We are concern that the entity might use out dated information. | 0
MOD-026-1 | R1. | R1. Each Transmission Planner shall provide the following requested information to the Generator Owner within 90 calendar days of receiving a written request: • Instructions on how to obtain the list of excitation control system or plant volt/var control function models that are acceptable to the Transmission Planner for use in dynamic simulation, • Instructions on how to obtain the dynamic excitation control system or plant volt/var control function model library block diagrams and/or data sheets for models that are acceptable to the Transmission Planner, or • Model data for any of the Generator Owner’s existing applicable unit specific excitation control system or plant volt/var control function contained in the Transmission Planner’s dynamic database from the current (in-use) models, including generator MVA base. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: No comment NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: No comment NERC: No comment | 0 | 0 | 0 | 0
MOD-026-1 | R2. | R2. Each Generator Owner shall provide for each applicable unit, a verified generator excitation control system or plant volt/var control function model, including documentation and data (as specified in Part 2.1) to its Transmission Planner in accordance with the periodicity specified in MOD-026 Attachment 1. 2.1. Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s), or both. Each verification shall include the following: 2.1.1. Documentation demonstrating the applicable unit’s model response matches the recorded response for a voltage excursion from either a staged test or a measured system disturbance, 2.1.2 Manufacturer, model number (if available), and type of the excitation control system including, but not limited to static, AC brushless, DC rotating, and/or the plant volt/var control function (if installed), 2.1.3. Model structure and data including, but not limited to reactance, time constants, saturation factors, total rotational inertia, or equivalent data for the generator, 2.1.4. Model structure and data for the excitation control system, including the closed loop voltage regulator if a closed loop voltage regulator is installed or the model structure and data for the plant volt/var control function system, 2.1.5. Compensation settings (such as droop, line drop, differential compensation), if used, and 2.1.6. Model structure and data for power system stabilizer, if so equipped. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:2 OC:13 PC:11 RE:13 NERC:12 | OC: No comment PC: We haved checked off NO for Columns G, I, and L. We believe that the MOD-026-1 and MOD-027-1 standards have a gap in that they have left out elements like SVCs and STATCOMs. These devices provide essentially reliability services. They are installed to increase transfer limits. The fact that they are omitted results in a gap and the belief that this is not technologically neutral. We have checked of NO for Column O because the standard only requires tests completed, and relies on the GO or TO to exercise their own judgement/determination on the degree of adequacy and completeness of these tests. For example the Generator, Exciter, PSS, and VC models must be confirmed "Documentation demonstrating the applicable unit’s model response matches the recorded response for a voltage excursion from either a staged test or a measured system disturbance" One cannot truly provide an accurate model without more than one test. That is to say, one can match the response to a voltage excursion with many parameters being incorrect. The wording in the standard only requires some voltage excursion. We support the guidance document from PPMVTF which provides more guidance on testing (to be finalized). We also find that the wording is 'loose' on the accuracy of the models, in that it does not provide sufficient specificity/criteria for judging accuracy. This may lead to circular arguments between the GO and TOP. For example, a GO who does not use the models may have a different view of what is accurate as compared to the planners using the models. Therefore they may submit a model and the TP may state it is not accurate enough, and the GO may argue that it is good (with a lot of back and forth and no resolution). RE: No comment NERC: Q3: May lead to omitting items like wind/inverter controls, only includes the plant level controller. | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:2 OC:13 PC:11 RE:13 NERC:12 | OC: No comment PC: We haved checked off NO for Columns G, I, and L. We believe that the MOD-026-1 and MOD-027-1 standards have a gap in that they have left out elements like SVCs and STATCOMs. These devices provide essentially reliability services. They are installed to increase transfer limits. The fact that they are omitted results in a gap and the belief that this is not technologically neutral. We have checked of NO for Column O because the standard only requires tests completed, and relies on the GO or TO to exercise their own judgement/determination on the degree of adequacy and completeness of these tests. For example the Generator, Exciter, PSS, and VC models must be confirmed "Documentation demonstrating the applicable unit’s model response matches the recorded response for a voltage excursion from either a staged test or a measured system disturbance" One cannot truly provide an accurate model without more than one test. That is to say, one can match the response to a voltage excursion with many parameters being incorrect. The wording in the standard only requires some voltage excursion. We support the guidance document from PPMVTF which provides more guidance on testing (to be finalized). We also find that the wording is 'loose' on the accuracy of the models, in that it does not provide sufficient specificity/criteria for judging accuracy. This may lead to circular arguments between the GO and TOP. For example, a GO who does not use the models may have a different view of what is accurate as compared to the planners using the models. Therefore they may submit a model and the TP may state it is not accurate enough, and the GO may argue that it is good (with a lot of back and forth and no resolution). RE: No comment NERC: Q3: May lead to omitting items like wind/inverter controls, only includes the plant level controller. | 0 | We haved checked off NO for Columns G, I, and L. We believe that the MOD-026-1 and MOD-027-1 standards have a gap in that they have left out elements like SVCs and STATCOMs. These devices provide essentially reliability services. They are installed to increase transfer limits. The fact that they are omitted results in a gap and the belief that this is not technologically neutral. We have checked of NO for Column O because the standard only requires tests completed, and relies on the GO or TO to exercise their own judgement/determination on the degree of adequacy and completeness of these tests. For example the Generator, Exciter, PSS, and VC models must be confirmed "Documentation demonstrating the applicable unit’s model response matches the recorded response for a voltage excursion from either a staged test or a measured system disturbance" One cannot truly provide an accurate model without more than one test. That is to say, one can match the response to a voltage excursion with many parameters being incorrect. The wording in the standard only requires some voltage excursion. We support the guidance document from PPMVTF which provides more guidance on testing (to be finalized). We also find that the wording is 'loose' on the accuracy of the models, in that it does not provide sufficient specificity/criteria for judging accuracy. This may lead to circular arguments between the GO and TOP. For example, a GO who does not use the models may have a different view of what is accurate as compared to the planners using the models. Therefore they may submit a model and the TP may state it is not accurate enough, and the GO may argue that it is good (with a lot of back and forth and no resolution). | 0 | Q3: May lead to omitting items like wind/inverter controls, only includes the plant level controller.
MOD-026-1 | R3. | R3. Each Generator Owner shall provide a written response to its Transmission Planner within 90 calendar days of receiving one of the following items for an applicable unit: • Written notification from its Transmission Planner (in accordance with Requirement R6) that the excitation control system or plant volt/var control function model is not usable, • Written comments from its Transmission Planner identifying technical concerns with the verification documentation related to the excitation control system or plant volt/var control function model, or • Written comments and supporting evidence from its Transmission Planner indicating that the simulated excitation control system or plant volt/var control function model response did not match the recorded response to a transmission system event. The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification (in accordance with Requirement R2). | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: No comment PC: See above. RE: In the written response to the Transmission Planner there is no schedule for submission of a new model to address the deficiency. There is a mention of a "plan" however this does not specifically include when the TP can expect the revised model. It is not clear in the requirement language however if you refer to Attachment 1 it provides the timeframe. NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: No comment PC: See above. RE: In the written response to the Transmission Planner there is no schedule for submission of a new model to address the deficiency. There is a mention of a "plan" however this does not specifically include when the TP can expect the revised model. It is not clear in the requirement language however if you refer to Attachment 1 it provides the timeframe. NERC: No comment | 0 | See above. | In the written response to the Transmission Planner there is no schedule for submission of a new model to address the deficiency. There is a mention of a "plan" however this does not specifically include when the TP can expect the revised model. It is not clear in the requirement language however if you refer to Attachment 1 it provides the timeframe. | 0
MOD-026-1 | R4. | R4. Each Generator Owner shall provide revised model data or plans to perform model verification (in accordance with Requirement R2) for an applicable unit to its Transmission Planner within 180 calendar days of making changes to the excitation control system or plant volt/var control function that alter the equipment response characteristic. | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:1 OC:13 PC:13 RE:12 NERC:13 | OC: No comment PC: No comment RE: Providing a model is not the same as providing a plan to perform model verification. Seems to be a gap of when the actual model will be provided when there are changes being made when model verification is required. What is the timeframe for the submission of the verified model? It is not clear in the requirement language however if you refer to Attachment 1 it provides the timeframe. NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:1 OC:13 PC:13 RE:12 NERC:13 | OC: No comment PC: No comment RE: Providing a model is not the same as providing a plan to perform model verification. Seems to be a gap of when the actual model will be provided when there are changes being made when model verification is required. What is the timeframe for the submission of the verified model? It is not clear in the requirement language however if you refer to Attachment 1 it provides the timeframe. NERC: No comment | 0 | 0 | Providing a model is not the same as providing a plan to perform model verification. Seems to be a gap of when the actual model will be provided when there are changes being made when model verification is required. What is the timeframe for the submission of the verified model? It is not clear in the requirement language however if you refer to Attachment 1 it provides the timeframe. | 0
MOD-026-1 | R5. | R5. Each Generator Owner shall provide a written response to its Transmission Planner, within 90 calendar days following receipt of a technically justified unit request from the Transmission Planner to perform a model review of a unit or plant that includes one of the following: • Details of plans to verify the model (in accordance with Requirement R2), or • Corrected model data including the source of revised model data such as discovery of manufacturer test values to replace generic model data or updating of data parameters based on an on-site review of the equipment. | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: No timeframe for when the verification and new model will be sent to the TP. It is not clear in the requirement language however if you refer to Attachment 1 it provides the timeframe. NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: No timeframe for when the verification and new model will be sent to the TP. It is not clear in the requirement language however if you refer to Attachment 1 it provides the timeframe. NERC: No comment | 0 | 0 | No timeframe for when the verification and new model will be sent to the TP. It is not clear in the requirement language however if you refer to Attachment 1 it provides the timeframe. | 0
MOD-026-1 | R6. | R6. Each Transmission Planner shall provide a written response to the Generator Owner within 90 calendar days of receiving the verified excitation control system or plant volt/var control function model information in accordance with Requirement R2 that the model is usable (meets the criteria specified in Parts 6.1 through 6.3) or is not usable. 6.1. The excitation control system or plant volt/var control function model initializes to compute modeling data without error, 6.2. A no-disturbance simulation results in negligible transients, and 6.3. For an otherwise stable simulation, a disturbance simulation results in the excitation control and plant volt/var control function model exhibiting positive damping. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: No comment NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: No comment NERC: No comment | 0 | 0 | 0 | 0
MOD-027-1 | R1. | R1. Each Transmission Planner shall provide the following requested information to the Generator Owner within 90 calendar days of receiving a written request: • Instructions on how to obtain the list of turbine/governor and load control or active power/frequency control system models that are acceptable to the Transmission Planner for use in dynamic simulation, • Instructions on how to obtain the dynamic turbine/governor and load control or active power/frequency control function model library block diagrams and/or data sheets for models that are acceptable to the Transmission Planner, or • Model data for any of the Generator Owner’s existing applicable unit specific turbine/governor and load control or active power/frequency control system contained in the Transmission Planner’s dynamic database from the current (in-use) models. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:13 NERC:13 | OC: No comment PC: No comment RE: No comment NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:13 NERC:13 | OC: No comment PC: No comment RE: No comment NERC: No comment | 0 | 0 | 0 | 0
MOD-027-1 | R2. | R2. Each Generator Owner shall provide, for each applicable unit, a verified turbine/governor and load control or active power/frequency control model, including documentation and data (as specified in Part 2.1) to its Transmission Planner in accordance with the periodicity specified in MOD-027 Attachment 1. 2.1. Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units rated less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s) or both. Each verification shall include the following: 2.1.1. Documentation comparing the applicable unit’s MW model response to the recorded MW response for either: • A frequency excursion from a system disturbance that meets MOD-027 Attachment 1 Note 1 with the applicable unit on-line, • A speed governor reference change with the applicable unit online, or • A partial load rejection test 2. 2.1.2. Type of governor and load control or active power control/frequency control3 equipment, 2.1.3. A description of the turbine (e.g. for hydro turbine - Kaplan, Francis, or Pelton; for steam turbine - boiler type, normal fuel type, and turbine type; for gas turbine - the type and manufacturer; for variable energy plant - type and manufacturer), 2.1.4. Model structure and data for turbine/governor and load control or active power/frequency control, and 2.1.5. Representation of the real power response effects of outer loop controls such as operator set point controls, and load control but excluding AGC control) that would override the governor response (including blocked or nonfunctioning governors or modes of operation that limit Frequency Response), if applicable. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:2 OC:13 PC:11 RE:13 NERC:12 | OC: No comment PC: See MOD-026 comments. RE: No comment NERC: Q3: May lead to omitting items like wind/inverter controls, only includes the plant level controller. | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:2 OC:13 PC:11 RE:13 NERC:12 | OC: No comment PC: See MOD-026 comments. RE: No comment NERC: Q3: May lead to omitting items like wind/inverter controls, only includes the plant level controller. | 0 | See MOD-026 comments. | 0 | Q3: May lead to omitting items like wind/inverter controls, only includes the plant level controller.
MOD-027-1 | R3. | R3. Each Generator Owner shall provide a written response to its Transmission Planner within 90 calendar days of receiving one of the following items for an applicable unit. • Written notification, from its Transmission Planner (in accordance with Requirement R5) that the turbine/governor and load control or active power/frequency control model is not “usable,” • Written comments from its Transmission Planner identifying technical concerns with the verification documentation related to the turbine/governor and load control or active power/frequency control model, or • Written comments and supporting evidence from its Transmission Planner indicating that the simulated turbine/governor and load control or active power/frequency control response did not approximate the recorded response for three or more transmission system events. The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification (in accordance with Requirement R2). The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification (in accordance with Requirement R2). | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:2 OC:13 PC:11 RE:13 NERC:13 | OC: No comment PC: We have checked off NO for Column O. Similarly with MOD-026-1, the wording is also 'loose' on the accuracy of the models, in that it does not provide sufficient specificity/criteria for judging accuracy. This may lead to circular arguments between the GO and TOP. For example, a GO who does not use the models may have a different view of what is accurate as compared to the planners using the models. Therefore they may submit a model and the TP may state it is not accurate enough, and the GO may argue that it is good (with a lot of back and forth and no resolution). Inaccurate/invalid models of governors have a negative effect on the entire interconnections' ability to study events. RE: In the written response to the Transmission Planner there is no schedule for submission of a new model to address the deficiency. There is a mention of a "plan" however this does not specifically include when the TP can expect the revised model. It is not clear in the requirement language however if you refer to Attachment 1 it provides the timeframe. NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:2 OC:13 PC:11 RE:13 NERC:13 | OC: No comment PC: We have checked off NO for Column O. Similarly with MOD-026-1, the wording is also 'loose' on the accuracy of the models, in that it does not provide sufficient specificity/criteria for judging accuracy. This may lead to circular arguments between the GO and TOP. For example, a GO who does not use the models may have a different view of what is accurate as compared to the planners using the models. Therefore they may submit a model and the TP may state it is not accurate enough, and the GO may argue that it is good (with a lot of back and forth and no resolution). Inaccurate/invalid models of governors have a negative effect on the entire interconnections' ability to study events. RE: In the written response to the Transmission Planner there is no schedule for submission of a new model to address the deficiency. There is a mention of a "plan" however this does not specifically include when the TP can expect the revised model. It is not clear in the requirement language however if you refer to Attachment 1 it provides the timeframe. NERC: No comment | 0 | We have checked off NO for Column O. Similarly with MOD-026-1, the wording is also 'loose' on the accuracy of the models, in that it does not provide sufficient specificity/criteria for judging accuracy. This may lead to circular arguments between the GO and TOP. For example, a GO who does not use the models may have a different view of what is accurate as compared to the planners using the models. Therefore they may submit a model and the TP may state it is not accurate enough, and the GO may argue that it is good (with a lot of back and forth and no resolution). Inaccurate/invalid models of governors have a negative effect on the entire interconnections' ability to study events. | In the written response to the Transmission Planner there is no schedule for submission of a new model to address the deficiency. There is a mention of a "plan" however this does not specifically include when the TP can expect the revised model. It is not clear in the requirement language however if you refer to Attachment 1 it provides the timeframe. | 0
MOD-027-1 | R4. | R4. Each Generator Owner shall provide revised model data or plans to perform model verification (in accordance with Requirement R2) for an applicable unit to its Transmission Planner within 180 calendar days of making changes to the turbine/governor and load control or active power/frequency control system that alter the equipment response characteristic. | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:1 OC:13 PC:12 RE:13 NERC:13 | OC: No comment PC: See above. RE: Providing a model is not the same as providing a plan to perform model verification. Seems to be a gap of when the actual model will be provided when there are changes being made when model verification is required. What is the timeframe for the submission of the verified model? It is not clear in the requirement language however if you refer to Attachment 1 it provides the timeframe. NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:1 OC:13 PC:12 RE:13 NERC:13 | OC: No comment PC: See above. RE: Providing a model is not the same as providing a plan to perform model verification. Seems to be a gap of when the actual model will be provided when there are changes being made when model verification is required. What is the timeframe for the submission of the verified model? It is not clear in the requirement language however if you refer to Attachment 1 it provides the timeframe. NERC: No comment | 0 | See above. | Providing a model is not the same as providing a plan to perform model verification. Seems to be a gap of when the actual model will be provided when there are changes being made when model verification is required. What is the timeframe for the submission of the verified model? It is not clear in the requirement language however if you refer to Attachment 1 it provides the timeframe. | 0
MOD-027-1 | R5. | R5. Each Transmission Planner shall provide a written response to the Generator Owner within 90 calendar days of receiving the turbine/governor and load control or active power/frequency control system verified model information in accordance with Requirement R2 that the model is usable (meets the criteria specified in Parts 5.1 through 5.3) or is not usable. 5.1. The turbine/governor and load control or active power/frequency control function model initializes to compute modeling data without error, 5.2 A no-disturbance simulation results in negligible transients, and 5.3. For an otherwise stable simulation, a disturbance simulation results in the turbine/governor and load control or active power/frequency control model exhibiting positive damping. | Delta:2 OC:3 PC:3 RE:1 NERC:2 | Delta:1 OC:13 PC:12 RE:13 NERC:13 | OC: No comment PC: See above. RE: No comment NERC: MOD-027 does not include a go and fix it requirement like MOD-026, as noted below: MOD-026, R5. Each Generator Owner shall provide a written response to its Transmission Planner, within 90 calendar days following receipt of a technically justified unit request from the Transmission Planner to perform a model review of a unit or plant that includes one of the following: (See full requirement in the above rows.) | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | Delta:2 OC:3 PC:3 RE:1 NERC:2 | Delta:1 OC:13 PC:12 RE:13 NERC:13 | OC: No comment PC: See above. RE: No comment NERC: MOD-027 does not include a go and fix it requirement like MOD-026, as noted below: MOD-026, R5. Each Generator Owner shall provide a written response to its Transmission Planner, within 90 calendar days following receipt of a technically justified unit request from the Transmission Planner to perform a model review of a unit or plant that includes one of the following: (See full requirement in the above rows.) | 0 | See above. | 0 | MOD-027 does not include a go and fix it requirement like MOD-026, as noted below: MOD-026, R5. Each Generator Owner shall provide a written response to its Transmission Planner, within 90 calendar days following receipt of a technically justified unit request from the Transmission Planner to perform a model review of a unit or plant that includes one of the following: (See full requirement in the above rows.)
MOD-028-2 | R1. | R1. Each Transmission Service Provider shall include in its Available Transfer Capability Implementation Document (ATCID), at a minimum, the following information relative to its methodology for determining Total Transfer Capability (TTC): R1.1. Information describing how the selected methodology has been implemented, in such detail that, given the same information used by the Transmission Operator, the results of the TTC calculations can be validated. R1.2. A description of the manner in which the Transmission Operator will account for Interchange Schedules in the calculation of TTC. R1.3. Any contractual obligations for allocation of TTC. R1.4. A description of the manner in which Contingencies are identified for use in the TTC process. R1.5. The following information on how source and sink for transmission service is accounted for in ATC calculations including: R1.5.1. Define if the source used for Available Transfer Capability (ATC) calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation R1.5.2. Define if the sink used for ATC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation R1.5.3. The source/sink or POR/POD identification and mapping to the model. R1.5.4. If the Transmission Service Provider’s ATC calculation process involves a grouping of generation, the ATCID must identify how these generators participate in the group. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. PC: We believe this standard would be better as a business practice than a standalone standard. RE: No comment NERC: Consider providing a reference that this document refers to calculating TTC for ATC Paths by the Transmission Operator in Requirements R2-R4. | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. PC: We believe this standard would be better as a business practice than a standalone standard. RE: No comment NERC: Consider providing a reference that this document refers to calculating TTC for ATC Paths by the Transmission Operator in Requirements R2-R4. | Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. | We believe this standard would be better as a business practice than a standalone standard. | 0 | Consider providing a reference that this document refers to calculating TTC for ATC Paths by the Transmission Operator in Requirements R2-R4.
MOD-028-2 | R10. | R10. When calculating firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall utilize the following algorithm: ATCF = TTC – ETCF – CBM – TRM + PostbacksF + counterflowsF Where: ATCF is the firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm Transmission commitments for the ATC Path during that period. CBM is the Capacity Benefit Margin for the ATC Path during that period. TRM is the Transmission Reliability Margin for the ATC Path during that period. PostbacksF¬ are changes to firm ATC due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsF are adjustments to firm ATC as determined by the Transmission Service Provider and specified in the ATCID. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. PC: We believe this standard would be better as a business practice than a standalone standard. RE: No comment NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. PC: We believe this standard would be better as a business practice than a standalone standard. RE: No comment NERC: No comment | Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. | We believe this standard would be better as a business practice than a standalone standard. | 0 | 0
MOD-028-2 | R11. | R11. When calculating non-firm ATC for a ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: ATCNF = TTC – ETCF - ETCNF – CBMS – TRMU + PostbacksNF + counterflowsNF Where: ATCNF is the non-firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm Transmission commitments for the ATC Path during that period. ETCNF is the sum of existing non-firm Transmission commitments for the ATC Path during that period. CBMS is the Capacity Benefit Margin for the ATC Path that has been scheduled without a separate reservation during that period. TRMU is the Transmission Reliability Margin for the ATC Path that has not been released for sale (unreleased) as non-firm capacity by the Transmission Service Provider during that period. PostbacksNF¬ are changes to non-firm ATC due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsNF are adjustments to non-firm ATC as determined by the Transmission Service Provider and specified in the ATCID. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. PC: We believe this standard would be better as a business practice than a standalone standard. RE: No comment NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. PC: We believe this standard would be better as a business practice than a standalone standard. RE: No comment NERC: No comment | Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. | We believe this standard would be better as a business practice than a standalone standard. | 0 | 0
MOD-028-2 | R2. | R2. When calculating TTC for ATC Paths, the Transmission Operator shall use a Transmission model that contains all of the following: R2.1. Modeling data and topology of its Reliability Coordinator’s area of responsibility. Equivalent representation of radial lines and facilities 161 kV or below is allowed. R2.2. Modeling data and topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination areas. R2.3. Facility Ratings specified by the Generator Owners and Transmission Owners. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. PC: We believe this standard would be better as a business practice than a standalone standard. RE: No comment NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. PC: We believe this standard would be better as a business practice than a standalone standard. RE: No comment NERC: No comment | Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. | We believe this standard would be better as a business practice than a standalone standard. | 0 | 0
MOD-028-2 | R3. | R3. When calculating TTCs for ATC Paths, the Transmission Operator shall include the following data for the Transmission Service Provider’s area. The Transmission Operator shall also include the following data associated with Facilities that are explicitly represented in the Transmission model, as provided by adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed: R3.1. For TTCs, use the following (as well as any other values and additional parameters as specified in the ATCID): R3.1.1. Expected generation and Transmission outages, additions, and retirements, included as specified in the ATCID. R3.1.2. A daily or hourly load forecast for TTCs used in current-day and next-day ATC calculations. R3.1.3. A daily load forecast for TTCs used in ATC calculations for days two through 31. R3.1.4. A monthly load forecast for TTCs used in ATC calculations for months two through 13 months TTCs. R3.1.5. Unit commitment and dispatch order, to include all designated network resources and other resources that are committed or have the legal obligation to run, (within or out of economic dispatch) as they are expected to run. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. PC: We believe this standard would be better as a business practice than a standalone standard. RE: No comment NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. PC: We believe this standard would be better as a business practice than a standalone standard. RE: No comment NERC: No comment | Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. | We believe this standard would be better as a business practice than a standalone standard. | 0 | 0
MOD-028-2 | R4. | R4. When calculating TTCs for ATC Paths, the Transmission Operator shall meet all of the following conditions: R4.1. Use all Contingencies meeting the criteria described in the ATCID. R4.2. Respect any contractual allocations of TTC. R4.3. Include, for each time period, the Firm Transmission Service expected to be scheduled as specified in the ATCID (filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers) for the Transmission Service Provider, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed modeling the source and sink as follows: - If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the source, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point shall as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can not be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is to be delivered as the sink. - If the sink, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is being delivered as the sink. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. PC: We believe this standard would be better as a business practice than a standalone standard. RE: No comment NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. PC: We believe this standard would be better as a business practice than a standalone standard. RE: No comment NERC: No comment | Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. | We believe this standard would be better as a business practice than a standalone standard. | 0 | 0
MOD-028-2 | R5. | R5. Each Transmission Operator shall establish TTC for each ATC Path as defined below: R5.1. At least once within the seven calendar days prior to the specified period for TTCs used in hourly and daily ATC calculations. R5.2. At least once per calendar month for TTCs used in monthly ATC calculations. R5.3. Within 24 hours of the unexpected outage of a 500 kV or higher transmission Facility or a transformer with a low-side voltage of 200 kV or higher for TTCs in effect during the anticipated duration of the outage, provided such outage is expected to last 24 hours or longer. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. PC: We believe this standard would be better as a business practice than a standalone standard. RE: No comment NERC: Should large generator units and/or plants be considered in how the loss of generation impacts TTC and ATC? | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. PC: We believe this standard would be better as a business practice than a standalone standard. RE: No comment NERC: Should large generator units and/or plants be considered in how the loss of generation impacts TTC and ATC? | Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. | We believe this standard would be better as a business practice than a standalone standard. | 0 | Should large generator units and/or plants be considered in how the loss of generation impacts TTC and ATC?
MOD-028-2 | R6. | R6. Each Transmission Operator shall establish TTC for each ATC Path using the following process: R6.1. Determine the incremental Transfer Capability for each ATC Path by increasing generation and/or decreasing load within the source Balancing Authority area and decreasing generation and/or increasing load within the sink Balancing Authority area until either: - A System Operating Limit is reached on the Transmission Service Provider’s system, or - A SOL is reached on any other adjacent system in the Transmission model that is not on the study path and the distribution factor is 5% or greater. R6.2. If the limit in step R6.1 can not be reached by adjusting any combination of load or generation, then set the incremental Transfer Capability by the results of the case where the maximum adjustments were applied. R6.3. Use (as the TTC) the lesser of: - The sum of the incremental Transfer Capability and the impacts of Firm Transmission Services, as specified in the Transmission Service Provider’s ATCID, that were included in the study model, or - The sum of Facility Ratings of all ties comprising the ATC Path. R6.4. For ATC Paths whose capacity uses jointly-owned or allocated Facilities, limit TTC for each Transmission Service Provider so the TTC does not exceed each Transmission Service Provider’s contractual rights. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. PC: We believe this standard would be better as a business practice than a standalone standard. RE: No comment NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. PC: We believe this standard would be better as a business practice than a standalone standard. RE: No comment NERC: No comment | Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. | We believe this standard would be better as a business practice than a standalone standard. | 0 | 0
MOD-028-2 | R7. | R7. The Transmission Operator shall provide the Transmission Service Provider of that ATC Path with the most current value for TTC for that ATC Path no more than: R7.1. One calendar day after its determination for TTCs used in hourly and daily ATC calculations. R7.2. Seven calendar days after its determination for TTCs used in monthly ATC calculations. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. PC: We believe this standard would be better as a business practice than a standalone standard. RE: No comment NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. PC: We believe this standard would be better as a business practice than a standalone standard. RE: No comment NERC: No comment | Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. | We believe this standard would be better as a business practice than a standalone standard. | 0 | 0
MOD-028-2 | R8. | R8. When calculating Existing Transmission Commitments (ETCs) for firm commitments (ETCF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: ETCF = NITSF + GFF + PTPF + RORF + OSF Where: NITSF is the firm capacity set aside for Network Integration Transmission Service (including the capacity used to serve bundled load within the Transmission Service Provider’s area with external sources) on ATC Paths that serve as interfaces with other Balancing Authorities. GFF is the firm capacity set aside for Grandfathered Firm Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or safe harbor tariff on ATC Paths that serve as interfaces with other Balancing Authorities. PTPF is the firm capacity reserved for confirmed Point-to-Point Transmission Service. RORF is the capacity reserved for roll-over rights for Firm Transmission Service contracts granting Transmission Customers the right of first refusal to take or continue to take Transmission Service when the Transmission Customer’s Transmission Service contract expires or is eligible for renewal. OSF is the firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using Firm Transmission Service, including any other firm adjustments to reflect impacts from other ATC Paths of the Transmission Service Provider as specified in the ATCID. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. PC: We believe this standard would be better as a business practice than a standalone standard. RE: No comment NERC: No comment | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. PC: We believe this standard would be better as a business practice than a standalone standard. RE: No comment NERC: No comment | Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. | We believe this standard would be better as a business practice than a standalone standard. | 0 | 0
MOD-028-2 | R9. | R9. When calculating ETC for non-firm commitments (ETCNF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: ETCNF = NITSNF + GFNF + PTPNF + OSNF Where: NITSNF is the non-firm capacity set aside for Network Integration Transmission Service (i.e., secondary service , including the capacity used to serve bundled load within the Transmission Service Provider’s area with external sources) reserved on ATC Paths that serve as interfaces with other Balancing Authorities. GFNF is the non-firm capacity reserved for Grandfathered Non-Firm Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or safe harbor tariff on ATC Paths that serve as interfaces with other Balancing Authorities. PTPNF is non-firm capacity reserved for confirmed Point-to-Point Transmission Service. OSNF is the non-firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using Non-Firm Transmission Service, including any other firm adjustments to reflect impacts from other ATC Paths of the Transmission Service Provider as specified in the ATCID. | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. PC: We believe this standard would be better as a business practice than a standalone standard. RE: No comment NERC: Is Financial Transmission Rights (FTR) captured in OSNF? | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:No PC:No RE:No NERC:No | OC:No PC:No RE:No NERC:No | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | OC:Yes PC:Yes RE:No NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:Yes RE:Yes NERC:Yes | OC:Yes PC:No RE:Yes NERC:Yes | Delta:0 OC:3 PC:3 RE:3 NERC:3 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. PC: We believe this standard would be better as a business practice than a standalone standard. RE: No comment NERC: Is Financial Transmission Rights (FTR) captured in OSNF? | Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard. | We believe this standard would be better as a business practice than a standalone standard. | 0 | Is Financial Transmission Rights (FTR) captured in OSNF?
Note on A1: Rose colored file indicates a "NO" answer from one of the four contributors.

## OC
[6 empty] | Content Questions from the Standards Independent Experts Report |  |  | Quality Questions from the Standards Independent Experts Report
[9 empty] | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | Q9 | Q10 | Q11 | Q12 | Q13
Standard Number | Requirement Number | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Supports a Reliability Objective (as defined by the Reliability Principles) | Meets the Paragraph 81 criteria? | Appropriate as a guide rather than a standard? | C1. Is the content of the requirement technically correct, including identifying who does what and when? | C2. Are the correct functional entities identified? | C3. Are the appropriate actions, for which there should be accountability, included or is there a gap? | Q1. Should the requirement stand alone as is (or should it be consolidated with other standards)? | Q2. Is it drafted as a results-based standard (RBS) requirement (performance, risk (prevention) or capability) and does it follow the RBS format (e.g., sub-requirement structure)? | Q3. Is it technologically neutral? | Q4. Are the expectations for each function clear? | Q5. Does the requirement align with the purpose? | Q6. Is it a higher solution than the lowest common denominator? | Q7. Is it measureable? | Q8. Does it have a technical basis in engineering and operations? | Q9. Is it complete and self-contained? | Q10. Is the language clear and does not contain ambiguous or outdated terms? | Q11. Can it be practically implemented? | Q12. Does it use consistent terminology? | Q13. Is the Standard cost effective in achieving the reliability purpose or objective of the Standard and mitigating the risk to the BES? | Content Score (0-3) | Quality Score (0-13) | Comment/Rationale
CIP-014-2 | R1. | R1. Each Transmission Owner shall perform an initial risk assessment and subsequent risk assessments of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria specified in Applicability Section 4.1.1. The initial and subsequent risk assessments shall consist of a transmission analysis or transmission analyses designed to identify the Transmission station(s) and Transmission substation(s) that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection. 1.1. Subsequent risk assessments shall be performed: • At least once every 30 calendar months for a Transmission Owner that hasidentified in its previous risk assessment (as verified according to Requirement R2) one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection; or • At least once every 60 calendar months for a Transmission Owner that has not identified in its previous risk assessment (as verified according to Requirement R2) any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. 1.2. The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
CIP-014-2 | R2. | R2. Each Transmission Owner shall have an unaffiliated third party verify the risk assessment performed under Requirement R1. The verification may occur concurrent with or after the risk assessment performed under Requirement R1. 2.1. Each Transmission Owner shall select an unaffiliated verifying entity that is either: • A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or • An entity that has transmission planning or analysis experience. 2.2. The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment. 2.3. If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station(s) or Transmission substation(s) from, its identification under Requirement R1, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation: • Modify its identification under Requirement R1 consistent with the recommendation; or • Document the technical basis for not modifying the identification in accordance with the recommendation. 2.4. Each Transmission Owner shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
CIP-014-2 | R3. | R3. For a primary control center(s) identified by the Transmission Owner according to Requirement R1, Part 1.2 that a) operationally controls an identified Transmission station or Transmission substation verified according to Requirement R2, and b) is not under the operational control of the Transmission Owner: the Transmission Owner shall, within seven calendar days following completion of Requirement R2, notify the Transmission Operator that has operational control of the primary control center of such identification and the date of completion of Requirement R2. 3.1. If a Transmission station or Transmission substation previously identified under Requirement R1 and verified according to Requirement R2 is removed from the identification during a subsequent risk assessment performed according to Requirement R1 or a verification according to Requirement R2, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
CIP-014-2 | R4. | R4. Each Transmission Owner that identified a Transmission station, Transmission substation, or a primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall conduct an evaluation of the potential threats and vulnerabilities of a physical attack to each of their respective Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2. The evaluation shall consider the following: 4.1. Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); 4.2. Prior history of attack on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events; and 4.3. Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
CIP-014-2 | R5. | R5. Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall develop and implement a documented physical security plan(s) that covers their respective Transmission station(s), Transmission substation(s), and primary control center(s). The physical security plan(s) shall be developed within 120 calendar days following the completion of Requirement R2 and executed according to the timeline specified in the physical security plan(s). The physical security plan(s) shall include the following attributes: 5.1. Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R4. 5.2. Law enforcement contact and coordination information. 5.3. A timeline for executing the physical security enhancements and modifications specified in the physical security plan. 5.4. Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). | Yes | No | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
CIP-014-2 | R6. | R6. Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall have an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5. The review may occur concurrently with or after completion of the evaluation performed under Requirement R4 and the security plan development under Requirement R5. 6.1. Each Transmission Owner and Transmission Operator shall select an unaffiliated third party reviewer from the following: • An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification. • An entity or organization approved by the ERO. • A governmental agency with physical security expertise. • An entity or organization with demonstrated law enforcement, government, or military physical security expertise. 6.2. The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. 6.3. If the unaffiliated third party reviewer recommends changes to the evaluation performed under Requirement R4 or security plan(s) developed under Requirement R5, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation: • Modify its evaluation or security plan(s) consistent with the recommendation; or • Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. 6.4. Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
COM-002-4 | R1. | R1. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall develop documented communications protocols for its operating personnel that issue and receive Operating Instructions. The protocols shall, at a minimum: 1.1. Require its operating personnel that issue and receive an oral or written Operating Instruction to use the English language, unless agreed to otherwise. An alternate language may be used for internal operations. 1.2. Require its operating personnel that issue an oral two-party, person-to-person Operating Instruction to take one of the following actions: • Confirm the receiver’s response if the repeated information is correct. • Reissue the Operating Instruction if the repeated information is incorrect or if requested by the receiver. • Take an alternative action if a response is not received or if the Operating Instruction was not understood by the receiver. 1.3. Require its operating personnel that receive an oral two-party, person-to-person Operating Instruction to take one of the following actions: • Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct. • Request that the issuer reissue the Operating Instruction. 1.4. Require its operating personnel that issue a written or oral single-party to multiple-party burst Operating Instruction to confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. 1.5. Specify the instances that require time identification when issuing an oral or written Operating Instruction and the format for that time identification. 1.6. Specify the nomenclature for Transmission interface Elements and Transmission interface Facilities when issuing an oral or written Operating Instruction. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
COM-002-4 | R2. | R2. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall conduct initial training for each of its operating personnel responsible for the Real-time operation of the interconnected Bulk Electric System on the documented communications protocols developed in Requirement R1 prior to that individual operator issuing an Operating Instruction. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | 3 | 11 | Move to PER-005 (training) or remove. All training requirements should be in one place and need to decide whether we need to list every subject that needs training.
COM-002-4 | R3. | R3. Each Distribution Provider and Generator Operator shall conduct initial training for each of its operating personnel who can receive an oral two-party, person-to-person Operating Instruction prior to that individual operator receiving an oral two-party, person-to-person Operating Instruction to either: • Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or • Request that the issuer reissue the Operating Instruction. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | 3 | 11 | Move to PER-005 (training) or remove. All training requirements should be in one place and need to decide whether we need to list every subject that needs training.
COM-002-4 | R4. | R4. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall at least once every twelve (12) calendar months: 4.1. Assess adherence to the documented communications protocols in Requirement R1 by its operating personnel that issue and receive Operating Instructions, provide feedback to those operating personnel and take corrective action, as deemed appropriate by the entity, to address deviations from the documented protocols. 4.2. Assess the effectiveness of its documented communications protocols in Requirement R1 for its operating personnel that issue and receive Operating Instructions and modify its documented communication protocols, as necessary. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | 3 | 11 | R4 should move to R1 and align with M1.
COM-002-4 | R5. | R5. Each Balancing Authority, Reliability Coordinator, and Transmission Operator that issues an oral two-party, person-to-person Operating Instruction during an Emergency, excluding written or oral single-party to multiple-party burst Operating Instructions, shall either: • Confirm the receiver’s response if the repeated information is correct (in accordance with Requirement R6). • Reissue the Operating Instruction if the repeated information is incorrect or if requested by the receiver, or • Take an alternative action if a response is not received or if the Operating Instruction was not understood by the receiver. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | 3 | 11 | Combine with R1 to simplify.
COM-002-4 | R6. | R6. Each Balancing Authority, Distribution Provider, Generator Operator, and Transmission Operator that receives an oral two-party, person-to-person Operating Instruction during an Emergency, excluding written or oral single-party to multiple-party burst Operating Instructions, shall either: • Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or • Request that the issuer reissue the Operating Instruction. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | 3 | 11 | Combine with R1 to simplify.
COM-002-4 | R7. | R7. Each Balancing Authority, Reliability Coordinator, and Transmission Operator that issues a written or oral single-party to multiple-party burst Operating Instruction during an Emergency shall confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | 3 | 11 | Combine with R1 to simplify.
FAC-003-4 | R1. | R1. Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the Minimum Vegetation Clearance Distance (MVCD) of its applicable line(s) which are either an element of an IROL, or an element of a Major WECC Transfer Path; operating within their Rating and all Rated Electrical Operating Conditions of the types shown below: 1.1. An encroachment into the MVCD as shown in FAC-003-Table 2, observed in Real-time, absent a Sustained Outage, 1.2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, 1.3. An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, 1.4. An encroachment due to vegetation growth into the MVCD that caused a vegetation-related Sustained Outage. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
FAC-003-4 | R2. | R2. Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are not either an element of an IROL, or an element of a Major WECC Transfer Path; operating within its Rating and all Rated Electrical Operating Conditions of the types shown below: 2.1. An encroachment into the MVCD, observed in Real-time, absent a Sustained Outage, 2.2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, 2.3. An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, 2.4. An encroachment due to vegetation growth into the line MVCD that caused a vegetation-related Sustained Outage. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
FAC-003-4 | R3. | R3. Each applicable Transmission Owner and applicable Generator Owner shall have documented maintenance strategies or procedures or processes or specifications it uses to prevent the encroachment of vegetation into the MVCD of its applicable lines that accounts for the following: 3.1. Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; 3.2. Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
FAC-003-4 | R4. | R4. Each applicable Transmission Owner and applicable Generator Owner, without any intentional time delay, shall notify the control center holding switching authority for the associated applicable line when the applicable Transmission Owner and applicable Generator Owner has confirmed the existence of a vegetation condition that is likely to cause a Fault at any moment. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
FAC-003-4 | R5. | R5. When an applicable Transmission Owner and an applicable Generator Owner are constrained from performing vegetation work on an applicable line operating within its Rating and all Rated Electrical Operating Conditions, and the constraint may lead to a vegetation encroachment into the MVCD prior to the implementation of the next annual work plan, then the applicable Transmission Owner or applicable Generator Owner shall take corrective action to ensure continued vegetation management to prevent encroachments. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
FAC-003-4 | R6. | R6. Each applicable Transmission Owner and applicable Generator Owner shall perform a Vegetation Inspection of 100% of its applicable transmission lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) at least once per calendar year and with no more than 18 calendar months between inspections on the same ROW. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
FAC-003-4 | R7. | R7. Each applicable Transmission Owner and applicable Generator Owner shall complete 100% of its annual vegetation work plan of applicable lines to ensure no vegetation encroachments occur within the MVCD. Modifications to the work plan in response to changing conditions or to findings from vegetation inspections may be made (provided they do not allow encroachment of vegetation into the MVCD) and must be documented. The percent completed calculation is based on the number of units actually completed divided by the number of units in the final amended plan (measured in units of choice - circuit, pole line, line miles or kilometers, etc.). Examples of reasons for modification to annual plan may include. 7.1. Change in expected growth rate/environmental factors 7.2. Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner 7.3. Rescheduling work between growing seasons 7.4. Crew or contractor availability/Mutual assistance agreements 7.5. Identified unanticipated high priority work 7.6. Weather conditions/Accessibility 7.7. Permitting delays 7.8. Land ownership changes/Change in land use by the landowner 7.9. Emerging technologies | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
FAC-013-2 | R1. | R1. Each Planning Coordinator shall have a documented methodology it uses to perform an annual assessment of Transfer Capability in the Near-Term Transmission Planning Horizon (Transfer Capability methodology). The Transfer Capability methodology shall include, at a minimum, the following information: [See standard pdf for requirements of the Transfer Capability methodology] 1.1. Criteria for the selection of the transfers to be assessed. 1.2. A statement that the assessment shall respect known System Operating Limits (SOLs). 1.3. A statement that the assumptions and criteria used to perform the assessment are consistent with the Planning Coordinator’s planning practices. 1.4. A description of how each of the following assumptions and criteria used in performing the assessment are addressed: 1.4.1. Generation dispatch, including but not limited to long term planned outages, additions and retirements. 1.4.2. Transmission system topology, including but not limited to long term planned Transmission outages, additions, and retirements. 1.4.3. System demand. 1.4.4. Current approved and projected Transmission uses. 1.4.5. Parallel path (loop flow) adjustments. 1.4.6. Contingencies 1.4.7. Monitored Facilities. 1.5. A description of how simulations of transfers are performed through the adjustment of generation, Load or both. | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | 3 | 11 | Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard.
FAC-013-2 | R2. | R2. Each Planning Coordinator shall issue its Transfer Capability methodology, and any revisions to the Transfer Capability methodology, to the following entities subject to the following: [See standard pdf for requirements of issuing the Transfer Capability Methodology] 2.1. Distribute to the following prior to the effectiveness of such revisions: 2.1.1. Each Planning Coordinator adjacent to the Planning Coordinator’s Planning Coordinator area or overlapping the Planning Coordinator’s area. 2.1.2. Each Transmission Planner within the Planning Coordinator’s Planning Coordinator area. 2.2. Distribute to each functional entity that has a reliability-related need for the Transfer Capability methodology and submits a request for that methodology within 30 calendar days of receiving that written request. | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | 3 | 11 | Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard.
FAC-013-2 | R3. | R3. (INACTIVE) If a recipient of the Transfer Capability methodology provides documented concerns with the methodology, the Planning Coordinator shall provide a documented response to that recipient within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Transfer Capability methodology and, if no change will be made to that Transfer Capability methodology, the reason why. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard.
FAC-013-2 | R4. | R4. During each calendar year, each Planning Coordinator shall conduct simulations and document an assessment based on those simulations in accordance with its Transfer Capability methodology for at least one year in the Near-Term Transmission Planning Horizon. | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | 3 | 11 | Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard.
FAC-013-2 | R5. | R5. Each Planning Coordinator shall make the documented Transfer Capability assessment results available within 45 calendar days of the completion of the assessment to the recipients of its Transfer Capability methodology pursuant to Requirement R2, Parts 2.1 and Part 2.2. However, if a functional entity that has a reliability related need for the results of the annual assessment of the Transfer Capabilities makes a written request for such an assessment after the completion of the assessment, the Planning Coordinator shall make the documented Transfer Capability assessment results available to that entity within 45 calendar days of receipt of the request | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | 3 | 11 | Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard.
FAC-013-2 | R6. | R6. If a recipient of a documented Transfer Capability assessment requests data to support the assessment results, the Planning Coordinator shall provide such data to that entity within 45 calendar days of receipt of the request. The provision of such data shall be subject to the legal and regulatory obligations of the Planning Coordinator’s area regarding the disclosure of confidential and/or sensitive information. | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | 3 | 11 | Redundant with TPL standard. TPL covers all aspects of reliability with the BES transmission system. Now with TPL in place, this standard could be retired or minimized to a guideline. Transfer Capability has no bearing in long-term planning. This standard should be retired now that TPL-001-4 is effective. Although the requirement aligns with the purpose, also believe that there is no purpose for performing incremental Transfers above firm base transfers in long-term planning horizon. Although this standard can be implemented, do not think it is practical in long-term planning horizon. This standard is not cost effective because we are spending valuable resources on work that is accomplished via TPL standard.
IRO-006-5 | R1. | R1. Each Reliability Coordinator and Balancing Authority that receives a request pursuant to an Interconnection-wide transmission loading relief procedure (such as Eastern Interconnection TLR, WECC Unscheduled Flow Mitigation, or congestion management procedures from the ERCOT Protocols) from any Reliability Coordinator, Balancing Authority, or Transmission Operator in another Interconnection to curtail an Interchange Transaction that crosses an Interconnection boundary shall comply with the request, unless it provides a reliability reason to the requestor why it cannot comply with the request. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-020-0 | R1. | R1. The Load-Serving Entity, Transmission Planner, and Resource Planner shall each make known its amount of interruptible demands and Direct Control Load Management (DCLM) to Transmission Operators, Balancing Authorities, and Reliability Coordinators on request within 30 calendar days. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-025-2 | R1. | R1. Each Generator Owner shall provide its Transmission Planner with verification of the Real Power capability of its applicable Facilities as follows: 1.1. Verify the Real Power capability of its generating units in accordance with Attachment 1. 1.2. Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-025-2 | R2. | R2. Each Generator Owner shall provide its Transmission Planner with verification of the Reactive Power capability of its applicable Facilities as follows: 2.1. Verify, in accordance with Attachment 1, (i) the Reactive Power capability of its generating units and (ii) the Reactive Power capability of its synchronous condenser units. 2.2. Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-025-2 | R3. | R3. Each Transmission Owner shall provide its Transmission Planner with verification of the Reactive Power capability of its applicable Facilities as follows: 3.1. Verify, in accordance with Attachment 1, the Reactive Power capability of its synchronous condenser units. 3.2. Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-026-1 | R1. | R1. Each Transmission Planner shall provide the following requested information to the Generator Owner within 90 calendar days of receiving a written request: • Instructions on how to obtain the list of excitation control system or plant volt/var control function models that are acceptable to the Transmission Planner for use in dynamic simulation, • Instructions on how to obtain the dynamic excitation control system or plant volt/var control function model library block diagrams and/or data sheets for models that are acceptable to the Transmission Planner, or • Model data for any of the Generator Owner’s existing applicable unit specific excitation control system or plant volt/var control function contained in the Transmission Planner’s dynamic database from the current (in-use) models, including generator MVA base. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-026-1 | R2. | R2. Each Generator Owner shall provide for each applicable unit, a verified generator excitation control system or plant volt/var control function model, including documentation and data (as specified in Part 2.1) to its Transmission Planner in accordance with the periodicity specified in MOD-026 Attachment 1. 2.1. Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s), or both. Each verification shall include the following: 2.1.1. Documentation demonstrating the applicable unit’s model response matches the recorded response for a voltage excursion from either a staged test or a measured system disturbance, 2.1.2 Manufacturer, model number (if available), and type of the excitation control system including, but not limited to static, AC brushless, DC rotating, and/or the plant volt/var control function (if installed), 2.1.3. Model structure and data including, but not limited to reactance, time constants, saturation factors, total rotational inertia, or equivalent data for the generator, 2.1.4. Model structure and data for the excitation control system, including the closed loop voltage regulator if a closed loop voltage regulator is installed or the model structure and data for the plant volt/var control function system, 2.1.5. Compensation settings (such as droop, line drop, differential compensation), if used, and 2.1.6. Model structure and data for power system stabilizer, if so equipped. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-026-1 | R3. | R3. Each Generator Owner shall provide a written response to its Transmission Planner within 90 calendar days of receiving one of the following items for an applicable unit: • Written notification from its Transmission Planner (in accordance with Requirement R6) that the excitation control system or plant volt/var control function model is not usable, • Written comments from its Transmission Planner identifying technical concerns with the verification documentation related to the excitation control system or plant volt/var control function model, or • Written comments and supporting evidence from its Transmission Planner indicating that the simulated excitation control system or plant volt/var control function model response did not match the recorded response to a transmission system event. The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification (in accordance with Requirement R2). | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-026-1 | R4. | R4. Each Generator Owner shall provide revised model data or plans to perform model verification (in accordance with Requirement R2) for an applicable unit to its Transmission Planner within 180 calendar days of making changes to the excitation control system or plant volt/var control function that alter the equipment response characteristic. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-026-1 | R5. | R5. Each Generator Owner shall provide a written response to its Transmission Planner, within 90 calendar days following receipt of a technically justified unit request from the Transmission Planner to perform a model review of a unit or plant that includes one of the following: • Details of plans to verify the model (in accordance with Requirement R2), or • Corrected model data including the source of revised model data such as discovery of manufacturer test values to replace generic model data or updating of data parameters based on an on-site review of the equipment. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-026-1 | R6. | R6. Each Transmission Planner shall provide a written response to the Generator Owner within 90 calendar days of receiving the verified excitation control system or plant volt/var control function model information in accordance with Requirement R2 that the model is usable (meets the criteria specified in Parts 6.1 through 6.3) or is not usable. 6.1. The excitation control system or plant volt/var control function model initializes to compute modeling data without error, 6.2. A no-disturbance simulation results in negligible transients, and 6.3. For an otherwise stable simulation, a disturbance simulation results in the excitation control and plant volt/var control function model exhibiting positive damping. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-027-1 | R1. | R1. Each Transmission Planner shall provide the following requested information to the Generator Owner within 90 calendar days of receiving a written request: • Instructions on how to obtain the list of turbine/governor and load control or active power/frequency control system models that are acceptable to the Transmission Planner for use in dynamic simulation, • Instructions on how to obtain the dynamic turbine/governor and load control or active power/frequency control function model library block diagrams and/or data sheets for models that are acceptable to the Transmission Planner, or • Model data for any of the Generator Owner’s existing applicable unit specific turbine/governor and load control or active power/frequency control system contained in the Transmission Planner’s dynamic database from the current (in-use) models. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-027-1 | R2. | R2. Each Generator Owner shall provide, for each applicable unit, a verified turbine/governor and load control or active power/frequency control model, including documentation and data (as specified in Part 2.1) to its Transmission Planner in accordance with the periodicity specified in MOD-027 Attachment 1. 2.1. Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units rated less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s) or both. Each verification shall include the following: 2.1.1. Documentation comparing the applicable unit’s MW model response to the recorded MW response for either: • A frequency excursion from a system disturbance that meets MOD-027 Attachment 1 Note 1 with the applicable unit on-line, • A speed governor reference change with the applicable unit online, or • A partial load rejection test 2. 2.1.2. Type of governor and load control or active power control/frequency control3 equipment, 2.1.3. A description of the turbine (e.g. for hydro turbine - Kaplan, Francis, or Pelton; for steam turbine - boiler type, normal fuel type, and turbine type; for gas turbine - the type and manufacturer; for variable energy plant - type and manufacturer), 2.1.4. Model structure and data for turbine/governor and load control or active power/frequency control, and 2.1.5. Representation of the real power response effects of outer loop controls such as operator set point controls, and load control but excluding AGC control) that would override the governor response (including blocked or nonfunctioning governors or modes of operation that limit Frequency Response), if applicable. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-027-1 | R3. | R3. Each Generator Owner shall provide a written response to its Transmission Planner within 90 calendar days of receiving one of the following items for an applicable unit. • Written notification, from its Transmission Planner (in accordance with Requirement R5) that the turbine/governor and load control or active power/frequency control model is not “usable,” • Written comments from its Transmission Planner identifying technical concerns with the verification documentation related to the turbine/governor and load control or active power/frequency control model, or • Written comments and supporting evidence from its Transmission Planner indicating that the simulated turbine/governor and load control or active power/frequency control response did not approximate the recorded response for three or more transmission system events. The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification (in accordance with Requirement R2). The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification (in accordance with Requirement R2). | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-027-1 | R4. | R4. Each Generator Owner shall provide revised model data or plans to perform model verification (in accordance with Requirement R2) for an applicable unit to its Transmission Planner within 180 calendar days of making changes to the turbine/governor and load control or active power/frequency control system that alter the equipment response characteristic. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-027-1 | R5. | R5. Each Transmission Planner shall provide a written response to the Generator Owner within 90 calendar days of receiving the turbine/governor and load control or active power/frequency control system verified model information in accordance with Requirement R2 that the model is usable (meets the criteria specified in Parts 5.1 through 5.3) or is not usable. 5.1. The turbine/governor and load control or active power/frequency control function model initializes to compute modeling data without error, 5.2 A no-disturbance simulation results in negligible transients, and 5.3. For an otherwise stable simulation, a disturbance simulation results in the turbine/governor and load control or active power/frequency control model exhibiting positive damping. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-028-2 | R1. | R1. Each Transmission Service Provider shall include in its Available Transfer Capability Implementation Document (ATCID), at a minimum, the following information relative to its methodology for determining Total Transfer Capability (TTC): R1.1. Information describing how the selected methodology has been implemented, in such detail that, given the same information used by the Transmission Operator, the results of the TTC calculations can be validated. R1.2. A description of the manner in which the Transmission Operator will account for Interchange Schedules in the calculation of TTC. R1.3. Any contractual obligations for allocation of TTC. R1.4. A description of the manner in which Contingencies are identified for use in the TTC process. R1.5. The following information on how source and sink for transmission service is accounted for in ATC calculations including: R1.5.1. Define if the source used for Available Transfer Capability (ATC) calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation R1.5.2. Define if the sink used for ATC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation R1.5.3. The source/sink or POR/POD identification and mapping to the model. R1.5.4. If the Transmission Service Provider’s ATC calculation process involves a grouping of generation, the ATCID must identify how these generators participate in the group. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard.
MOD-028-2 | R10. | R10. When calculating firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall utilize the following algorithm: ATCF = TTC – ETCF – CBM – TRM + PostbacksF + counterflowsF Where: ATCF is the firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm Transmission commitments for the ATC Path during that period. CBM is the Capacity Benefit Margin for the ATC Path during that period. TRM is the Transmission Reliability Margin for the ATC Path during that period. PostbacksF¬ are changes to firm ATC due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsF are adjustments to firm ATC as determined by the Transmission Service Provider and specified in the ATCID. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard.
MOD-028-2 | R11. | R11. When calculating non-firm ATC for a ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: ATCNF = TTC – ETCF - ETCNF – CBMS – TRMU + PostbacksNF + counterflowsNF Where: ATCNF is the non-firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm Transmission commitments for the ATC Path during that period. ETCNF is the sum of existing non-firm Transmission commitments for the ATC Path during that period. CBMS is the Capacity Benefit Margin for the ATC Path that has been scheduled without a separate reservation during that period. TRMU is the Transmission Reliability Margin for the ATC Path that has not been released for sale (unreleased) as non-firm capacity by the Transmission Service Provider during that period. PostbacksNF¬ are changes to non-firm ATC due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsNF are adjustments to non-firm ATC as determined by the Transmission Service Provider and specified in the ATCID. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard.
MOD-028-2 | R2. | R2. When calculating TTC for ATC Paths, the Transmission Operator shall use a Transmission model that contains all of the following: R2.1. Modeling data and topology of its Reliability Coordinator’s area of responsibility. Equivalent representation of radial lines and facilities 161 kV or below is allowed. R2.2. Modeling data and topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination areas. R2.3. Facility Ratings specified by the Generator Owners and Transmission Owners. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard.
MOD-028-2 | R3. | R3. When calculating TTCs for ATC Paths, the Transmission Operator shall include the following data for the Transmission Service Provider’s area. The Transmission Operator shall also include the following data associated with Facilities that are explicitly represented in the Transmission model, as provided by adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed: R3.1. For TTCs, use the following (as well as any other values and additional parameters as specified in the ATCID): R3.1.1. Expected generation and Transmission outages, additions, and retirements, included as specified in the ATCID. R3.1.2. A daily or hourly load forecast for TTCs used in current-day and next-day ATC calculations. R3.1.3. A daily load forecast for TTCs used in ATC calculations for days two through 31. R3.1.4. A monthly load forecast for TTCs used in ATC calculations for months two through 13 months TTCs. R3.1.5. Unit commitment and dispatch order, to include all designated network resources and other resources that are committed or have the legal obligation to run, (within or out of economic dispatch) as they are expected to run. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard.
MOD-028-2 | R4. | R4. When calculating TTCs for ATC Paths, the Transmission Operator shall meet all of the following conditions: R4.1. Use all Contingencies meeting the criteria described in the ATCID. R4.2. Respect any contractual allocations of TTC. R4.3. Include, for each time period, the Firm Transmission Service expected to be scheduled as specified in the ATCID (filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers) for the Transmission Service Provider, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed modeling the source and sink as follows: - If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the source, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point shall as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can not be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is to be delivered as the sink. - If the sink, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is being delivered as the sink. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard.
MOD-028-2 | R5. | R5. Each Transmission Operator shall establish TTC for each ATC Path as defined below: R5.1. At least once within the seven calendar days prior to the specified period for TTCs used in hourly and daily ATC calculations. R5.2. At least once per calendar month for TTCs used in monthly ATC calculations. R5.3. Within 24 hours of the unexpected outage of a 500 kV or higher transmission Facility or a transformer with a low-side voltage of 200 kV or higher for TTCs in effect during the anticipated duration of the outage, provided such outage is expected to last 24 hours or longer. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard.
MOD-028-2 | R6. | R6. Each Transmission Operator shall establish TTC for each ATC Path using the following process: R6.1. Determine the incremental Transfer Capability for each ATC Path by increasing generation and/or decreasing load within the source Balancing Authority area and decreasing generation and/or increasing load within the sink Balancing Authority area until either: - A System Operating Limit is reached on the Transmission Service Provider’s system, or - A SOL is reached on any other adjacent system in the Transmission model that is not on the study path and the distribution factor is 5% or greater. R6.2. If the limit in step R6.1 can not be reached by adjusting any combination of load or generation, then set the incremental Transfer Capability by the results of the case where the maximum adjustments were applied. R6.3. Use (as the TTC) the lesser of: - The sum of the incremental Transfer Capability and the impacts of Firm Transmission Services, as specified in the Transmission Service Provider’s ATCID, that were included in the study model, or - The sum of Facility Ratings of all ties comprising the ATC Path. R6.4. For ATC Paths whose capacity uses jointly-owned or allocated Facilities, limit TTC for each Transmission Service Provider so the TTC does not exceed each Transmission Service Provider’s contractual rights. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard.
MOD-028-2 | R7. | R7. The Transmission Operator shall provide the Transmission Service Provider of that ATC Path with the most current value for TTC for that ATC Path no more than: R7.1. One calendar day after its determination for TTCs used in hourly and daily ATC calculations. R7.2. Seven calendar days after its determination for TTCs used in monthly ATC calculations. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard.
MOD-028-2 | R8. | R8. When calculating Existing Transmission Commitments (ETCs) for firm commitments (ETCF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: ETCF = NITSF + GFF + PTPF + RORF + OSF Where: NITSF is the firm capacity set aside for Network Integration Transmission Service (including the capacity used to serve bundled load within the Transmission Service Provider’s area with external sources) on ATC Paths that serve as interfaces with other Balancing Authorities. GFF is the firm capacity set aside for Grandfathered Firm Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or safe harbor tariff on ATC Paths that serve as interfaces with other Balancing Authorities. PTPF is the firm capacity reserved for confirmed Point-to-Point Transmission Service. RORF is the capacity reserved for roll-over rights for Firm Transmission Service contracts granting Transmission Customers the right of first refusal to take or continue to take Transmission Service when the Transmission Customer’s Transmission Service contract expires or is eligible for renewal. OSF is the firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using Firm Transmission Service, including any other firm adjustments to reflect impacts from other ATC Paths of the Transmission Service Provider as specified in the ATCID. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard.
MOD-028-2 | R9. | R9. When calculating ETC for non-firm commitments (ETCNF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: ETCNF = NITSNF + GFNF + PTPNF + OSNF Where: NITSNF is the non-firm capacity set aside for Network Integration Transmission Service (i.e., secondary service , including the capacity used to serve bundled load within the Transmission Service Provider’s area with external sources) reserved on ATC Paths that serve as interfaces with other Balancing Authorities. GFNF is the non-firm capacity reserved for Grandfathered Non-Firm Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or safe harbor tariff on ATC Paths that serve as interfaces with other Balancing Authorities. PTPNF is non-firm capacity reserved for confirmed Point-to-Point Transmission Service. OSNF is the non-firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using Non-Firm Transmission Service, including any other firm adjustments to reflect impacts from other ATC Paths of the Transmission Service Provider as specified in the ATCID. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | Standard being replaced by MOD-001-2 which is currently awaiting FERC approval. Any effort on this standard should wait until the new standard is approved and review the new standard.

## PC
[6 empty] | Content Questions from the Standards Independent Experts Report |  |  | Quality Questions from the Standards Independent Experts Report
Standard Number | Requirement Number | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Supports a Reliability Objective (as defined by the Reliability Principles) | Meets the Paragraph 81 criteria? | Appropriate as a guide rather than a standard? | C1. Is the content of the requirement technically correct, including identifying who does what and when? | C2. Are the correct functional entities identified? | C3. Are the appropriate actions, for which there should be accountability, included or is there a gap? | Q1. Should the requirement stand alone as is (or should it be consolidated with other standards)? | Q2. Is it drafted as a results-based standard (RBS) requirement (performance, risk (prevention) or capability) and does it follow the RBS format (e.g., sub-requirement structure)? | Q3. Is it technologically neutral? | Q4. Are the expectations for each function clear? | Q5. Does the requirement align with the purpose? | Q6. Is it a higher solution than the lowest common denominator? | Q7. Is it measureable? | Q8. Does it have a technical basis in engineering and operations? | Q9. Is it complete and self-contained? | Q10. Is the language clear and does not contain ambiguous or outdated terms? | Q11. Can it be practically implemented? | Q12. Does it use consistent terminology? | Q13. Is the Standard cost effective in achieving the reliability purpose or objective of the Standard and mitigating the risk to the BES? | Content Score (0-3) | Quality Score (0-13) | Comment/Rationale
CIP-014-2 | R1. | R1. Each Transmission Owner shall perform an initial risk assessment and subsequent risk assessments of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria specified in Applicability Section 4.1.1. The initial and subsequent risk assessments shall consist of a transmission analysis or transmission analyses designed to identify the Transmission station(s) and Transmission substation(s) that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection. 1.1. Subsequent risk assessments shall be performed: • At least once every 30 calendar months for a Transmission Owner that hasidentified in its previous risk assessment (as verified according to Requirement R2) one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection; or • At least once every 60 calendar months for a Transmission Owner that has not identified in its previous risk assessment (as verified according to Requirement R2) any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. 1.2. The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
CIP-014-2 | R2. | R2. Each Transmission Owner shall have an unaffiliated third party verify the risk assessment performed under Requirement R1. The verification may occur concurrent with or after the risk assessment performed under Requirement R1. 2.1. Each Transmission Owner shall select an unaffiliated verifying entity that is either: • A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or • An entity that has transmission planning or analysis experience. 2.2. The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment. 2.3. If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station(s) or Transmission substation(s) from, its identification under Requirement R1, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation: • Modify its identification under Requirement R1 consistent with the recommendation; or • Document the technical basis for not modifying the identification in accordance with the recommendation. 2.4. Each Transmission Owner shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
CIP-014-2 | R3. | R3. For a primary control center(s) identified by the Transmission Owner according to Requirement R1, Part 1.2 that a) operationally controls an identified Transmission station or Transmission substation verified according to Requirement R2, and b) is not under the operational control of the Transmission Owner: the Transmission Owner shall, within seven calendar days following completion of Requirement R2, notify the Transmission Operator that has operational control of the primary control center of such identification and the date of completion of Requirement R2. 3.1. If a Transmission station or Transmission substation previously identified under Requirement R1 and verified according to Requirement R2 is removed from the identification during a subsequent risk assessment performed according to Requirement R1 or a verification according to Requirement R2, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
CIP-014-2 | R4. | R4. Each Transmission Owner that identified a Transmission station, Transmission substation, or a primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall conduct an evaluation of the potential threats and vulnerabilities of a physical attack to each of their respective Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2. The evaluation shall consider the following: 4.1. Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); 4.2. Prior history of attack on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events; and 4.3. Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
CIP-014-2 | R5. | R5. Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall develop and implement a documented physical security plan(s) that covers their respective Transmission station(s), Transmission substation(s), and primary control center(s). The physical security plan(s) shall be developed within 120 calendar days following the completion of Requirement R2 and executed according to the timeline specified in the physical security plan(s). The physical security plan(s) shall include the following attributes: 5.1. Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R4. 5.2. Law enforcement contact and coordination information. 5.3. A timeline for executing the physical security enhancements and modifications specified in the physical security plan. 5.4. Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
CIP-014-2 | R6. | R6. Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall have an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5. The review may occur concurrently with or after completion of the evaluation performed under Requirement R4 and the security plan development under Requirement R5. 6.1. Each Transmission Owner and Transmission Operator shall select an unaffiliated third party reviewer from the following: • An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification. • An entity or organization approved by the ERO. • A governmental agency with physical security expertise. • An entity or organization with demonstrated law enforcement, government, or military physical security expertise. 6.2. The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. 6.3. If the unaffiliated third party reviewer recommends changes to the evaluation performed under Requirement R4 or security plan(s) developed under Requirement R5, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation: • Modify its evaluation or security plan(s) consistent with the recommendation; or • Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. 6.4. Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
COM-002-4 | R1. | R1. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall develop documented communications protocols for its operating personnel that issue and receive Operating Instructions. The protocols shall, at a minimum: 1.1. Require its operating personnel that issue and receive an oral or written Operating Instruction to use the English language, unless agreed to otherwise. An alternate language may be used for internal operations. 1.2. Require its operating personnel that issue an oral two-party, person-to-person Operating Instruction to take one of the following actions: • Confirm the receiver’s response if the repeated information is correct. • Reissue the Operating Instruction if the repeated information is incorrect or if requested by the receiver. • Take an alternative action if a response is not received or if the Operating Instruction was not understood by the receiver. 1.3. Require its operating personnel that receive an oral two-party, person-to-person Operating Instruction to take one of the following actions: • Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct. • Request that the issuer reissue the Operating Instruction. 1.4. Require its operating personnel that issue a written or oral single-party to multiple-party burst Operating Instruction to confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. 1.5. Specify the instances that require time identification when issuing an oral or written Operating Instruction and the format for that time identification. 1.6. Specify the nomenclature for Transmission interface Elements and Transmission interface Facilities when issuing an oral or written Operating Instruction. | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 2 | 12 | C2: DP and GOP should be included and required to develop documented communication protocols for receiving Operating Instructions. Q6: Assuming Operating Instructions are the lowest common denominator, we believe that the term Directive should be reintroduced into the standard to distinguish between common every day Operating Instructions (ex: switching orders) and critical reliability related instructions (i.e. Directives).
COM-002-4 | R2. | R2. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall conduct initial training for each of its operating personnel responsible for the Real-time operation of the interconnected Bulk Electric System on the documented communications protocols developed in Requirement R1 prior to that individual operator issuing an Operating Instruction. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
COM-002-4 | R3. | R3. Each Distribution Provider and Generator Operator shall conduct initial training for each of its operating personnel who can receive an oral two-party, person-to-person Operating Instruction prior to that individual operator receiving an oral two-party, person-to-person Operating Instruction to either: • Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or • Request that the issuer reissue the Operating Instruction. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
COM-002-4 | R4. | R4. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall at least once every twelve (12) calendar months: 4.1. Assess adherence to the documented communications protocols in Requirement R1 by its operating personnel that issue and receive Operating Instructions, provide feedback to those operating personnel and take corrective action, as deemed appropriate by the entity, to address deviations from the documented protocols. 4.2. Assess the effectiveness of its documented communications protocols in Requirement R1 for its operating personnel that issue and receive Operating Instructions and modify its documented communication protocols, as necessary. | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 13 | We believe R1-R3 satisfy the purpose of this standard, while R4 should be a guide. C2: GOP should be included since they are the receiving party in three part communication.
COM-002-4 | R5. | R5. Each Balancing Authority, Reliability Coordinator, and Transmission Operator that issues an oral two-party, person-to-person Operating Instruction during an Emergency, excluding written or oral single-party to multiple-party burst Operating Instructions, shall either: • Confirm the receiver’s response if the repeated information is correct (in accordance with Requirement R6). • Reissue the Operating Instruction if the repeated information is incorrect or if requested by the receiver, or • Take an alternative action if a response is not received or if the Operating Instruction was not understood by the receiver. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
COM-002-4 | R6. | R6. Each Balancing Authority, Distribution Provider, Generator Operator, and Transmission Operator that receives an oral two-party, person-to-person Operating Instruction during an Emergency, excluding written or oral single-party to multiple-party burst Operating Instructions, shall either: • Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or • Request that the issuer reissue the Operating Instruction. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
COM-002-4 | R7. | R7. Each Balancing Authority, Reliability Coordinator, and Transmission Operator that issues a written or oral single-party to multiple-party burst Operating Instruction during an Emergency shall confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
FAC-003-4 | R1. | R1. Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the Minimum Vegetation Clearance Distance (MVCD) of its applicable line(s) which are either an element of an IROL, or an element of a Major WECC Transfer Path; operating within their Rating and all Rated Electrical Operating Conditions of the types shown below: 1.1. An encroachment into the MVCD as shown in FAC-003-Table 2, observed in Real-time, absent a Sustained Outage, 1.2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, 1.3. An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, 1.4. An encroachment due to vegetation growth into the MVCD that caused a vegetation-related Sustained Outage. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
FAC-003-4 | R2. | R2. Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are not either an element of an IROL, or an element of a Major WECC Transfer Path; operating within its Rating and all Rated Electrical Operating Conditions of the types shown below: 2.1. An encroachment into the MVCD, observed in Real-time, absent a Sustained Outage, 2.2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, 2.3. An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, 2.4. An encroachment due to vegetation growth into the line MVCD that caused a vegetation-related Sustained Outage. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 12 | Clear definition of Sustained Outage.
FAC-003-4 | R3. | R3. Each applicable Transmission Owner and applicable Generator Owner shall have documented maintenance strategies or procedures or processes or specifications it uses to prevent the encroachment of vegetation into the MVCD of its applicable lines that accounts for the following: 3.1. Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; 3.2. Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | This Requirement acts as a control to support compliance with R1 and R2. R1 and R2 are the ultimate goal - no vegetation encroachment within the MVCD and no faults. This Requirement deals with how NERC expects the Transmission Owner to achieve compliance with R1 and R2.
FAC-003-4 | R4. | R4. Each applicable Transmission Owner and applicable Generator Owner, without any intentional time delay, shall notify the control center holding switching authority for the associated applicable line when the applicable Transmission Owner and applicable Generator Owner has confirmed the existence of a vegetation condition that is likely to cause a Fault at any moment. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
FAC-003-4 | R5. | R5. When an applicable Transmission Owner and an applicable Generator Owner are constrained from performing vegetation work on an applicable line operating within its Rating and all Rated Electrical Operating Conditions, and the constraint may lead to a vegetation encroachment into the MVCD prior to the implementation of the next annual work plan, then the applicable Transmission Owner or applicable Generator Owner shall take corrective action to ensure continued vegetation management to prevent encroachments. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | This Requirement acts as a control to support compliance with R1 and R2. R1 and R2 are the ultimate goal - no vegetation encroachment within the MVCD and no faults. This Requirement deals with how NERC expects the Transmission Owner to achieve compliance with R1 and R2.
FAC-003-4 | R6. | R6. Each applicable Transmission Owner and applicable Generator Owner shall perform a Vegetation Inspection of 100% of its applicable transmission lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) at least once per calendar year and with no more than 18 calendar months between inspections on the same ROW. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | This Requirement acts as a control to support compliance with R1 and R2. R1 and R2 are the ultimate goal - no vegetation encroachment within the MVCD and no faults. This Requirement deals with how NERC expects the Transmission Owner to achieve compliance with R1 and R2.
FAC-003-4 | R7. | R7. Each applicable Transmission Owner and applicable Generator Owner shall complete 100% of its annual vegetation work plan of applicable lines to ensure no vegetation encroachments occur within the MVCD. Modifications to the work plan in response to changing conditions or to findings from vegetation inspections may be made (provided they do not allow encroachment of vegetation into the MVCD) and must be documented. The percent completed calculation is based on the number of units actually completed divided by the number of units in the final amended plan (measured in units of choice - circuit, pole line, line miles or kilometers, etc.). Examples of reasons for modification to annual plan may include. 7.1. Change in expected growth rate/environmental factors 7.2. Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner 7.3. Rescheduling work between growing seasons 7.4. Crew or contractor availability/Mutual assistance agreements 7.5. Identified unanticipated high priority work 7.6. Weather conditions/Accessibility 7.7. Permitting delays 7.8. Land ownership changes/Change in land use by the landowner 7.9. Emerging technologies | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | This Requirement acts as a control to support compliance with R1 and R2. R1 and R2 are the ultimate goal - no vegetation encroachment within the MVCD and no faults. This Requirement deals with how NERC expects the Transmission Owner to achieve compliance with R1 and R2.
FAC-013-2 | R1. | R1. Each Planning Coordinator shall have a documented methodology it uses to perform an annual assessment of Transfer Capability in the Near-Term Transmission Planning Horizon (Transfer Capability methodology). The Transfer Capability methodology shall include, at a minimum, the following information: [See standard pdf for requirements of the Transfer Capability methodology] 1.1. Criteria for the selection of the transfers to be assessed. 1.2. A statement that the assessment shall respect known System Operating Limits (SOLs). 1.3. A statement that the assumptions and criteria used to perform the assessment are consistent with the Planning Coordinator’s planning practices. 1.4. A description of how each of the following assumptions and criteria used in performing the assessment are addressed: 1.4.1. Generation dispatch, including but not limited to long term planned outages, additions and retirements. 1.4.2. Transmission system topology, including but not limited to long term planned Transmission outages, additions, and retirements. 1.4.3. System demand. 1.4.4. Current approved and projected Transmission uses. 1.4.5. Parallel path (loop flow) adjustments. 1.4.6. Contingencies 1.4.7. Monitored Facilities. 1.5. A description of how simulations of transfers are performed through the adjustment of generation, Load or both. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
FAC-013-2 | R2. | R2. Each Planning Coordinator shall issue its Transfer Capability methodology, and any revisions to the Transfer Capability methodology, to the following entities subject to the following: [See standard pdf for requirements of issuing the Transfer Capability Methodology] 2.1. Distribute to the following prior to the effectiveness of such revisions: 2.1.1. Each Planning Coordinator adjacent to the Planning Coordinator’s Planning Coordinator area or overlapping the Planning Coordinator’s area. 2.1.2. Each Transmission Planner within the Planning Coordinator’s Planning Coordinator area. 2.2. Distribute to each functional entity that has a reliability-related need for the Transfer Capability methodology and submits a request for that methodology within 30 calendar days of receiving that written request. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
FAC-013-2 | R3. | R3. (INACTIVE) If a recipient of the Transfer Capability methodology provides documented concerns with the methodology, the Planning Coordinator shall provide a documented response to that recipient within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Transfer Capability methodology and, if no change will be made to that Transfer Capability methodology, the reason why. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
FAC-013-2 | R4. | R4. During each calendar year, each Planning Coordinator shall conduct simulations and document an assessment based on those simulations in accordance with its Transfer Capability methodology for at least one year in the Near-Term Transmission Planning Horizon. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
FAC-013-2 | R5. | R5. Each Planning Coordinator shall make the documented Transfer Capability assessment results available within 45 calendar days of the completion of the assessment to the recipients of its Transfer Capability methodology pursuant to Requirement R2, Parts 2.1 and Part 2.2. However, if a functional entity that has a reliability related need for the results of the annual assessment of the Transfer Capabilities makes a written request for such an assessment after the completion of the assessment, the Planning Coordinator shall make the documented Transfer Capability assessment results available to that entity within 45 calendar days of receipt of the request | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
FAC-013-2 | R6. | R6. If a recipient of a documented Transfer Capability assessment requests data to support the assessment results, the Planning Coordinator shall provide such data to that entity within 45 calendar days of receipt of the request. The provision of such data shall be subject to the legal and regulatory obligations of the Planning Coordinator’s area regarding the disclosure of confidential and/or sensitive information. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
IRO-006-5 | R1. | R1. Each Reliability Coordinator and Balancing Authority that receives a request pursuant to an Interconnection-wide transmission loading relief procedure (such as Eastern Interconnection TLR, WECC Unscheduled Flow Mitigation, or congestion management procedures from the ERCOT Protocols) from any Reliability Coordinator, Balancing Authority, or Transmission Operator in another Interconnection to curtail an Interchange Transaction that crosses an Interconnection boundary shall comply with the request, unless it provides a reliability reason to the requestor why it cannot comply with the request. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 12 | Q10: We believe that "in another interconnection" should be removed. The wording of the requirement could lead one to believe that the standard only applies to TLRs across interconnections. However, we believe this should apply to all TLRs regardless of interconnection boundaries.
MOD-020-0 | R1. | R1. The Load-Serving Entity, Transmission Planner, and Resource Planner shall each make known its amount of interruptible demands and Direct Control Load Management (DCLM) to Transmission Operators, Balancing Authorities, and Reliability Coordinators on request within 30 calendar days. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | The Load-Serving Entity function has been removed by NERC. Consequently, the LES be removed as an applicable function. From our perspective, this is more appropriate as a guideline. However, we recognize the need may be different in regions where TOPs, BAs, and RCs may have trouble getting this type of information from their TPs, LSEs, etc.
MOD-025-2 | R1. | R1. Each Generator Owner shall provide its Transmission Planner with verification of the Real Power capability of its applicable Facilities as follows: 1.1. Verify the Real Power capability of its generating units in accordance with Attachment 1. 1.2. Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-025-2 | R2. | R2. Each Generator Owner shall provide its Transmission Planner with verification of the Reactive Power capability of its applicable Facilities as follows: 2.1. Verify, in accordance with Attachment 1, (i) the Reactive Power capability of its generating units and (ii) the Reactive Power capability of its synchronous condenser units. 2.2. Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | The requirement only requiring GOs to perform a reactive power capability test without considering system conditions which would likely limit the demonstration of FULL reactive power capability.
MOD-025-2 | R3. | R3. Each Transmission Owner shall provide its Transmission Planner with verification of the Reactive Power capability of its applicable Facilities as follows: 3.1. Verify, in accordance with Attachment 1, the Reactive Power capability of its synchronous condenser units. 3.2. Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | The requirement only requiring GOs to perform a reactive power capability test without considering system conditions which would likely limit the demonstration of FULL reactive power capability.
MOD-026-1 | R1. | R1. Each Transmission Planner shall provide the following requested information to the Generator Owner within 90 calendar days of receiving a written request: • Instructions on how to obtain the list of excitation control system or plant volt/var control function models that are acceptable to the Transmission Planner for use in dynamic simulation, • Instructions on how to obtain the dynamic excitation control system or plant volt/var control function model library block diagrams and/or data sheets for models that are acceptable to the Transmission Planner, or • Model data for any of the Generator Owner’s existing applicable unit specific excitation control system or plant volt/var control function contained in the Transmission Planner’s dynamic database from the current (in-use) models, including generator MVA base. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-026-1 | R2. | R2. Each Generator Owner shall provide for each applicable unit, a verified generator excitation control system or plant volt/var control function model, including documentation and data (as specified in Part 2.1) to its Transmission Planner in accordance with the periodicity specified in MOD-026 Attachment 1. 2.1. Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s), or both. Each verification shall include the following: 2.1.1. Documentation demonstrating the applicable unit’s model response matches the recorded response for a voltage excursion from either a staged test or a measured system disturbance, 2.1.2 Manufacturer, model number (if available), and type of the excitation control system including, but not limited to static, AC brushless, DC rotating, and/or the plant volt/var control function (if installed), 2.1.3. Model structure and data including, but not limited to reactance, time constants, saturation factors, total rotational inertia, or equivalent data for the generator, 2.1.4. Model structure and data for the excitation control system, including the closed loop voltage regulator if a closed loop voltage regulator is installed or the model structure and data for the plant volt/var control function system, 2.1.5. Compensation settings (such as droop, line drop, differential compensation), if used, and 2.1.6. Model structure and data for power system stabilizer, if so equipped. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | We haved checked off NO for Columns G, I, and L. We believe that the MOD-026-1 and MOD-027-1 standards have a gap in that they have left out elements like SVCs and STATCOMs. These devices provide essentially reliability services. They are installed to increase transfer limits. The fact that they are omitted results in a gap and the belief that this is not technologically neutral. We have checked of NO for Column O because the standard only requires tests completed, and relies on the GO or TO to exercise their own judgement/determination on the degree of adequacy and completeness of these tests. For example the Generator, Exciter, PSS, and VC models must be confirmed "Documentation demonstrating the applicable unit’s model response matches the recorded response for a voltage excursion from either a staged test or a measured system disturbance" One cannot truly provide an accurate model without more than one test. That is to say, one can match the response to a voltage excursion with many parameters being incorrect. The wording in the standard only requires some voltage excursion. We support the guidance document from PPMVTF which provides more guidance on testing (to be finalized). We also find that the wording is 'loose' on the accuracy of the models, in that it does not provide sufficient specificity/criteria for judging accuracy. This may lead to circular arguments between the GO and TOP. For example, a GO who does not use the models may have a different view of what is accurate as compared to the planners using the models. Therefore they may submit a model and the TP may state it is not accurate enough, and the GO may argue that it is good (with a lot of back and forth and no resolution).
MOD-026-1 | R3. | R3. Each Generator Owner shall provide a written response to its Transmission Planner within 90 calendar days of receiving one of the following items for an applicable unit: • Written notification from its Transmission Planner (in accordance with Requirement R6) that the excitation control system or plant volt/var control function model is not usable, • Written comments from its Transmission Planner identifying technical concerns with the verification documentation related to the excitation control system or plant volt/var control function model, or • Written comments and supporting evidence from its Transmission Planner indicating that the simulated excitation control system or plant volt/var control function model response did not match the recorded response to a transmission system event. The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification (in accordance with Requirement R2). | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | See above.
MOD-026-1 | R4. | R4. Each Generator Owner shall provide revised model data or plans to perform model verification (in accordance with Requirement R2) for an applicable unit to its Transmission Planner within 180 calendar days of making changes to the excitation control system or plant volt/var control function that alter the equipment response characteristic. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-026-1 | R5. | R5. Each Generator Owner shall provide a written response to its Transmission Planner, within 90 calendar days following receipt of a technically justified unit request from the Transmission Planner to perform a model review of a unit or plant that includes one of the following: • Details of plans to verify the model (in accordance with Requirement R2), or • Corrected model data including the source of revised model data such as discovery of manufacturer test values to replace generic model data or updating of data parameters based on an on-site review of the equipment. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-026-1 | R6. | R6. Each Transmission Planner shall provide a written response to the Generator Owner within 90 calendar days of receiving the verified excitation control system or plant volt/var control function model information in accordance with Requirement R2 that the model is usable (meets the criteria specified in Parts 6.1 through 6.3) or is not usable. 6.1. The excitation control system or plant volt/var control function model initializes to compute modeling data without error, 6.2. A no-disturbance simulation results in negligible transients, and 6.3. For an otherwise stable simulation, a disturbance simulation results in the excitation control and plant volt/var control function model exhibiting positive damping. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-027-1 | R1. | R1. Each Transmission Planner shall provide the following requested information to the Generator Owner within 90 calendar days of receiving a written request: • Instructions on how to obtain the list of turbine/governor and load control or active power/frequency control system models that are acceptable to the Transmission Planner for use in dynamic simulation, • Instructions on how to obtain the dynamic turbine/governor and load control or active power/frequency control function model library block diagrams and/or data sheets for models that are acceptable to the Transmission Planner, or • Model data for any of the Generator Owner’s existing applicable unit specific turbine/governor and load control or active power/frequency control system contained in the Transmission Planner’s dynamic database from the current (in-use) models. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
MOD-027-1 | R2. | R2. Each Generator Owner shall provide, for each applicable unit, a verified turbine/governor and load control or active power/frequency control model, including documentation and data (as specified in Part 2.1) to its Transmission Planner in accordance with the periodicity specified in MOD-027 Attachment 1. 2.1. Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units rated less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s) or both. Each verification shall include the following: 2.1.1. Documentation comparing the applicable unit’s MW model response to the recorded MW response for either: • A frequency excursion from a system disturbance that meets MOD-027 Attachment 1 Note 1 with the applicable unit on-line, • A speed governor reference change with the applicable unit online, or • A partial load rejection test 2. 2.1.2. Type of governor and load control or active power control/frequency control3 equipment, 2.1.3. A description of the turbine (e.g. for hydro turbine - Kaplan, Francis, or Pelton; for steam turbine - boiler type, normal fuel type, and turbine type; for gas turbine - the type and manufacturer; for variable energy plant - type and manufacturer), 2.1.4. Model structure and data for turbine/governor and load control or active power/frequency control, and 2.1.5. Representation of the real power response effects of outer loop controls such as operator set point controls, and load control but excluding AGC control) that would override the governor response (including blocked or nonfunctioning governors or modes of operation that limit Frequency Response), if applicable. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 11 | See MOD-026 comments.
MOD-027-1 | R3. | R3. Each Generator Owner shall provide a written response to its Transmission Planner within 90 calendar days of receiving one of the following items for an applicable unit. • Written notification, from its Transmission Planner (in accordance with Requirement R5) that the turbine/governor and load control or active power/frequency control model is not “usable,” • Written comments from its Transmission Planner identifying technical concerns with the verification documentation related to the turbine/governor and load control or active power/frequency control model, or • Written comments and supporting evidence from its Transmission Planner indicating that the simulated turbine/governor and load control or active power/frequency control response did not approximate the recorded response for three or more transmission system events. The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification (in accordance with Requirement R2). The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification (in accordance with Requirement R2). | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 11 | We have checked off NO for Column O. Similarly with MOD-026-1, the wording is also 'loose' on the accuracy of the models, in that it does not provide sufficient specificity/criteria for judging accuracy. This may lead to circular arguments between the GO and TOP. For example, a GO who does not use the models may have a different view of what is accurate as compared to the planners using the models. Therefore they may submit a model and the TP may state it is not accurate enough, and the GO may argue that it is good (with a lot of back and forth and no resolution). Inaccurate/invalid models of governors have a negative effect on the entire interconnections' ability to study events.
MOD-027-1 | R4. | R4. Each Generator Owner shall provide revised model data or plans to perform model verification (in accordance with Requirement R2) for an applicable unit to its Transmission Planner within 180 calendar days of making changes to the turbine/governor and load control or active power/frequency control system that alter the equipment response characteristic. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12 | See above.
MOD-027-1 | R5. | R5. Each Transmission Planner shall provide a written response to the Generator Owner within 90 calendar days of receiving the turbine/governor and load control or active power/frequency control system verified model information in accordance with Requirement R2 that the model is usable (meets the criteria specified in Parts 5.1 through 5.3) or is not usable. 5.1. The turbine/governor and load control or active power/frequency control function model initializes to compute modeling data without error, 5.2 A no-disturbance simulation results in negligible transients, and 5.3. For an otherwise stable simulation, a disturbance simulation results in the turbine/governor and load control or active power/frequency control model exhibiting positive damping. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12 | See above.
MOD-028-2 | R1. | R1. Each Transmission Service Provider shall include in its Available Transfer Capability Implementation Document (ATCID), at a minimum, the following information relative to its methodology for determining Total Transfer Capability (TTC): R1.1. Information describing how the selected methodology has been implemented, in such detail that, given the same information used by the Transmission Operator, the results of the TTC calculations can be validated. R1.2. A description of the manner in which the Transmission Operator will account for Interchange Schedules in the calculation of TTC. R1.3. Any contractual obligations for allocation of TTC. R1.4. A description of the manner in which Contingencies are identified for use in the TTC process. R1.5. The following information on how source and sink for transmission service is accounted for in ATC calculations including: R1.5.1. Define if the source used for Available Transfer Capability (ATC) calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation R1.5.2. Define if the sink used for ATC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation R1.5.3. The source/sink or POR/POD identification and mapping to the model. R1.5.4. If the Transmission Service Provider’s ATC calculation process involves a grouping of generation, the ATCID must identify how these generators participate in the group. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12 | We believe this standard would be better as a business practice than a standalone standard.
MOD-028-2 | R10. | R10. When calculating firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall utilize the following algorithm: ATCF = TTC – ETCF – CBM – TRM + PostbacksF + counterflowsF Where: ATCF is the firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm Transmission commitments for the ATC Path during that period. CBM is the Capacity Benefit Margin for the ATC Path during that period. TRM is the Transmission Reliability Margin for the ATC Path during that period. PostbacksF¬ are changes to firm ATC due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsF are adjustments to firm ATC as determined by the Transmission Service Provider and specified in the ATCID. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12 | We believe this standard would be better as a business practice than a standalone standard.
MOD-028-2 | R11. | R11. When calculating non-firm ATC for a ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: ATCNF = TTC – ETCF - ETCNF – CBMS – TRMU + PostbacksNF + counterflowsNF Where: ATCNF is the non-firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm Transmission commitments for the ATC Path during that period. ETCNF is the sum of existing non-firm Transmission commitments for the ATC Path during that period. CBMS is the Capacity Benefit Margin for the ATC Path that has been scheduled without a separate reservation during that period. TRMU is the Transmission Reliability Margin for the ATC Path that has not been released for sale (unreleased) as non-firm capacity by the Transmission Service Provider during that period. PostbacksNF¬ are changes to non-firm ATC due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsNF are adjustments to non-firm ATC as determined by the Transmission Service Provider and specified in the ATCID. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12 | We believe this standard would be better as a business practice than a standalone standard.
MOD-028-2 | R2. | R2. When calculating TTC for ATC Paths, the Transmission Operator shall use a Transmission model that contains all of the following: R2.1. Modeling data and topology of its Reliability Coordinator’s area of responsibility. Equivalent representation of radial lines and facilities 161 kV or below is allowed. R2.2. Modeling data and topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination areas. R2.3. Facility Ratings specified by the Generator Owners and Transmission Owners. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12 | We believe this standard would be better as a business practice than a standalone standard.
MOD-028-2 | R3. | R3. When calculating TTCs for ATC Paths, the Transmission Operator shall include the following data for the Transmission Service Provider’s area. The Transmission Operator shall also include the following data associated with Facilities that are explicitly represented in the Transmission model, as provided by adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed: R3.1. For TTCs, use the following (as well as any other values and additional parameters as specified in the ATCID): R3.1.1. Expected generation and Transmission outages, additions, and retirements, included as specified in the ATCID. R3.1.2. A daily or hourly load forecast for TTCs used in current-day and next-day ATC calculations. R3.1.3. A daily load forecast for TTCs used in ATC calculations for days two through 31. R3.1.4. A monthly load forecast for TTCs used in ATC calculations for months two through 13 months TTCs. R3.1.5. Unit commitment and dispatch order, to include all designated network resources and other resources that are committed or have the legal obligation to run, (within or out of economic dispatch) as they are expected to run. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12 | We believe this standard would be better as a business practice than a standalone standard.
MOD-028-2 | R4. | R4. When calculating TTCs for ATC Paths, the Transmission Operator shall meet all of the following conditions: R4.1. Use all Contingencies meeting the criteria described in the ATCID. R4.2. Respect any contractual allocations of TTC. R4.3. Include, for each time period, the Firm Transmission Service expected to be scheduled as specified in the ATCID (filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers) for the Transmission Service Provider, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed modeling the source and sink as follows: - If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the source, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point shall as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can not be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is to be delivered as the sink. - If the sink, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is being delivered as the sink. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12 | We believe this standard would be better as a business practice than a standalone standard.
MOD-028-2 | R5. | R5. Each Transmission Operator shall establish TTC for each ATC Path as defined below: R5.1. At least once within the seven calendar days prior to the specified period for TTCs used in hourly and daily ATC calculations. R5.2. At least once per calendar month for TTCs used in monthly ATC calculations. R5.3. Within 24 hours of the unexpected outage of a 500 kV or higher transmission Facility or a transformer with a low-side voltage of 200 kV or higher for TTCs in effect during the anticipated duration of the outage, provided such outage is expected to last 24 hours or longer. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12 | We believe this standard would be better as a business practice than a standalone standard.
MOD-028-2 | R6. | R6. Each Transmission Operator shall establish TTC for each ATC Path using the following process: R6.1. Determine the incremental Transfer Capability for each ATC Path by increasing generation and/or decreasing load within the source Balancing Authority area and decreasing generation and/or increasing load within the sink Balancing Authority area until either: - A System Operating Limit is reached on the Transmission Service Provider’s system, or - A SOL is reached on any other adjacent system in the Transmission model that is not on the study path and the distribution factor is 5% or greater. R6.2. If the limit in step R6.1 can not be reached by adjusting any combination of load or generation, then set the incremental Transfer Capability by the results of the case where the maximum adjustments were applied. R6.3. Use (as the TTC) the lesser of: - The sum of the incremental Transfer Capability and the impacts of Firm Transmission Services, as specified in the Transmission Service Provider’s ATCID, that were included in the study model, or - The sum of Facility Ratings of all ties comprising the ATC Path. R6.4. For ATC Paths whose capacity uses jointly-owned or allocated Facilities, limit TTC for each Transmission Service Provider so the TTC does not exceed each Transmission Service Provider’s contractual rights. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12 | We believe this standard would be better as a business practice than a standalone standard.
MOD-028-2 | R7. | R7. The Transmission Operator shall provide the Transmission Service Provider of that ATC Path with the most current value for TTC for that ATC Path no more than: R7.1. One calendar day after its determination for TTCs used in hourly and daily ATC calculations. R7.2. Seven calendar days after its determination for TTCs used in monthly ATC calculations. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12 | We believe this standard would be better as a business practice than a standalone standard.
MOD-028-2 | R8. | R8. When calculating Existing Transmission Commitments (ETCs) for firm commitments (ETCF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: ETCF = NITSF + GFF + PTPF + RORF + OSF Where: NITSF is the firm capacity set aside for Network Integration Transmission Service (including the capacity used to serve bundled load within the Transmission Service Provider’s area with external sources) on ATC Paths that serve as interfaces with other Balancing Authorities. GFF is the firm capacity set aside for Grandfathered Firm Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or safe harbor tariff on ATC Paths that serve as interfaces with other Balancing Authorities. PTPF is the firm capacity reserved for confirmed Point-to-Point Transmission Service. RORF is the capacity reserved for roll-over rights for Firm Transmission Service contracts granting Transmission Customers the right of first refusal to take or continue to take Transmission Service when the Transmission Customer’s Transmission Service contract expires or is eligible for renewal. OSF is the firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using Firm Transmission Service, including any other firm adjustments to reflect impacts from other ATC Paths of the Transmission Service Provider as specified in the ATCID. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12 | We believe this standard would be better as a business practice than a standalone standard.
MOD-028-2 | R9. | R9. When calculating ETC for non-firm commitments (ETCNF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: ETCNF = NITSNF + GFNF + PTPNF + OSNF Where: NITSNF is the non-firm capacity set aside for Network Integration Transmission Service (i.e., secondary service , including the capacity used to serve bundled load within the Transmission Service Provider’s area with external sources) reserved on ATC Paths that serve as interfaces with other Balancing Authorities. GFNF is the non-firm capacity reserved for Grandfathered Non-Firm Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or safe harbor tariff on ATC Paths that serve as interfaces with other Balancing Authorities. PTPNF is non-firm capacity reserved for confirmed Point-to-Point Transmission Service. OSNF is the non-firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using Non-Firm Transmission Service, including any other firm adjustments to reflect impacts from other ATC Paths of the Transmission Service Provider as specified in the ATCID. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12 | We believe this standard would be better as a business practice than a standalone standard.

## RE
[6 empty] | Content Questions from the Standards Independent Experts Report |  |  | Quality Questions from the Standards Independent Experts Report
Standard Number | Requirement Number | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Supports a Reliability Objective (as defined by the Reliability Principles) | Meets the Paragraph 81 criteria? | Appropriate as a guide rather than a standard? | C1. Is the content of the requirement technically correct, including identifying who does what and when? | C2. Are the correct functional entities identified? | C3. Are the appropriate actions, for which there should be accountability, included or is there a gap? | Q1. Should the requirement stand alone as is (or should it be consolidated with other standards)? | Q2. Is it drafted as a results-based standard (RBS) requirement (performance, risk (prevention) or capability) and does it follow the RBS format (e.g., sub-requirement structure)? | Q3. Is it technologically neutral? | Q4. Are the expectations for each function clear? | Q5. Does the requirement align with the purpose? | Q6. Is it a higher solution than the lowest common denominator? | Q7. Is it measureable? | Q8. Does it have a technical basis in engineering and operations? | Q9. Is it complete and self-contained? | Q10. Is the language clear and does not contain ambiguous or outdated terms? | Q11. Can it be practically implemented? | Q12. Does it use consistent terminology? | Q13. Is the Standard cost effective in achieving the reliability purpose or objective of the Standard and mitigating the risk to the BES? | Content Score (0-3) | Quality Score (0-13) | Comment/Rationale
CIP-014-2 | R1. | R1. Each Transmission Owner shall perform an initial risk assessment and subsequent risk assessments of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria specified in Applicability Section 4.1.1. The initial and subsequent risk assessments shall consist of a transmission analysis or transmission analyses designed to identify the Transmission station(s) and Transmission substation(s) that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection. 1.1. Subsequent risk assessments shall be performed: • At least once every 30 calendar months for a Transmission Owner that hasidentified in its previous risk assessment (as verified according to Requirement R2) one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection; or • At least once every 60 calendar months for a Transmission Owner that has not identified in its previous risk assessment (as verified according to Requirement R2) any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. 1.2. The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. | Yes | No | No | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 12 | This requirement needs additional clarity. Additional clarity necessary in regards to subsequent risk assessments under R1.1. (The concern is that if your initial risk assessment is satisfied you do not have to do another risk assessment until 5 years later, 5 years is a long time frame.) Does the TO have the expertise to do the assessment? If the TO is also TP then yes however if the TO is not a TP then they might need to hire a third party contractor to do the assessment. How long does the TO have to be compliant for a new facility. Unclear how co-owned facilities risk assessments should be done, the entire facility should be looked at regardless of ownership.
CIP-014-2 | R2. | R2. Each Transmission Owner shall have an unaffiliated third party verify the risk assessment performed under Requirement R1. The verification may occur concurrent with or after the risk assessment performed under Requirement R1. 2.1. Each Transmission Owner shall select an unaffiliated verifying entity that is either: • A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or • An entity that has transmission planning or analysis experience. 2.2. The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment. 2.3. If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station(s) or Transmission substation(s) from, its identification under Requirement R1, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation: • Modify its identification under Requirement R1 consistent with the recommendation; or • Document the technical basis for not modifying the identification in accordance with the recommendation. 2.4. Each Transmission Owner shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 13 | The concern is the requirement does not have any way to ensure the quality of the unaffiliated third party's review. The entity conducting the verification required by R2 should not be the same entity that conducted R1.
CIP-014-2 | R3. | R3. For a primary control center(s) identified by the Transmission Owner according to Requirement R1, Part 1.2 that a) operationally controls an identified Transmission station or Transmission substation verified according to Requirement R2, and b) is not under the operational control of the Transmission Owner: the Transmission Owner shall, within seven calendar days following completion of Requirement R2, notify the Transmission Operator that has operational control of the primary control center of such identification and the date of completion of Requirement R2. 3.1. If a Transmission station or Transmission substation previously identified under Requirement R1 and verified according to Requirement R2 is removed from the identification during a subsequent risk assessment performed according to Requirement R1 or a verification according to Requirement R2, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | This is strictly a notification requirement and could be combined with a different requirement. R1.2 is a candidate that potentially could be reviewed to include this requirement "prior" to the verification process. This would enable the entity owning or TOP controlling the primary control center to provide input to the decision made by the TO.
CIP-014-2 | R4. | R4. Each Transmission Owner that identified a Transmission station, Transmission substation, or a primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall conduct an evaluation of the potential threats and vulnerabilities of a physical attack to each of their respective Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2. The evaluation shall consider the following: 4.1. Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); 4.2. Prior history of attack on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events; and 4.3. Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 13 | It is possible that the threat evaluation could not be comprehensive enough if only 4.1 through 4.3 are considered. Additional resources could be provided in a guidance document.
CIP-014-2 | R5. | R5. Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall develop and implement a documented physical security plan(s) that covers their respective Transmission station(s), Transmission substation(s), and primary control center(s). The physical security plan(s) shall be developed within 120 calendar days following the completion of Requirement R2 and executed according to the timeline specified in the physical security plan(s). The physical security plan(s) shall include the following attributes: 5.1. Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R4. 5.2. Law enforcement contact and coordination information. 5.3. A timeline for executing the physical security enhancements and modifications specified in the physical security plan. 5.4. Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | 2 | 11 | The term resiliency is also undefined and concepts of what constitutes resilience is under discussion. There are also no specific industry standards on what would represent adequate deterrence or detection as well as response. No specified time frame in which to implement physical security plan(s). In a perfect world, the entity would implement as quickly as possible, but the language of the standard allows them to set their own timeline.
CIP-014-2 | R6. | R6. Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall have an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5. The review may occur concurrently with or after completion of the evaluation performed under Requirement R4 and the security plan development under Requirement R5. 6.1. Each Transmission Owner and Transmission Operator shall select an unaffiliated third party reviewer from the following: • An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification. • An entity or organization approved by the ERO. • A governmental agency with physical security expertise. • An entity or organization with demonstrated law enforcement, government, or military physical security expertise. 6.2. The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. 6.3. If the unaffiliated third party reviewer recommends changes to the evaluation performed under Requirement R4 or security plan(s) developed under Requirement R5, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation: • Modify its evaluation or security plan(s) consistent with the recommendation; or • Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. 6.4. Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 2 | 12 | The entity conducting the verification required by R6 should not be the same entity that conducted R4 and R5. The GTB did a good job in explaining everything but it is unclear in the requirement language.
COM-002-4 | R1. | R1. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall develop documented communications protocols for its operating personnel that issue and receive Operating Instructions. The protocols shall, at a minimum: 1.1. Require its operating personnel that issue and receive an oral or written Operating Instruction to use the English language, unless agreed to otherwise. An alternate language may be used for internal operations. 1.2. Require its operating personnel that issue an oral two-party, person-to-person Operating Instruction to take one of the following actions: • Confirm the receiver’s response if the repeated information is correct. • Reissue the Operating Instruction if the repeated information is incorrect or if requested by the receiver. • Take an alternative action if a response is not received or if the Operating Instruction was not understood by the receiver. 1.3. Require its operating personnel that receive an oral two-party, person-to-person Operating Instruction to take one of the following actions: • Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct. • Request that the issuer reissue the Operating Instruction. 1.4. Require its operating personnel that issue a written or oral single-party to multiple-party burst Operating Instruction to confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. 1.5. Specify the instances that require time identification when issuing an oral or written Operating Instruction and the format for that time identification. 1.6. Specify the nomenclature for Transmission interface Elements and Transmission interface Facilities when issuing an oral or written Operating Instruction. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
COM-002-4 | R2. | R2. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall conduct initial training for each of its operating personnel responsible for the Real-time operation of the interconnected Bulk Electric System on the documented communications protocols developed in Requirement R1 prior to that individual operator issuing an Operating Instruction. | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 13 | Personnel should be trained more than just initially. At a minimum, the operating personnel should be trained annually, or when an issue arises and when getting re-certified as a System Operator (or other appropriate licensing/certification).
COM-002-4 | R3. | R3. Each Distribution Provider and Generator Operator shall conduct initial training for each of its operating personnel who can receive an oral two-party, person-to-person Operating Instruction prior to that individual operator receiving an oral two-party, person-to-person Operating Instruction to either: • Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or • Request that the issuer reissue the Operating Instruction. | Yes | No | No | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 11 | UFLS-only DP should be added to the applicability of the requirement. If UFLS-only DP is not added to the applicability, that entity may not do the training required by COM-002-4 Requirement R3 or three-part communication as required by COM-002-4 Requirement R6. A UFLS-only DP may receive Operating Instructions to coordinate the re-energization of underfrequency relay equipped load. That would indicate the need for proper communications between the appropriate parties. Furthermore, during a Blackstart scenario the UFLS-only DP may be required to not re-energize load (through an Operating Instruction) to help coordinate the stabilization of the grid during restoration. Personnel should be trained more than just initially. At a minimum, the operating personnel should be trained annually, or when an issue arises and when getting re-certified as a System Operator (or other appropriate licensing/certification).
COM-002-4 | R4. | R4. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall at least once every twelve (12) calendar months: 4.1. Assess adherence to the documented communications protocols in Requirement R1 by its operating personnel that issue and receive Operating Instructions, provide feedback to those operating personnel and take corrective action, as deemed appropriate by the entity, to address deviations from the documented protocols. 4.2. Assess the effectiveness of its documented communications protocols in Requirement R1 for its operating personnel that issue and receive Operating Instructions and modify its documented communication protocols, as necessary. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | The concern is "deemed appropriate" language is vague.
COM-002-4 | R5. | R5. Each Balancing Authority, Reliability Coordinator, and Transmission Operator that issues an oral two-party, person-to-person Operating Instruction during an Emergency, excluding written or oral single-party to multiple-party burst Operating Instructions, shall either: • Confirm the receiver’s response if the repeated information is correct (in accordance with Requirement R6). • Reissue the Operating Instruction if the repeated information is incorrect or if requested by the receiver, or • Take an alternative action if a response is not received or if the Operating Instruction was not understood by the receiver. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
COM-002-4 | R6. | R6. Each Balancing Authority, Distribution Provider, Generator Operator, and Transmission Operator that receives an oral two-party, person-to-person Operating Instruction during an Emergency, excluding written or oral single-party to multiple-party burst Operating Instructions, shall either: • Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or • Request that the issuer reissue the Operating Instruction. | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 13 | UFLS-only DP should be added to the applicability of the requirement. If UFLS-only DP is not added to the applicability, that entity may not do the training required by COM-002-4 Requirement R3 or three-part communication as required by COM-002-4 Requirement R6. A UFLS-only DP may receive Operating Instructions to coordinate the re-energization of underfrequency relay equipped load. That would indicate the need for proper communications between the appropriate parties. Furthermore, during a Blackstart scenario the UFLS-only DP may be required to not re-energize load (through an Operating Instruction) to help coordinate the stabilization of the grid during restoration.
COM-002-4 | R7. | R7. Each Balancing Authority, Reliability Coordinator, and Transmission Operator that issues a written or oral single-party to multiple-party burst Operating Instruction during an Emergency shall confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
FAC-003-4 | R1. | R1. Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the Minimum Vegetation Clearance Distance (MVCD) of its applicable line(s) which are either an element of an IROL, or an element of a Major WECC Transfer Path; operating within their Rating and all Rated Electrical Operating Conditions of the types shown below: 1.1. An encroachment into the MVCD as shown in FAC-003-Table 2, observed in Real-time, absent a Sustained Outage, 1.2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, 1.3. An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, 1.4. An encroachment due to vegetation growth into the MVCD that caused a vegetation-related Sustained Outage. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | In the Applicability section there is reference to PCs identifying IROLs for lines less than 200 kV. This needs to be revisited. The FAC project team is moving forward with recommending retirement of FAC-010 because PC's don't develop IROLs. All references to PCs identifying IROLs will have to be revisited. Specifically in this standard and the CIP-002 standard.
FAC-003-4 | R2. | R2. Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are not either an element of an IROL, or an element of a Major WECC Transfer Path; operating within its Rating and all Rated Electrical Operating Conditions of the types shown below: 2.1. An encroachment into the MVCD, observed in Real-time, absent a Sustained Outage, 2.2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, 2.3. An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, 2.4. An encroachment due to vegetation growth into the line MVCD that caused a vegetation-related Sustained Outage. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | 3 | 12 | Requirement 2.1 is missing "as shown in FAC-003-Table 2". The language is not consistent however it is referenced in the VSLs.
FAC-003-4 | R3. | R3. Each applicable Transmission Owner and applicable Generator Owner shall have documented maintenance strategies or procedures or processes or specifications it uses to prevent the encroachment of vegetation into the MVCD of its applicable lines that accounts for the following: 3.1. Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; 3.2. Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | The reliability objective of the standard is not necessarily contingent to a specific method or strategy or even having one. The objective is to have no vegetation related outages and specificity of how that is achieved is a detail appropriate for a guideline.
FAC-003-4 | R4. | R4. Each applicable Transmission Owner and applicable Generator Owner, without any intentional time delay, shall notify the control center holding switching authority for the associated applicable line when the applicable Transmission Owner and applicable Generator Owner has confirmed the existence of a vegetation condition that is likely to cause a Fault at any moment. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | 3 | 10 | The phrase "without any intentional time delay" has questionable value in this context and from a compliance point is difficult to measure. Can be consolidated with R1.
FAC-003-4 | R5. | R5. When an applicable Transmission Owner and an applicable Generator Owner are constrained from performing vegetation work on an applicable line operating within its Rating and all Rated Electrical Operating Conditions, and the constraint may lead to a vegetation encroachment into the MVCD prior to the implementation of the next annual work plan, then the applicable Transmission Owner or applicable Generator Owner shall take corrective action to ensure continued vegetation management to prevent encroachments. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Can be consolidated with Requirements.
FAC-003-4 | R6. | R6. Each applicable Transmission Owner and applicable Generator Owner shall perform a Vegetation Inspection of 100% of its applicable transmission lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) at least once per calendar year and with no more than 18 calendar months between inspections on the same ROW. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | 3 | 11 | The applicability section refers to "applicable line", whereas the requirement uses the term "applicable transmission line". These terms should be the same if they are intending to refer to the same thing. Can be consolidated with other Requirements.
FAC-003-4 | R7. | R7. Each applicable Transmission Owner and applicable Generator Owner shall complete 100% of its annual vegetation work plan of applicable lines to ensure no vegetation encroachments occur within the MVCD. Modifications to the work plan in response to changing conditions or to findings from vegetation inspections may be made (provided they do not allow encroachment of vegetation into the MVCD) and must be documented. The percent completed calculation is based on the number of units actually completed divided by the number of units in the final amended plan (measured in units of choice - circuit, pole line, line miles or kilometers, etc.). Examples of reasons for modification to annual plan may include. 7.1. Change in expected growth rate/environmental factors 7.2. Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner 7.3. Rescheduling work between growing seasons 7.4. Crew or contractor availability/Mutual assistance agreements 7.5. Identified unanticipated high priority work 7.6. Weather conditions/Accessibility 7.7. Permitting delays 7.8. Land ownership changes/Change in land use by the landowner 7.9. Emerging technologies | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Can be consolidated with Requirements.
FAC-013-2 | R1. | R1. Each Planning Coordinator shall have a documented methodology it uses to perform an annual assessment of Transfer Capability in the Near-Term Transmission Planning Horizon (Transfer Capability methodology). The Transfer Capability methodology shall include, at a minimum, the following information: [See standard pdf for requirements of the Transfer Capability methodology] 1.1. Criteria for the selection of the transfers to be assessed. 1.2. A statement that the assessment shall respect known System Operating Limits (SOLs). 1.3. A statement that the assumptions and criteria used to perform the assessment are consistent with the Planning Coordinator’s planning practices. 1.4. A description of how each of the following assumptions and criteria used in performing the assessment are addressed: 1.4.1. Generation dispatch, including but not limited to long term planned outages, additions and retirements. 1.4.2. Transmission system topology, including but not limited to long term planned Transmission outages, additions, and retirements. 1.4.3. System demand. 1.4.4. Current approved and projected Transmission uses. 1.4.5. Parallel path (loop flow) adjustments. 1.4.6. Contingencies 1.4.7. Monitored Facilities. 1.5. A description of how simulations of transfers are performed through the adjustment of generation, Load or both. | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Doesn't seem to be RBS, but I see the need for such methodology.
FAC-013-2 | R2. | R2. Each Planning Coordinator shall issue its Transfer Capability methodology, and any revisions to the Transfer Capability methodology, to the following entities subject to the following: [See standard pdf for requirements of issuing the Transfer Capability Methodology] 2.1. Distribute to the following prior to the effectiveness of such revisions: 2.1.1. Each Planning Coordinator adjacent to the Planning Coordinator’s Planning Coordinator area or overlapping the Planning Coordinator’s area. 2.1.2. Each Transmission Planner within the Planning Coordinator’s Planning Coordinator area. 2.2. Distribute to each functional entity that has a reliability-related need for the Transfer Capability methodology and submits a request for that methodology within 30 calendar days of receiving that written request. | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Doesn't seem to be RBS, but I see the need for such methodology.
FAC-013-2 | R3. | R3. (INACTIVE) If a recipient of the Transfer Capability methodology provides documented concerns with the methodology, the Planning Coordinator shall provide a documented response to that recipient within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Transfer Capability methodology and, if no change will be made to that Transfer Capability methodology, the reason why. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | Inactive.
FAC-013-2 | R4. | R4. During each calendar year, each Planning Coordinator shall conduct simulations and document an assessment based on those simulations in accordance with its Transfer Capability methodology for at least one year in the Near-Term Transmission Planning Horizon. | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 13 | The Near-Term Planning Horizon is five years. Why does only one year need to be assessed? Is that enough for reliability?
FAC-013-2 | R5. | R5. Each Planning Coordinator shall make the documented Transfer Capability assessment results available within 45 calendar days of the completion of the assessment to the recipients of its Transfer Capability methodology pursuant to Requirement R2, Parts 2.1 and Part 2.2. However, if a functional entity that has a reliability related need for the results of the annual assessment of the Transfer Capabilities makes a written request for such an assessment after the completion of the assessment, the Planning Coordinator shall make the documented Transfer Capability assessment results available to that entity within 45 calendar days of receipt of the request | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 12 | Reliability related need is undefined. Ambiguous term.
FAC-013-2 | R6. | R6. If a recipient of a documented Transfer Capability assessment requests data to support the assessment results, the Planning Coordinator shall provide such data to that entity within 45 calendar days of receipt of the request. The provision of such data shall be subject to the legal and regulatory obligations of the Planning Coordinator’s area regarding the disclosure of confidential and/or sensitive information. | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Potential combining this requirement with R5.
IRO-006-5 | R1. | R1. Each Reliability Coordinator and Balancing Authority that receives a request pursuant to an Interconnection-wide transmission loading relief procedure (such as Eastern Interconnection TLR, WECC Unscheduled Flow Mitigation, or congestion management procedures from the ERCOT Protocols) from any Reliability Coordinator, Balancing Authority, or Transmission Operator in another Interconnection to curtail an Interchange Transaction that crosses an Interconnection boundary shall comply with the request, unless it provides a reliability reason to the requestor why it cannot comply with the request. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-020-0 | R1. | R1. The Load-Serving Entity, Transmission Planner, and Resource Planner shall each make known its amount of interruptible demands and Direct Control Load Management (DCLM) to Transmission Operators, Balancing Authorities, and Reliability Coordinators on request within 30 calendar days. | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 2 | 12 | The LSE is included in the applicability section. "make known" is vague.
MOD-025-2 | R1. | R1. Each Generator Owner shall provide its Transmission Planner with verification of the Real Power capability of its applicable Facilities as follows: 1.1. Verify the Real Power capability of its generating units in accordance with Attachment 1. 1.2. Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 12 | The term "historical operational data" is undefined. We are concern that the entity might use out dated information.
MOD-025-2 | R2. | R2. Each Generator Owner shall provide its Transmission Planner with verification of the Reactive Power capability of its applicable Facilities as follows: 2.1. Verify, in accordance with Attachment 1, (i) the Reactive Power capability of its generating units and (ii) the Reactive Power capability of its synchronous condenser units. 2.2. Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 12 | The term "historical operational data" is undefined. We are concern that the entity might use out dated information.
MOD-025-2 | R3. | R3. Each Transmission Owner shall provide its Transmission Planner with verification of the Reactive Power capability of its applicable Facilities as follows: 3.1. Verify, in accordance with Attachment 1, the Reactive Power capability of its synchronous condenser units. 3.2. Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 12 | The term "historical operational data" is undefined. We are concern that the entity might use out dated information.
MOD-026-1 | R1. | R1. Each Transmission Planner shall provide the following requested information to the Generator Owner within 90 calendar days of receiving a written request: • Instructions on how to obtain the list of excitation control system or plant volt/var control function models that are acceptable to the Transmission Planner for use in dynamic simulation, • Instructions on how to obtain the dynamic excitation control system or plant volt/var control function model library block diagrams and/or data sheets for models that are acceptable to the Transmission Planner, or • Model data for any of the Generator Owner’s existing applicable unit specific excitation control system or plant volt/var control function contained in the Transmission Planner’s dynamic database from the current (in-use) models, including generator MVA base. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-026-1 | R2. | R2. Each Generator Owner shall provide for each applicable unit, a verified generator excitation control system or plant volt/var control function model, including documentation and data (as specified in Part 2.1) to its Transmission Planner in accordance with the periodicity specified in MOD-026 Attachment 1. 2.1. Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s), or both. Each verification shall include the following: 2.1.1. Documentation demonstrating the applicable unit’s model response matches the recorded response for a voltage excursion from either a staged test or a measured system disturbance, 2.1.2 Manufacturer, model number (if available), and type of the excitation control system including, but not limited to static, AC brushless, DC rotating, and/or the plant volt/var control function (if installed), 2.1.3. Model structure and data including, but not limited to reactance, time constants, saturation factors, total rotational inertia, or equivalent data for the generator, 2.1.4. Model structure and data for the excitation control system, including the closed loop voltage regulator if a closed loop voltage regulator is installed or the model structure and data for the plant volt/var control function system, 2.1.5. Compensation settings (such as droop, line drop, differential compensation), if used, and 2.1.6. Model structure and data for power system stabilizer, if so equipped. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-026-1 | R3. | R3. Each Generator Owner shall provide a written response to its Transmission Planner within 90 calendar days of receiving one of the following items for an applicable unit: • Written notification from its Transmission Planner (in accordance with Requirement R6) that the excitation control system or plant volt/var control function model is not usable, • Written comments from its Transmission Planner identifying technical concerns with the verification documentation related to the excitation control system or plant volt/var control function model, or • Written comments and supporting evidence from its Transmission Planner indicating that the simulated excitation control system or plant volt/var control function model response did not match the recorded response to a transmission system event. The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification (in accordance with Requirement R2). | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 2 | 12 | In the written response to the Transmission Planner there is no schedule for submission of a new model to address the deficiency. There is a mention of a "plan" however this does not specifically include when the TP can expect the revised model. It is not clear in the requirement language however if you refer to Attachment 1 it provides the timeframe.
MOD-026-1 | R4. | R4. Each Generator Owner shall provide revised model data or plans to perform model verification (in accordance with Requirement R2) for an applicable unit to its Transmission Planner within 180 calendar days of making changes to the excitation control system or plant volt/var control function that alter the equipment response characteristic. | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 2 | 12 | Providing a model is not the same as providing a plan to perform model verification. Seems to be a gap of when the actual model will be provided when there are changes being made when model verification is required. What is the timeframe for the submission of the verified model? It is not clear in the requirement language however if you refer to Attachment 1 it provides the timeframe.
MOD-026-1 | R5. | R5. Each Generator Owner shall provide a written response to its Transmission Planner, within 90 calendar days following receipt of a technically justified unit request from the Transmission Planner to perform a model review of a unit or plant that includes one of the following: • Details of plans to verify the model (in accordance with Requirement R2), or • Corrected model data including the source of revised model data such as discovery of manufacturer test values to replace generic model data or updating of data parameters based on an on-site review of the equipment. | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 13 | No timeframe for when the verification and new model will be sent to the TP. It is not clear in the requirement language however if you refer to Attachment 1 it provides the timeframe.
MOD-026-1 | R6. | R6. Each Transmission Planner shall provide a written response to the Generator Owner within 90 calendar days of receiving the verified excitation control system or plant volt/var control function model information in accordance with Requirement R2 that the model is usable (meets the criteria specified in Parts 6.1 through 6.3) or is not usable. 6.1. The excitation control system or plant volt/var control function model initializes to compute modeling data without error, 6.2. A no-disturbance simulation results in negligible transients, and 6.3. For an otherwise stable simulation, a disturbance simulation results in the excitation control and plant volt/var control function model exhibiting positive damping. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-027-1 | R1. | R1. Each Transmission Planner shall provide the following requested information to the Generator Owner within 90 calendar days of receiving a written request: • Instructions on how to obtain the list of turbine/governor and load control or active power/frequency control system models that are acceptable to the Transmission Planner for use in dynamic simulation, • Instructions on how to obtain the dynamic turbine/governor and load control or active power/frequency control function model library block diagrams and/or data sheets for models that are acceptable to the Transmission Planner, or • Model data for any of the Generator Owner’s existing applicable unit specific turbine/governor and load control or active power/frequency control system contained in the Transmission Planner’s dynamic database from the current (in-use) models. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-027-1 | R2. | R2. Each Generator Owner shall provide, for each applicable unit, a verified turbine/governor and load control or active power/frequency control model, including documentation and data (as specified in Part 2.1) to its Transmission Planner in accordance with the periodicity specified in MOD-027 Attachment 1. 2.1. Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units rated less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s) or both. Each verification shall include the following: 2.1.1. Documentation comparing the applicable unit’s MW model response to the recorded MW response for either: • A frequency excursion from a system disturbance that meets MOD-027 Attachment 1 Note 1 with the applicable unit on-line, • A speed governor reference change with the applicable unit online, or • A partial load rejection test 2. 2.1.2. Type of governor and load control or active power control/frequency control3 equipment, 2.1.3. A description of the turbine (e.g. for hydro turbine - Kaplan, Francis, or Pelton; for steam turbine - boiler type, normal fuel type, and turbine type; for gas turbine - the type and manufacturer; for variable energy plant - type and manufacturer), 2.1.4. Model structure and data for turbine/governor and load control or active power/frequency control, and 2.1.5. Representation of the real power response effects of outer loop controls such as operator set point controls, and load control but excluding AGC control) that would override the governor response (including blocked or nonfunctioning governors or modes of operation that limit Frequency Response), if applicable. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-027-1 | R3. | R3. Each Generator Owner shall provide a written response to its Transmission Planner within 90 calendar days of receiving one of the following items for an applicable unit. • Written notification, from its Transmission Planner (in accordance with Requirement R5) that the turbine/governor and load control or active power/frequency control model is not “usable,” • Written comments from its Transmission Planner identifying technical concerns with the verification documentation related to the turbine/governor and load control or active power/frequency control model, or • Written comments and supporting evidence from its Transmission Planner indicating that the simulated turbine/governor and load control or active power/frequency control response did not approximate the recorded response for three or more transmission system events. The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification (in accordance with Requirement R2). The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification (in accordance with Requirement R2). | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 13 | In the written response to the Transmission Planner there is no schedule for submission of a new model to address the deficiency. There is a mention of a "plan" however this does not specifically include when the TP can expect the revised model. It is not clear in the requirement language however if you refer to Attachment 1 it provides the timeframe.
MOD-027-1 | R4. | R4. Each Generator Owner shall provide revised model data or plans to perform model verification (in accordance with Requirement R2) for an applicable unit to its Transmission Planner within 180 calendar days of making changes to the turbine/governor and load control or active power/frequency control system that alter the equipment response characteristic. | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 13 | Providing a model is not the same as providing a plan to perform model verification. Seems to be a gap of when the actual model will be provided when there are changes being made when model verification is required. What is the timeframe for the submission of the verified model? It is not clear in the requirement language however if you refer to Attachment 1 it provides the timeframe.
MOD-027-1 | R5. | R5. Each Transmission Planner shall provide a written response to the Generator Owner within 90 calendar days of receiving the turbine/governor and load control or active power/frequency control system verified model information in accordance with Requirement R2 that the model is usable (meets the criteria specified in Parts 5.1 through 5.3) or is not usable. 5.1. The turbine/governor and load control or active power/frequency control function model initializes to compute modeling data without error, 5.2 A no-disturbance simulation results in negligible transients, and 5.3. For an otherwise stable simulation, a disturbance simulation results in the turbine/governor and load control or active power/frequency control model exhibiting positive damping. | Yes | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 13
MOD-028-2 | R1. | R1. Each Transmission Service Provider shall include in its Available Transfer Capability Implementation Document (ATCID), at a minimum, the following information relative to its methodology for determining Total Transfer Capability (TTC): R1.1. Information describing how the selected methodology has been implemented, in such detail that, given the same information used by the Transmission Operator, the results of the TTC calculations can be validated. R1.2. A description of the manner in which the Transmission Operator will account for Interchange Schedules in the calculation of TTC. R1.3. Any contractual obligations for allocation of TTC. R1.4. A description of the manner in which Contingencies are identified for use in the TTC process. R1.5. The following information on how source and sink for transmission service is accounted for in ATC calculations including: R1.5.1. Define if the source used for Available Transfer Capability (ATC) calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation R1.5.2. Define if the sink used for ATC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation R1.5.3. The source/sink or POR/POD identification and mapping to the model. R1.5.4. If the Transmission Service Provider’s ATC calculation process involves a grouping of generation, the ATCID must identify how these generators participate in the group. | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
MOD-028-2 | R10. | R10. When calculating firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall utilize the following algorithm: ATCF = TTC – ETCF – CBM – TRM + PostbacksF + counterflowsF Where: ATCF is the firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm Transmission commitments for the ATC Path during that period. CBM is the Capacity Benefit Margin for the ATC Path during that period. TRM is the Transmission Reliability Margin for the ATC Path during that period. PostbacksF¬ are changes to firm ATC due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsF are adjustments to firm ATC as determined by the Transmission Service Provider and specified in the ATCID. | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
MOD-028-2 | R11. | R11. When calculating non-firm ATC for a ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: ATCNF = TTC – ETCF - ETCNF – CBMS – TRMU + PostbacksNF + counterflowsNF Where: ATCNF is the non-firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm Transmission commitments for the ATC Path during that period. ETCNF is the sum of existing non-firm Transmission commitments for the ATC Path during that period. CBMS is the Capacity Benefit Margin for the ATC Path that has been scheduled without a separate reservation during that period. TRMU is the Transmission Reliability Margin for the ATC Path that has not been released for sale (unreleased) as non-firm capacity by the Transmission Service Provider during that period. PostbacksNF¬ are changes to non-firm ATC due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsNF are adjustments to non-firm ATC as determined by the Transmission Service Provider and specified in the ATCID. | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
MOD-028-2 | R2. | R2. When calculating TTC for ATC Paths, the Transmission Operator shall use a Transmission model that contains all of the following: R2.1. Modeling data and topology of its Reliability Coordinator’s area of responsibility. Equivalent representation of radial lines and facilities 161 kV or below is allowed. R2.2. Modeling data and topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination areas. R2.3. Facility Ratings specified by the Generator Owners and Transmission Owners. | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
MOD-028-2 | R3. | R3. When calculating TTCs for ATC Paths, the Transmission Operator shall include the following data for the Transmission Service Provider’s area. The Transmission Operator shall also include the following data associated with Facilities that are explicitly represented in the Transmission model, as provided by adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed: R3.1. For TTCs, use the following (as well as any other values and additional parameters as specified in the ATCID): R3.1.1. Expected generation and Transmission outages, additions, and retirements, included as specified in the ATCID. R3.1.2. A daily or hourly load forecast for TTCs used in current-day and next-day ATC calculations. R3.1.3. A daily load forecast for TTCs used in ATC calculations for days two through 31. R3.1.4. A monthly load forecast for TTCs used in ATC calculations for months two through 13 months TTCs. R3.1.5. Unit commitment and dispatch order, to include all designated network resources and other resources that are committed or have the legal obligation to run, (within or out of economic dispatch) as they are expected to run. | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
MOD-028-2 | R4. | R4. When calculating TTCs for ATC Paths, the Transmission Operator shall meet all of the following conditions: R4.1. Use all Contingencies meeting the criteria described in the ATCID. R4.2. Respect any contractual allocations of TTC. R4.3. Include, for each time period, the Firm Transmission Service expected to be scheduled as specified in the ATCID (filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers) for the Transmission Service Provider, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed modeling the source and sink as follows: - If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the source, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point shall as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can not be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is to be delivered as the sink. - If the sink, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is being delivered as the sink. | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
MOD-028-2 | R5. | R5. Each Transmission Operator shall establish TTC for each ATC Path as defined below: R5.1. At least once within the seven calendar days prior to the specified period for TTCs used in hourly and daily ATC calculations. R5.2. At least once per calendar month for TTCs used in monthly ATC calculations. R5.3. Within 24 hours of the unexpected outage of a 500 kV or higher transmission Facility or a transformer with a low-side voltage of 200 kV or higher for TTCs in effect during the anticipated duration of the outage, provided such outage is expected to last 24 hours or longer. | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
MOD-028-2 | R6. | R6. Each Transmission Operator shall establish TTC for each ATC Path using the following process: R6.1. Determine the incremental Transfer Capability for each ATC Path by increasing generation and/or decreasing load within the source Balancing Authority area and decreasing generation and/or increasing load within the sink Balancing Authority area until either: - A System Operating Limit is reached on the Transmission Service Provider’s system, or - A SOL is reached on any other adjacent system in the Transmission model that is not on the study path and the distribution factor is 5% or greater. R6.2. If the limit in step R6.1 can not be reached by adjusting any combination of load or generation, then set the incremental Transfer Capability by the results of the case where the maximum adjustments were applied. R6.3. Use (as the TTC) the lesser of: - The sum of the incremental Transfer Capability and the impacts of Firm Transmission Services, as specified in the Transmission Service Provider’s ATCID, that were included in the study model, or - The sum of Facility Ratings of all ties comprising the ATC Path. R6.4. For ATC Paths whose capacity uses jointly-owned or allocated Facilities, limit TTC for each Transmission Service Provider so the TTC does not exceed each Transmission Service Provider’s contractual rights. | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
MOD-028-2 | R7. | R7. The Transmission Operator shall provide the Transmission Service Provider of that ATC Path with the most current value for TTC for that ATC Path no more than: R7.1. One calendar day after its determination for TTCs used in hourly and daily ATC calculations. R7.2. Seven calendar days after its determination for TTCs used in monthly ATC calculations. | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
MOD-028-2 | R8. | R8. When calculating Existing Transmission Commitments (ETCs) for firm commitments (ETCF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: ETCF = NITSF + GFF + PTPF + RORF + OSF Where: NITSF is the firm capacity set aside for Network Integration Transmission Service (including the capacity used to serve bundled load within the Transmission Service Provider’s area with external sources) on ATC Paths that serve as interfaces with other Balancing Authorities. GFF is the firm capacity set aside for Grandfathered Firm Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or safe harbor tariff on ATC Paths that serve as interfaces with other Balancing Authorities. PTPF is the firm capacity reserved for confirmed Point-to-Point Transmission Service. RORF is the capacity reserved for roll-over rights for Firm Transmission Service contracts granting Transmission Customers the right of first refusal to take or continue to take Transmission Service when the Transmission Customer’s Transmission Service contract expires or is eligible for renewal. OSF is the firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using Firm Transmission Service, including any other firm adjustments to reflect impacts from other ATC Paths of the Transmission Service Provider as specified in the ATCID. | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
MOD-028-2 | R9. | R9. When calculating ETC for non-firm commitments (ETCNF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: ETCNF = NITSNF + GFNF + PTPNF + OSNF Where: NITSNF is the non-firm capacity set aside for Network Integration Transmission Service (i.e., secondary service , including the capacity used to serve bundled load within the Transmission Service Provider’s area with external sources) reserved on ATC Paths that serve as interfaces with other Balancing Authorities. GFNF is the non-firm capacity reserved for Grandfathered Non-Firm Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or safe harbor tariff on ATC Paths that serve as interfaces with other Balancing Authorities. PTPNF is non-firm capacity reserved for confirmed Point-to-Point Transmission Service. OSNF is the non-firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using Non-Firm Transmission Service, including any other firm adjustments to reflect impacts from other ATC Paths of the Transmission Service Provider as specified in the ATCID. | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12

## NERC
[6 empty] | Content Questions from the Standards Independent Experts Report |  |  | Quality Questions from the Standards Independent Experts Report
Standard Number | Requirement Number | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Supports a Reliability Objective (as defined by the Reliability Principles) | Meets the Paragraph 81 criteria? | Appropriate as a guide rather than a standard? | C1. Is the content of the requirement technically correct, including identifying who does what and when? | C2. Are the correct functional entities identified? | C3. Are the appropriate actions, for which there should be accountability, included or is there a gap? | Q1. Should the requirement stand alone as is (or should it be consolidated with other standards)? | Q2. Is it drafted as a results-based standard (RBS) requirement (performance, risk (prevention) or capability) and does it follow the RBS format (e.g., sub-requirement structure)? | Q3. Is it technologically neutral? | Q4. Are the expectations for each function clear? | Q5. Does the requirement align with the purpose? | Q6. Is it a higher solution than the lowest common denominator? | Q7. Is it measureable? | Q8. Does it have a technical basis in engineering and operations? | Q9. Is it complete and self-contained? | Q10. Is the language clear and does not contain ambiguous or outdated terms? | Q11. Can it be practically implemented? | Q12. Does it use consistent terminology? | Q13. Is the Standard cost effective in achieving the reliability purpose or objective of the Standard and mitigating the risk to the BES? | Content Score (0-3) | Quality Score (0-13) | Comment/Rationale
CIP-014-2 | R1. | R1. Each Transmission Owner shall perform an initial risk assessment and subsequent risk assessments of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria specified in Applicability Section 4.1.1. The initial and subsequent risk assessments shall consist of a transmission analysis or transmission analyses designed to identify the Transmission station(s) and Transmission substation(s) that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection. 1.1. Subsequent risk assessments shall be performed: • At least once every 30 calendar months for a Transmission Owner that hasidentified in its previous risk assessment (as verified according to Requirement R2) one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection; or • At least once every 60 calendar months for a Transmission Owner that has not identified in its previous risk assessment (as verified according to Requirement R2) any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. 1.2. The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | 2 | 11 | 1st Question & Q8: The standard is open-ended and does not specify a specific assessment methodology. Two entities could have differing approaches for the same identified facilities and result in differing conclusions. C1. Not clear on adjacent stations/substations. What happens during topology changes? Q11. Lack of methodology does not make it practical/duplicate over time.
CIP-014-2 | R2. | R2. Each Transmission Owner shall have an unaffiliated third party verify the risk assessment performed under Requirement R1. The verification may occur concurrent with or after the risk assessment performed under Requirement R1. 2.1. Each Transmission Owner shall select an unaffiliated verifying entity that is either: • A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or • An entity that has transmission planning or analysis experience. 2.2. The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment. 2.3. If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station(s) or Transmission substation(s) from, its identification under Requirement R1, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation: • Modify its identification under Requirement R1 consistent with the recommendation; or • Document the technical basis for not modifying the identification in accordance with the recommendation. 2.4. Each Transmission Owner shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | C1. The lack of a defined methodology could prohibit the third-party from appropriately measuring the entity's risk assessment.
CIP-014-2 | R3. | R3. For a primary control center(s) identified by the Transmission Owner according to Requirement R1, Part 1.2 that a) operationally controls an identified Transmission station or Transmission substation verified according to Requirement R2, and b) is not under the operational control of the Transmission Owner: the Transmission Owner shall, within seven calendar days following completion of Requirement R2, notify the Transmission Operator that has operational control of the primary control center of such identification and the date of completion of Requirement R2. 3.1. If a Transmission station or Transmission substation previously identified under Requirement R1 and verified according to Requirement R2 is removed from the identification during a subsequent risk assessment performed according to Requirement R1 or a verification according to Requirement R2, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Q1 & Q6: There could be opportunities to prevent potential duplication and overlap with other standards (e.g., CIP-006).
CIP-014-2 | R4. | R4. Each Transmission Owner that identified a Transmission station, Transmission substation, or a primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall conduct an evaluation of the potential threats and vulnerabilities of a physical attack to each of their respective Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2. The evaluation shall consider the following: 4.1. Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); 4.2. Prior history of attack on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events; and 4.3. Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
CIP-014-2 | R5. | R5. Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall develop and implement a documented physical security plan(s) that covers their respective Transmission station(s), Transmission substation(s), and primary control center(s). The physical security plan(s) shall be developed within 120 calendar days following the completion of Requirement R2 and executed according to the timeline specified in the physical security plan(s). The physical security plan(s) shall include the following attributes: 5.1. Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R4. 5.2. Law enforcement contact and coordination information. 5.3. A timeline for executing the physical security enhancements and modifications specified in the physical security plan. 5.4. Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
CIP-014-2 | R6. | R6. Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall have an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5. The review may occur concurrently with or after completion of the evaluation performed under Requirement R4 and the security plan development under Requirement R5. 6.1. Each Transmission Owner and Transmission Operator shall select an unaffiliated third party reviewer from the following: • An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification. • An entity or organization approved by the ERO. • A governmental agency with physical security expertise. • An entity or organization with demonstrated law enforcement, government, or military physical security expertise. 6.2. The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. 6.3. If the unaffiliated third party reviewer recommends changes to the evaluation performed under Requirement R4 or security plan(s) developed under Requirement R5, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation: • Modify its evaluation or security plan(s) consistent with the recommendation; or • Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. 6.4. Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Q1 & Q6: There could be opportunities to prevent potential duplication and overlap with other standards (e.g., CIP-006).
COM-002-4 | R1. | R1. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall develop documented communications protocols for its operating personnel that issue and receive Operating Instructions. The protocols shall, at a minimum: 1.1. Require its operating personnel that issue and receive an oral or written Operating Instruction to use the English language, unless agreed to otherwise. An alternate language may be used for internal operations. 1.2. Require its operating personnel that issue an oral two-party, person-to-person Operating Instruction to take one of the following actions: • Confirm the receiver’s response if the repeated information is correct. • Reissue the Operating Instruction if the repeated information is incorrect or if requested by the receiver. • Take an alternative action if a response is not received or if the Operating Instruction was not understood by the receiver. 1.3. Require its operating personnel that receive an oral two-party, person-to-person Operating Instruction to take one of the following actions: • Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct. • Request that the issuer reissue the Operating Instruction. 1.4. Require its operating personnel that issue a written or oral single-party to multiple-party burst Operating Instruction to confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. 1.5. Specify the instances that require time identification when issuing an oral or written Operating Instruction and the format for that time identification. 1.6. Specify the nomenclature for Transmission interface Elements and Transmission interface Facilities when issuing an oral or written Operating Instruction. | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 11 | Q1: Generally speaking, R2-R7 create the protocol, so why does it need to be listed? R4 requires assessment with the standard. Q10: 1.1 "unless agreed to otherwise" is unclear - doesn't it mean between the parties or agreed on by a specific entity. Q10: 1.6 "Specify the nomenclature for Transmission interface Elements and Transmission interface Facilities" is unclear - is this common line identifiers?
COM-002-4 | R2. | R2. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall conduct initial training for each of its operating personnel responsible for the Real-time operation of the interconnected Bulk Electric System on the documented communications protocols developed in Requirement R1 prior to that individual operator issuing an Operating Instruction. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
COM-002-4 | R3. | R3. Each Distribution Provider and Generator Operator shall conduct initial training for each of its operating personnel who can receive an oral two-party, person-to-person Operating Instruction prior to that individual operator receiving an oral two-party, person-to-person Operating Instruction to either: • Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or • Request that the issuer reissue the Operating Instruction. | Yes | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 13 | C2: Should the GO and TO be included in the realm of "operating personnel".
COM-002-4 | R4. | R4. Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall at least once every twelve (12) calendar months: 4.1. Assess adherence to the documented communications protocols in Requirement R1 by its operating personnel that issue and receive Operating Instructions, provide feedback to those operating personnel and take corrective action, as deemed appropriate by the entity, to address deviations from the documented protocols. 4.2. Assess the effectiveness of its documented communications protocols in Requirement R1 for its operating personnel that issue and receive Operating Instructions and modify its documented communication protocols, as necessary. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
COM-002-4 | R5. | R5. Each Balancing Authority, Reliability Coordinator, and Transmission Operator that issues an oral two-party, person-to-person Operating Instruction during an Emergency, excluding written or oral single-party to multiple-party burst Operating Instructions, shall either: • Confirm the receiver’s response if the repeated information is correct (in accordance with Requirement R6). • Reissue the Operating Instruction if the repeated information is incorrect or if requested by the receiver, or • Take an alternative action if a response is not received or if the Operating Instruction was not understood by the receiver. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
COM-002-4 | R6. | R6. Each Balancing Authority, Distribution Provider, Generator Operator, and Transmission Operator that receives an oral two-party, person-to-person Operating Instruction during an Emergency, excluding written or oral single-party to multiple-party burst Operating Instructions, shall either: • Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or • Request that the issuer reissue the Operating Instruction. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
COM-002-4 | R7. | R7. Each Balancing Authority, Reliability Coordinator, and Transmission Operator that issues a written or oral single-party to multiple-party burst Operating Instruction during an Emergency shall confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
FAC-003-4 | R1. | R1. Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the Minimum Vegetation Clearance Distance (MVCD) of its applicable line(s) which are either an element of an IROL, or an element of a Major WECC Transfer Path; operating within their Rating and all Rated Electrical Operating Conditions of the types shown below: 1.1. An encroachment into the MVCD as shown in FAC-003-Table 2, observed in Real-time, absent a Sustained Outage, 1.2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, 1.3. An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, 1.4. An encroachment due to vegetation growth into the MVCD that caused a vegetation-related Sustained Outage. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 12 | Q7: WECC is moving away from Major WECC Transfer Path.
FAC-003-4 | R2. | R2. Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are not either an element of an IROL, or an element of a Major WECC Transfer Path; operating within its Rating and all Rated Electrical Operating Conditions of the types shown below: 2.1. An encroachment into the MVCD, observed in Real-time, absent a Sustained Outage, 2.2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, 2.3. An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, 2.4. An encroachment due to vegetation growth into the line MVCD that caused a vegetation-related Sustained Outage. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | 3 | 11 | Q7: WECC is moving away from Major WECC Transfer Path. Q12: Table 2 for MVCD is not referenced in 2.1 like it is in 1.1.
FAC-003-4 | R3. | R3. Each applicable Transmission Owner and applicable Generator Owner shall have documented maintenance strategies or procedures or processes or specifications it uses to prevent the encroachment of vegetation into the MVCD of its applicable lines that accounts for the following: 3.1. Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; 3.2. Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
FAC-003-4 | R4. | R4. Each applicable Transmission Owner and applicable Generator Owner, without any intentional time delay, shall notify the control center holding switching authority for the associated applicable line when the applicable Transmission Owner and applicable Generator Owner has confirmed the existence of a vegetation condition that is likely to cause a Fault at any moment. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
FAC-003-4 | R5. | R5. When an applicable Transmission Owner and an applicable Generator Owner are constrained from performing vegetation work on an applicable line operating within its Rating and all Rated Electrical Operating Conditions, and the constraint may lead to a vegetation encroachment into the MVCD prior to the implementation of the next annual work plan, then the applicable Transmission Owner or applicable Generator Owner shall take corrective action to ensure continued vegetation management to prevent encroachments. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
FAC-003-4 | R6. | R6. Each applicable Transmission Owner and applicable Generator Owner shall perform a Vegetation Inspection of 100% of its applicable transmission lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) at least once per calendar year and with no more than 18 calendar months between inspections on the same ROW. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
FAC-003-4 | R7. | R7. Each applicable Transmission Owner and applicable Generator Owner shall complete 100% of its annual vegetation work plan of applicable lines to ensure no vegetation encroachments occur within the MVCD. Modifications to the work plan in response to changing conditions or to findings from vegetation inspections may be made (provided they do not allow encroachment of vegetation into the MVCD) and must be documented. The percent completed calculation is based on the number of units actually completed divided by the number of units in the final amended plan (measured in units of choice - circuit, pole line, line miles or kilometers, etc.). Examples of reasons for modification to annual plan may include. 7.1. Change in expected growth rate/environmental factors 7.2. Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner 7.3. Rescheduling work between growing seasons 7.4. Crew or contractor availability/Mutual assistance agreements 7.5. Identified unanticipated high priority work 7.6. Weather conditions/Accessibility 7.7. Permitting delays 7.8. Land ownership changes/Change in land use by the landowner 7.9. Emerging technologies | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 13 | Q1: Examples given in 7.1-7.9 are only examples and perhaps should be removed or moved to the GTB or measure.
FAC-013-2 | R1. | R1. Each Planning Coordinator shall have a documented methodology it uses to perform an annual assessment of Transfer Capability in the Near-Term Transmission Planning Horizon (Transfer Capability methodology). The Transfer Capability methodology shall include, at a minimum, the following information: [See standard pdf for requirements of the Transfer Capability methodology] 1.1. Criteria for the selection of the transfers to be assessed. 1.2. A statement that the assessment shall respect known System Operating Limits (SOLs). 1.3. A statement that the assumptions and criteria used to perform the assessment are consistent with the Planning Coordinator’s planning practices. 1.4. A description of how each of the following assumptions and criteria used in performing the assessment are addressed: 1.4.1. Generation dispatch, including but not limited to long term planned outages, additions and retirements. 1.4.2. Transmission system topology, including but not limited to long term planned Transmission outages, additions, and retirements. 1.4.3. System demand. 1.4.4. Current approved and projected Transmission uses. 1.4.5. Parallel path (loop flow) adjustments. 1.4.6. Contingencies 1.4.7. Monitored Facilities. 1.5. A description of how simulations of transfers are performed through the adjustment of generation, Load or both. | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 13 | C3: In reference to R1, 1.4.6 and 1.4.7 should neighboring systems be considered and coordinated. C3: Should be aware of possible simultaneous transfers.
FAC-013-2 | R2. | R2. Each Planning Coordinator shall issue its Transfer Capability methodology, and any revisions to the Transfer Capability methodology, to the following entities subject to the following: [See standard pdf for requirements of issuing the Transfer Capability Methodology] 2.1. Distribute to the following prior to the effectiveness of such revisions: 2.1.1. Each Planning Coordinator adjacent to the Planning Coordinator’s Planning Coordinator area or overlapping the Planning Coordinator’s area. 2.1.2. Each Transmission Planner within the Planning Coordinator’s Planning Coordinator area. 2.2. Distribute to each functional entity that has a reliability-related need for the Transfer Capability methodology and submits a request for that methodology within 30 calendar days of receiving that written request. | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 13 | C3: Should the Reliability Coordinator be included to receive the Transfer Capability methodology?
FAC-013-2 | R3. | R3. (INACTIVE) If a recipient of the Transfer Capability methodology provides documented concerns with the methodology, the Planning Coordinator shall provide a documented response to that recipient within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Transfer Capability methodology and, if no change will be made to that Transfer Capability methodology, the reason why. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
FAC-013-2 | R4. | R4. During each calendar year, each Planning Coordinator shall conduct simulations and document an assessment based on those simulations in accordance with its Transfer Capability methodology for at least one year in the Near-Term Transmission Planning Horizon. | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | C3: Requirement only mandates simulating and documenting at least one year of the Near-Term Transmission Planning Horizon when this horizon includes years 1 through 5. Q6: See above, only requires one of five years.
FAC-013-2 | R5. | R5. Each Planning Coordinator shall make the documented Transfer Capability assessment results available within 45 calendar days of the completion of the assessment to the recipients of its Transfer Capability methodology pursuant to Requirement R2, Parts 2.1 and Part 2.2. However, if a functional entity that has a reliability related need for the results of the annual assessment of the Transfer Capabilities makes a written request for such an assessment after the completion of the assessment, the Planning Coordinator shall make the documented Transfer Capability assessment results available to that entity within 45 calendar days of receipt of the request | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 13 | C3: Should the Reliability Coordinator be included to receive the Transfer Capability results?
FAC-013-2 | R6. | R6. If a recipient of a documented Transfer Capability assessment requests data to support the assessment results, the Planning Coordinator shall provide such data to that entity within 45 calendar days of receipt of the request. The provision of such data shall be subject to the legal and regulatory obligations of the Planning Coordinator’s area regarding the disclosure of confidential and/or sensitive information. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
IRO-006-5 | R1. | R1. Each Reliability Coordinator and Balancing Authority that receives a request pursuant to an Interconnection-wide transmission loading relief procedure (such as Eastern Interconnection TLR, WECC Unscheduled Flow Mitigation, or congestion management procedures from the ERCOT Protocols) from any Reliability Coordinator, Balancing Authority, or Transmission Operator in another Interconnection to curtail an Interchange Transaction that crosses an Interconnection boundary shall comply with the request, unless it provides a reliability reason to the requestor why it cannot comply with the request. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | Note: The phrase "Interconnection-wide transmission loading relief procedure" is generic and could use more specific terminology.
MOD-020-0 | R1. | R1. The Load-Serving Entity, Transmission Planner, and Resource Planner shall each make known its amount of interruptible demands and Direct Control Load Management (DCLM) to Transmission Operators, Balancing Authorities, and Reliability Coordinators on request within 30 calendar days. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-025-2 | R1. | R1. Each Generator Owner shall provide its Transmission Planner with verification of the Real Power capability of its applicable Facilities as follows: 1.1. Verify the Real Power capability of its generating units in accordance with Attachment 1. 1.2. Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | 3 | 11 | Q9: Battery storage systems are not identified. Q10: Attachment - the use of "normally expected to operate" (2.1.1 At the minimum Real Power output at which they are normally expected to operate collect maximum leading and lagging reactive values as soon as a limit is reached.) is not clear. The expected normal operation can refer to minimum operation dictated by the market or the system operator, or it can refer to minimum power that the generator can normally operate at without changing any alarms or protection (e.g. reverse power).
MOD-025-2 | R2. | R2. Each Generator Owner shall provide its Transmission Planner with verification of the Reactive Power capability of its applicable Facilities as follows: 2.1. Verify, in accordance with Attachment 1, (i) the Reactive Power capability of its generating units and (ii) the Reactive Power capability of its synchronous condenser units. 2.2. Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-025-2 | R3. | R3. Each Transmission Owner shall provide its Transmission Planner with verification of the Reactive Power capability of its applicable Facilities as follows: 3.1. Verify, in accordance with Attachment 1, the Reactive Power capability of its synchronous condenser units. 3.2. Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-026-1 | R1. | R1. Each Transmission Planner shall provide the following requested information to the Generator Owner within 90 calendar days of receiving a written request: • Instructions on how to obtain the list of excitation control system or plant volt/var control function models that are acceptable to the Transmission Planner for use in dynamic simulation, • Instructions on how to obtain the dynamic excitation control system or plant volt/var control function model library block diagrams and/or data sheets for models that are acceptable to the Transmission Planner, or • Model data for any of the Generator Owner’s existing applicable unit specific excitation control system or plant volt/var control function contained in the Transmission Planner’s dynamic database from the current (in-use) models, including generator MVA base. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-026-1 | R2. | R2. Each Generator Owner shall provide for each applicable unit, a verified generator excitation control system or plant volt/var control function model, including documentation and data (as specified in Part 2.1) to its Transmission Planner in accordance with the periodicity specified in MOD-026 Attachment 1. 2.1. Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s), or both. Each verification shall include the following: 2.1.1. Documentation demonstrating the applicable unit’s model response matches the recorded response for a voltage excursion from either a staged test or a measured system disturbance, 2.1.2 Manufacturer, model number (if available), and type of the excitation control system including, but not limited to static, AC brushless, DC rotating, and/or the plant volt/var control function (if installed), 2.1.3. Model structure and data including, but not limited to reactance, time constants, saturation factors, total rotational inertia, or equivalent data for the generator, 2.1.4. Model structure and data for the excitation control system, including the closed loop voltage regulator if a closed loop voltage regulator is installed or the model structure and data for the plant volt/var control function system, 2.1.5. Compensation settings (such as droop, line drop, differential compensation), if used, and 2.1.6. Model structure and data for power system stabilizer, if so equipped. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Q3: May lead to omitting items like wind/inverter controls, only includes the plant level controller.
MOD-026-1 | R3. | R3. Each Generator Owner shall provide a written response to its Transmission Planner within 90 calendar days of receiving one of the following items for an applicable unit: • Written notification from its Transmission Planner (in accordance with Requirement R6) that the excitation control system or plant volt/var control function model is not usable, • Written comments from its Transmission Planner identifying technical concerns with the verification documentation related to the excitation control system or plant volt/var control function model, or • Written comments and supporting evidence from its Transmission Planner indicating that the simulated excitation control system or plant volt/var control function model response did not match the recorded response to a transmission system event. The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification (in accordance with Requirement R2). | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-026-1 | R4. | R4. Each Generator Owner shall provide revised model data or plans to perform model verification (in accordance with Requirement R2) for an applicable unit to its Transmission Planner within 180 calendar days of making changes to the excitation control system or plant volt/var control function that alter the equipment response characteristic. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-026-1 | R5. | R5. Each Generator Owner shall provide a written response to its Transmission Planner, within 90 calendar days following receipt of a technically justified unit request from the Transmission Planner to perform a model review of a unit or plant that includes one of the following: • Details of plans to verify the model (in accordance with Requirement R2), or • Corrected model data including the source of revised model data such as discovery of manufacturer test values to replace generic model data or updating of data parameters based on an on-site review of the equipment. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-026-1 | R6. | R6. Each Transmission Planner shall provide a written response to the Generator Owner within 90 calendar days of receiving the verified excitation control system or plant volt/var control function model information in accordance with Requirement R2 that the model is usable (meets the criteria specified in Parts 6.1 through 6.3) or is not usable. 6.1. The excitation control system or plant volt/var control function model initializes to compute modeling data without error, 6.2. A no-disturbance simulation results in negligible transients, and 6.3. For an otherwise stable simulation, a disturbance simulation results in the excitation control and plant volt/var control function model exhibiting positive damping. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-027-1 | R1. | R1. Each Transmission Planner shall provide the following requested information to the Generator Owner within 90 calendar days of receiving a written request: • Instructions on how to obtain the list of turbine/governor and load control or active power/frequency control system models that are acceptable to the Transmission Planner for use in dynamic simulation, • Instructions on how to obtain the dynamic turbine/governor and load control or active power/frequency control function model library block diagrams and/or data sheets for models that are acceptable to the Transmission Planner, or • Model data for any of the Generator Owner’s existing applicable unit specific turbine/governor and load control or active power/frequency control system contained in the Transmission Planner’s dynamic database from the current (in-use) models. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-027-1 | R2. | R2. Each Generator Owner shall provide, for each applicable unit, a verified turbine/governor and load control or active power/frequency control model, including documentation and data (as specified in Part 2.1) to its Transmission Planner in accordance with the periodicity specified in MOD-027 Attachment 1. 2.1. Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units rated less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s) or both. Each verification shall include the following: 2.1.1. Documentation comparing the applicable unit’s MW model response to the recorded MW response for either: • A frequency excursion from a system disturbance that meets MOD-027 Attachment 1 Note 1 with the applicable unit on-line, • A speed governor reference change with the applicable unit online, or • A partial load rejection test 2. 2.1.2. Type of governor and load control or active power control/frequency control3 equipment, 2.1.3. A description of the turbine (e.g. for hydro turbine - Kaplan, Francis, or Pelton; for steam turbine - boiler type, normal fuel type, and turbine type; for gas turbine - the type and manufacturer; for variable energy plant - type and manufacturer), 2.1.4. Model structure and data for turbine/governor and load control or active power/frequency control, and 2.1.5. Representation of the real power response effects of outer loop controls such as operator set point controls, and load control but excluding AGC control) that would override the governor response (including blocked or nonfunctioning governors or modes of operation that limit Frequency Response), if applicable. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Q3: May lead to omitting items like wind/inverter controls, only includes the plant level controller.
MOD-027-1 | R3. | R3. Each Generator Owner shall provide a written response to its Transmission Planner within 90 calendar days of receiving one of the following items for an applicable unit. • Written notification, from its Transmission Planner (in accordance with Requirement R5) that the turbine/governor and load control or active power/frequency control model is not “usable,” • Written comments from its Transmission Planner identifying technical concerns with the verification documentation related to the turbine/governor and load control or active power/frequency control model, or • Written comments and supporting evidence from its Transmission Planner indicating that the simulated turbine/governor and load control or active power/frequency control response did not approximate the recorded response for three or more transmission system events. The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification (in accordance with Requirement R2). The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification (in accordance with Requirement R2). | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-027-1 | R4. | R4. Each Generator Owner shall provide revised model data or plans to perform model verification (in accordance with Requirement R2) for an applicable unit to its Transmission Planner within 180 calendar days of making changes to the turbine/governor and load control or active power/frequency control system that alter the equipment response characteristic. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-027-1 | R5. | R5. Each Transmission Planner shall provide a written response to the Generator Owner within 90 calendar days of receiving the turbine/governor and load control or active power/frequency control system verified model information in accordance with Requirement R2 that the model is usable (meets the criteria specified in Parts 5.1 through 5.3) or is not usable. 5.1. The turbine/governor and load control or active power/frequency control function model initializes to compute modeling data without error, 5.2 A no-disturbance simulation results in negligible transients, and 5.3. For an otherwise stable simulation, a disturbance simulation results in the turbine/governor and load control or active power/frequency control model exhibiting positive damping. | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 13 | MOD-027 does not include a go and fix it requirement like MOD-026, as noted below: MOD-026, R5. Each Generator Owner shall provide a written response to its Transmission Planner, within 90 calendar days following receipt of a technically justified unit request from the Transmission Planner to perform a model review of a unit or plant that includes one of the following: (See full requirement in the above rows.)
MOD-028-2 | R1. | R1. Each Transmission Service Provider shall include in its Available Transfer Capability Implementation Document (ATCID), at a minimum, the following information relative to its methodology for determining Total Transfer Capability (TTC): R1.1. Information describing how the selected methodology has been implemented, in such detail that, given the same information used by the Transmission Operator, the results of the TTC calculations can be validated. R1.2. A description of the manner in which the Transmission Operator will account for Interchange Schedules in the calculation of TTC. R1.3. Any contractual obligations for allocation of TTC. R1.4. A description of the manner in which Contingencies are identified for use in the TTC process. R1.5. The following information on how source and sink for transmission service is accounted for in ATC calculations including: R1.5.1. Define if the source used for Available Transfer Capability (ATC) calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation R1.5.2. Define if the sink used for ATC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation R1.5.3. The source/sink or POR/POD identification and mapping to the model. R1.5.4. If the Transmission Service Provider’s ATC calculation process involves a grouping of generation, the ATCID must identify how these generators participate in the group. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | Consider providing a reference that this document refers to calculating TTC for ATC Paths by the Transmission Operator in Requirements R2-R4.
MOD-028-2 | R10. | R10. When calculating firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall utilize the following algorithm: ATCF = TTC – ETCF – CBM – TRM + PostbacksF + counterflowsF Where: ATCF is the firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm Transmission commitments for the ATC Path during that period. CBM is the Capacity Benefit Margin for the ATC Path during that period. TRM is the Transmission Reliability Margin for the ATC Path during that period. PostbacksF¬ are changes to firm ATC due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsF are adjustments to firm ATC as determined by the Transmission Service Provider and specified in the ATCID. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-028-2 | R11. | R11. When calculating non-firm ATC for a ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: ATCNF = TTC – ETCF - ETCNF – CBMS – TRMU + PostbacksNF + counterflowsNF Where: ATCNF is the non-firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm Transmission commitments for the ATC Path during that period. ETCNF is the sum of existing non-firm Transmission commitments for the ATC Path during that period. CBMS is the Capacity Benefit Margin for the ATC Path that has been scheduled without a separate reservation during that period. TRMU is the Transmission Reliability Margin for the ATC Path that has not been released for sale (unreleased) as non-firm capacity by the Transmission Service Provider during that period. PostbacksNF¬ are changes to non-firm ATC due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsNF are adjustments to non-firm ATC as determined by the Transmission Service Provider and specified in the ATCID. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-028-2 | R2. | R2. When calculating TTC for ATC Paths, the Transmission Operator shall use a Transmission model that contains all of the following: R2.1. Modeling data and topology of its Reliability Coordinator’s area of responsibility. Equivalent representation of radial lines and facilities 161 kV or below is allowed. R2.2. Modeling data and topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination areas. R2.3. Facility Ratings specified by the Generator Owners and Transmission Owners. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-028-2 | R3. | R3. When calculating TTCs for ATC Paths, the Transmission Operator shall include the following data for the Transmission Service Provider’s area. The Transmission Operator shall also include the following data associated with Facilities that are explicitly represented in the Transmission model, as provided by adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed: R3.1. For TTCs, use the following (as well as any other values and additional parameters as specified in the ATCID): R3.1.1. Expected generation and Transmission outages, additions, and retirements, included as specified in the ATCID. R3.1.2. A daily or hourly load forecast for TTCs used in current-day and next-day ATC calculations. R3.1.3. A daily load forecast for TTCs used in ATC calculations for days two through 31. R3.1.4. A monthly load forecast for TTCs used in ATC calculations for months two through 13 months TTCs. R3.1.5. Unit commitment and dispatch order, to include all designated network resources and other resources that are committed or have the legal obligation to run, (within or out of economic dispatch) as they are expected to run. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-028-2 | R4. | R4. When calculating TTCs for ATC Paths, the Transmission Operator shall meet all of the following conditions: R4.1. Use all Contingencies meeting the criteria described in the ATCID. R4.2. Respect any contractual allocations of TTC. R4.3. Include, for each time period, the Firm Transmission Service expected to be scheduled as specified in the ATCID (filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers) for the Transmission Service Provider, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed modeling the source and sink as follows: - If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the source, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point shall as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can not be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is to be delivered as the sink. - If the sink, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is being delivered as the sink. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-028-2 | R5. | R5. Each Transmission Operator shall establish TTC for each ATC Path as defined below: R5.1. At least once within the seven calendar days prior to the specified period for TTCs used in hourly and daily ATC calculations. R5.2. At least once per calendar month for TTCs used in monthly ATC calculations. R5.3. Within 24 hours of the unexpected outage of a 500 kV or higher transmission Facility or a transformer with a low-side voltage of 200 kV or higher for TTCs in effect during the anticipated duration of the outage, provided such outage is expected to last 24 hours or longer. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | Should large generator units and/or plants be considered in how the loss of generation impacts TTC and ATC?
MOD-028-2 | R6. | R6. Each Transmission Operator shall establish TTC for each ATC Path using the following process: R6.1. Determine the incremental Transfer Capability for each ATC Path by increasing generation and/or decreasing load within the source Balancing Authority area and decreasing generation and/or increasing load within the sink Balancing Authority area until either: - A System Operating Limit is reached on the Transmission Service Provider’s system, or - A SOL is reached on any other adjacent system in the Transmission model that is not on the study path and the distribution factor is 5% or greater. R6.2. If the limit in step R6.1 can not be reached by adjusting any combination of load or generation, then set the incremental Transfer Capability by the results of the case where the maximum adjustments were applied. R6.3. Use (as the TTC) the lesser of: - The sum of the incremental Transfer Capability and the impacts of Firm Transmission Services, as specified in the Transmission Service Provider’s ATCID, that were included in the study model, or - The sum of Facility Ratings of all ties comprising the ATC Path. R6.4. For ATC Paths whose capacity uses jointly-owned or allocated Facilities, limit TTC for each Transmission Service Provider so the TTC does not exceed each Transmission Service Provider’s contractual rights. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-028-2 | R7. | R7. The Transmission Operator shall provide the Transmission Service Provider of that ATC Path with the most current value for TTC for that ATC Path no more than: R7.1. One calendar day after its determination for TTCs used in hourly and daily ATC calculations. R7.2. Seven calendar days after its determination for TTCs used in monthly ATC calculations. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-028-2 | R8. | R8. When calculating Existing Transmission Commitments (ETCs) for firm commitments (ETCF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: ETCF = NITSF + GFF + PTPF + RORF + OSF Where: NITSF is the firm capacity set aside for Network Integration Transmission Service (including the capacity used to serve bundled load within the Transmission Service Provider’s area with external sources) on ATC Paths that serve as interfaces with other Balancing Authorities. GFF is the firm capacity set aside for Grandfathered Firm Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or safe harbor tariff on ATC Paths that serve as interfaces with other Balancing Authorities. PTPF is the firm capacity reserved for confirmed Point-to-Point Transmission Service. RORF is the capacity reserved for roll-over rights for Firm Transmission Service contracts granting Transmission Customers the right of first refusal to take or continue to take Transmission Service when the Transmission Customer’s Transmission Service contract expires or is eligible for renewal. OSF is the firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using Firm Transmission Service, including any other firm adjustments to reflect impacts from other ATC Paths of the Transmission Service Provider as specified in the ATCID. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13
MOD-028-2 | R9. | R9. When calculating ETC for non-firm commitments (ETCNF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: ETCNF = NITSNF + GFNF + PTPNF + OSNF Where: NITSNF is the non-firm capacity set aside for Network Integration Transmission Service (i.e., secondary service , including the capacity used to serve bundled load within the Transmission Service Provider’s area with external sources) reserved on ATC Paths that serve as interfaces with other Balancing Authorities. GFNF is the non-firm capacity reserved for Grandfathered Non-Firm Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or safe harbor tariff on ATC Paths that serve as interfaces with other Balancing Authorities. PTPNF is non-firm capacity reserved for confirmed Point-to-Point Transmission Service. OSNF is the non-firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using Non-Firm Transmission Service, including any other firm adjustments to reflect impacts from other ATC Paths of the Transmission Service Provider as specified in the ATCID. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | Is Financial Transmission Rights (FTR) captured in OSNF?