## Requirements
Standard | Standard ID | Requirement Number | Requirement ID | Requirement Language | Additional Information | Requirement Applicability | BA | DP | DP-UFLS | FRSG | GO | GOP | IA | LSE | NERC | PCPA | PSE | RC | RE | RP | RRO | RRSG | RSG | TO | TOP | TP | TSP | Time Horizon(s) | Violation Risk Factor (VRF) | Violation Severity Level (Lower) | Violation Severity Level (Moderate) | Violation Severity Level (High) | Violation Severity Level (Severe) | Measure | Effective Date of Requirement | Pending Inactive | Inactive Date of Requirement | Additional Effective Date Details | Additional Applicability Details | Prior Version(s) | Region Jurisdiction(s) | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | Rank ID (Req)
BAL-001-0 | 1 | R1. | 1 | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. See Standard for Formula. The equation for ACE is: ACE = (NIA - NIS) - 10B (FA - FS) - IME where: · NIA is the algebraic sum of actual flows on all tie lines. · NIS is the algebraic sum of scheduled flows on all tie lines. · B is the Frequency Bias Setting (MW/0.1 Hz) for the Balancing Authority. The constant factor 10 converts the frequency setting to MW/Hz. · FA is the actual frequency. · FS is the scheduled frequency. FS is normally 60 Hz but may be offset to effect manual time error corrections. IME is the meter error correction factor typically estimated from the difference between the integrated hourly average of the net tie line flows (NIA) and the hourly net interchange demand measurement (megawatt-hour). This term should normally be very small or zero. |  | BA | BA | [21 empty] | Low | The Balancing Authority Area’s value of CPS1 is less than 100% but greater than or equal to 95%. | The Balancing Authority Area’s value of CPS1 is less than 95% but greater than or equal to 90%. | The Balancing Authority Area’s value of CPS1 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS1 is less than 85%. | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%. See Standard for Formula | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-001-0 | 1 | R2. | 2 | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. See Standard for Formula. |  | BA | BA | [21 empty] | Low | The Balancing Authority Area’s value of CPS2 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS2 is less than 85% but greater than or equal to 80%. | The Balancing Authority Area’s value of CPS2 is less than 80% but greater than or equal to 75%. | The Balancing Authority Area’s value of CPS2 is less than 75%. | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE A compliance percentage is calculated as follows: See Standard for formula | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-001-0 | 1 | R3. | 3 | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement R1 (i.e., Control Performance Standard 1 or CPS1) and Requirement R2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority providing Overlap Regulation Service failed to use a combined ACE and frequency bias. |  | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-001-0 | 1 | R4. | 4 | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). |  | BA | BA | [21 empty] | Low | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-001-0.1a | 2 | R1. | 5 | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. The equation for ACE is: ACE = (NIA - NIS) - 10B (FA - FS) - IME where: · NIA is the algebraic sum of actual flows on all tie lines. · NIS is the algebraic sum of scheduled flows on all tie lines. · B is the Frequency Bias Setting (MW/0.1 Hz) for the Balancing Authority. The constant factor 10 converts the frequency setting to MW/Hz. · FA is the actual frequency. · FS is the scheduled frequency. FS is normally 60 Hz but may be offset to effect manual time error corrections. · IME is the meter error correction factor typically estimated from the difference between the integrated hourly average of the net tie line flows (NIA) and the hourly net interchange demand measurement (megawatt-hour). This term should normally be very small or zero. | See Standard for Formulas | BA | BA | [21 empty] | Medium | The Balancing Authority Area’s value of CPS1 is less than 100% but greater than or equal to 95%. | The Balancing Authority Area’s value of CPS1 is less than 95% but greater than or equal to 90%. | The Balancing Authority Area’s value of CPS1 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS1 is less than 85%. | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: where:1 is defined in Requirement R1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. | 2009-05-13 |  | 2014-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-001-0.1a | 2 | R2. | 6 | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. ?10 is a constant derived from the targeted frequency bound. It is the targeted root-mean-square (RMS) value of ten-minute average Frequency Error based on frequency performance over a given year. The bound, ?10, is the same for every Balancing Authority Area within an Interconnection, and Bs is the sum of the Frequency Bias Settings of the Balancing Authority Areas in the respective Interconnection. For Balancing Authority Areas with variable bias, this is equal to the sum of the minimum Frequency Bias Settings. | See Standard for Formulas | BA | BA | [21 empty] | Medium | The Balancing Authority Area’s value of CPS2 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS2 is less than 85% but greater than or equal to 80%. | The Balancing Authority Area’s value of CPS2 is less than 80% but greater than or equal to 75%. | The Balancing Authority Area’s value of CPS2 is less than 75%. | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE. A compliance percentage is calculated as follows: The violations per month are a count of the number of periods that ACE clock-ten-minutes exceeded L10. ACE clock-ten-minutes is the sum of valid ACE samples within a clock-ten-minute period divided by the number of valid samples. Violation clock-ten-minutes = 0 if = 1 if Each Balancing Authority shall report the total number of violations and unavailable periods for the month. L10 is defined in Requirement R2. Since CPS2 requires that ACE be averaged over a discrete time period, the same factors that limit total periods per month will limit violations per month. The calculation of total periods per month and violations per month, therefore, must be discussed jointly. A condition may arise which may impact the normal calculation of total periods per month and violations per month. This condition is a sustained interruption in the recording of ACE. In order to ensure that the average ACE calculated for any ten-minute interval is representative of that ten-minute interval, it is necessary that at least half the ACE data samples are present for that interval. Should half or more of the ACE data be unavailable due to loss of telemetering or computer unavailability, that ten-minute interval shall be omitted from the calculation of CPS2. | 2009-05-13 |  | 2014-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-001-0.1a | 2 | R3. | 7 | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement R1 (i.e., Control Performance Standard 1 or CPS1) and Requirement R2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority providing Overlap Regulation Service failed to use a combined ACE and frequency bias. |  | 2009-05-13 |  | 2014-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-001-0.1a | 2 | R4. | 8 | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority receiving Overlap Regulation Service failed to ensure that control performance was being evaluated in a manner consistent with the calculation methodology as described in BAL-001-01 R3. |  | 2009-05-13 |  | 2014-03-31 |  |  | BAL-001-0.1a R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-001-0.1a (British Columbia) | 666700000010000 | R1. | 666700000010337 | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. The equation for ACE is: ACE = (NIA - NIS) - 10B (FA - FS) - IME where: · NIA is the algebraic sum of actual flows on all tie lines. · NIS is the algebraic sum of scheduled flows on all tie lines. · B is the Frequency Bias Setting (MW/0.1 Hz) for the Balancing Authority. The constant factor 10 converts the frequency setting to MW/Hz. · FA is the actual frequency. · FS is the scheduled frequency. FS is normally 60 Hz but may be offset to effect manual time error corrections. · IME is the meter error correction factor typically estimated from the difference between the integrated hourly average of the net tie line flows (NIA) and the hourly net interchange demand measurement (megawatt-hour). This term should normally be very small or zero. | See Standard for Formulas | BA | BA | [21 empty] | Medium | The Balancing Authority Area’s value of CPS1 is less than 100% but greater than or equal to 95%. | The Balancing Authority Area’s value of CPS1 is less than 95% but greater than or equal to 90%. | The Balancing Authority Area’s value of CPS1 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS1 is less than 85%. | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: where:1 is defined in Requirement R1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. | 2011-01-01 |  | 2014-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
BAL-001-0.1a (British Columbia) | 666700000010000 | R2. | 666700000010338 | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. ?10 is a constant derived from the targeted frequency bound. It is the targeted root-mean-square (RMS) value of ten-minute average Frequency Error based on frequency performance over a given year. The bound, ?10, is the same for every Balancing Authority Area within an Interconnection, and Bs is the sum of the Frequency Bias Settings of the Balancing Authority Areas in the respective Interconnection. For Balancing Authority Areas with variable bias, this is equal to the sum of the minimum Frequency Bias Settings. | See Standard for Formulas | BA | BA | [21 empty] | Medium | The Balancing Authority Area’s value of CPS2 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS2 is less than 85% but greater than or equal to 80%. | The Balancing Authority Area’s value of CPS2 is less than 80% but greater than or equal to 75%. | The Balancing Authority Area’s value of CPS2 is less than 75%. | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE. A compliance percentage is calculated as follows: The violations per month are a count of the number of periods that ACE clock-ten-minutes exceeded L10. ACE clock-ten-minutes is the sum of valid ACE samples within a clock-ten-minute period divided by the number of valid samples. Violation clock-ten-minutes = 0 if = 1 if Each Balancing Authority shall report the total number of violations and unavailable periods for the month. L10 is defined in Requirement R2. Since CPS2 requires that ACE be averaged over a discrete time period, the same factors that limit total periods per month will limit violations per month. The calculation of total periods per month and violations per month, therefore, must be discussed jointly. A condition may arise which may impact the normal calculation of total periods per month and violations per month. This condition is a sustained interruption in the recording of ACE. In order to ensure that the average ACE calculated for any ten-minute interval is representative of that ten-minute interval, it is necessary that at least half the ACE data samples are present for that interval. Should half or more of the ACE data be unavailable due to loss of telemetering or computer unavailability, that ten-minute interval shall be omitted from the calculation of CPS2. | 2011-01-01 |  | 2014-09-30 |  |  |  | WECC-BC | [6 empty] | 20000000
BAL-001-0.1a (British Columbia) | 666700000010000 | R3. | 666700000010339 | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement R1 (i.e., Control Performance Standard 1 or CPS1) and Requirement R2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority providing Overlap Regulation Service failed to use a combined ACE and frequency bias. |  | 2011-01-01 |  | 2014-09-30 |  |  |  | WECC-BC | [6 empty] | 30000000
BAL-001-0.1a (British Columbia) | 666700000010000 | R4. | 666700000010340 | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority receiving Overlap Regulation Service failed to ensure that control performance was being evaluated in a manner consistent with the calculation methodology as described in BAL-001-01 R3. |  | 2011-01-01 |  | 2014-09-30 |  |  |  | WECC-BC | [6 empty] | 40000000
BAL-001-0.1a (Manitoba) | 776600000002 | R1. | 776600000005 | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. The equation for ACE is: ACE = (NIA - NIS) - 10B (FA - FS) - IME where: · NIA is the algebraic sum of actual flows on all tie lines. · NIS is the algebraic sum of scheduled flows on all tie lines. · B is the Frequency Bias Setting (MW/0.1 Hz) for the Balancing Authority. The constant factor 10 converts the frequency setting to MW/Hz. · FA is the actual frequency. · FS is the scheduled frequency. FS is normally 60 Hz but may be offset to effect manual time error corrections. · IME is the meter error correction factor typically estimated from the difference between the integrated hourly average of the net tie line flows (NIA) and the hourly net interchange demand measurement (megawatt-hour). This term should normally be very small or zero. | See Standard for Formulas | BA | BA | [21 empty] | Medium | The Balancing Authority Area’s value of CPS1 is less than 100% but greater than or equal to 95%. | The Balancing Authority Area’s value of CPS1 is less than 95% but greater than or equal to 90%. | The Balancing Authority Area’s value of CPS1 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS1 is less than 85%. | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: where:1 is defined in Requirement R1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
BAL-001-0.1a (Manitoba) | 776600000002 | R2. | 776600000006 | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. ?10 is a constant derived from the targeted frequency bound. It is the targeted root-mean-square (RMS) value of ten-minute average Frequency Error based on frequency performance over a given year. The bound, ?10, is the same for every Balancing Authority Area within an Interconnection, and Bs is the sum of the Frequency Bias Settings of the Balancing Authority Areas in the respective Interconnection. For Balancing Authority Areas with variable bias, this is equal to the sum of the minimum Frequency Bias Settings. | See Standard for Formulas | BA | BA | [21 empty] | Medium | The Balancing Authority Area’s value of CPS2 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS2 is less than 85% but greater than or equal to 80%. | The Balancing Authority Area’s value of CPS2 is less than 80% but greater than or equal to 75%. | The Balancing Authority Area’s value of CPS2 is less than 75%. | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE. A compliance percentage is calculated as follows: The violations per month are a count of the number of periods that ACE clock-ten-minutes exceeded L10. ACE clock-ten-minutes is the sum of valid ACE samples within a clock-ten-minute period divided by the number of valid samples. Violation clock-ten-minutes = 0 if = 1 if Each Balancing Authority shall report the total number of violations and unavailable periods for the month. L10 is defined in Requirement R2. Since CPS2 requires that ACE be averaged over a discrete time period, the same factors that limit total periods per month will limit violations per month. The calculation of total periods per month and violations per month, therefore, must be discussed jointly. A condition may arise which may impact the normal calculation of total periods per month and violations per month. This condition is a sustained interruption in the recording of ACE. In order to ensure that the average ACE calculated for any ten-minute interval is representative of that ten-minute interval, it is necessary that at least half the ACE data samples are present for that interval. Should half or more of the ACE data be unavailable due to loss of telemetering or computer unavailability, that ten-minute interval shall be omitted from the calculation of CPS2. | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
BAL-001-0.1a (Manitoba) | 776600000002 | R3. | 776600000007 | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement R1 (i.e., Control Performance Standard 1 or CPS1) and Requirement R2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority providing Overlap Regulation Service failed to use a combined ACE and frequency bias. |  | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
BAL-001-0.1a (Manitoba) | 776600000002 | R4. | 776600000008 | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority receiving Overlap Regulation Service failed to ensure that control performance was being evaluated in a manner consistent with the calculation methodology as described in BAL-001-01 R3. |  | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 40000000
BAL-001-0.1a (Ontario) | 79780000002 | R1. | 79780000005 | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit ??? is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. | See Standard for Formulas | BA | BA | [21 empty] | Medium | The Balancing Authority Area’s value of CPS1 is less than 100% but greater than or equal to 95%. | The Balancing Authority Area’s value of CPS1 is less than 95% but greater than or equal to 90%. | The Balancing Authority Area’s value of CPS1 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS1 is less than 85%. | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%.&lt;br/&gt;CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows:&lt;br/&gt;CPS1 = (2 - CF) * 100%&lt;br/&gt;The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound:&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;where:1 is defined in Requirement R1.&lt;br/&gt;&lt;br/&gt;The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings.&lt;br/&gt;A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute.&lt;br/&gt; &lt;br/&gt;&lt;br/&gt; &lt;br/&gt;&lt;br/&gt;The Balancing Authority’s clock-minute compliance factor (CF) becomes:&lt;br/&gt;&lt;br/&gt; &lt;br/&gt;&lt;br/&gt;Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter.&lt;br/&gt; &lt;br/&gt;&lt;br/&gt;The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400).&lt;br/&gt; &lt;br/&gt;&lt;br/&gt;The 12-month compliance factor becomes:&lt;br/&gt; &lt;br/&gt;In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. | 2009-05-13 |  | 2014-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-001-0.1a (Ontario) | 79780000002 | R2. | 79780000006 | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. ?10 is a constant derived from the targeted frequency bound. It is the targeted root-mean-square (RMS) value of ten-minute average Frequency Error based on frequency performance over a given year. The bound, ?10, is the same for every Balancing Authority Area within an Interconnection, and Bs is the sum of the Frequency Bias Settings of the Balancing Authority Areas in the respective Interconnection. For Balancing Authority Areas with variable bias, this is equal to the sum of the minimum Frequency Bias Settings. | See Standard for Formulas | BA | BA | [21 empty] | Medium | The Balancing Authority Area’s value of CPS2 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS2 is less than 85% but greater than or equal to 80%. | The Balancing Authority Area’s value of CPS2 is less than 80% but greater than or equal to 75%. | The Balancing Authority Area’s value of CPS2 is less than 75%. | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE. A compliance percentage is calculated as follows:&lt;br/&gt; &lt;br/&gt;&lt;br/&gt;The violations per month are a count of the number of periods that ACE clock-ten-minutes exceeded L10. ACE clock-ten-minutes is the sum of valid ACE samples within a clock-ten-minute period divided by the number of valid samples.&lt;br/&gt;Violation clock-ten-minutes&lt;br/&gt; = 0 if&lt;br/&gt; &lt;br/&gt;&lt;br/&gt; = 1 if &lt;br/&gt; &lt;br/&gt;&lt;br/&gt;Each Balancing Authority shall report the total number of violations and unavailable periods for the month. L10 is defined in Requirement R2.&lt;br/&gt;Since CPS2 requires that ACE be averaged over a discrete time period, the same factors that limit total periods per month will limit violations per month. The calculation of total periods per month and violations per month, therefore, must be discussed jointly.&lt;br/&gt;A condition may arise which may impact the normal calculation of total periods per month and violations per month. This condition is a sustained interruption in the recording of ACE.&lt;br/&gt;In order to ensure that the average ACE calculated for any ten-minute interval is representative of that ten-minute interval, it is necessary that at least half the ACE data samples are present for that interval. Should half or more of the ACE data be unavailable due to loss of telemetering or computer unavailability, that ten-minute interval shall be omitted from the calculation of CPS2. | 2009-05-13 |  | 2014-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-001-0.1a (Ontario) | 79780000002 | R3. | 79780000007 | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement R1 (i.e., Control Performance Standard 1 or CPS1) and Requirement R2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority providing Overlap Regulation Service failed to use a combined ACE and frequency bias. |  | 2009-05-13 |  | 2014-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-001-0.1a (Ontario) | 79780000002 | R4. | 79780000008 | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority receiving Overlap Regulation Service failed to ensure that control performance was being evaluated in a manner consistent with the calculation methodology as described in BAL-001-01 R3. |  | 2009-05-13 |  | 2014-03-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-001-0.1a (Saskatchewan) | 837500000002 | R1. | 837500000005 | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. The equation for ACE is: ACE = (NIA - NIS) - 10B (FA - FS) - IME where: · NIA is the algebraic sum of actual flows on all tie lines. · NIS is the algebraic sum of scheduled flows on all tie lines. · B is the Frequency Bias Setting (MW/0.1 Hz) for the Balancing Authority. The constant factor 10 converts the frequency setting to MW/Hz. · FA is the actual frequency. · FS is the scheduled frequency. FS is normally 60 Hz but may be offset to effect manual time error corrections. · IME is the meter error correction factor typically estimated from the difference between the integrated hourly average of the net tie line flows (NIA) and the hourly net interchange demand measurement (megawatt-hour). This term should normally be very small or zero. | See Standard for Formulas | BA | BA | [21 empty] | Medium | The Balancing Authority Area’s value of CPS1 is less than 100% but greater than or equal to 95%. | The Balancing Authority Area’s value of CPS1 is less than 95% but greater than or equal to 90%. | The Balancing Authority Area’s value of CPS1 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS1 is less than 85%. | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: where:1 is defined in Requirement R1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. | 2010-03-30 |  | 2014-04-01 |  |  |  | MRO-SK | [6 empty] | 10000000
BAL-001-0.1a (Saskatchewan) | 837500000002 | R2. | 837500000006 | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. ?10 is a constant derived from the targeted frequency bound. It is the targeted root-mean-square (RMS) value of ten-minute average Frequency Error based on frequency performance over a given year. The bound, ?10, is the same for every Balancing Authority Area within an Interconnection, and Bs is the sum of the Frequency Bias Settings of the Balancing Authority Areas in the respective Interconnection. For Balancing Authority Areas with variable bias, this is equal to the sum of the minimum Frequency Bias Settings. | See Standard for Formulas | BA | BA | [21 empty] | Medium | The Balancing Authority Area’s value of CPS2 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS2 is less than 85% but greater than or equal to 80%. | The Balancing Authority Area’s value of CPS2 is less than 80% but greater than or equal to 75%. | The Balancing Authority Area’s value of CPS2 is less than 75%. | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE. A compliance percentage is calculated as follows: The violations per month are a count of the number of periods that ACE clock-ten-minutes exceeded L10. ACE clock-ten-minutes is the sum of valid ACE samples within a clock-ten-minute period divided by the number of valid samples. Violation clock-ten-minutes = 0 if = 1 if Each Balancing Authority shall report the total number of violations and unavailable periods for the month. L10 is defined in Requirement R2. Since CPS2 requires that ACE be averaged over a discrete time period, the same factors that limit total periods per month will limit violations per month. The calculation of total periods per month and violations per month, therefore, must be discussed jointly. A condition may arise which may impact the normal calculation of total periods per month and violations per month. This condition is a sustained interruption in the recording of ACE. In order to ensure that the average ACE calculated for any ten-minute interval is representative of that ten-minute interval, it is necessary that at least half the ACE data samples are present for that interval. Should half or more of the ACE data be unavailable due to loss of telemetering or computer unavailability, that ten-minute interval shall be omitted from the calculation of CPS2. | 2010-03-30 |  | 2014-04-01 |  |  |  | MRO-SK | [6 empty] | 20000000
BAL-001-0.1a (Saskatchewan) | 837500000002 | R3. | 837500000007 | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement R1 (i.e., Control Performance Standard 1 or CPS1) and Requirement R2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority providing Overlap Regulation Service failed to use a combined ACE and frequency bias. |  | 2010-03-30 |  | 2014-04-01 |  |  |  | MRO-SK | [6 empty] | 30000000
BAL-001-0.1a (Saskatchewan) | 837500000002 | R4. | 837500000008 | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority receiving Overlap Regulation Service failed to ensure that control performance was being evaluated in a manner consistent with the calculation methodology as described in BAL-001-01 R3. |  | 2010-03-30 |  | 2014-04-01 |  |  |  | MRO-SK | [6 empty] | 40000000
BAL-001-0a | 3 | R1. | 9 | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit ??? is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. See standard for equation. The equation for ACE is: ACE = (NIA - NIS) - 10B (FA - FS) - IME where: · NIA is the algebraic sum of actual flows on all tie lines. · NIS is the algebraic sum of scheduled flows on all tie lines. · B is the Frequency Bias Setting (MW/0.1 Hz) for the Balancing Authority. The constant factor 10 converts the frequency setting to MW/Hz. · FA is the actual frequency. · FS is the scheduled frequency. FS is normally 60 Hz but may be offset to effect manual time error corrections. IME is the meter error correction factor typically estimated from the difference between the integrated hourly average of the net tie line flows (NIA) and the hourly net interchange demand measurement (megawatt-hour). This term should normally be very small or zero. | See Standard for Formulas | BA | BA | [22 empty] | The Balancing Authority Area’s value of CPS1 is less than 100% but greater than or equal to 95%. | The Balancing Authority Area’s value of CPS1 is less than 95% but greater than or equal to 90%. | The Balancing Authority Area’s value of CPS1 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS1 is less than 85%. | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: where:1 is defined in Requirement R1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. | 2008-08-27 |  | 2009-05-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-001-0a | 3 | R2. | 10 | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. See standard for formula. E10 is a constant derived from the targeted frequency bound. It is the targeted root-mean-square (RMS) value of ten-minute average Frequency Error based on frequency performance over a given year. The bound, e10, is the same for every Balancing Authority Area within an Interconnection, and Bs is the sum of the Frequency Bias Settings of the Balancing Authority Areas in the respective Interconnection. For Balancing Authority Areas with variable bias, this is equal to the sum of the minimum Frequency Bias Settings. | See Standard for Formulas | BA | BA | [22 empty] | The Balancing Authority Area’s value of CPS2 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS2 is less than 85% but greater than or equal to 80%. | The Balancing Authority Area’s value of CPS2 is less than 80% but greater than or equal to 75%. | The Balancing Authority Area’s value of CPS2 is less than 75%. | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE. A compliance percentage is calculated as follows: The violations per month are a count of the number of periods that ACE clock-ten-minutes exceeded L10. ACE clock-ten-minutes is the sum of valid ACE samples within a clock-ten-minute period divided by the number of valid samples. Violation clock-ten-minutes = 0 if = 1 if Each Balancing Authority shall report the total number of violations and unavailable periods for the month. L10 is defined in Requirement R2. Since CPS2 requires that ACE be averaged over a discrete time period, the same factors that limit total periods per month will limit violations per month. The calculation of total periods per month and violations per month, therefore, must be discussed jointly. A condition may arise which may impact the normal calculation of total periods per month and violations per month. This condition is a sustained interruption in the recording of ACE. In order to ensure that the average ACE calculated for any ten-minute interval is representative of that ten-minute interval, it is necessary that at least half the ACE data samples are present for that interval. Should half or more of the ACE data be unavailable due to loss of telemetering or computer unavailability, that ten-minute interval shall be omitted from the calculation of CPS2. | 2008-08-27 |  | 2009-05-12 |  |  | BAL-001-0a R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-001-0a | 3 | R3. | 11 | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement M1 (i.e., Control Performance Standard 1 or CPS1) and Requirement M2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. |  | BA | BA | [25 empty] | The Balancing Authority providing Overlap Regulation Service failed to use a combined ACE and frequency bias. |  | 2008-08-27 |  | 2009-05-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-001-0a | 3 | R4. | 12 | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). |  | BA | BA | [25 empty] | The Balancing Authority receiving Overlap Regulation Service failed to ensure that control performance was being evaluated in a manner consistent with the calculation methodology as described in BAL-001-01 R3. |  | 2008-08-27 |  | 2009-05-12 |  |  | BAL-001-0a R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-001-0a (British Columbia) | 666700000010001 | R1. | 666700000010341 | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit ??? is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. See standard for equation. The equation for ACE is: ACE = (NIA - NIS) - 10B (FA - FS) - IME where: · NIA is the algebraic sum of actual flows on all tie lines. · NIS is the algebraic sum of scheduled flows on all tie lines. · B is the Frequency Bias Setting (MW/0.1 Hz) for the Balancing Authority. The constant factor 10 converts the frequency setting to MW/Hz. · FA is the actual frequency. · FS is the scheduled frequency. FS is normally 60 Hz but may be offset to effect manual time error corrections. IME is the meter error correction factor typically estimated from the difference between the integrated hourly average of the net tie line flows (NIA) and the hourly net interchange demand measurement (megawatt-hour). This term should normally be very small or zero. | See Standard for Formulas | BA | BA | [22 empty] | The Balancing Authority Area’s value of CPS1 is less than 100% but greater than or equal to 95%. | The Balancing Authority Area’s value of CPS1 is less than 95% but greater than or equal to 90%. | The Balancing Authority Area’s value of CPS1 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS1 is less than 85%. | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: where:1 is defined in Requirement R1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 10000000
BAL-001-0a (British Columbia) | 666700000010001 | R2. | 666700000010342 | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. See standard for formula. E10 is a constant derived from the targeted frequency bound. It is the targeted root-mean-square (RMS) value of ten-minute average Frequency Error based on frequency performance over a given year. The bound, e10, is the same for every Balancing Authority Area within an Interconnection, and Bs is the sum of the Frequency Bias Settings of the Balancing Authority Areas in the respective Interconnection. For Balancing Authority Areas with variable bias, this is equal to the sum of the minimum Frequency Bias Settings. | See Standard for Formulas | BA | BA | [22 empty] | The Balancing Authority Area’s value of CPS2 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS2 is less than 85% but greater than or equal to 80%. | The Balancing Authority Area’s value of CPS2 is less than 80% but greater than or equal to 75%. | The Balancing Authority Area’s value of CPS2 is less than 75%. | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE. A compliance percentage is calculated as follows: The violations per month are a count of the number of periods that ACE clock-ten-minutes exceeded L10. ACE clock-ten-minutes is the sum of valid ACE samples within a clock-ten-minute period divided by the number of valid samples. Violation clock-ten-minutes = 0 if = 1 if Each Balancing Authority shall report the total number of violations and unavailable periods for the month. L10 is defined in Requirement R2. Since CPS2 requires that ACE be averaged over a discrete time period, the same factors that limit total periods per month will limit violations per month. The calculation of total periods per month and violations per month, therefore, must be discussed jointly. A condition may arise which may impact the normal calculation of total periods per month and violations per month. This condition is a sustained interruption in the recording of ACE. In order to ensure that the average ACE calculated for any ten-minute interval is representative of that ten-minute interval, it is necessary that at least half the ACE data samples are present for that interval. Should half or more of the ACE data be unavailable due to loss of telemetering or computer unavailability, that ten-minute interval shall be omitted from the calculation of CPS2. | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 20000000
BAL-001-0a (British Columbia) | 666700000010001 | R3. | 666700000010343 | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement M1 (i.e., Control Performance Standard 1 or CPS1) and Requirement M2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. |  | BA | BA | [25 empty] | The Balancing Authority providing Overlap Regulation Service failed to use a combined ACE and frequency bias. |  | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 30000000
BAL-001-0a (British Columbia) | 666700000010001 | R4. | 666700000010344 | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). |  | BA | BA | [25 empty] | The Balancing Authority receiving Overlap Regulation Service failed to ensure that control performance was being evaluated in a manner consistent with the calculation methodology as described in BAL-001-01 R3. |  | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 40000000
BAL-001-0a (Ontario) | 79780000003 | R1. | 79780000009 | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit ??? is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. See standard for equation. | See Standard for Formulas | BA | BA | [22 empty] | The Balancing Authority Area’s value of CPS1 is less than 100% but greater than or equal to 95%. | The Balancing Authority Area’s value of CPS1 is less than 95% but greater than or equal to 90%. | The Balancing Authority Area’s value of CPS1 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS1 is less than 85%. | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%.&lt;br/&gt;CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows:&lt;br/&gt;CPS1 = (2 - CF) * 100%&lt;br/&gt;The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound:&lt;br/&gt; &lt;br/&gt;&lt;br/&gt;where:1 is defined in Requirement R1.&lt;br/&gt;&lt;br/&gt;The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings.&lt;br/&gt;A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute.&lt;br/&gt; &lt;br/&gt;&lt;br/&gt; &lt;br/&gt;&lt;br/&gt;The Balancing Authority’s clock-minute compliance factor (CF) becomes:&lt;br/&gt;&lt;br/&gt; &lt;br/&gt;&lt;br/&gt;Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter.&lt;br/&gt; &lt;br/&gt;&lt;br/&gt;The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400).&lt;br/&gt; &lt;br/&gt;&lt;br/&gt; &lt;br/&gt;&lt;br/&gt;The 12-month compliance factor becomes:&lt;br/&gt; &lt;br/&gt;&lt;br/&gt;In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-001-0a (Ontario) | 79780000003 | R2. | 79780000010 | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. See standard for formula. | See Standard for Formulas | BA | BA | [22 empty] | The Balancing Authority Area’s value of CPS2 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS2 is less than 85% but greater than or equal to 80%. | The Balancing Authority Area’s value of CPS2 is less than 80% but greater than or equal to 75%. | The Balancing Authority Area’s value of CPS2 is less than 75%. | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE. A compliance percentage is calculated as follows:&lt;br/&gt; &lt;br/&gt;&lt;br/&gt;The violations per month are a count of the number of periods that ACE clock-ten-minutes exceeded L10. ACE clock-ten-minutes is the sum of valid ACE samples within a clock-ten-minute period divided by the number of valid samples.&lt;br/&gt;Violation clock-ten-minutes&lt;br/&gt; = 0 if&lt;br/&gt; &lt;br/&gt;&lt;br/&gt; = 1 if &lt;br/&gt; &lt;br/&gt;&lt;br/&gt;Each Balancing Authority shall report the total number of violations and unavailable periods for the month. L10 is defined in Requirement R2.&lt;br/&gt;Since CPS2 requires that ACE be averaged over a discrete time period, the same factors that limit total periods per month will limit violations per month. The calculation of total periods per month and violations per month, therefore, must be discussed jointly.&lt;br/&gt;A condition may arise which may impact the normal calculation of total periods per month and violations per month. This condition is a sustained interruption in the recording of ACE.&lt;br/&gt;In order to ensure that the average ACE calculated for any ten-minute interval is representative of that ten-minute interval, it is necessary that at least half the ACE data samples are present for that interval. Should half or more of the ACE data be unavailable due to loss of telemetering or computer unavailability, that ten-minute interval shall be omitted from the calculation of CPS2. | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-001-0a (Ontario) | 79780000003 | R3. | 79780000011 | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement M1 (i.e., Control Performance Standard 1 or CPS1) and Requirement M2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. |  | BA | BA | [25 empty] | The Balancing Authority providing Overlap Regulation Service failed to use a combined ACE and frequency bias. |  | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-001-0a (Ontario) | 79780000003 | R4. | 79780000012 | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). |  | BA | BA | [25 empty] | The Balancing Authority receiving Overlap Regulation Service failed to ensure that control performance was being evaluated in a manner consistent with the calculation methodology as described in BAL-001-01 R3. |  | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-001-0a (Saskatchewan) | 837500000003 | R1. | 837500000009 | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit ??? is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. See standard for equation. The equation for ACE is: ACE = (NIA - NIS) - 10B (FA - FS) - IME where: · NIA is the algebraic sum of actual flows on all tie lines. · NIS is the algebraic sum of scheduled flows on all tie lines. · B is the Frequency Bias Setting (MW/0.1 Hz) for the Balancing Authority. The constant factor 10 converts the frequency setting to MW/Hz. · FA is the actual frequency. · FS is the scheduled frequency. FS is normally 60 Hz but may be offset to effect manual time error corrections. IME is the meter error correction factor typically estimated from the difference between the integrated hourly average of the net tie line flows (NIA) and the hourly net interchange demand measurement (megawatt-hour). This term should normally be very small or zero. | See Standard for Formulas | BA | BA | [22 empty] | The Balancing Authority Area’s value of CPS1 is less than 100% but greater than or equal to 95%. | The Balancing Authority Area’s value of CPS1 is less than 95% but greater than or equal to 90%. | The Balancing Authority Area’s value of CPS1 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS1 is less than 85%. | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: where:1 is defined in Requirement R1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. |  |  | 2014-04-01 |  |  |  | MRO-SK | [6 empty] | 10000000
BAL-001-0a (Saskatchewan) | 837500000003 | R2. | 8375000000010 | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. See standard for formula. E10 is a constant derived from the targeted frequency bound. It is the targeted root-mean-square (RMS) value of ten-minute average Frequency Error based on frequency performance over a given year. The bound, e10, is the same for every Balancing Authority Area within an Interconnection, and Bs is the sum of the Frequency Bias Settings of the Balancing Authority Areas in the respective Interconnection. For Balancing Authority Areas with variable bias, this is equal to the sum of the minimum Frequency Bias Settings. | See Standard for Formulas | BA | BA | [22 empty] | The Balancing Authority Area’s value of CPS2 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS2 is less than 85% but greater than or equal to 80%. | The Balancing Authority Area’s value of CPS2 is less than 80% but greater than or equal to 75%. | The Balancing Authority Area’s value of CPS2 is less than 75%. | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE. A compliance percentage is calculated as follows: The violations per month are a count of the number of periods that ACE clock-ten-minutes exceeded L10. ACE clock-ten-minutes is the sum of valid ACE samples within a clock-ten-minute period divided by the number of valid samples. Violation clock-ten-minutes = 0 if = 1 if Each Balancing Authority shall report the total number of violations and unavailable periods for the month. L10 is defined in Requirement R2. Since CPS2 requires that ACE be averaged over a discrete time period, the same factors that limit total periods per month will limit violations per month. The calculation of total periods per month and violations per month, therefore, must be discussed jointly. A condition may arise which may impact the normal calculation of total periods per month and violations per month. This condition is a sustained interruption in the recording of ACE. In order to ensure that the average ACE calculated for any ten-minute interval is representative of that ten-minute interval, it is necessary that at least half the ACE data samples are present for that interval. Should half or more of the ACE data be unavailable due to loss of telemetering or computer unavailability, that ten-minute interval shall be omitted from the calculation of CPS2. |  |  | 2014-04-01 |  |  |  | MRO-SK | [6 empty] | 20000000
BAL-001-0a (Saskatchewan) | 837500000003 | R3. | 8375000000011 | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement M1 (i.e., Control Performance Standard 1 or CPS1) and Requirement M2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. |  | BA | BA | [25 empty] | The Balancing Authority providing Overlap Regulation Service failed to use a combined ACE and frequency bias. |  |  |  | 2014-04-01 |  |  |  | MRO-SK | [6 empty] | 30000000
BAL-001-0a (Saskatchewan) | 837500000003 | R4. | 8375000000012 | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). |  | BA | BA | [25 empty] | The Balancing Authority receiving Overlap Regulation Service failed to ensure that control performance was being evaluated in a manner consistent with the calculation methodology as described in BAL-001-01 R3. |  |  |  | 2014-04-01 |  |  |  | MRO-SK | [6 empty] | 40000000
BAL-001-0 (Manitoba) | 776600000001 | R1. | 776600000001 | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. See Standard for Formula. The equation for ACE is: ACE = (NIA - NIS) - 10B (FA - FS) - IME where: · NIA is the algebraic sum of actual flows on all tie lines. · NIS is the algebraic sum of scheduled flows on all tie lines. · B is the Frequency Bias Setting (MW/0.1 Hz) for the Balancing Authority. The constant factor 10 converts the frequency setting to MW/Hz. · FA is the actual frequency. · FS is the scheduled frequency. FS is normally 60 Hz but may be offset to effect manual time error corrections. IME is the meter error correction factor typically estimated from the difference between the integrated hourly average of the net tie line flows (NIA) and the hourly net interchange demand measurement (megawatt-hour). This term should normally be very small or zero. |  | BA | BA | [21 empty] | Low | The Balancing Authority Area’s value of CPS1 is less than 100% but greater than or equal to 95%. | The Balancing Authority Area’s value of CPS1 is less than 95% but greater than or equal to 90%. | The Balancing Authority Area’s value of CPS1 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS1 is less than 85%. | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%. See Standard for Formula | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 10000000
BAL-001-0 (Manitoba) | 776600000001 | R2. | 776600000002 | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. See Standard for Formula. |  | BA | BA | [21 empty] | Low | The Balancing Authority Area’s value of CPS2 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS2 is less than 85% but greater than or equal to 80%. | The Balancing Authority Area’s value of CPS2 is less than 80% but greater than or equal to 75%. | The Balancing Authority Area’s value of CPS2 is less than 75%. | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE A compliance percentage is calculated as follows: See Standard for formula | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 20000000
BAL-001-0 (Manitoba) | 776600000001 | R3. | 776600000003 | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement R1 (i.e., Control Performance Standard 1 or CPS1) and Requirement R2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority providing Overlap Regulation Service failed to use a combined ACE and frequency bias. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 30000000
BAL-001-0 (Manitoba) | 776600000001 | R4. | 776600000004 | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). |  | BA | BA | [21 empty] | Low | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 40000000
BAL-001-0 (Ontario) | 79780000001 | R1. | 79780000001 | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. See Standard for Formula.&lt;br/&gt;&lt;br/&gt;1.1 testing 1&lt;br/&gt;1.2 testing 2&lt;br/&gt;1.2 testing 3 |  | BA | BA | [21 empty] | Low | The Balancing Authority Area’s value of CPS1 is less than 100% but greater than or equal to 95%. | The Balancing Authority Area’s value of CPS1 is less than 95% but greater than or equal to 90%. | The Balancing Authority Area’s value of CPS1 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS1 is less than 85%. | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%. See Standard for Formula | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-001-0 (Ontario) | 79780000001 | R2. | 79780000002 | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. See Standard for Formula. |  | BA | BA | [21 empty] | Low | The Balancing Authority Area’s value of CPS2 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS2 is less than 85% but greater than or equal to 80%. | The Balancing Authority Area’s value of CPS2 is less than 80% but greater than or equal to 75%. | The Balancing Authority Area’s value of CPS2 is less than 75%. | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE A compliance percentage is calculated as follows: See Standard for formula | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-001-0 (Ontario) | 79780000001 | R3. | 79780000003 | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement R1 (i.e., Control Performance Standard 1 or CPS1) and Requirement R2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority providing Overlap Regulation Service failed to use a combined ACE and frequency bias. |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-001-0 (Ontario) | 79780000001 | R4. | 79780000004 | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). |  | BA | BA | [21 empty] | Low | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-001-1 | 356 | E.B.1. | 4516 | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit e-1-2 is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee.(please see standard for formulas) |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority Area’s value of CPS1 was less than 100% but greater than or equal to 95%. | The Balancing Authority Area’s value of CPS1 was less than 95% but greater than or equal to 90%. | The Balancing Authority Area’s value of CPS1 was less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS1 was less than 85%. | M.E.B.1. Each Balancing Authority shall achieve, as a minimum, Requirement E.B.1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: where:1 is defined in Requirement E.B.1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. | 2014-04-01 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 100000
BAL-001-1 | 356 | E.B.2. | 4517 | Each Balancing Authority shall limit the absolute value of I-ATEC, the Automatic Time Error Correction term as follows:(please see standard for formula) |  | BA | BA | [20 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Balancing Authority Area’s absolute value for IATEC was greater than L-max | M.E.B.2. Forms of acceptable evidence for Requirement E.B.2 may include, but are not limited to: • Dated Energy Management System (EMS) displays, • WECC Interchange Tool, EMS application code, or • Other archived data that demonstrates compliance. | 2014-04-01 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 200000
BAL-001-1 | 356 | E.B.3. | 4518 | Each Balancing Authority shall set L-max within the limits as follows:(please see standard for formula) |  | BA | BA | [20 empty] | Operations Planning | Medium | N/A | N/A | N/A | The Balancing Authority did not set L-max to within the limits in E.B.3 (please see standard for formula) | M.E.B.3. Forms of acceptable evidence for Requirement E.B.3 may include, but is not limited to: • Dated Energy Management System (EMS) displays, • WECC Interchange Tool, EMS application code, or • Other archived data that demonstrates compliance. | 2014-04-01 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 300000
BAL-001-1 | 356 | R1. | 4512 | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit ??? is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. (See standard for formulas) The equation for ACE is: ACE = (NIA − NIS) − 10B (FA − FS) − IME where: • NIA is the algebraic sum of actual flows on all tie lines. • NIS is the algebraic sum of scheduled flows on all tie lines. • B is the Frequency Bias Setting (MW/0.1 Hz) for the Balancing Authority. The constant factor 10 converts the frequency setting to MW/Hz. • FA is the actual frequency. • FS is the scheduled frequency. FS is normally 60 Hz but may be offset to effect manual time error corrections. • IME is the meter error correction factor typically estimated from the difference between the integrated hourly average of the net tie line flows (NIA) and the hourly net interchange demand measurement (megawatt-hour). This term should normally be very small or zero. |  | BA | BA | [21 empty] | Medium |  |  |  |  | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: (See standard for formula) where:E1 is defined in Requirement R1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. (See standard for formulas) The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. | 2014-04-01 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-001-1 | 356 | R2. | 4513 | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. (See standard for formulas) ?10 is a constant derived from the targeted frequency bound. It is the targeted root-mean-square (RMS) value of ten-minute average Frequency Error based on frequency performance over a given year. The bound, ?10, is the same for every Balancing Authority Area within an Interconnection, and Bs is the sum of the Frequency Bias Settings of the Balancing Authority Areas in the respective Interconnection. For Balancing Authority Areas with variable bias, this is equal to the sum of the minimum Frequency Bias Settings. |  | BA | BA | [21 empty] | Medium |  |  |  |  | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE. A compliance percentage is calculated as follows: (See standard for formulas) The violations per month are a count of the number of periods that ACE clock-ten-minutes exceeded L10. ACE clock-ten-minutes is the sum of valid ACE samples within a clock-ten-minute period divided by the number of valid samples. Violation clock-ten-minutes = 0 if = 1 if Each Balancing Authority shall report the total number of violations and unavailable periods for the month. L10 is defined in Requirement R2. Since CPS2 requires that ACE be averaged over a discrete time period, the same factors that limit total periods per month will limit violations per month. The calculation of total periods per month and violations per month, therefore, must be discussed jointly. A condition may arise which may impact the normal calculation of total periods per month and violations per month. This condition is a sustained interruption in the recording of ACE. In order to ensure that the average ACE calculated for any ten-minute interval is representative of that ten-minute interval, it is necessary that at least half the ACE data samples are present for that interval. Should half or more of the ACE data be unavailable due to loss of telemetering or computer unavailability, that ten-minute interval shall be omitted from the calculation of CPS2. | 2014-04-01 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-001-1 | 356 | R3. | 4514 | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement R1 (i.e., Control Performance Standard 1 or CPS1) and Requirement R2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. |  | BA | BA | [21 empty] | Low | [5 empty] | 2014-04-01 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-001-1 | 356 | R4. | 4515 | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). |  | BA | BA | [21 empty] | Low | [5 empty] | 2014-04-01 |  | 2016-06-30 |  |  | BAL-001-1 R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-001-1 (British Columbia) | 666700000010002 | E.B.1. | 666700000010345 | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit e-1-2 is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee.(please see standard for formulas) |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority Area’s value of CPS1 was less than 100% but greater than or equal to 95%. | The Balancing Authority Area’s value of CPS1 was less than 95% but greater than or equal to 90%. | The Balancing Authority Area’s value of CPS1 was less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS1 was less than 85%. | M.E.B.1. Each Balancing Authority shall achieve, as a minimum, Requirement E.B.1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: where:1 is defined in Requirement E.B.1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. | 2014-10-01 |  | 2016-06-30 |  |  |  | WECC-BC | [6 empty] | 100000
BAL-001-1 (British Columbia) | 666700000010002 | E.B.2. | 666700000010346 | Each Balancing Authority shall limit the absolute value of I-ATEC, the Automatic Time Error Correction term as follows:(please see standard for formula) |  | BA | BA | [20 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Balancing Authority Area’s absolute value for IATEC was greater than L-max | M.E.B.2. Forms of acceptable evidence for Requirement E.B.2 may include, but are not limited to: • Dated Energy Management System (EMS) displays, • WECC Interchange Tool, EMS application code, or • Other archived data that demonstrates compliance. | 2014-10-01 |  | 2016-06-30 |  |  |  | WECC-BC | [6 empty] | 200000
BAL-001-1 (British Columbia) | 666700000010002 | E.B.3. | 666700000010347 | Each Balancing Authority shall set L-max within the limits as follows:(please see standard for formula) |  | BA | BA | [20 empty] | Operations Planning | Medium | N/A | N/A | N/A | The Balancing Authority did not set L-max to within the limits in E.B.3 (please see standard for formula) | M.E.B.3. Forms of acceptable evidence for Requirement E.B.3 may include, but is not limited to: • Dated Energy Management System (EMS) displays, • WECC Interchange Tool, EMS application code, or • Other archived data that demonstrates compliance. | 2014-10-01 |  | 2016-06-30 |  |  |  | WECC-BC | [6 empty] | 300000
BAL-001-1 (British Columbia) | 666700000010002 | R1. | 666700000010348 | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit ??? is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. (See standard for formulas) The equation for ACE is: ACE = (NIA − NIS) − 10B (FA − FS) − IME where: • NIA is the algebraic sum of actual flows on all tie lines. • NIS is the algebraic sum of scheduled flows on all tie lines. • B is the Frequency Bias Setting (MW/0.1 Hz) for the Balancing Authority. The constant factor 10 converts the frequency setting to MW/Hz. • FA is the actual frequency. • FS is the scheduled frequency. FS is normally 60 Hz but may be offset to effect manual time error corrections. • IME is the meter error correction factor typically estimated from the difference between the integrated hourly average of the net tie line flows (NIA) and the hourly net interchange demand measurement (megawatt-hour). This term should normally be very small or zero. |  | BA | BA | [21 empty] | Medium |  |  |  |  | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: (See standard for formula) where:E1 is defined in Requirement R1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. (See standard for formulas) The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. | 2014-10-01 |  | 2016-06-30 |  |  |  | WECC-BC | [6 empty] | 10000000
BAL-001-1 (British Columbia) | 666700000010002 | R2. | 666700000010349 | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. (See standard for formulas) ?10 is a constant derived from the targeted frequency bound. It is the targeted root-mean-square (RMS) value of ten-minute average Frequency Error based on frequency performance over a given year. The bound, ?10, is the same for every Balancing Authority Area within an Interconnection, and Bs is the sum of the Frequency Bias Settings of the Balancing Authority Areas in the respective Interconnection. For Balancing Authority Areas with variable bias, this is equal to the sum of the minimum Frequency Bias Settings. |  | BA | BA | [21 empty] | Medium |  |  |  |  | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE. A compliance percentage is calculated as follows: (See standard for formulas) The violations per month are a count of the number of periods that ACE clock-ten-minutes exceeded L10. ACE clock-ten-minutes is the sum of valid ACE samples within a clock-ten-minute period divided by the number of valid samples. Violation clock-ten-minutes = 0 if = 1 if Each Balancing Authority shall report the total number of violations and unavailable periods for the month. L10 is defined in Requirement R2. Since CPS2 requires that ACE be averaged over a discrete time period, the same factors that limit total periods per month will limit violations per month. The calculation of total periods per month and violations per month, therefore, must be discussed jointly. A condition may arise which may impact the normal calculation of total periods per month and violations per month. This condition is a sustained interruption in the recording of ACE. In order to ensure that the average ACE calculated for any ten-minute interval is representative of that ten-minute interval, it is necessary that at least half the ACE data samples are present for that interval. Should half or more of the ACE data be unavailable due to loss of telemetering or computer unavailability, that ten-minute interval shall be omitted from the calculation of CPS2. | 2014-10-01 |  | 2016-06-30 |  |  |  | WECC-BC | [6 empty] | 20000000
BAL-001-1 (British Columbia) | 666700000010002 | R3. | 666700000010350 | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement R1 (i.e., Control Performance Standard 1 or CPS1) and Requirement R2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. |  | BA | BA | [21 empty] | Low | [5 empty] | 2014-10-01 |  | 2016-06-30 |  |  |  | WECC-BC | [6 empty] | 30000000
BAL-001-1 (British Columbia) | 666700000010002 | R4. | 666700000010351 | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). |  | BA | BA | [21 empty] | Low | [5 empty] | 2014-10-01 |  | 2016-06-30 |  |  |  | WECC-BC | [6 empty] | 40000000
BAL-001-1 (Manitoba) | 77660000000356 | E.B.1. | 776600000004516 | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit e-1-2 is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee.(please see standard for formulas) |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority Area’s value of CPS1 was less than 100% but greater than or equal to 95%. | The Balancing Authority Area’s value of CPS1 was less than 95% but greater than or equal to 90%. | The Balancing Authority Area’s value of CPS1 was less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS1 was less than 85%. | M.E.B.1. Each Balancing Authority shall achieve, as a minimum, Requirement E.B.1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: where:1 is defined in Requirement E.B.1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. | 2016-07-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 100000
BAL-001-1 (Manitoba) | 77660000000356 | E.B.2. | 776600000004517 | Each Balancing Authority shall limit the absolute value of I-ATEC, the Automatic Time Error Correction term as follows:(please see standard for formula) |  | BA | BA | [20 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Balancing Authority Area’s absolute value for IATEC was greater than L-max | M.E.B.2. Forms of acceptable evidence for Requirement E.B.2 may include, but are not limited to: • Dated Energy Management System (EMS) displays, • WECC Interchange Tool, EMS application code, or • Other archived data that demonstrates compliance. | 2016-07-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 200000
BAL-001-1 (Manitoba) | 77660000000356 | E.B.3. | 776600000004518 | Each Balancing Authority shall set L-max within the limits as follows:(please see standard for formula) |  | BA | BA | [20 empty] | Operations Planning | Medium | N/A | N/A | N/A | The Balancing Authority did not set L-max to within the limits in E.B.3 (please see standard for formula) | M.E.B.3. Forms of acceptable evidence for Requirement E.B.3 may include, but is not limited to: • Dated Energy Management System (EMS) displays, • WECC Interchange Tool, EMS application code, or • Other archived data that demonstrates compliance. | 2016-07-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 300000
BAL-001-1 (Manitoba) | 77660000000356 | R1. | 776600000004512 | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit ??? is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. (See standard for formulas) The equation for ACE is: ACE = (NIA − NIS) − 10B (FA − FS) − IME where: • NIA is the algebraic sum of actual flows on all tie lines. • NIS is the algebraic sum of scheduled flows on all tie lines. • B is the Frequency Bias Setting (MW/0.1 Hz) for the Balancing Authority. The constant factor 10 converts the frequency setting to MW/Hz. • FA is the actual frequency. • FS is the scheduled frequency. FS is normally 60 Hz but may be offset to effect manual time error corrections. • IME is the meter error correction factor typically estimated from the difference between the integrated hourly average of the net tie line flows (NIA) and the hourly net interchange demand measurement (megawatt-hour). This term should normally be very small or zero. |  | BA | BA | [21 empty] | Medium |  |  |  |  | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: (See standard for formula) where:E1 is defined in Requirement R1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. (See standard for formulas) The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. | 2016-07-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
BAL-001-1 (Manitoba) | 77660000000356 | R2. | 776600000004513 | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. (See standard for formulas) ?10 is a constant derived from the targeted frequency bound. It is the targeted root-mean-square (RMS) value of ten-minute average Frequency Error based on frequency performance over a given year. The bound, ?10, is the same for every Balancing Authority Area within an Interconnection, and Bs is the sum of the Frequency Bias Settings of the Balancing Authority Areas in the respective Interconnection. For Balancing Authority Areas with variable bias, this is equal to the sum of the minimum Frequency Bias Settings. |  | BA | BA | [21 empty] | Medium |  |  |  |  | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE. A compliance percentage is calculated as follows: (See standard for formulas) The violations per month are a count of the number of periods that ACE clock-ten-minutes exceeded L10. ACE clock-ten-minutes is the sum of valid ACE samples within a clock-ten-minute period divided by the number of valid samples. Violation clock-ten-minutes = 0 if = 1 if Each Balancing Authority shall report the total number of violations and unavailable periods for the month. L10 is defined in Requirement R2. Since CPS2 requires that ACE be averaged over a discrete time period, the same factors that limit total periods per month will limit violations per month. The calculation of total periods per month and violations per month, therefore, must be discussed jointly. A condition may arise which may impact the normal calculation of total periods per month and violations per month. This condition is a sustained interruption in the recording of ACE. In order to ensure that the average ACE calculated for any ten-minute interval is representative of that ten-minute interval, it is necessary that at least half the ACE data samples are present for that interval. Should half or more of the ACE data be unavailable due to loss of telemetering or computer unavailability, that ten-minute interval shall be omitted from the calculation of CPS2. | 2016-07-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
BAL-001-1 (Manitoba) | 77660000000356 | R3. | 776600000004514 | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement R1 (i.e., Control Performance Standard 1 or CPS1) and Requirement R2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. |  | BA | BA | [21 empty] | Low | [5 empty] | 2016-07-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
BAL-001-1 (Manitoba) | 77660000000356 | R4. | 776600000004515 | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). |  | BA | BA | [21 empty] | Low | [5 empty] | 2016-07-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 40000000
BAL-001-1 (Ontario) | 79780000356 | R1. | 79780004512 | &lt;p&gt;Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit ??? is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. (See standard for formulas)&lt;/p&gt; &lt;p&gt;The equation for ACE is: ACE = (NIA − NIS) − 10B (FA − FS) − IME where: • NIA is the algebraic sum of actual flows on all tie lines. • NIS is the algebraic sum of scheduled flows on all tie lines. • B is the Frequency Bias Setting (MW/0.1 Hz) for the Balancing Authority. The constant factor 10 converts the frequency setting to MW/Hz. • FA is the actual frequency. • FS is the scheduled frequency. FS is normally 60 Hz but may be offset to effect manual time error corrections. • IME is the meter error correction factor typically estimated from the difference between the integrated hourly average of the net tie line flows (NIA) and the hourly net interchange demand measurement (megawatt-hour). This term should normally be very small or zero.&lt;/p&gt; |  | BA | BA | [21 empty] | Medium |  |  |  |  | &lt;p&gt;M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%.&lt;br/&gt;CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows:&lt;br/&gt;CPS1 = (2 - CF) * 100%&lt;br/&gt;The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound:&lt;/p&gt; &lt;p&gt;(See standard for formula)&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;where:E1 is defined in Requirement R1.&lt;br/&gt;&lt;br/&gt;The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings.&lt;br/&gt;A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. (See standard for formulas)&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;The Balancing Authority’s clock-minute compliance factor (CF) becomes:&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter.&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400).&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;The 12-month compliance factor becomes:&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1.&lt;/p&gt; | 2014-04-01 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-001-1 (Ontario) | 79780000356 | R2. | 79780004513 | &lt;p&gt;Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. (See standard for formulas)&lt;/p&gt; &lt;p&gt;?10 is a constant derived from the targeted frequency bound. It is the targeted root-mean-square (RMS) value of ten-minute average Frequency Error based on frequency performance over a given year. The bound, ?10, is the same for every Balancing Authority Area within an Interconnection, and Bs is the sum of the Frequency Bias Settings of the Balancing Authority Areas in the respective Interconnection. For Balancing Authority Areas with variable bias, this is equal to the sum of the minimum Frequency Bias Settings.&lt;/p&gt; |  | BA | BA | [21 empty] | Medium |  |  |  |  | &lt;p&gt;M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE. A compliance percentage is calculated as follows: (See standard for formulas)&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;The violations per month are a count of the number of periods that ACE clock-ten-minutes exceeded L10. ACE clock-ten-minutes is the sum of valid ACE samples within a clock-ten-minute period divided by the number of valid samples.&lt;br/&gt;Violation clock-ten-minutes&lt;br/&gt;= 0 if&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;= 1 if &lt;br/&gt;&lt;br/&gt;&lt;br/&gt;Each Balancing Authority shall report the total number of violations and unavailable periods for the month. L10 is defined in Requirement R2.&lt;br/&gt;Since CPS2 requires that ACE be averaged over a discrete time period, the same factors that limit total periods per month will limit violations per month. The calculation of total periods per month and violations per month, therefore, must be discussed jointly.&lt;br/&gt;A condition may arise which may impact the normal calculation of total periods per month and violations per month. This condition is a sustained interruption in the recording of ACE.&lt;br/&gt;In order to ensure that the average ACE calculated for any ten-minute interval is representative of that ten-minute interval, it is necessary that at least half the ACE data samples are present for that interval. Should half or more of the ACE data be unavailable due to loss of telemetering or computer unavailability, that ten-minute interval shall be omitted from the calculation of CPS2.&lt;/p&gt; | 2014-04-01 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-001-1 (Ontario) | 79780000356 | R3. | 79780004514 | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement R1 (i.e., Control Performance Standard 1 or CPS1) and Requirement R2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. |  | BA | BA | [21 empty] | Low | [5 empty] | 2014-04-01 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-001-1 (Ontario) | 79780000356 | R4. | 79780004515 | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). |  | BA | BA | [21 empty] | Low | [5 empty] | 2014-04-01 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-001-1 (Saskatchewan) | 83750000000356 | E.B.1. | 837500000004516 | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit e-1-2 is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee.(please see standard for formulas) |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority Area’s value of CPS1 was less than 100% but greater than or equal to 95%. | The Balancing Authority Area’s value of CPS1 was less than 95% but greater than or equal to 90%. | The Balancing Authority Area’s value of CPS1 was less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS1 was less than 85%. | M.E.B.1. Each Balancing Authority shall achieve, as a minimum, Requirement E.B.1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: where:1 is defined in Requirement E.B.1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. | 2014-04-01 |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 100000
BAL-001-1 (Saskatchewan) | 83750000000356 | E.B.2. | 837500000004517 | Each Balancing Authority shall limit the absolute value of I-ATEC, the Automatic Time Error Correction term as follows:(please see standard for formula) |  | BA | BA | [20 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Balancing Authority Area’s absolute value for IATEC was greater than L-max | M.E.B.2. Forms of acceptable evidence for Requirement E.B.2 may include, but are not limited to: • Dated Energy Management System (EMS) displays, • WECC Interchange Tool, EMS application code, or • Other archived data that demonstrates compliance. | 2014-04-01 |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 200000
BAL-001-1 (Saskatchewan) | 83750000000356 | E.B.3. | 837500000004518 | Each Balancing Authority shall set L-max within the limits as follows:(please see standard for formula) |  | BA | BA | [20 empty] | Operations Planning | Medium | N/A | N/A | N/A | The Balancing Authority did not set L-max to within the limits in E.B.3 (please see standard for formula) | M.E.B.3. Forms of acceptable evidence for Requirement E.B.3 may include, but is not limited to: • Dated Energy Management System (EMS) displays, • WECC Interchange Tool, EMS application code, or • Other archived data that demonstrates compliance. | 2014-04-01 |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 300000
BAL-001-1 (Saskatchewan) | 83750000000356 | R1. | 837500000004512 | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit ??? is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. (See standard for formulas) The equation for ACE is: ACE = (NIA − NIS) − 10B (FA − FS) − IME where: • NIA is the algebraic sum of actual flows on all tie lines. • NIS is the algebraic sum of scheduled flows on all tie lines. • B is the Frequency Bias Setting (MW/0.1 Hz) for the Balancing Authority. The constant factor 10 converts the frequency setting to MW/Hz. • FA is the actual frequency. • FS is the scheduled frequency. FS is normally 60 Hz but may be offset to effect manual time error corrections. • IME is the meter error correction factor typically estimated from the difference between the integrated hourly average of the net tie line flows (NIA) and the hourly net interchange demand measurement (megawatt-hour). This term should normally be very small or zero. |  | BA | BA | [21 empty] | Medium |  |  |  |  | M1. Each Balancing Authority shall achieve, as a minimum, Requirement 1 (CPS1) compliance of 100%. CPS1 is calculated by converting a compliance ratio to a compliance percentage as follows: CPS1 = (2 - CF) * 100% The frequency-related compliance factor, CF, is a ratio of all one-minute compliance parameters accumulated over 12 months divided by the target frequency bound: (See standard for formula) where:E1 is defined in Requirement R1. The rating index CF12-month is derived from 12 months of data. The basic unit of data comes from one-minute averages of ACE, Frequency Error and Frequency Bias Settings. A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e., for ACE and for Frequency Error) for each sampling cycle during a given clock-minute. (See standard for formulas) The Balancing Authority’s clock-minute compliance factor (CF) becomes: Normally, sixty (60) clock-minute averages of the reporting Balancing Authority’s ACE and of the respective Interconnection’s Frequency Error will be used to compute the respective hourly average compliance parameter. The reporting Balancing Authority shall be able to recalculate and store each of the respective clock-hour averages (CF clock-hour average-month) as well as the respective number of samples for each of the twenty-four (24) hours (one for each clock-hour, i.e., hour-ending (HE) 0100, HE 0200, ..., HE 2400). The 12-month compliance factor becomes: In order to ensure that the average ACE and Frequency Deviation calculated for any one-minute interval is representative of that one-minute interval, it is necessary that at least 50% of both ACE and Frequency Deviation samples during that one-minute interval be present. Should a sustained interruption in the recording of ACE or Frequency Deviation due to loss of telemetering or computer unavailability result in a one-minute interval not containing at least 50% of samples of both ACE and Frequency Deviation, that one-minute interval shall be excluded from the calculation of CPS1. | 2014-04-01 |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 10000000
BAL-001-1 (Saskatchewan) | 83750000000356 | R2. | 837500000004513 | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. (See standard for formulas) ?10 is a constant derived from the targeted frequency bound. It is the targeted root-mean-square (RMS) value of ten-minute average Frequency Error based on frequency performance over a given year. The bound, ?10, is the same for every Balancing Authority Area within an Interconnection, and Bs is the sum of the Frequency Bias Settings of the Balancing Authority Areas in the respective Interconnection. For Balancing Authority Areas with variable bias, this is equal to the sum of the minimum Frequency Bias Settings. |  | BA | BA | [21 empty] | Medium |  |  |  |  | M2. Each Balancing Authority shall achieve, as a minimum, Requirement R2 (CPS2) compliance of 90%. CPS2 relates to a bound on the ten-minute average of ACE. A compliance percentage is calculated as follows: (See standard for formulas) The violations per month are a count of the number of periods that ACE clock-ten-minutes exceeded L10. ACE clock-ten-minutes is the sum of valid ACE samples within a clock-ten-minute period divided by the number of valid samples. Violation clock-ten-minutes = 0 if = 1 if Each Balancing Authority shall report the total number of violations and unavailable periods for the month. L10 is defined in Requirement R2. Since CPS2 requires that ACE be averaged over a discrete time period, the same factors that limit total periods per month will limit violations per month. The calculation of total periods per month and violations per month, therefore, must be discussed jointly. A condition may arise which may impact the normal calculation of total periods per month and violations per month. This condition is a sustained interruption in the recording of ACE. In order to ensure that the average ACE calculated for any ten-minute interval is representative of that ten-minute interval, it is necessary that at least half the ACE data samples are present for that interval. Should half or more of the ACE data be unavailable due to loss of telemetering or computer unavailability, that ten-minute interval shall be omitted from the calculation of CPS2. | 2014-04-01 |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 20000000
BAL-001-1 (Saskatchewan) | 83750000000356 | R3. | 837500000004514 | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement R1 (i.e., Control Performance Standard 1 or CPS1) and Requirement R2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. |  | BA | BA | [21 empty] | Low | [5 empty] | 2014-04-01 |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 30000000
BAL-001-1 (Saskatchewan) | 83750000000356 | R4. | 837500000004515 | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). |  | BA | BA | [21 empty] | Low | [5 empty] | 2014-04-01 |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 40000000
BAL-001-2 | 378 | R1. | 4781 | The Responsible Entity shall operate such that the Control Performance Standard 1 (CPS1), calculated in accordance with Attachment 1, is greater than or equal to 100 percent for the applicable Interconnection in which it operates for each preceding 12 consecutive calendar month period, evaluated monthly. |  | BA, RRSG | BA | [14 empty] | RRSG | [5 empty] | Real-Time Operations | Medium | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 100 percent but greater than or equal to 95 percent for the applicable Interconnection. | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 95 percent, but greater than or equal to 90 percent for the applicable Interconnection. | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 90 percent, but greater than or equal to 85 percent for the applicable Interconnection. | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 85 percent for the applicable Interconnection. | M1. The Responsible Entity shall provide evidence, upon request, such as dated calculation output from spreadsheets, system logs, software programs, or other evidence (either in hard copy or electronic format) to demonstrate compliance with Requirement R1. | 2016-07-01 |  |  |  | 4.1.1 A Balancing Authority receiving Overlap Regulation Service is not subject to Control Performance Standard 1 (CPS1) or Balancing Authority ACE Limit (BAAL) compliance evaluation. 4.1.2 A Balancing Authority that is a member of a Regulation Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or the governing rules for the Regulation Reserve Sharing Group. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-001-2 | 378 | R2. | 4782 | Each Balancing Authority shall operate such that its clock-minute average of Reporting ACE does not exceed its clock-minute Balancing Authority ACE Limit (BAAL) for more than 30 consecutive clock-minutes, calculated in accordance with Attachment 2, for the applicable Interconnection in which the Balancing Authority operates. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority exceeded its clock-minute BAAL for more than 30 consecutive clock minutes but for 45 consecutive clock-minutes or less for the applicable Interconnection. | The Balancing Authority exceeded its clock-minute BAAL for greater than 45 consecutive clock minutes but for 60 consecutive clock-minutes or less for the applicable Interconnection. | The Balancing Authority exceeded its clock-minute BAAL for greater than 60 consecutive clock minutes but for 75 consecutive clock-minutes or less for the applicable Interconnection. | The Balancing Authority exceeded its clock-minute BAAL for greater than 75 consecutive clock-minutes for the applicable Interconnection. | M2. Each Balancing Authority shall provide evidence, upon request, such as dated calculation output from spreadsheets, system logs, software programs, or other evidence (either in hard copy or electronic format) to demonstrate compliance with Requirement R2. | 2016-07-01 |  |  |  | 4.1.1 A Balancing Authority receiving Overlap Regulation Service is not subject to Control Performance Standard 1 (CPS1) or Balancing Authority ACE Limit (BAAL) compliance evaluation. 4.1.2 A Balancing Authority that is a member of a Regulation Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or the governing rules for the Regulation Reserve Sharing Group. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-001-2 (British Columbia) | 666700000010003 | R1. | 666700000010352 | The Responsible Entity shall operate such that the Control Performance Standard 1 (CPS1), calculated in accordance with Attachment 1, is greater than or equal to 100 percent for the applicable Interconnection in which it operates for each preceding 12 consecutive calendar month period, evaluated monthly. |  | BA, RRSG | BA | [14 empty] | RRSG | [5 empty] | Real-Time Operations | Medium | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 100 percent but greater than or equal to 95 percent for the applicable Interconnection. | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 95 percent, but greater than or equal to 90 percent for the applicable Interconnection. | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 90 percent, but greater than or equal to 85 percent for the applicable Interconnection. | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 85 percent for the applicable Interconnection. | M1. The Responsible Entity shall provide evidence, upon request, such as dated calculation output from spreadsheets, system logs, software programs, or other evidence (either in hard copy or electronic format) to demonstrate compliance with Requirement R1. | 2016-07-01 |  |  |  | 4.1.1 A Balancing Authority receiving Overlap Regulation Service is not subject to Control Performance Standard 1 (CPS1) or Balancing Authority ACE Limit (BAAL) compliance evaluation. 4.1.2 A Balancing Authority that is a member of a Regulation Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or the governing rules for the Regulation Reserve Sharing Group. |  | WECC-BC | [6 empty] | 10000000
BAL-001-2 (British Columbia) | 666700000010003 | R2. | 666700000010353 | Each Balancing Authority shall operate such that its clock-minute average of Reporting ACE does not exceed its clock-minute Balancing Authority ACE Limit (BAAL) for more than 30 consecutive clock-minutes, calculated in accordance with Attachment 2, for the applicable Interconnection in which the Balancing Authority operates. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority exceeded its clock-minute BAAL for more than 30 consecutive clock minutes but for 45 consecutive clock-minutes or less for the applicable Interconnection. | The Balancing Authority exceeded its clock-minute BAAL for greater than 45 consecutive clock minutes but for 60 consecutive clock-minutes or less for the applicable Interconnection. | The Balancing Authority exceeded its clock-minute BAAL for greater than 60 consecutive clock minutes but for 75 consecutive clock-minutes or less for the applicable Interconnection. | The Balancing Authority exceeded its clock-minute BAAL for greater than 75 consecutive clock-minutes for the applicable Interconnection. | M2. Each Balancing Authority shall provide evidence, upon request, such as dated calculation output from spreadsheets, system logs, software programs, or other evidence (either in hard copy or electronic format) to demonstrate compliance with Requirement R2. | 2016-07-01 |  |  |  | 4.1.1 A Balancing Authority receiving Overlap Regulation Service is not subject to Control Performance Standard 1 (CPS1) or Balancing Authority ACE Limit (BAAL) compliance evaluation. 4.1.2 A Balancing Authority that is a member of a Regulation Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or the governing rules for the Regulation Reserve Sharing Group. |  | WECC-BC | [6 empty] | 20000000
BAL-001-2 (Manitoba) | 77660000000378 | R1. | 776600000004781 | The Responsible Entity shall operate such that the Control Performance Standard 1 (CPS1), calculated in accordance with Attachment 1, is greater than or equal to 100 percent for the applicable Interconnection in which it operates for each preceding 12 consecutive calendar month period, evaluated monthly. |  | BA, RRSG | BA | [14 empty] | RRSG | [5 empty] | Real-Time Operations | Medium | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 100 percent but greater than or equal to 95 percent for the applicable Interconnection. | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 95 percent, but greater than or equal to 90 percent for the applicable Interconnection. | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 90 percent, but greater than or equal to 85 percent for the applicable Interconnection. | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 85 percent for the applicable Interconnection. | M1. The Responsible Entity shall provide evidence, upon request, such as dated calculation output from spreadsheets, system logs, software programs, or other evidence (either in hard copy or electronic format) to demonstrate compliance with Requirement R1. | 2017-07-01 |  |  |  | 4.1.1 A Balancing Authority receiving Overlap Regulation Service is not subject to Control Performance Standard 1 (CPS1) or Balancing Authority ACE Limit (BAAL) compliance evaluation. 4.1.2 A Balancing Authority that is a member of a Regulation Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or the governing rules for the Regulation Reserve Sharing Group. |  | MRO-MB | [6 empty] | 10000000
BAL-001-2 (Manitoba) | 77660000000378 | R2. | 776600000004782 | Each Balancing Authority shall operate such that its clock-minute average of Reporting ACE does not exceed its clock-minute Balancing Authority ACE Limit (BAAL) for more than 30 consecutive clock-minutes, calculated in accordance with Attachment 2, for the applicable Interconnection in which the Balancing Authority operates. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority exceeded its clock-minute BAAL for more than 30 consecutive clock minutes but for 45 consecutive clock-minutes or less for the applicable Interconnection. | The Balancing Authority exceeded its clock-minute BAAL for greater than 45 consecutive clock minutes but for 60 consecutive clock-minutes or less for the applicable Interconnection. | The Balancing Authority exceeded its clock-minute BAAL for greater than 60 consecutive clock minutes but for 75 consecutive clock-minutes or less for the applicable Interconnection. | The Balancing Authority exceeded its clock-minute BAAL for greater than 75 consecutive clock-minutes for the applicable Interconnection. | M2. Each Balancing Authority shall provide evidence, upon request, such as dated calculation output from spreadsheets, system logs, software programs, or other evidence (either in hard copy or electronic format) to demonstrate compliance with Requirement R2. | 2017-07-01 |  |  |  | 4.1.1 A Balancing Authority receiving Overlap Regulation Service is not subject to Control Performance Standard 1 (CPS1) or Balancing Authority ACE Limit (BAAL) compliance evaluation. 4.1.2 A Balancing Authority that is a member of a Regulation Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or the governing rules for the Regulation Reserve Sharing Group. |  | MRO-MB | [6 empty] | 20000000
BAL-001-2 (Nova Scotia) | 78830000000378 | R1. | 788300000004781 | The Responsible Entity shall operate such that the Control Performance Standard 1 (CPS1), calculated in accordance with Attachment 1, is greater than or equal to 100 percent for the applicable Interconnection in which it operates for each preceding 12 consecutive calendar month period, evaluated monthly. |  | BA, RRSG | BA | [14 empty] | RRSG | [5 empty] | Real-Time Operations | Medium | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 100 percent but greater than or equal to 95 percent for the applicable Interconnection. | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 95 percent, but greater than or equal to 90 percent for the applicable Interconnection. | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 90 percent, but greater than or equal to 85 percent for the applicable Interconnection. | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 85 percent for the applicable Interconnection. | M1. The Responsible Entity shall provide evidence, upon request, such as dated calculation output from spreadsheets, system logs, software programs, or other evidence (either in hard copy or electronic format) to demonstrate compliance with Requirement R1. | 2016-07-01 |  |  |  | 4.1.1 A Balancing Authority receiving Overlap Regulation Service is not subject to Control Performance Standard 1 (CPS1) or Balancing Authority ACE Limit (BAAL) compliance evaluation. 4.1.2 A Balancing Authority that is a member of a Regulation Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or the governing rules for the Regulation Reserve Sharing Group. |  | NPCC-NS | [6 empty] | 10000000
BAL-001-2 (Nova Scotia) | 78830000000378 | R2. | 788300000004782 | Each Balancing Authority shall operate such that its clock-minute average of Reporting ACE does not exceed its clock-minute Balancing Authority ACE Limit (BAAL) for more than 30 consecutive clock-minutes, calculated in accordance with Attachment 2, for the applicable Interconnection in which the Balancing Authority operates. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority exceeded its clock-minute BAAL for more than 30 consecutive clock minutes but for 45 consecutive clock-minutes or less for the applicable Interconnection. | The Balancing Authority exceeded its clock-minute BAAL for greater than 45 consecutive clock minutes but for 60 consecutive clock-minutes or less for the applicable Interconnection. | The Balancing Authority exceeded its clock-minute BAAL for greater than 60 consecutive clock minutes but for 75 consecutive clock-minutes or less for the applicable Interconnection. | The Balancing Authority exceeded its clock-minute BAAL for greater than 75 consecutive clock-minutes for the applicable Interconnection. | M2. Each Balancing Authority shall provide evidence, upon request, such as dated calculation output from spreadsheets, system logs, software programs, or other evidence (either in hard copy or electronic format) to demonstrate compliance with Requirement R2. | 2016-07-01 |  |  |  | 4.1.1 A Balancing Authority receiving Overlap Regulation Service is not subject to Control Performance Standard 1 (CPS1) or Balancing Authority ACE Limit (BAAL) compliance evaluation. 4.1.2 A Balancing Authority that is a member of a Regulation Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or the governing rules for the Regulation Reserve Sharing Group. |  | NPCC-NS | [6 empty] | 20000000
BAL-001-2 (Ontario) | 79780000378 | R1. | 79780004781 | The Responsible Entity shall operate such that the Control Performance Standard 1 (CPS1), calculated in accordance with Attachment 1, is greater than or equal to 100 percent for the applicable Interconnection in which it operates for each preceding 12 consecutive calendar month period, evaluated monthly. |  | BA, RRSG | BA | [14 empty] | RRSG | [5 empty] | Real-Time Operations | Medium | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 100 percent but greater than or equal to 95 percent for the applicable Interconnection. | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 95 percent, but greater than or equal to 90 percent for the applicable Interconnection. | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 90 percent, but greater than or equal to 85 percent for the applicable Interconnection. | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 85 percent for the applicable Interconnection. | M1. The Responsible Entity shall provide evidence, upon request, such as dated calculation output from spreadsheets, system logs, software programs, or other evidence (either in hard copy or electronic format) to demonstrate compliance with Requirement R1. | 2016-07-01 |  |  |  | 4.1.1 A Balancing Authority receiving Overlap Regulation Service is not subject to Control Performance Standard 1 (CPS1) or Balancing Authority ACE Limit (BAAL) compliance evaluation.&lt;br/&gt;&lt;br/&gt;4.1.2 A Balancing Authority that is a member of a Regulation Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or the governing rules for the Regulation Reserve Sharing Group. |  | NPCC-ON | [6 empty] | 10000000
BAL-001-2 (Ontario) | 79780000378 | R2. | 79780004782 | Each Balancing Authority shall operate such that its clock-minute average of Reporting ACE does not exceed its clock-minute Balancing Authority ACE Limit (BAAL) for more than 30 consecutive clock-minutes, calculated in accordance with Attachment 2, for the applicable Interconnection in which the Balancing Authority operates. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority exceeded its clock-minute BAAL for more than 30 consecutive clock minutes but for 45 consecutive clock-minutes or less for the applicable Interconnection. | The Balancing Authority exceeded its clock-minute BAAL for greater than 45 consecutive clock minutes but for 60 consecutive clock-minutes or less for the applicable Interconnection. | The Balancing Authority exceeded its clock-minute BAAL for greater than 60 consecutive clock minutes but for 75 consecutive clock-minutes or less for the applicable Interconnection. | The Balancing Authority exceeded its clock-minute BAAL for greater than 75 consecutive clock-minutes for the applicable Interconnection. | M2. Each Balancing Authority shall provide evidence, upon request, such as dated calculation output from spreadsheets, system logs, software programs, or other evidence (either in hard copy or electronic format) to demonstrate compliance with Requirement R2. | 2016-07-01 |  |  |  | 4.1.1 A Balancing Authority receiving Overlap Regulation Service is not subject to Control Performance Standard 1 (CPS1) or Balancing Authority ACE Limit (BAAL) compliance evaluation.&lt;br/&gt;&lt;br/&gt;4.1.2 A Balancing Authority that is a member of a Regulation Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or the governing rules for the Regulation Reserve Sharing Group. |  | NPCC-ON | [6 empty] | 20000000
BAL-001-2 (Saskatchewan) | 83750000000378 | R1. | 837500000004781 | The Responsible Entity shall operate such that the Control Performance Standard 1 (CPS1), calculated in accordance with Attachment 1, is greater than or equal to 100 percent for the applicable Interconnection in which it operates for each preceding 12 consecutive calendar month period, evaluated monthly. |  | BA, RRSG | BA | [14 empty] | RRSG | [5 empty] | Real-Time Operations | Medium | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 100 percent but greater than or equal to 95 percent for the applicable Interconnection. | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 95 percent, but greater than or equal to 90 percent for the applicable Interconnection. | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 90 percent, but greater than or equal to 85 percent for the applicable Interconnection. | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 85 percent for the applicable Interconnection. | M1. The Responsible Entity shall provide evidence, upon request, such as dated calculation output from spreadsheets, system logs, software programs, or other evidence (either in hard copy or electronic format) to demonstrate compliance with Requirement R1. | 2016-07-01 |  |  |  | 4.1.1 A Balancing Authority receiving Overlap Regulation Service is not subject to Control Performance Standard 1 (CPS1) or Balancing Authority ACE Limit (BAAL) compliance evaluation. 4.1.2 A Balancing Authority that is a member of a Regulation Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or the governing rules for the Regulation Reserve Sharing Group. |  | MRO-SK | [6 empty] | 10000000
BAL-001-2 (Saskatchewan) | 83750000000378 | R2. | 837500000004782 | Each Balancing Authority shall operate such that its clock-minute average of Reporting ACE does not exceed its clock-minute Balancing Authority ACE Limit (BAAL) for more than 30 consecutive clock-minutes, calculated in accordance with Attachment 2, for the applicable Interconnection in which the Balancing Authority operates. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority exceeded its clock-minute BAAL for more than 30 consecutive clock minutes but for 45 consecutive clock-minutes or less for the applicable Interconnection. | The Balancing Authority exceeded its clock-minute BAAL for greater than 45 consecutive clock minutes but for 60 consecutive clock-minutes or less for the applicable Interconnection. | The Balancing Authority exceeded its clock-minute BAAL for greater than 60 consecutive clock minutes but for 75 consecutive clock-minutes or less for the applicable Interconnection. | The Balancing Authority exceeded its clock-minute BAAL for greater than 75 consecutive clock-minutes for the applicable Interconnection. | M2. Each Balancing Authority shall provide evidence, upon request, such as dated calculation output from spreadsheets, system logs, software programs, or other evidence (either in hard copy or electronic format) to demonstrate compliance with Requirement R2. | 2016-07-01 |  |  |  | 4.1.1 A Balancing Authority receiving Overlap Regulation Service is not subject to Control Performance Standard 1 (CPS1) or Balancing Authority ACE Limit (BAAL) compliance evaluation. 4.1.2 A Balancing Authority that is a member of a Regulation Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or the governing rules for the Regulation Reserve Sharing Group. |  | MRO-SK | [6 empty] | 20000000
BAL-001-AB-2 (Alberta) | 656600000009000 | R1. | 656600000009062 | The ISO must operate such that the control performance standard 1, calculated in accordance with Appendix 1, is greater than or equal to 100% for each preceding 12 consecutive month period, evaluated monthly. |  | ISO | [28 empty] | 2019-07-01 | [5 empty] | WECC-AB | [6 empty] | 10000000
BAL-001-AB-2 (Alberta) | 656600000009000 | R2. | 656600000009063 | The ISO must operate such that its clock-minute average of reporting area control error does not exceed the clock-minute area control error limit of the balancing authority for more than 30 consecutive clock-minutes, calculated in accordance with Appendix 2. |  | ISO | [28 empty] | 2019-07-01 | [5 empty] | WECC-AB | [6 empty] | 20000000
BAL-001-TRE-1 | 380 | R1. | 4784 | The BA shall identify Frequency Measurable Events (FMEs), and within 14 calendar days after each FME the BA shall notify the Compliance Enforcement Authority and make FME information (time of FME (t(0)), pre-perturbation average frequency, post- perturbation average frequency) publicly available. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [15 empty] | Operations Assessment | Low | The BA reported an FME more than 14 days but less than 31 days after identification of the event. | The BA reported an FME more than 30 days but less than 51 days after identification of the event. | The BA reported an FME more than 50 days but less than 71 days after identification of the event. | The BA reported an FME more than 70 days after identification of the event. | M1. The BA shall have evidence it reported each FME to the Compliance Enforcement Authority and that it made FME information publicly available within 14 calendar days after the FME as required in Requirement R1. | 2014-04-01 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | TXRE-US |  |  |  |  | TXRE-US |  | 10000000
BAL-001-TRE-1 | 380 | R10. | 4793 | Each GO shall meet a minimum 12-month rolling average sustained Primary Frequency Response performance of 0.75 on each generating unit/generating facility, based on participation in at least eight FMEs. [Please see the standard for more information] | See Standard for calculations | BA, GO, GOP | BA |  |  |  | GO | GOP | [15 empty] | Operations Assessment | Medium | A GO’s rolling average sustained Primary Frequency Response performance per R10 was < 0.75 and = 0.65. | A GO’s rolling average sustained Primary Frequency Response performance per R10 was < 0.65 and = 0.55. | A GO’s rolling average sustained Primary Frequency Response performance per R10 was < 0.55 and = 0.45. | A GO’s rolling average sustained Primary Frequency Response performance per R10 was < 0.45. | M10. Each GO shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of sustained Primary Frequency Response performance of at least 0.75 as described in Requirement R10. Each GO shall have documented evidence of any Frequency Measurable Events where generating unit performance should be excluded from the rolling average calculation. | 2014-04-01 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | TXRE-US |  |  |  |  | TXRE-US |  | 100000000
BAL-001-TRE-1 | 380 | R2. | 4785 | The BA shall calculate the Primary Frequency Response of each generating unit/generating facility in accordance with this standard and the Primary Frequency Response Reference Document. This calculation shall provide a 12-month rolling average of initial and sustained Primary Frequency Response performance. This calculation shall be completed each month for the preceding 12 calendar months. [Please see the standard for more information] | See Standard for calculations | BA, GO, GOP | BA |  |  |  | GO | GOP | [15 empty] | Operations Assessment | Low | The BA submitted a monthly report more than one month but less than 51 days after the end of the reporting month. | The BA submitted a monthly report more than 50 days but less than 71 days after the end of the reporting month. | The BA submitted a monthly report more than 70 days but less than 91 days after the end of the reporting month. | The BA failed to submit a monthly report within 90 days after the end of the reporting month. | M2. The BA shall have evidence it calculated and reported the rolling average initial and sustained Primary Frequency Response performance of each generating unit/generating facility monthly as required in Requirement R2. | 2014-04-01 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | TXRE-US |  |  |  |  | TXRE-US |  | 20000000
BAL-001-TRE-1 | 380 | R3. | 4786 | The BA shall determine the Interconnection minimum Frequency Response (IMFR) in December of each year for the following year, and make the IMFR, the methodology for calculation and the criteria for determination of the IMFR publicly available. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [15 empty] | Operations Planning | Low | The BA did not make the calculation and criteria for determination of the IMFR publicly available. | The BA did not make the IMFR publicly available. | The BA did not calculate the IMFR for the following year in December. | The BA did not calculate the IMFR for a calendar year. | M3. The BA shall demonstrate that the IMFR was determined in December of each year per Requirement R3. The BA shall demonstrate that the IMFR, the methodology for calculation and the criteria for determination of the IMFR are publicly available. | 2014-04-01 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | TXRE-US |  |  |  |  | TXRE-US |  | 30000000
BAL-001-TRE-1 | 380 | R4. | 4787 | After each calendar month in which one or more FMEs occurs, the BA shall determine and make publicly available the Interconnection’s combined Frequency Response performance for a rolling average of the last six (6) FMEs by the end of the following calendar month. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [15 empty] | Operations Planning | Medium | N/A | N/A | The BA did not make public the six-FME rolling average Interconnection combined Frequency Response by the end of the following month. | The BA did not calculate the six-FME rolling average Interconnection combined Frequency Response for any month in which an FME occurred. | M4. The BA shall provide evidence that the rolling average of the Interconnection’s combined Frequency Response performance for the last six (6) FMEs was calculated and made public per Requirement R4. | 2014-04-01 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | TXRE-US |  |  |  |  | TXRE-US |  | 40000000
BAL-001-TRE-1 | 380 | R5. | 4788 | Following any FME that causes the Interconnection’s six-FME rolling average combined Frequency Response performance to be less than the IMFR, the BA shall direct any necessary actions to improve Frequency Response, which may include, but are not limited to, directing adjustment of Governor deadband and/or droop settings. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [15 empty] | Operations Planning | Medium | N/A | N/A | N/A | The BA did not take action to improve Frequency Response when the Interconnection’s rolling-average combined Frequency Response performance was less than the IMFR. | M5. The BA shall provide evidence that actions were taken to improve the Interconnection’s Frequency Response if the Interconnection’s six-FME rolling average combined Frequency Response performance was less than the IMFR, per Requirement R5. | 2014-04-01 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | TXRE-US |  |  |  |  | TXRE-US |  | 50000000
BAL-001-TRE-1 | 380 | R6. | 4789 | Each GO shall set its Governor parameters as follows: [Please see the standard for more information] | See Standard for calculations | BA, GO, GOP | BA |  |  |  | GO | GOP | [15 empty] | Operations Planning | Medium | Any Governor parameter setting was > 10% and = 20% outside setting range specified in R6. | Any Governor parameter setting was > 20% and = 30% outside setting range specified in R6. | Any Governor parameter setting was > 30% and = 40% outside setting range specified in R6. | Any Governor parameter setting was > 40% outside setting range specified in R6, – OR – an electronic or digital Governor was set to step into the droop curve. | M6. Each GO shall have evidence that it set its Governor parameters in accordance with Requirement R6. Examples of evidence include but are not limited to: • Governor test reports • Governor setting sheets • Performance monitoring reports | 2014-04-01 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | TXRE-US |  |  |  |  | TXRE-US |  | 60000000
BAL-001-TRE-1 | 380 | R7. | 4790 | Each GO shall operate each generating unit/generating facility that is connected to the interconnected transmission system with the Governor in service and responsive to frequency when the generating unit/generating facility is online and released for dispatch, unless the GO has a valid reason for operating with the Governor not in service and the GOP has been notified that the Governor is not in service. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The GO operated with its Governor out of service and did not notify the GOP upon discovery of its Governor out of service. | M7. Each GO shall have evidence that it notified the GOP as soon as practical each time it discovered a Governor not in service when the generating unit/generating facility was online and released for dispatch. Evidence may include but not be limited to: operator logs, voice logs, or electronic communications. | 2014-04-01 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | TXRE-US |  |  |  |  | TXRE-US |  | 70000000
BAL-001-TRE-1 | 380 | R8. | 4791 | Each GOP shall notify the BA as soon as practical but within 30 minutes of the discovery of a status change (in service, out of service) of a Governor. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [15 empty] | Real-Time Operations | Medium | The GOP notified the BA of a change in Governor status between 31 minutes and one hour after the GOP was notified of the discovery of the change. | The GOP notified the BA of a change in Governor status more than 1 hour but within 4 hours after the GOP was notified of the discovery of the change. | The GOP notified the BA of a change in Governor status more than 4 hours but within 24 hours after the GOP was notified of the discovery of the change. | The GOP failed to notify the BA of a change in Governor status within 24 hours after the GOP was notified of the discovery of the change. | M8. Each GOP shall have evidence that it notified the BA within 30 minutes of each discovery of a status change (in service, out of service) of a Governor. | 2014-04-01 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | TXRE-US |  |  |  |  | TXRE-US |  | 80000000
BAL-001-TRE-1 | 380 | R9. | 4792 | Each GO shall meet a minimum 12-month rolling average initial Primary Frequency Response performance of 0.75 on each generating unit/generating facility, based on participation in at least eight FMEs. [Please see the standard for more information] | See Standard for calculations | BA, GO, GOP | BA |  |  |  | GO | GOP | [15 empty] | Operations Assessment | Medium | A GO’s rolling average initial Primary Frequency Response performance per R9 was < 0.75 and = 0.65. | A GO’s rolling average initial Primary Frequency Response performance per R9 was < 0.65 and = 0.55. | A GO’s rolling average initial Primary Frequency Response performance per R9 was < 0.55 and = 0.45. | A GO’s rolling average initial Primary Frequency Response performance per R9 was < 0.45. | M9. Each GO shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of initial Primary Frequency Response performance level of at least 0.75 as described in Requirement R9. Each GO shall have documented evidence of any FMEs where the generating unit performance should be excluded from the rolling average calculation. | 2014-04-01 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | TXRE-US |  |  |  |  | TXRE-US |  | 90000000
BAL-001-TRE-2 | 622 | R1. | 9227 | The Balancing Authority shall identify Frequency Measurable Events (FMEs), and within 14 calendar days after each FME the Balancing Authority shall notify the Compliance Enforcement Authority and make FME information (time of FME (t(0)), pre-perturbation average frequency, post- perturbation average frequency) publicly available. |  | BA | BA | [20 empty] | Operations Assessment | Low | The Balancing Authority reported an FME more than 14 days but less than 31 days after identification of the event. | The Balancing Authority reported an FME more than 30 days but less than 51 days after identification of the event. | The Balancing Authority reported an FME more than 50 days but less than 71 days after identification of the event. | The Balancing Authority reported an FME more than 70 days after identification of the event. | M1. The Balancing Authority shall have evidence it reported each FME to the Compliance Enforcement Authority and that it made FME information publicly available within 14 calendar days after the FME as required in Requirement R1. | 2020-07-01 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | TXRE-US |  |  |  |  | TXRE-US |  | 10000000
BAL-001-TRE-2 | 622 | R10. | 9245 | Each Generator Owner shall meet a minimum 12-month rolling average sustained Primary Frequency Response performance of 0.75 on each generating unit/generating facility, based on participation in at least eight FMEs. [Please see the standard for more information] |  | GO |  |  |  |  | GO | [16 empty] | Operations Assessment | Medium | A Generator Owner’s rolling average sustained Primary Frequency Response performance per R10 was < 0.75 and = 0.65. | A Generator Owner’s rolling average sustained Primary Frequency Response performance per R10 was < 0.65 and = 0.55. | A Generator Owner’s rolling average sustained Primary Frequency Response performance per R10 was < 0.55 and = 0.45. | A Generator Owner’s rolling average sustained Primary Frequency Response performance per R10 was < 0.45. | M10. Each Generator Owner shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of sustained Primary Frequency Response performance of at least 0.75 as described in Requirement R10. Each Generator Owner shall have documented evidence of any Frequency Measurable Events where generating unit performance was excluded from the rolling average calculation. | 2020-07-01 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | TXRE-US |  |  |  |  | TXRE-US |  | 100000000
BAL-001-TRE-2 | 622 | R2. | 9228 | The Balancing Authority shall calculate the Primary Frequency Response of each generating unit/generating facility in accordance with this standard and the Primary Frequency Response Reference Document. This calculation shall provide a 12-month rolling average of initial and sustained Primary Frequency Response performance. This calculation shall be completed each month for the preceding 12 calendar months. The Primary Frequency Response Reference Document contains the calculations that the Balancing Authority will use to determine Primary Frequency Response performance of generating units/generating facilities. This reference document is a Texas RE-controlled document that is subject to revision by the Texas RE Board of Directors. |  | BA | BA | [20 empty] | Operations Assessment | Low | The Balancing Authority submitted a monthly report more than one month but less than 51 days after the end of the reporting month. | The Balancing Authority submitted a monthly report more than 50 days but less than 71 days after the end of the reporting month. | The Balancing Authority submitted a monthly report more than 70 days but less than 91 days after the end of the reporting month. | The Balancing Authority failed to submit a monthly report within 90 days after the end of the reporting month. | M2. The Balancing Authority shall have evidence it calculated and reported the rolling average initial and sustained Primary Frequency Response performance of each generating unit/generating facility monthly as required in Requirement R2. | 2020-07-01 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | TXRE-US |  |  |  |  | TXRE-US |  | 20000000
BAL-001-TRE-2 | 622 | R3. | 9232 | The Balancing Authority shall determine the Interconnection minimum Frequency Response (IMFR) in December of each year for the following year, and make the IMFR, the methodology for calculation and the criteria for determination of the IMFR publicly available. |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not make the calculation and criteria for determination of the IMFR publicly available. | The Balancing Authority did not make the IMFR publicly available. | The Balancing Authority did not calculate the IMFR for the following year in December. | The Balancing Authority did not calculate the IMFR for a calendar year. | M3. The Balancing Authority shall demonstrate that the IMFR was determined in December of each year per per Requirement R3. The Balancing Authority shall demonstrate that the IMFR, the methodology for calculation and the criteria for determination of the IMFR are publicly available. | 2020-07-01 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | TXRE-US |  |  |  |  | TXRE-US |  | 30000000
BAL-001-TRE-2 | 622 | R4. | 9233 | After each calendar month in which one or more FMEs occurs, the Balancing Authority shall determine and make publicly available the Interconnection’s combined Frequency Response performance for a rolling average of the last six (6) FMEs by the end of the following calendar month. |  | BA | BA | [20 empty] | Operations Planning | Medium | N/A | N/A | The Balancing Authority did not make public the six-FME rolling average Interconnection combined Frequency Response by the end of the following month. | The Balancing Authority did not calculate the six-FME rolling average Interconnection combined Frequency Response for any month in which an FME occurred. | M4. The Balancing Authority shall provide evidence that the rolling average of the Interconnection’s combined Frequency Response performance for the last six (6) FMEs was calculated and made public per Requirement R4. | 2020-07-01 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | TXRE-US |  |  |  |  | TXRE-US |  | 40000000
BAL-001-TRE-2 | 622 | R5. | 9234 | Following any FME that causes the Interconnection’s six-FME rolling average combined Frequency Response performance to be less than the IMFR, the Balancing Authority shall direct any necessary actions to improve Frequency Response, which may include, but are not limited to, directing adjustment of Governor deadband and/or droop settings. |  | BA | BA | [20 empty] | Operations Planning | Medium | N/A | N/A | N/A | The Balancing Authority did not take action to improve Frequency Response when the Interconnection’s rolling-average combined Frequency Response performance was less than the IMFR. | M5. The Balancing Authority shall provide evidence that actions were taken to improve the Interconnection’s Frequency Response if the Interconnection’s six-FME rolling average combined Frequency Response performance was less than the IMFR, per Requirement R5. | 2020-07-01 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | TXRE-US |  |  |  |  | TXRE-US |  | 50000000
BAL-001-TRE-2 | 622 | R6. | 9235 | Each Generator Owner shall set its Governor parameters as follows: [Please see the standard for more information] |  | GO |  |  |  |  | GO | [16 empty] | Operations Planning | Medium | Any Governor parameter setting was > 10% and = 20% outside setting range specified in R6. | Any Governor parameter setting was > 20% and = 30% outside setting range specified in R6. | Any Governor parameter setting was > 30% and = 40% outside setting range specified in R6. | Any Governor parameter setting was > 40% outside setting range specified in R6, – OR – an electronic or digital Governor was set to step into the droop curve. | M6. Each Generator Owner shall have evidence that it set its Governor parameters in accordance with Requirement R6. Examples of evidence include but are not limited to:  Governor test reports  Governor setting sheets  Performance monitoring reports | 2020-07-01 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | TXRE-US |  |  |  |  | TXRE-US |  | 60000000
BAL-001-TRE-2 | 622 | R7. | 9239 | Each Generator Owner shall operate each generating unit/generating facility that is connected to the interconnected transmission system with the Governor in service and responsive to frequency when the generating unit/generating facility is online and released for dispatch, unless the Generator Owner has a valid reason for operating with the Governor not in service and the Generator Operator has been notified that the Governor is not in service. |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Generator Owner operated with its Governor out of service and did not notify the Generator Operator upon discovery of its Governor out of service. | M7. Each Generator Owner shall have evidence that it notified the Generator Operator as soon as practical each time it discovered a Governor not in service when the generating unit/generating facility was online and released for dispatch. Evidence may include but not be limited to: operator logs, voice logs, or electronic communications. | 2020-07-01 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | TXRE-US |  |  |  |  | TXRE-US |  | 70000000
BAL-001-TRE-2 | 622 | R8. | 9240 | Each Generator Operator shall notify the Balancing Authority as soon as practical but within 30 minutes of the discovery of a status change (in service, out of service) of a Governor. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | The Generator Operator notified the Balancing Authority of a change in Governor status between 31 minutes and one hour after the General Operator was notified of the discovery of the change. | The General Operator notified the Balancing Authority of a change in Governor status more than 1 hour but within 4 hours after the Generator Operator was notified of the discovery of the change. | The Generator Operator notified the Balancing Authority of a change in Governor status more than 4 hours but within 24 hours after the Generator Operator was notified of the discovery of the change. | The Generator Operator failed to notify the Balancing Authority of a change in Governor status within 24 hours after the Generator Operator was notified of the discovery of the change. | M8. Each Generator Operator shall have evidence that it notified the Balancing Authority within 30 minutes of each discovery of a status change (in service, out of service) of a Governor. | 2020-07-01 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | TXRE-US |  |  |  |  | TXRE-US |  | 80000000
BAL-001-TRE-2 | 622 | R9. | 9241 | Each Generator Owner shall meet a minimum 12-month rolling average initial Primary Frequency Response performance of 0.75 on each generating unit/generating facility, based on participation in at least eight FMEs. [Please see the standard for more information] |  | GO |  |  |  |  | GO | [16 empty] | Operations Assessment | Medium | A Generator Owner’s rolling average initial Primary Frequency Response performance per R9 was < 0.75 and = 0.65. | A Generator Owner’s rolling average initial Primary Frequency Response performance per R9 was < 0.65 and = 0.55. | A Generator Owner’s rolling average initial Primary Frequency Response performance per R9 was < 0.55 and = 0.45. | A Generator Owner’s rolling average initial Primary Frequency Response performance per R9 was < 0.45. | M9. Each Generator Owner shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of initial Primary Frequency Response performance level of at least 0.75 as described in Requirement R9. Each Generator Owner shall have documented evidence of any FMEs where the generating unit performance was excluded from the rolling average calculation. | 2020-07-01 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | TXRE-US |  |  |  |  | TXRE-US |  | 90000000
BAL-002-0 | 5 | R1. | 17 | Each Balancing Authority shall have access to and/or operate Contingency Reserve to respond to Disturbances. Contingency Reserve may be supplied from generation, controllable load resources, or coordinated adjustments to Interchange Schedules. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | High |  |  |  | The Balancing Authority does not have access to and/or operate Contingency Reserve to respond to Disturbances. |  | 2007-06-18 |  | 2012-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-002-0 | 5 | R2. | 19 | Each Regional Reliability Organization, sub-Regional Reliability Organization or Reserve Sharing Group shall specify its Contingency Reserve policies, including: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Low | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 1 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 2 or 3 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 4 or 5 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify all 6 of the following sub-requirements. |  | 2007-06-18 |  | 2012-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-002-0 | 5 | R3. | 26 | Each Balancing Authority or Reserve Sharing Group shall activate sufficient Contingency Reserve to comply with the DCS. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | High | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 100% but greater than or equal to 95%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 95% but greater than or equal to 90%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 90% but greater than or equal to 85%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 85%. |  | 2007-06-18 |  | 2012-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-002-0 | 5 | R4. | 28 | A Balancing Authority or Reserve Sharing Group shall meet the Disturbance Recovery Criterion within the Disturbance Recovery Period for 100% of Reportable Disturbances. The Disturbance Recovery Criterion is: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Low | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 90% and less than 100% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | 2007-06-18 |  | 2012-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-002-0 | 5 | R5. | 31 | Each Reserve Sharing Group shall comply with the DCS. A Reserve Sharing Group shall be considered in a Reportable Disturbance condition whenever a group member has experienced a Reportable Disturbance and calls for the activation of Contingency Reserves from one or more other group members. (If a group member has experienced a Reportable Disturbance but does not call for reserve activation from other members of the Reserve Sharing Group, then that member shall report as a single Balancing Authority.) Compliance may be demonstrated by either of the following two methods: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Low | The Reserve Sharing Group met the DCS requirement for more than 90% and less than 100% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | 2007-06-18 |  | 2012-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
BAL-002-0 | 5 | R6. | 34 | A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Medium | The Balancing Authority or Reserve Sharing Group restored less than 100% but greater than 90% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 90% but greater than 80% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 80% but greater than or equal to 70% of its Contingency Reserve during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than 70% of its Contingency Reserves during the Contingency Reserve Restoration Period. |  | 2007-06-18 |  | 2012-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
BAL-002-0 (British Columbia) | 666700000010004 | R1. | 666700000010354 | Each Balancing Authority shall have access to and/or operate Contingency Reserve to respond to Disturbances. Contingency Reserve may be supplied from generation, controllable load resources, or coordinated adjustments to Interchange Schedules. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | High |  |  |  | The Balancing Authority does not have access to and/or operate Contingency Reserve to respond to Disturbances. |  | 2010-11-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 10000000
BAL-002-0 (British Columbia) | 666700000010004 | R2. | 666700000010355 | Each Regional Reliability Organization, sub-Regional Reliability Organization or Reserve Sharing Group shall specify its Contingency Reserve policies, including: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Low | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 1 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 2 or 3 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 4 or 5 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify all 6 of the following sub-requirements. |  | 2010-11-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 20000000
BAL-002-0 (British Columbia) | 666700000010004 | R3. | 666700000010356 | Each Balancing Authority or Reserve Sharing Group shall activate sufficient Contingency Reserve to comply with the DCS. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | High | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 100% but greater than or equal to 95%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 95% but greater than or equal to 90%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 90% but greater than or equal to 85%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 85%. |  | 2010-11-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 30000000
BAL-002-0 (British Columbia) | 666700000010004 | R4. | 666700000010357 | A Balancing Authority or Reserve Sharing Group shall meet the Disturbance Recovery Criterion within the Disturbance Recovery Period for 100% of Reportable Disturbances. The Disturbance Recovery Criterion is: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Low | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 90% and less than 100% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | 2010-11-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 40000000
BAL-002-0 (British Columbia) | 666700000010004 | R5. | 666700000010358 | Each Reserve Sharing Group shall comply with the DCS. A Reserve Sharing Group shall be considered in a Reportable Disturbance condition whenever a group member has experienced a Reportable Disturbance and calls for the activation of Contingency Reserves from one or more other group members. (If a group member has experienced a Reportable Disturbance but does not call for reserve activation from other members of the Reserve Sharing Group, then that member shall report as a single Balancing Authority.) Compliance may be demonstrated by either of the following two methods: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Low | The Reserve Sharing Group met the DCS requirement for more than 90% and less than 100% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | 2010-11-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 50000000
BAL-002-0 (British Columbia) | 666700000010004 | R6. | 666700000010359 | A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Medium | The Balancing Authority or Reserve Sharing Group restored less than 100% but greater than 90% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 90% but greater than 80% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 80% but greater than or equal to 70% of its Contingency Reserve during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than 70% of its Contingency Reserves during the Contingency Reserve Restoration Period. |  | 2010-11-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 60000000
BAL-002-0 (Manitoba) | 776600000005 | R1. | 7766000000017 | Each Balancing Authority shall have access to and/or operate Contingency Reserve to respond to Disturbances. Contingency Reserve may be supplied from generation, controllable load resources, or coordinated adjustments to Interchange Schedules. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | High |  |  |  | The Balancing Authority does not have access to and/or operate Contingency Reserve to respond to Disturbances. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 10000000
BAL-002-0 (Manitoba) | 776600000005 | R2. | 7766000000019 | Each Regional Reliability Organization, sub-Regional Reliability Organization or Reserve Sharing Group shall specify its Contingency Reserve policies, including: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Low | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 1 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 2 or 3 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 4 or 5 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify all 6 of the following sub-requirements. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 20000000
BAL-002-0 (Manitoba) | 776600000005 | R3. | 7766000000026 | Each Balancing Authority or Reserve Sharing Group shall activate sufficient Contingency Reserve to comply with the DCS. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | High | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 100% but greater than or equal to 95%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 95% but greater than or equal to 90%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 90% but greater than or equal to 85%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 85%. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 30000000
BAL-002-0 (Manitoba) | 776600000005 | R4. | 7766000000028 | A Balancing Authority or Reserve Sharing Group shall meet the Disturbance Recovery Criterion within the Disturbance Recovery Period for 100% of Reportable Disturbances. The Disturbance Recovery Criterion is: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Low | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 90% and less than 100% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 40000000
BAL-002-0 (Manitoba) | 776600000005 | R5. | 7766000000031 | Each Reserve Sharing Group shall comply with the DCS. A Reserve Sharing Group shall be considered in a Reportable Disturbance condition whenever a group member has experienced a Reportable Disturbance and calls for the activation of Contingency Reserves from one or more other group members. (If a group member has experienced a Reportable Disturbance but does not call for reserve activation from other members of the Reserve Sharing Group, then that member shall report as a single Balancing Authority.) Compliance may be demonstrated by either of the following two methods: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Low | The Reserve Sharing Group met the DCS requirement for more than 90% and less than 100% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 50000000
BAL-002-0 (Manitoba) | 776600000005 | R6. | 7766000000034 | A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Medium | The Balancing Authority or Reserve Sharing Group restored less than 100% but greater than 90% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 90% but greater than 80% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 80% but greater than or equal to 70% of its Contingency Reserve during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than 70% of its Contingency Reserves during the Contingency Reserve Restoration Period. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 60000000
BAL-002-0 (Ontario) | 79780000005 | R1. | 79780000017 | Each Balancing Authority shall have access to and/or operate Contingency Reserve to respond to Disturbances. Contingency Reserve may be supplied from generation, controllable load resources, or coordinated adjustments to Interchange Schedules. |  | BA | BA | [21 empty] | High |  |  |  | The Balancing Authority does not have access to and/or operate Contingency Reserve to respond to Disturbances. |  | 2007-06-18 |  | 2012-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-002-0 (Ontario) | 79780000005 | R2. | 79780000019 | Each Regional Reliability Organization, sub-Regional Reliability Organization or Reserve Sharing Group shall specify its Contingency Reserve policies, including: |  | RRO, RSG | [14 empty] | RRO |  | RSG | [5 empty] | Low | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 1 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 2 or 3 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 4 or 5 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify all 6 of the following sub-requirements. |  | 2007-06-18 |  | 2012-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-002-0 (Ontario) | 79780000005 | R3. | 79780000026 | Each Balancing Authority or Reserve Sharing Group shall activate sufficient Contingency Reserve to comply with the DCS. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | High | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 100% but greater than or equal to 95%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 95% but greater than or equal to 90%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 90% but greater than or equal to 85%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 85%. |  | 2007-06-18 |  | 2012-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-002-0 (Ontario) | 79780000005 | R4. | 79780000028 | A Balancing Authority or Reserve Sharing Group shall meet the Disturbance Recovery Criterion within the Disturbance Recovery Period for 100% of Reportable Disturbances. The Disturbance Recovery Criterion is: |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | Low | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 90% and less than 100% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | 2007-06-18 |  | 2012-03-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-002-0 (Ontario) | 79780000005 | R5. | 79780000031 | Each Reserve Sharing Group shall comply with the DCS. A Reserve Sharing Group shall be considered in a Reportable Disturbance condition whenever a group member has experienced a Reportable Disturbance and calls for the activation of Contingency Reserves from one or more other group members. (If a group member has experienced a Reportable Disturbance but does not call for reserve activation from other members of the Reserve Sharing Group, then that member shall report as a single Balancing Authority.) Compliance may be demonstrated by either of the following two methods: |  | RSG | [16 empty] | RSG | [5 empty] | Low | The Reserve Sharing Group met the DCS requirement for more than 90% and less than 100% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | 2007-06-18 |  | 2012-03-31 |  |  |  | NPCC-ON | [6 empty] | 50000000
BAL-002-0 (Ontario) | 79780000005 | R6. | 79780000034 | A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | Medium | The Balancing Authority or Reserve Sharing Group restored less than 100% but greater than 90% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 90% but greater than 80% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 80% but greater than or equal to 70% of its Contingency Reserve during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than 70% of its Contingency Reserves during the Contingency Reserve Restoration Period. |  | 2007-06-18 |  | 2012-03-31 |  |  |  | NPCC-ON | [6 empty] | 60000000
BAL-002-0 (Saskatchewan) | 837500000005 | R1. | 8375000000017 | Each Balancing Authority shall have access to and/or operate Contingency Reserve to respond to Disturbances. Contingency Reserve may be supplied from generation, controllable load resources, or coordinated adjustments to Interchange Schedules. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | High |  |  |  | The Balancing Authority does not have access to and/or operate Contingency Reserve to respond to Disturbances. |  | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 10000000
BAL-002-0 (Saskatchewan) | 837500000005 | R2. | 8375000000019 | Each Regional Reliability Organization, sub-Regional Reliability Organization or Reserve Sharing Group shall specify its Contingency Reserve policies, including: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Low | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 1 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 2 or 3 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 4 or 5 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify all 6 of the following sub-requirements. |  | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 20000000
BAL-002-0 (Saskatchewan) | 837500000005 | R3. | 8375000000026 | Each Balancing Authority or Reserve Sharing Group shall activate sufficient Contingency Reserve to comply with the DCS. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | High | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 100% but greater than or equal to 95%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 95% but greater than or equal to 90%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 90% but greater than or equal to 85%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 85%. |  | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 30000000
BAL-002-0 (Saskatchewan) | 837500000005 | R4. | 8375000000028 | A Balancing Authority or Reserve Sharing Group shall meet the Disturbance Recovery Criterion within the Disturbance Recovery Period for 100% of Reportable Disturbances. The Disturbance Recovery Criterion is: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Low | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 90% and less than 100% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 40000000
BAL-002-0 (Saskatchewan) | 837500000005 | R5. | 8375000000031 | Each Reserve Sharing Group shall comply with the DCS. A Reserve Sharing Group shall be considered in a Reportable Disturbance condition whenever a group member has experienced a Reportable Disturbance and calls for the activation of Contingency Reserves from one or more other group members. (If a group member has experienced a Reportable Disturbance but does not call for reserve activation from other members of the Reserve Sharing Group, then that member shall report as a single Balancing Authority.) Compliance may be demonstrated by either of the following two methods: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Low | The Reserve Sharing Group met the DCS requirement for more than 90% and less than 100% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 50000000
BAL-002-0 (Saskatchewan) | 837500000005 | R6. | 8375000000034 | A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Medium | The Balancing Authority or Reserve Sharing Group restored less than 100% but greater than 90% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 90% but greater than 80% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 80% but greater than or equal to 70% of its Contingency Reserve during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than 70% of its Contingency Reserves during the Contingency Reserve Restoration Period. |  | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 60000000
BAL-002-1 | 245 | R1. | 3183 | Each Balancing Authority shall have access to and/or operate Contingency Reserve to respond to Disturbances. Contingency Reserve may be supplied from generation, controllable load resources, or coordinated adjustments to Interchange Schedules. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | High |  |  |  |  | M1. A Balancing Authority or Reserve Sharing Group shall calculate and report compliance with the Disturbance Control Standard for all Disturbances greater than or equal to 80% of the magnitude of the Balancing Authority’s or of the Reserve Sharing Group’s most severe single contingency loss. Regions may, at their discretion, require a lower reporting threshold. Disturbance Control Standard is measured as the percentage recovery (Ri). (Please see standard for formulas) For loss of generation: if ACEA < 0 then if ACEA > 0 then where: • MWLOSS is the MW size of the Disturbance as measured at the beginning of the loss, • ACEA is the pre-disturbance ACE, • ACEM is the maximum algebraic value of ACE measured within the fifteen minutes following the Disturbance. A Balancing Authority or Reserve Sharing Group may, at its discretion, set ACEM = ACE15 min, and The Balancing Authority or Reserve Sharing Group shall record the MWLOSS value as measured at the site of the loss to the extent possible. The value should not be measured as a change in ACE since governor response and AGC response may introduce error. The Balancing Authority or Reserve Sharing Group shall base the value for ACEA on the average ACE over the period just prior to the start of the Disturbance (10 and 60 seconds prior and including at least 4 scans of ACE). In the illustration below, the horizontal line represents an averaging of ACE for 15 seconds prior to the start of the Disturbance with a result of ACEA = - 25 MW. The average percent recovery is the arithmetic average of all the calculated Ri’s for Reportable Disturbances during a given quarter. Average percent recovery is similarly calculated for excludable Disturbances. | 2012-04-01 |  | 2017-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-002-1 | 245 | R2. | 3185 | Each Regional Reliability Organization, sub-Regional Reliability Organization or Reserve Sharing Group shall specify its Contingency Reserve policies, including: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Medium | [5 empty] | 2012-04-01 |  | 2017-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-002-1 | 245 | R3. | 3192 | Each Balancing Authority or Reserve Sharing Group shall activate sufficient Contingency Reserve to comply with the DCS. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | High | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 100% but greater than or equal to 95%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 95% but greater than or equal to 90%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 90% but greater than or equal to 85%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 85%. |  | 2012-04-01 |  | 2017-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-002-1 | 245 | R4. | 3194 | A Balancing Authority or Reserve Sharing Group shall meet the Disturbance Recovery Criterion within the Disturbance Recovery Period for 100% of Reportable Disturbances. The Disturbance Recovery Criterion is: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Medium | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 90% and less than 100% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | 2012-04-01 |  | 2017-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-002-1 | 245 | R5. | 3197 | Each Reserve Sharing Group shall comply with the DCS. A Reserve Sharing Group shall be considered in a Reportable Disturbance condition whenever a group member has experienced a Reportable Disturbance and calls for the activation of Contingency Reserves from one or more other group members. (If a group member has experienced a Reportable Disturbance but does not call for reserve activation from other members of the Reserve Sharing Group, then that member shall report as a single Balancing Authority.) Compliance may be demonstrated by either of the following two methods: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Low | The Reserve Sharing Group met the DCS requirement for more than 90% and less than 100% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | 2012-04-01 |  | 2017-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
BAL-002-1 | 245 | R6. | 3200 | A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Medium | The Balancing Authority or Reserve Sharing Group restored less than 100% but greater than 90% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 90% but greater than 80% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 80% but greater than or equal to 70% of its Contingency Reserve during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than 70% of its Contingency Reserves during the Contingency Reserve Restoration Period. |  | 2012-04-01 |  | 2017-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
BAL-002-1a | 342 | R1. | 4438 | Each Balancing Authority shall have access to and/or operate Contingency Reserve to respond to Disturbances. Contingency Reserve may be supplied from generation, controllable load resources, or coordinated adjustments to Interchange Schedules. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | High | N/A | N/A | N/A | The Balancing Authority does not have access to and/or operate Contingency Reserve to respond to Disturbances. | M1. A Balancing Authority or Reserve Sharing Group shall calculate and report compliance with the Disturbance Control Standard for all Disturbances greater than or equal to 80% of the magnitude of the Balancing Authority’s or of the Reserve Sharing Group’s most severe single contingency loss. Regions may, at their discretion, require a lower reporting threshold. Disturbance Control Standard is measured as the percentage recovery (Ri). (Please see standard for formulas) For loss of generation: if ACEA < 0 then MW ACE ACE R    if ACEA > 0 then *100% max(0, ) Loss Loss M i MW MW ACE R    where:  MWLOSS is the MW size of the Disturbance as measured at the beginning of the loss,  ACEA is the pre-disturbance ACE,  ACEM is the maximum algebraic value of ACE measured within the fifteen minutes following the Disturbance. A Balancing Authority or Reserve Sharing Group may, at its discretion, set ACEM = ACE15 min, and The Balancing Authority or Reserve Sharing Group shall record the MWLOSS value as measured at the site of the loss to the extent possible. The value should not be measured as a change in ACE since governor response and AGC response may introduce error. The Balancing Authority or Reserve Sharing Group shall base the value for ACEA on the average ACE over the period just prior to the start of the Disturbance (10 and 60 seconds prior and including at least 4 scans of ACE). In the illustration below, the horizontal line represents an averaging of ACE for 15 seconds prior to the start of the Disturbance with a result of ACEA = - 25 MW. The average percent recovery is the arithmetic average of all the calculated Ri’s for Reportable Disturbances during a given quarter. Average percent recovery is similarly calculated for excludable Disturbances. |  |  | 2017-02-17 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-002-1a | 342 | R2. | 4439 | Each Regional Reliability Organization, sub-Regional Reliability Organization or Reserve Sharing Group shall specify its Contingency Reserve policies, including: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Medium | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 1 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 2 or 3 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 4 or 5 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify all 6 of the following sub-requirements. |  |  |  | 2017-02-17 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-002-1a | 342 | R3. | 4441 | Each Balancing Authority or Reserve Sharing Group shall activate sufficient Contingency Reserve to comply with the DCS. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | High | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 100% but greater than or equal to 95%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 95% but greater than or equal to 90%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 90% but greater than or equal to 85%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 85%. |  |  |  | 2017-02-17 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-002-1a | 342 | R4. | 4440 | A Balancing Authority or Reserve Sharing Group shall meet the Disturbance Recovery Criterion within the Disturbance Recovery Period for 100% of Reportable Disturbances. The Disturbance Recovery Criterion is: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Medium | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 90% and less than 100% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 0% and less than or equal to 70% of Reportable Disturbances. |  |  |  | 2017-02-17 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-002-1a | 342 | R5. | 4437 | Each Reserve Sharing Group shall comply with the DCS. A Reserve Sharing Group shall be considered in a Reportable Disturbance condition whenever a group member has experienced a Reportable Disturbance and calls for the activation of Contingency Reserves from one or more other group members. (If a group member has experienced a Reportable Disturbance but does not call for reserve activation from other members of the Reserve Sharing Group, then that member shall report as a single Balancing Authority.) Compliance may be demonstrated by either of the following two methods: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG |  |  |  |  | Real-Time Operations | Low | The Reserve Sharing Group met the DCS requirement for more than 90% and less than 100% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 0% and less than or equal to 70% of Reportable Disturbances. |  |  |  | 2017-02-17 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
BAL-002-1a | 342 | R6. | 4442 | A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG |  |  |  |  | Real-Time Operations | Medium | The Balancing Authority or Reserve Sharing Group restored less than 100% but greater than 90% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 90% but greater than 80% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 80% but greater than or equal to 70% of its Contingency Reserve during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than 70% of its Contingency Reserves during the Contingency Reserve Restoration Period. |  |  |  | 2017-02-17 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
BAL-002-1a (Ontario) | 79780000342 | R1. | 79780004438 | Each Balancing Authority shall have access to and/or operate Contingency Reserve to respond to Disturbances. Contingency Reserve may be supplied from generation, controllable load resources, or coordinated adjustments to Interchange Schedules. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | High | N/A | N/A | N/A | The Balancing Authority does not have access to and/or operate Contingency Reserve to respond to Disturbances. | &lt;p&gt;M1. A Balancing Authority or Reserve Sharing Group shall calculate and report compliance with the Disturbance Control Standard for all Disturbances greater than or equal to 80% of the magnitude of the Balancing Authority’s or of the Reserve Sharing Group’s most severe single contingency loss. Regions may, at their discretion, require a lower reporting threshold. Disturbance Control Standard is measured as the percentage recovery (Ri). (Please see standard for formulas)&lt;/p&gt; &lt;p&gt;For loss of generation: if ACEA &amp;lt; 0 then&lt;/p&gt; &lt;p&gt;MW ACE ACE R    if ACEA &amp;gt; 0 then *100% max(0, ) Loss Loss M i MW MW ACE R    where:  MWLOSS is the MW size of the Disturbance as measured at the beginning of the loss,  ACEA is the pre-disturbance ACE,  ACEM is the maximum algebraic value of ACE measured within the fifteen minutes following the Disturbance. A Balancing Authority or Reserve Sharing Group may, at its discretion, set ACEM = ACE15 min, and The Balancing Authority or Reserve Sharing Group shall record the MWLOSS value as measured at the site of the loss to the extent possible. The value should not be measured as a change in ACE since governor response and AGC response may introduce error. The Balancing Authority or Reserve Sharing Group shall base the value for ACEA on the average ACE over the period just prior to the start of the Disturbance (10 and 60 seconds prior and including at least 4 scans of ACE). In the illustration below, the horizontal line represents an averaging of ACE for 15 seconds prior to the start of the Disturbance with a result of ACEA = - 25 MW.&lt;/p&gt; &lt;p&gt;The average percent recovery is the arithmetic average of all the calculated Ri’s for Reportable Disturbances during a given quarter. Average percent recovery is similarly calculated for excludable Disturbances.&lt;/p&gt; |  |  | 2017-02-17 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-002-1a (Ontario) | 79780000342 | R2. | 79780004439 | Each Regional Reliability Organization, sub-Regional Reliability Organization or Reserve Sharing Group shall specify its Contingency Reserve policies, including: |  | RRO, RSG | [14 empty] | RRO |  | RSG | [5 empty] | Medium | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 1 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 2 or 3 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 4 or 5 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify all 6 of the following sub-requirements. |  |  |  | 2017-02-17 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-002-1a (Ontario) | 79780000342 | R3. | 79780004441 | Each Balancing Authority or Reserve Sharing Group shall activate sufficient Contingency Reserve to comply with the DCS. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | High | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 100% but greater than or equal to 95%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 95% but greater than or equal to 90%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 90% but greater than or equal to 85%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 85%. |  |  |  | 2017-02-17 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-002-1a (Ontario) | 79780000342 | R4. | 79780004440 | A Balancing Authority or Reserve Sharing Group shall meet the Disturbance Recovery Criterion within the Disturbance Recovery Period for 100% of Reportable Disturbances. The Disturbance Recovery Criterion is: |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | Medium | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 90% and less than 100% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 0% and less than or equal to 70% of Reportable Disturbances. |  |  |  | 2017-02-17 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-002-1a (Ontario) | 79780000342 | R5. | 79780004437 | Each Reserve Sharing Group shall comply with the DCS. A Reserve Sharing Group shall be considered in a Reportable Disturbance condition whenever a group member has experienced a Reportable Disturbance and calls for the activation of Contingency Reserves from one or more other group members. (If a group member has experienced a Reportable Disturbance but does not call for reserve activation from other members of the Reserve Sharing Group, then that member shall report as a single Balancing Authority.) Compliance may be demonstrated by either of the following two methods: |  | RSG | [16 empty] | RSG |  |  |  |  | Real-Time Operations | Low | The Reserve Sharing Group met the DCS requirement for more than 90% and less than 100% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 0% and less than or equal to 70% of Reportable Disturbances. | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. |  |  | 2017-02-17 |  |  |  | NPCC-ON | [6 empty] | 50000000
BAL-002-1a (Ontario) | 79780000342 | R6. | 79780004442 | A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | Medium | The Balancing Authority or Reserve Sharing Group restored less than 100% but greater than 90% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 90% but greater than 80% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 80% but greater than or equal to 70% of its Contingency Reserve during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than 70% of its Contingency Reserves during the Contingency Reserve Restoration Period. |  |  |  | 2017-02-17 |  |  |  | NPCC-ON | [6 empty] | 60000000
BAL-002-1 (British Columbia) | 666700000010005 | R1. | 666700000010360 | Each Balancing Authority shall have access to and/or operate Contingency Reserve to respond to Disturbances. Contingency Reserve may be supplied from generation, controllable load resources, or coordinated adjustments to Interchange Schedules. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | High |  |  |  |  | M1. A Balancing Authority or Reserve Sharing Group shall calculate and report compliance with the Disturbance Control Standard for all Disturbances greater than or equal to 80% of the magnitude of the Balancing Authority’s or of the Reserve Sharing Group’s most severe single contingency loss. Regions may, at their discretion, require a lower reporting threshold. Disturbance Control Standard is measured as the percentage recovery (Ri). (Please see standard for formulas) For loss of generation: if ACEA < 0 then if ACEA > 0 then where: • MWLOSS is the MW size of the Disturbance as measured at the beginning of the loss, • ACEA is the pre-disturbance ACE, • ACEM is the maximum algebraic value of ACE measured within the fifteen minutes following the Disturbance. A Balancing Authority or Reserve Sharing Group may, at its discretion, set ACEM = ACE15 min, and The Balancing Authority or Reserve Sharing Group shall record the MWLOSS value as measured at the site of the loss to the extent possible. The value should not be measured as a change in ACE since governor response and AGC response may introduce error. The Balancing Authority or Reserve Sharing Group shall base the value for ACEA on the average ACE over the period just prior to the start of the Disturbance (10 and 60 seconds prior and including at least 4 scans of ACE). In the illustration below, the horizontal line represents an averaging of ACE for 15 seconds prior to the start of the Disturbance with a result of ACEA = - 25 MW. The average percent recovery is the arithmetic average of all the calculated Ri’s for Reportable Disturbances during a given quarter. Average percent recovery is similarly calculated for excludable Disturbances. | 2013-12-12 |  | 2017-12-31 |  |  |  | WECC-BC | [6 empty] | 10000000
BAL-002-1 (British Columbia) | 666700000010005 | R2. | 666700000010361 | Each Regional Reliability Organization, sub-Regional Reliability Organization or Reserve Sharing Group shall specify its Contingency Reserve policies, including: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Medium | [5 empty] | 2013-12-12 |  | 2017-12-31 |  |  |  | WECC-BC | [6 empty] | 20000000
BAL-002-1 (British Columbia) | 666700000010005 | R3. | 666700000010362 | Each Balancing Authority or Reserve Sharing Group shall activate sufficient Contingency Reserve to comply with the DCS. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | High | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 100% but greater than or equal to 95%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 95% but greater than or equal to 90%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 90% but greater than or equal to 85%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 85%. |  | 2013-12-12 |  | 2017-12-31 |  |  |  | WECC-BC | [6 empty] | 30000000
BAL-002-1 (British Columbia) | 666700000010005 | R4. | 666700000010363 | A Balancing Authority or Reserve Sharing Group shall meet the Disturbance Recovery Criterion within the Disturbance Recovery Period for 100% of Reportable Disturbances. The Disturbance Recovery Criterion is: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Medium | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 90% and less than 100% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | 2013-12-12 |  | 2017-12-31 |  |  |  | WECC-BC | [6 empty] | 40000000
BAL-002-1 (British Columbia) | 666700000010005 | R5. | 666700000010364 | Each Reserve Sharing Group shall comply with the DCS. A Reserve Sharing Group shall be considered in a Reportable Disturbance condition whenever a group member has experienced a Reportable Disturbance and calls for the activation of Contingency Reserves from one or more other group members. (If a group member has experienced a Reportable Disturbance but does not call for reserve activation from other members of the Reserve Sharing Group, then that member shall report as a single Balancing Authority.) Compliance may be demonstrated by either of the following two methods: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Low | The Reserve Sharing Group met the DCS requirement for more than 90% and less than 100% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | 2013-12-12 |  | 2017-12-31 |  |  |  | WECC-BC | [6 empty] | 50000000
BAL-002-1 (British Columbia) | 666700000010005 | R6. | 666700000010365 | A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Medium | The Balancing Authority or Reserve Sharing Group restored less than 100% but greater than 90% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 90% but greater than 80% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 80% but greater than or equal to 70% of its Contingency Reserve during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than 70% of its Contingency Reserves during the Contingency Reserve Restoration Period. |  | 2013-12-12 |  | 2017-12-31 |  |  |  | WECC-BC | [6 empty] | 60000000
BAL-002-1 (Manitoba) | 77660000000245 | R1. | 776600000003183 | Each Balancing Authority shall have access to and/or operate Contingency Reserve to respond to Disturbances. Contingency Reserve may be supplied from generation, controllable load resources, or coordinated adjustments to Interchange Schedules. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | High |  |  |  |  | M1. A Balancing Authority or Reserve Sharing Group shall calculate and report compliance with the Disturbance Control Standard for all Disturbances greater than or equal to 80% of the magnitude of the Balancing Authority’s or of the Reserve Sharing Group’s most severe single contingency loss. Regions may, at their discretion, require a lower reporting threshold. Disturbance Control Standard is measured as the percentage recovery (Ri). (Please see standard for formulas) For loss of generation: if ACEA < 0 then if ACEA > 0 then where: • MWLOSS is the MW size of the Disturbance as measured at the beginning of the loss, • ACEA is the pre-disturbance ACE, • ACEM is the maximum algebraic value of ACE measured within the fifteen minutes following the Disturbance. A Balancing Authority or Reserve Sharing Group may, at its discretion, set ACEM = ACE15 min, and The Balancing Authority or Reserve Sharing Group shall record the MWLOSS value as measured at the site of the loss to the extent possible. The value should not be measured as a change in ACE since governor response and AGC response may introduce error. The Balancing Authority or Reserve Sharing Group shall base the value for ACEA on the average ACE over the period just prior to the start of the Disturbance (10 and 60 seconds prior and including at least 4 scans of ACE). In the illustration below, the horizontal line represents an averaging of ACE for 15 seconds prior to the start of the Disturbance with a result of ACEA = - 25 MW. The average percent recovery is the arithmetic average of all the calculated Ri’s for Reportable Disturbances during a given quarter. Average percent recovery is similarly calculated for excludable Disturbances. | 2014-02-14 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
BAL-002-1 (Manitoba) | 77660000000245 | R2. | 776600000003185 | Each Regional Reliability Organization, sub-Regional Reliability Organization or Reserve Sharing Group shall specify its Contingency Reserve policies, including: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Medium | [5 empty] | 2014-02-14 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
BAL-002-1 (Manitoba) | 77660000000245 | R3. | 776600000003192 | Each Balancing Authority or Reserve Sharing Group shall activate sufficient Contingency Reserve to comply with the DCS. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | High | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 100% but greater than or equal to 95%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 95% but greater than or equal to 90%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 90% but greater than or equal to 85%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 85%. |  | 2014-02-14 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
BAL-002-1 (Manitoba) | 77660000000245 | R4. | 776600000003194 | A Balancing Authority or Reserve Sharing Group shall meet the Disturbance Recovery Criterion within the Disturbance Recovery Period for 100% of Reportable Disturbances. The Disturbance Recovery Criterion is: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Medium | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 90% and less than 100% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | 2014-02-14 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 40000000
BAL-002-1 (Manitoba) | 77660000000245 | R5. | 776600000003197 | Each Reserve Sharing Group shall comply with the DCS. A Reserve Sharing Group shall be considered in a Reportable Disturbance condition whenever a group member has experienced a Reportable Disturbance and calls for the activation of Contingency Reserves from one or more other group members. (If a group member has experienced a Reportable Disturbance but does not call for reserve activation from other members of the Reserve Sharing Group, then that member shall report as a single Balancing Authority.) Compliance may be demonstrated by either of the following two methods: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Low | The Reserve Sharing Group met the DCS requirement for more than 90% and less than 100% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | 2014-02-14 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 50000000
BAL-002-1 (Manitoba) | 77660000000245 | R6. | 776600000003200 | A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Medium | The Balancing Authority or Reserve Sharing Group restored less than 100% but greater than 90% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 90% but greater than 80% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 80% but greater than or equal to 70% of its Contingency Reserve during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than 70% of its Contingency Reserves during the Contingency Reserve Restoration Period. |  | 2014-02-14 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 60000000
BAL-002-1 (Ontario) | 79780000245 | R1. | 79780003183 | Each Balancing Authority shall have access to and/or operate Contingency Reserve to respond to Disturbances. Contingency Reserve may be supplied from generation, controllable load resources, or coordinated adjustments to Interchange Schedules. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | High |  |  |  |  | &lt;p&gt;M1. A Balancing Authority or Reserve Sharing Group shall calculate and report compliance with the Disturbance Control Standard for all Disturbances greater than or equal to 80% of the magnitude of the Balancing Authority’s or of the Reserve Sharing Group’s most severe single contingency loss. Regions may, at their discretion, require a lower reporting threshold. Disturbance Control Standard is measured as the percentage recovery (Ri). (Please see standard for formulas)&lt;br/&gt;&lt;br/&gt;For loss of generation:&lt;br/&gt;&lt;br/&gt;if ACEA &amp;lt; 0&lt;br/&gt;then&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;if ACEA &amp;gt; 0&lt;br/&gt;then &lt;br/&gt;&lt;br/&gt;&lt;br/&gt;where: &lt;br/&gt;• MWLOSS is the MW size of the Disturbance as measured at the beginning of the loss,&lt;br/&gt;• ACEA is the pre-disturbance ACE,&lt;br/&gt;• ACEM is the maximum algebraic value of ACE measured within the fifteen minutes following the Disturbance. A Balancing Authority or Reserve Sharing Group may, at its discretion, set ACEM = ACE15 min, and&lt;br/&gt;The Balancing Authority or Reserve Sharing Group shall record the MWLOSS value as measured at the site of the loss to the extent possible. The value should not be measured as a change in ACE since governor response and AGC response may introduce error.&lt;br/&gt;The Balancing Authority or Reserve Sharing Group shall base the value for ACEA on the average ACE over the period just prior to the start of the Disturbance (10 and 60 seconds prior and including at least 4 scans of ACE). In the illustration below, the horizontal line represents an averaging of ACE for 15 seconds prior to the start of the Disturbance with a result of ACEA = - 25 MW.&lt;br/&gt;&lt;br/&gt;The average percent recovery is the arithmetic average of all the calculated Ri’s for Reportable Disturbances during a given quarter. Average percent recovery is similarly calculated for excludable Disturbances.&lt;/p&gt; | 2012-04-01 |  | 2017-12-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-002-1 (Ontario) | 79780000245 | R2. | 79780003185 | Each Regional Reliability Organization, sub-Regional Reliability Organization or Reserve Sharing Group shall specify its Contingency Reserve policies, including: |  | RRO, RSG | [14 empty] | RRO |  | RSG | [5 empty] | Medium | [5 empty] | 2012-04-01 |  | 2017-12-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-002-1 (Ontario) | 79780000245 | R3. | 79780003192 | Each Balancing Authority or Reserve Sharing Group shall activate sufficient Contingency Reserve to comply with the DCS. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | High | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 100% but greater than or equal to 95%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 95% but greater than or equal to 90%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 90% but greater than or equal to 85%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 85%. |  | 2012-04-01 |  | 2017-12-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-002-1 (Ontario) | 79780000245 | R4. | 79780003194 | A Balancing Authority or Reserve Sharing Group shall meet the Disturbance Recovery Criterion within the Disturbance Recovery Period for 100% of Reportable Disturbances. The Disturbance Recovery Criterion is: |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | Medium | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 90% and less than 100% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | 2012-04-01 |  | 2017-12-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-002-1 (Ontario) | 79780000245 | R5. | 79780003197 | Each Reserve Sharing Group shall comply with the DCS. A Reserve Sharing Group shall be considered in a Reportable Disturbance condition whenever a group member has experienced a Reportable Disturbance and calls for the activation of Contingency Reserves from one or more other group members. (If a group member has experienced a Reportable Disturbance but does not call for reserve activation from other members of the Reserve Sharing Group, then that member shall report as a single Balancing Authority.) Compliance may be demonstrated by either of the following two methods: |  | RSG | [16 empty] | RSG | [5 empty] | Low | The Reserve Sharing Group met the DCS requirement for more than 90% and less than 100% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | 2012-04-01 |  | 2017-12-31 |  |  |  | NPCC-ON | [6 empty] | 50000000
BAL-002-1 (Ontario) | 79780000245 | R6. | 79780003200 | A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | Medium | The Balancing Authority or Reserve Sharing Group restored less than 100% but greater than 90% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 90% but greater than 80% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 80% but greater than or equal to 70% of its Contingency Reserve during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than 70% of its Contingency Reserves during the Contingency Reserve Restoration Period. |  | 2012-04-01 |  | 2017-12-31 |  |  |  | NPCC-ON | [6 empty] | 60000000
BAL-002-1 (Saskatchewan) | 83750000000245 | R1. | 837500000003183 | Each Balancing Authority shall have access to and/or operate Contingency Reserve to respond to Disturbances. Contingency Reserve may be supplied from generation, controllable load resources, or coordinated adjustments to Interchange Schedules. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | High |  |  |  |  | M1. A Balancing Authority or Reserve Sharing Group shall calculate and report compliance with the Disturbance Control Standard for all Disturbances greater than or equal to 80% of the magnitude of the Balancing Authority’s or of the Reserve Sharing Group’s most severe single contingency loss. Regions may, at their discretion, require a lower reporting threshold. Disturbance Control Standard is measured as the percentage recovery (Ri). (Please see standard for formulas) For loss of generation: if ACEA < 0 then if ACEA > 0 then where: • MWLOSS is the MW size of the Disturbance as measured at the beginning of the loss, • ACEA is the pre-disturbance ACE, • ACEM is the maximum algebraic value of ACE measured within the fifteen minutes following the Disturbance. A Balancing Authority or Reserve Sharing Group may, at its discretion, set ACEM = ACE15 min, and The Balancing Authority or Reserve Sharing Group shall record the MWLOSS value as measured at the site of the loss to the extent possible. The value should not be measured as a change in ACE since governor response and AGC response may introduce error. The Balancing Authority or Reserve Sharing Group shall base the value for ACEA on the average ACE over the period just prior to the start of the Disturbance (10 and 60 seconds prior and including at least 4 scans of ACE). In the illustration below, the horizontal line represents an averaging of ACE for 15 seconds prior to the start of the Disturbance with a result of ACEA = - 25 MW. The average percent recovery is the arithmetic average of all the calculated Ri’s for Reportable Disturbances during a given quarter. Average percent recovery is similarly calculated for excludable Disturbances. | 2014-04-01 |  | 2019-09-30 |  |  |  | MRO-SK | [6 empty] | 10000000
BAL-002-1 (Saskatchewan) | 83750000000245 | R2. | 837500000003185 | Each Regional Reliability Organization, sub-Regional Reliability Organization or Reserve Sharing Group shall specify its Contingency Reserve policies, including: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Medium | [5 empty] | 2014-04-01 |  | 2019-09-30 |  |  |  | MRO-SK | [6 empty] | 20000000
BAL-002-1 (Saskatchewan) | 83750000000245 | R3. | 837500000003192 | Each Balancing Authority or Reserve Sharing Group shall activate sufficient Contingency Reserve to comply with the DCS. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | High | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 100% but greater than or equal to 95%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 95% but greater than or equal to 90%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 90% but greater than or equal to 85%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 85%. |  | 2014-04-01 |  | 2019-09-30 |  |  |  | MRO-SK | [6 empty] | 30000000
BAL-002-1 (Saskatchewan) | 83750000000245 | R4. | 837500000003194 | A Balancing Authority or Reserve Sharing Group shall meet the Disturbance Recovery Criterion within the Disturbance Recovery Period for 100% of Reportable Disturbances. The Disturbance Recovery Criterion is: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Medium | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 90% and less than 100% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | 2014-04-01 |  | 2019-09-30 |  |  |  | MRO-SK | [6 empty] | 40000000
BAL-002-1 (Saskatchewan) | 83750000000245 | R5. | 837500000003197 | Each Reserve Sharing Group shall comply with the DCS. A Reserve Sharing Group shall be considered in a Reportable Disturbance condition whenever a group member has experienced a Reportable Disturbance and calls for the activation of Contingency Reserves from one or more other group members. (If a group member has experienced a Reportable Disturbance but does not call for reserve activation from other members of the Reserve Sharing Group, then that member shall report as a single Balancing Authority.) Compliance may be demonstrated by either of the following two methods: |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Low | The Reserve Sharing Group met the DCS requirement for more than 90% and less than 100% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | 2014-04-01 |  | 2019-09-30 |  |  |  | MRO-SK | [6 empty] | 50000000
BAL-002-1 (Saskatchewan) | 83750000000245 | R6. | 837500000003200 | A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | Medium | The Balancing Authority or Reserve Sharing Group restored less than 100% but greater than 90% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 90% but greater than 80% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 80% but greater than or equal to 70% of its Contingency Reserve during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than 70% of its Contingency Reserves during the Contingency Reserve Restoration Period. |  | 2014-04-01 |  | 2019-09-30 |  |  |  | MRO-SK | [6 empty] | 60000000
BAL-002-2 | 543 | R1. | 7606 | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Responsible Entity achieved less than 100% but at least 90% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period OR The Responsible Entity failed to use CR Form 1 to document a Reportable Balancing Contingency Event. | The Responsible Entity achieved less than 90% but at least 80% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 80% but at least 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. |  |  | 2017-12-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-002-2 | 543 | R2. | 7607 | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Operations Planning | High | The Responsible Entity developed and implemented an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to maintain annually the Operating Process. | N/A | The Responsible Entity developed an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to implement the Operating Process. | The Responsible Entity failed to develop an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency. | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. |  |  | 2017-12-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-002-2 | 543 | R3. | 7613 | Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | Medium | The Responsible Entity restored less than 100% but at least 90% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 90% but at least 80% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 80% but at least 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | M3. Each Responsible Entity will have documentation demonstrating its Contingency Reserve was restored within the Contingency Reserve Restoration Period, such as historical data, computer logs or operator logs. |  |  | 2017-12-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-002-2 (British Columbia) | 666700000010006 | R1. | 666700000010366 | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Responsible Entity achieved less than 100% but at least 90% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period OR The Responsible Entity failed to use CR Form 1 to document a Reportable Balancing Contingency Event. | The Responsible Entity achieved less than 90% but at least 80% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 80% but at least 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. | 2018-01-01 |  | 2020-03-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | WECC-BC | [6 empty] | 10000000
BAL-002-2 (British Columbia) | 666700000010006 | R2. | 666700000010367 | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Operations Planning | High | The Responsible Entity developed and implemented an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to maintain annually the Operating Process. | N/A | The Responsible Entity developed an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to implement the Operating Process. | The Responsible Entity failed to develop an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency. | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. | 2018-01-01 |  | 2020-03-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | WECC-BC | [6 empty] | 20000000
BAL-002-2 (British Columbia) | 666700000010006 | R3. | 666700000010368 | Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | Medium | The Responsible Entity restored less than 100% but at least 90% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 90% but at least 80% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 80% but at least 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | M3. Each Responsible Entity will have documentation demonstrating its Contingency Reserve was restored within the Contingency Reserve Restoration Period, such as historical data, computer logs or operator logs. | 2018-01-01 |  | 2020-03-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | WECC-BC | [6 empty] | 30000000
BAL-002-2(i) | 566 | R1. | 8042 | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Responsible Entity achieved less than 100% but at least 90% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period OR The Responsible Entity failed to use CR Form 1 to document a Reportable Balancing Contingency Event. | The Responsible Entity achieved less than 90% but at least 80% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 80% but at least 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2018-01-01 |  | 2019-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-002-2(i) | 566 | R2. | 8048 | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Operations Planning | High | The Responsible Entity developed and implemented an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to maintain annually the Operating Process. | N/A | The Responsible Entity developed an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to implement the Operating Process. | The Responsible Entity failed to develop an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency. | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. | 2018-01-01 |  | 2019-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-002-2(i) | 566 | R3. | 8049 | Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | Medium | The Responsible Entity restored less than 100% but at least 90% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 90% but at least 80% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 80% but at least 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | Each Responsible Entity will have documentation demonstrating its Contingency Reserve was restored within the Contingency Reserve Restoration Period, such as historical data, computer logs or operator logs. | 2018-01-01 |  | 2019-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-002-2(i) (Manitoba) | 77660000000566 | R1. | 776600000008042 | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Responsible Entity achieved less than 100% but at least 90% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period OR The Responsible Entity failed to use CR Form 1 to document a Reportable Balancing Contingency Event. | The Responsible Entity achieved less than 90% but at least 80% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 80% but at least 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2019-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 10000000
BAL-002-2(i) (Manitoba) | 77660000000566 | R2. | 776600000008048 | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Operations Planning | High | The Responsible Entity developed and implemented an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to maintain annually the Operating Process. | N/A | The Responsible Entity developed an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to implement the Operating Process. | The Responsible Entity failed to develop an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency. | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. | 2019-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 20000000
BAL-002-2(i) (Manitoba) | 77660000000566 | R3. | 776600000008049 | Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | Medium | The Responsible Entity restored less than 100% but at least 90% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 90% but at least 80% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 80% but at least 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | Each Responsible Entity will have documentation demonstrating its Contingency Reserve was restored within the Contingency Reserve Restoration Period, such as historical data, computer logs or operator logs. | 2019-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 30000000
BAL-002-2(i) (Ontario) | 79780000566 | R1. | 79780008042 | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Responsible Entity achieved less than 100% but at least 90% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period OR The Responsible Entity failed to use CR Form 1 to document a Reportable Balancing Contingency Event. | The Responsible Entity achieved less than 90% but at least 80% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 80% but at least 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2018-01-01 |  | 2019-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-002-2(i) (Ontario) | 79780000566 | R2. | 79780008048 | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Operations Planning | High | The Responsible Entity developed and implemented an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to maintain annually the Operating Process. | N/A | The Responsible Entity developed an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to implement the Operating Process. | The Responsible Entity failed to develop an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency. | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2:&lt;br/&gt;• a dated Operating Process;&lt;br/&gt;• evidence to indicate that the Operating Process has been reviewed and maintained annually; and,&lt;br/&gt;• evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. | 2018-01-01 |  | 2019-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-002-2(i) (Ontario) | 79780000566 | R3. | 79780008049 | Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | Medium | The Responsible Entity restored less than 100% but at least 90% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 90% but at least 80% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 80% but at least 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | Each Responsible Entity will have documentation demonstrating its Contingency Reserve was restored within the Contingency Reserve Restoration Period, such as historical data, computer logs or operator logs. | 2018-01-01 |  | 2019-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-002-2 (Ontario) | 79780000543 | R1. | 79780007606 | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | &lt;p&gt;The Responsible Entity achieved less than 100% but at least 90% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period OR The Responsible Entity failed to use CR Form 1 to document a Reportable Balancing Contingency Event.&lt;/p&gt; | The Responsible Entity achieved less than 90% but at least 80% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 80% but at least 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | &lt;p&gt;M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2:&lt;/p&gt; &lt;p&gt;• a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process.&lt;/p&gt; |  |  | 2017-12-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | NPCC-ON | [6 empty] | 10000000
BAL-002-2 (Ontario) | 79780000543 | R2. | 79780007607 | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Operations Planning | High | &lt;p&gt;The Responsible Entity developed and implemented an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to maintain annually the Operating Process.&lt;/p&gt; | N/A | &lt;p&gt;The Responsible Entity developed an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to implement the Operating Process.&lt;/p&gt; | The Responsible Entity failed to develop an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency. | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2:&lt;br/&gt;• a dated Operating Process;&lt;br/&gt;• evidence to indicate that the Operating Process has been reviewed and maintained annually; and,&lt;br/&gt;• evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. |  |  | 2017-12-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | NPCC-ON | [6 empty] | 20000000
BAL-002-2 (Ontario) | 79780000543 | R3. | 79780007613 | Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | Medium | The Responsible Entity restored less than 100% but at least 90% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 90% but at least 80% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 80% but at least 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | M3. Each Responsible Entity will have documentation demonstrating its Contingency Reserve was restored within the Contingency Reserve Restoration Period, such as historical data, computer logs or operator logs. |  |  | 2017-12-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | NPCC-ON | [6 empty] | 30000000
BAL-002-2 (Saskatchewan) | 83750000000543 | R1. | 837500000007606 | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Responsible Entity achieved less than 100% but at least 90% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period OR The Responsible Entity failed to use CR Form 1 to document a Reportable Balancing Contingency Event. | The Responsible Entity achieved less than 90% but at least 80% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 80% but at least 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. |  |  | 2019-09-30 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | MRO-SK | [6 empty] | 10000000
BAL-002-2 (Saskatchewan) | 83750000000543 | R2. | 837500000007607 | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Operations Planning | High | The Responsible Entity developed and implemented an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to maintain annually the Operating Process. | N/A | The Responsible Entity developed an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to implement the Operating Process. | The Responsible Entity failed to develop an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency. | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. |  |  | 2019-09-30 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | MRO-SK | [6 empty] | 20000000
BAL-002-2 (Saskatchewan) | 83750000000543 | R3. | 837500000007613 | Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | Medium | The Responsible Entity restored less than 100% but at least 90% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 90% but at least 80% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 80% but at least 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | M3. Each Responsible Entity will have documentation demonstrating its Contingency Reserve was restored within the Contingency Reserve Restoration Period, such as historical data, computer logs or operator logs. |  |  | 2019-09-30 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | MRO-SK | [6 empty] | 30000000
BAL-002-3 | 585 | R1. | 8421 | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Responsible Entity achieved less than 100% but at least 90% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period OR The Responsible Entity failed to use CR Form 1 to document a Reportable Balancing Contingency Event. | The Responsible Entity achieved less than 90% but at least 80% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 80% but at least 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2019-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-002-3 | 585 | R2. | 8422 | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Operations Planning | High | The Responsible Entity developed and implemented an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to maintain annually the Operating Process. | N/A | The Responsible Entity developed an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to implement the Operating Process. | The Responsible Entity failed to develop an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency. | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. | 2019-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-002-3 | 585 | R3. | 8428 | Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | Medium | The Responsible Entity restored less than 100% but at least 90% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 90% but at least 80% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 80% but at least 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | M3. Each Responsible Entity will have documentation demonstrating its Contingency Reserve was restored within the Contingency Reserve Restoration Period, such as historical data, computer logs or operator logs. | 2019-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-002-3 (British Columbia) | 666700000010007 | R1. | 666700000010369 | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Responsible Entity achieved less than 100% but at least 90% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period OR The Responsible Entity failed to use CR Form 1 to document a Reportable Balancing Contingency Event. | The Responsible Entity achieved less than 90% but at least 80% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 80% but at least 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2020-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | WECC-BC | [6 empty] | 10000000
BAL-002-3 (British Columbia) | 666700000010007 | R2. | 666700000010370 | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Operations Planning | High | The Responsible Entity developed and implemented an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to maintain annually the Operating Process. | N/A | The Responsible Entity developed an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to implement the Operating Process. | The Responsible Entity failed to develop an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency. | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. | 2020-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | WECC-BC | [6 empty] | 20000000
BAL-002-3 (British Columbia) | 666700000010007 | R3. | 666700000010371 | Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | Medium | The Responsible Entity restored less than 100% but at least 90% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 90% but at least 80% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 80% but at least 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | M3. Each Responsible Entity will have documentation demonstrating its Contingency Reserve was restored within the Contingency Reserve Restoration Period, such as historical data, computer logs or operator logs. | 2020-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | WECC-BC | [6 empty] | 30000000
BAL-002-3 (Manitoba) | 77660000000585 | R1. | 776600000008421 | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Responsible Entity achieved less than 100% but at least 90% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period OR The Responsible Entity failed to use CR Form 1 to document a Reportable Balancing Contingency Event. | The Responsible Entity achieved less than 90% but at least 80% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 80% but at least 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2021-01-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | MRO-MB | [6 empty] | 10000000
BAL-002-3 (Manitoba) | 77660000000585 | R2. | 776600000008422 | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Operations Planning | High | The Responsible Entity developed and implemented an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to maintain annually the Operating Process. | N/A | The Responsible Entity developed an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to implement the Operating Process. | The Responsible Entity failed to develop an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency. | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. | 2021-01-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | MRO-MB | [6 empty] | 20000000
BAL-002-3 (Manitoba) | 77660000000585 | R3. | 776600000008428 | Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | Medium | The Responsible Entity restored less than 100% but at least 90% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 90% but at least 80% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 80% but at least 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | M3. Each Responsible Entity will have documentation demonstrating its Contingency Reserve was restored within the Contingency Reserve Restoration Period, such as historical data, computer logs or operator logs. | 2021-01-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | MRO-MB | [6 empty] | 30000000
BAL-002-3 (Nova Scotia) | 78830000000585 | R1. | 788300000008421 | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Responsible Entity achieved less than 100% but at least 90% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period OR The Responsible Entity failed to use CR Form 1 to document a Reportable Balancing Contingency Event. | The Responsible Entity achieved less than 90% but at least 80% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 80% but at least 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2019-10-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | NPCC-NS | [6 empty] | 10000000
BAL-002-3 (Nova Scotia) | 78830000000585 | R2. | 788300000008422 | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Operations Planning | High | The Responsible Entity developed and implemented an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to maintain annually the Operating Process. | N/A | The Responsible Entity developed an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to implement the Operating Process. | The Responsible Entity failed to develop an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency. | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. | 2019-10-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | NPCC-NS | [6 empty] | 20000000
BAL-002-3 (Nova Scotia) | 78830000000585 | R3. | 788300000008428 | Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | Medium | The Responsible Entity restored less than 100% but at least 90% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 90% but at least 80% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 80% but at least 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | M3. Each Responsible Entity will have documentation demonstrating its Contingency Reserve was restored within the Contingency Reserve Restoration Period, such as historical data, computer logs or operator logs. | 2019-10-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | NPCC-NS | [6 empty] | 30000000
BAL-002-3 (Ontario) | 79780000585 | R1. | 79780008421 | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Responsible Entity achieved less than 100% but at least 90% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period OR The Responsible Entity failed to use CR Form 1 to document a Reportable Balancing Contingency Event. | The Responsible Entity achieved less than 90% but at least 80% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 80% but at least 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2019-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | NPCC-ON | [6 empty] | 10000000
BAL-002-3 (Ontario) | 79780000585 | R2. | 79780008422 | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Operations Planning | High | The Responsible Entity developed and implemented an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to maintain annually the Operating Process. | N/A | The Responsible Entity developed an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to implement the Operating Process. | The Responsible Entity failed to develop an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency. | &lt;p&gt;M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2:&lt;/p&gt; &lt;p&gt;• a dated Operating Process;&lt;/p&gt; &lt;p&gt;• evidence to indicate that the Operating Process has been reviewed and maintained annually; &lt;br/&gt;and,&lt;/p&gt; &lt;p&gt;• evidence such as Operating Plans or other operator documentation that demonstrate that the &lt;br/&gt;entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or &lt;br/&gt;greater than its Most Severe Single Contingency are included in this process.&lt;/p&gt; &lt;p/&gt; | 2019-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | NPCC-ON | [6 empty] | 20000000
BAL-002-3 (Ontario) | 79780000585 | R3. | 79780008428 | Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | Medium | The Responsible Entity restored less than 100% but at least 90% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 90% but at least 80% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 80% but at least 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | M3. Each Responsible Entity will have documentation demonstrating its Contingency Reserve was restored within the Contingency Reserve Restoration Period, such as historical data, computer logs or operator logs. | 2019-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | NPCC-ON | [6 empty] | 30000000
BAL-002-3 (Saskatchewan) | 83750000000585 | R1. | 837500000008421 | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Responsible Entity achieved less than 100% but at least 90% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period OR The Responsible Entity failed to use CR Form 1 to document a Reportable Balancing Contingency Event. | The Responsible Entity achieved less than 90% but at least 80% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 80% but at least 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2019-10-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | MRO-SK | [6 empty] | 10000000
BAL-002-3 (Saskatchewan) | 83750000000585 | R2. | 837500000008422 | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Operations Planning | High | The Responsible Entity developed and implemented an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to maintain annually the Operating Process. | N/A | The Responsible Entity developed an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to implement the Operating Process. | The Responsible Entity failed to develop an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency. | M2. Each Responsible Entity will have the following documentation to show compliance with Requirement R2: • a dated Operating Process; • evidence to indicate that the Operating Process has been reviewed and maintained annually; and, • evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. | 2019-10-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | MRO-SK | [6 empty] | 20000000
BAL-002-3 (Saskatchewan) | 83750000000585 | R3. | 837500000008428 | Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | Medium | The Responsible Entity restored less than 100% but at least 90% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 90% but at least 80% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 80% but at least 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | M3. Each Responsible Entity will have documentation demonstrating its Contingency Reserve was restored within the Contingency Reserve Restoration Period, such as historical data, computer logs or operator logs. | 2019-10-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | MRO-SK | [6 empty] | 30000000
BAL-002-AB-3 (Alberta) | 656600000009001 | R1. | 656600000009064 | The ISO, when it is experiencing a reportable balancing contingency event must: |  | ISO | [28 empty] | 2019-07-01 | [5 empty] | WECC-AB | [6 empty] | 10000000
BAL-002-AB-3 (Alberta) | 656600000009001 | R2. | 656600000009065 | The ISO must develop, review, and maintain annually, and implement an operating process as part of its operating plan to determine its most severe single contingency and make preparations to have contingency reserve equal to, or greater than the ISO's most severe single contingency available for maintaining system reliability. |  | ISO | [28 empty] | 2019-07-01 | [5 empty] | WECC-AB | [6 empty] | 20000000
BAL-002-AB-3 (Alberta) | 656600000009001 | R3. | 656600000009066 | The ISO, following a reportable balancing contingency event, must restore its contingency reserve to at least its most severe single contingency, before the end of the contingency reserve restoration period, but any balancing contingency event that occurs before the end of a contingency reserve restoration period resets the beginning of the contingency event recovery period. |  | ISO | [28 empty] | 2019-07-01 | [5 empty] | WECC-AB | [6 empty] | 30000000
BAL-002-WECC-1 | 6 | R1. | 37 | Each Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group shall maintain as a minimum Contingency Reserve that is the sum of the following: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | Medium | There shall be a Lower Level of non-compliance if there is one hour during a calendar month in which the Balancing Authority's or the Reserve Sharing Group's Contingency Reserve is less than 100% but greater than or equal to 90% of the required Contingency Reserve. | There shall be a Moderate Level of non-compliance if there is one hour during a calendar month in which the Balancing Authority's or the Reserve Sharing Group's Contingency Reserve is less than 90% but greater than or equal to 80% of the required Contingency Reserve. | There shall be a High Level of non-compliance if there is one hour during a calendar month in which the Balancing Authority's or the Reserve Sharing Group's Contingency Reserve is less than 80% but greater than or equal to 70% of the required Contingency Reserve. | There shall be a Severe Level of non-compliance if there is one hour during a calendar month in which the Balancing Authority's or the Reserve Sharing Group's Contingency Reserve is less than 70% of the required Contingency Reserve. | The Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group has documentation that it maintained 100% of required Contingency Reserve levels based upon data integrated over each clock hour except within the first 105 minutes (15 minute Disturbance Recovery Period, plus 90 minute Contingency Reserve Restoration Period) following an event requiring the activation of Contingency Reserves. For each hour Reserve Sharing Group or Balancing Authority shall have and provide upon request their Contingency Reserve Requirement in MW, how the requirement was calculated, and amount of Contingency Reserve available in MW. Etags and/or contracts shall be provided to document any transactions under R1.2 and R1.3. |  |  | 2010-11-26 |  |  |  | WECC-US | [5 empty] | WECC-US | 10000000
BAL-002-WECC-1 | 6 | R2. | 43 | Each Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group shall maintain at least half of the Contingency Reserve in R1.1 as Spinning Reserve. Any Spinning Reserve specified in R1 shall meet the following requirements. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | There shall be a Lower Level of non-compliance if there is one hour during a calendar month in which the Balancing Authority's or the Reserve Sharing Group's Spinning Reserve is less than 100% but greater than or equal to 90% of the required Spinning Reserve. | There shall be a Moderate Level of non-compliance if there is one hour during a calendar month in which the Balancing Authority's or the Reserve Sharing Group's Spinning Reserve is less than 90% but greater than or equal to 80% of the required Spinning Reserve. | There shall be a High Level of non-compliance if there is one hour during a calendar month in which the Balancing Authority's or the Reserve Sharing Group's Spinning Reserve is less than 80% but greater than or equal to 70% of the required Spinning Reserve. | There shall be a Severe Level of non-compliance if there is one hour during a calendar month in which the Balancing Authority's or the Reserve Sharing Group's Spinning Reserve is less than 70% of the required Spinning Reserve. | The Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group has documentation that it maintained at least 100% of minimum Spinning Contingency Reserve required based upon data averaged over each clock hour except within the first 105 minutes following an event requiring the activation of Contingency Reserves. For each hour, Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group shall have and provide upon request the Spinning Reserve Requirement in MW and amount of Spinning Reserve available in MW that is automatically responsive to frequency and can be fully deployed in 10 minutes. |  |  | 2010-11-26 |  |  |  | WECC-US | [5 empty] | WECC-US | 20000000
BAL-002-WECC-1 | 6 | R3. | 46 | Each Reserve Sharing Group or Balancing Authority shall use the following acceptable types of reserve which must be fully deployable within 10 minutes of notification to meet R1: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | Medium | N/A | N/A | There shall be a High Level of non-compliance if there is one hour during a calendar month in which the Balancing Authority or Reserve Sharing Group used unacceptable resources for Contingency Reserves. | N/A | The Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group has documentation that it used the acceptable types of reserve for each hour to meet R3. |  |  | 2010-11-26 |  |  |  | WECC-US | [5 empty] | WECC-US | 30000000
BAL-002-WECC-2 | 343 | R1. | 4457 | Each Balancing Authority and each Reserve Sharing Group shall maintain a minimum amount of Contingency Reserve, except within the first sixty minutes following an event requiring the activation of Contingency Reserve, that is: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 100% but greater than or equal to 90% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 90% but greater than or equal to 80% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 80% but greater than or equal to 70% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 70% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | M1. Each Balancing Authority and each Reserve Sharing Group will have documentation demonstrating its Contingency Reserve was maintained, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. Part 1.1 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates its Contingency Reserve was maintained in accordance with the amounts identified in Requirement R1, Part 1.1, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. Attachment A is a practical illustration showing how the generation amount may be calculated under Requirement R1.  Where Dynamic Schedules are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1 may include, but is not limited to, documentation showing a reciprocal acknowledgement as to which entity is carrying the reserves. This transfer may be all or some portion of the physical generator and is not limited to the entire physical capability of the generator.  Where Pseudo-Ties are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1, may include, but is not limited to, documentation accounting for the transfers included in the PseudoTies. Part 1.2 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.2. Evidence may include, but is not limited to, documentation that reserves were comprised of the types listed in Requirement R1, Part 1.2 for purposes of meeting the Contingency Reserve obligation of Requirement R1. Additionally, for purposes of the last bullet of Requirement R1, Part 1.2, evidence of compliance may include, but is not limited to, documentation that the reliability coordinator had issued an energy emergency alert, indicating that firm Load interruption was imminent or was in progress. Part 1.3 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.3. Evidence of compliance with Requirement R1, Part 1.3 may include, but is not limited to, documentation that Contingency Reserve amounts are based upon load and generating data averaged over each Clock Hour and excludes Qualifying Facilities covered in 18 C.F.R.§ 292.101, as addressed in FERC Order 464. Part 1.4 Evidence of compliance with Requirement R1, Part 1.4 may include, but is not limited to, documentation that the reserves maintained to comply with Requirement R1, Part 1.4 are fully deployable within ten minutes. | 2014-10-01 |  | 2017-01-23 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1. The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-US | [5 empty] | WECC-US | 10000000
BAL-002-WECC-2 | 343 | R2. | 4458 | Each Balancing Authority and each Reserve Sharing Group shall maintain at least half of its minimum amount of Contingency Reserve identified in Requirement R1, as Operating Reserve – Spinning that meets both of the following reserve characteristics. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 100% but greater than or equal to 90% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 90% but greater than or equal to 80% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 80% but greater than or equal to 70% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 70% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. | M2. Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates it maintained at least half of the Contingency Reserve identified in Requirement R1 as Operating Reserve – Spinning, averaged over each Clock Hour, that met both of the reserve characteristics identified in Requirement R2, Part 2.1 and Requirement R2, Part 2.2. | 2014-10-01 |  | 2017-01-23 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1. The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-US | [5 empty] | WECC-US | 20000000
BAL-002-WECC-2 | 343 | R3. | 4459 | Each Sink Balancing Authority and each sink Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 100% but greater than or equal to 90% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 90% but greater than or equal to 80% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 80% but greater than or equal to 70% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 70% of the required Operating Reserve amount specified in Requirement R3. | M3. Each Sink Balancing Authority and each sink Reserve Sharing Group will have dated documentation demonstrating it maintained an amount of Operating Reserve, in addition to the Contingency Reserve identified in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, for the entire period of the transaction, except within the first sixty minutes following an event requiring the activation of Contingency Reserves, in accordance with Requirement 3. | 2014-10-01 |  | 2017-01-23 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1. The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-US | [5 empty] | WECC-US | 30000000
BAL-002-WECC-2 | 343 | R4. | 4460 | Each Source Balancing Authority and each source Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve amounts identified in Requirement R1, equal to the amount and type of Operating Reserves for any Operating Reserve transactions for which it is the Source Balancing Authority or source Reserve Sharing Group. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 100% but greater than or equal to 90% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 90% but greater than or equal to 80% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 80% but greater than or equal to 70% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 70% of the required Operating Reserve amount specified in Requirement R4. | M4. Each Source Balancing Authority and each source Reserve Sharing Group will have dated documentation that demonstrates it maintained an amount of additional Operating Reserves identified in Requirement R1, greater than or equal to the amount and type of that identified in Requirement 4, for the entire period of the transaction. | 2014-10-01 |  | 2017-01-23 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1. The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-US | [5 empty] | WECC-US | 40000000
BAL-002-WECC-2a | 557 | R1. | 7874 | Each Balancing Authority and each Reserve Sharing Group shall maintain a minimum amount of Contingency Reserve, except within the first sixty minutes following an event requiring the activation of Contingency Reserve, that is: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 100% but greater than or equal to 90% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 90% but greater than or equal to 80% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 80% but greater than or equal to 70% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 70% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | M1. Each Balancing Authority and each Reserve Sharing Group will have documentation demonstrating its Contingency Reserve was maintained, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. | 2017-01-24 |  | 2021-06-27 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1.The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-US | [5 empty] | WECC-US | 10000000
BAL-002-WECC-2a | 557 | R2. | 7879 | Each Balancing Authority and each Reserve Sharing Group shall maintain at least half of its minimum amount of Contingency Reserve identified in Requirement R1, as Operating Reserve – Spinning that meets both of the following reserve characteristics. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 100% but greater than or equal to 90% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 90% but greater than or equal to 80% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 80% but greater than or equal to 70% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 70% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. | M2. Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates it maintained at least half of the Contingency Reserve identified in Requirement R1 as Operating Reserve – Spinning, averaged over each Clock Hour, that met both of the reserve characteristics identified in Requirement R2, Part 2.1 and Requirement R2, Part 2.2. | 2017-01-24 |  | 2021-06-27 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1.The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-US | [5 empty] | WECC-US | 20000000
BAL-002-WECC-2a | 557 | R3. | 7882 | Each Sink Balancing Authority and each sink Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 100% but greater than or equal to 90% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 90% but greater than or equal to 80% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 80% but greater than or equal to 70% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 70% of the required Operating Reserve amount specified in Requirement R3. | M3. Each Sink Balancing Authority and each sink Reserve Sharing Group will have dated documentation demonstrating it maintained an amount of Operating Reserve, in addition to the Contingency Reserve identified in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, for the entire period of the transaction, except within the first sixty minutes following an event requiring the activation of Contingency Reserves, in accordance with Requirement 3. | 2017-01-24 |  | 2021-06-27 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1.The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-US | [5 empty] | WECC-US | 30000000
BAL-002-WECC-2a | 557 | R4. | 7883 | Each Source Balancing Authority and each source Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve amounts identified in Requirement R1, equal to the amount and type of Operating Reserves for any Operating Reserve transactions for which it is the Source Balancing Authority or source Reserve Sharing Group. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 100% but greater than or equal to 90% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 90% but greater than or equal to 80% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 80% but greater than or equal to 70% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 70% of the required Operating Reserve amount specified in Requirement R4. | M4. Each Source Balancing Authority and each source Reserve Sharing Group will have dated documentation that demonstrates it maintained an amount of additional Operating Reserves identified in Requirement R1, greater than or equal to the amount and type of that identified in Requirement 4, for the entire period of the transaction. | 2017-01-24 |  | 2021-06-27 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1.The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-US | [5 empty] | WECC-US | 40000000
BAL-002-WECC-2a (British Columbia) | 666700000010009 | R1. | 666700000010376 | Each Balancing Authority and each Reserve Sharing Group shall maintain a minimum amount of Contingency Reserve, except within the first sixty minutes following an event requiring the activation of Contingency Reserve, that is: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 100% but greater than or equal to 90% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 90% but greater than or equal to 80% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 80% but greater than or equal to 70% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 70% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | M1. Each Balancing Authority and each Reserve Sharing Group will have documentation demonstrating its Contingency Reserve was maintained, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. | 2017-07-26 |  | 2022-10-28 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1.The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-BC | [6 empty] | 10000000
BAL-002-WECC-2a (British Columbia) | 666700000010009 | R2. | 666700000010377 | Each Balancing Authority and each Reserve Sharing Group shall maintain at least half of its minimum amount of Contingency Reserve identified in Requirement R1, as Operating Reserve – Spinning that meets both of the following reserve characteristics. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 100% but greater than or equal to 90% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 90% but greater than or equal to 80% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 80% but greater than or equal to 70% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 70% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. | M2. Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates it maintained at least half of the Contingency Reserve identified in Requirement R1 as Operating Reserve – Spinning, averaged over each Clock Hour, that met both of the reserve characteristics identified in Requirement R2, Part 2.1 and Requirement R2, Part 2.2. | 2017-07-26 |  | 2022-10-28 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1.The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-BC | [6 empty] | 20000000
BAL-002-WECC-2a (British Columbia) | 666700000010009 | R3. | 666700000010378 | Each Sink Balancing Authority and each sink Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 100% but greater than or equal to 90% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 90% but greater than or equal to 80% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 80% but greater than or equal to 70% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 70% of the required Operating Reserve amount specified in Requirement R3. | M3. Each Sink Balancing Authority and each sink Reserve Sharing Group will have dated documentation demonstrating it maintained an amount of Operating Reserve, in addition to the Contingency Reserve identified in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, for the entire period of the transaction, except within the first sixty minutes following an event requiring the activation of Contingency Reserves, in accordance with Requirement 3. | 2017-07-26 |  | 2022-10-28 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1.The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-BC | [6 empty] | 30000000
BAL-002-WECC-2a (British Columbia) | 666700000010009 | R4. | 666700000010379 | Each Source Balancing Authority and each source Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve amounts identified in Requirement R1, equal to the amount and type of Operating Reserves for any Operating Reserve transactions for which it is the Source Balancing Authority or source Reserve Sharing Group. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 100% but greater than or equal to 90% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 90% but greater than or equal to 80% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 80% but greater than or equal to 70% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 70% of the required Operating Reserve amount specified in Requirement R4. | M4. Each Source Balancing Authority and each source Reserve Sharing Group will have dated documentation that demonstrates it maintained an amount of additional Operating Reserves identified in Requirement R1, greater than or equal to the amount and type of that identified in Requirement 4, for the entire period of the transaction. | 2017-07-26 |  | 2022-10-28 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1.The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-BC | [6 empty] | 40000000
BAL-002-WECC-2 (British Columbia) | 666700000010008 | R1. | 666700000010372 | Each Balancing Authority and each Reserve Sharing Group shall maintain a minimum amount of Contingency Reserve, except within the first sixty minutes following an event requiring the activation of Contingency Reserve, that is: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 100% but greater than or equal to 90% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 90% but greater than or equal to 80% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 80% but greater than or equal to 70% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 70% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | M1. Each Balancing Authority and each Reserve Sharing Group will have documentation demonstrating its Contingency Reserve was maintained, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. Part 1.1 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates its Contingency Reserve was maintained in accordance with the amounts identified in Requirement R1, Part 1.1, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. Attachment A is a practical illustration showing how the generation amount may be calculated under Requirement R1.  Where Dynamic Schedules are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1 may include, but is not limited to, documentation showing a reciprocal acknowledgement as to which entity is carrying the reserves. This transfer may be all or some portion of the physical generator and is not limited to the entire physical capability of the generator.  Where Pseudo-Ties are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1, may include, but is not limited to, documentation accounting for the transfers included in the PseudoTies. Part 1.2 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.2. Evidence may include, but is not limited to, documentation that reserves were comprised of the types listed in Requirement R1, Part 1.2 for purposes of meeting the Contingency Reserve obligation of Requirement R1. Additionally, for purposes of the last bullet of Requirement R1, Part 1.2, evidence of compliance may include, but is not limited to, documentation that the reliability coordinator had issued an energy emergency alert, indicating that firm Load interruption was imminent or was in progress. Part 1.3 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.3. Evidence of compliance with Requirement R1, Part 1.3 may include, but is not limited to, documentation that Contingency Reserve amounts are based upon load and generating data averaged over each Clock Hour and excludes Qualifying Facilities covered in 18 C.F.R.§ 292.101, as addressed in FERC Order 464. Part 1.4 Evidence of compliance with Requirement R1, Part 1.4 may include, but is not limited to, documentation that the reserves maintained to comply with Requirement R1, Part 1.4 are fully deployable within ten minutes. | 2014-10-01 |  | 2017-07-25 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1. The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-BC | [6 empty] | 10000000
BAL-002-WECC-2 (British Columbia) | 666700000010008 | R2. | 666700000010373 | Each Balancing Authority and each Reserve Sharing Group shall maintain at least half of its minimum amount of Contingency Reserve identified in Requirement R1, as Operating Reserve – Spinning that meets both of the following reserve characteristics. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 100% but greater than or equal to 90% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 90% but greater than or equal to 80% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 80% but greater than or equal to 70% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 70% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. | M2. Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates it maintained at least half of the Contingency Reserve identified in Requirement R1 as Operating Reserve – Spinning, averaged over each Clock Hour, that met both of the reserve characteristics identified in Requirement R2, Part 2.1 and Requirement R2, Part 2.2. | 2014-10-01 |  | 2017-07-25 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1. The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-BC | [6 empty] | 20000000
BAL-002-WECC-2 (British Columbia) | 666700000010008 | R3. | 666700000010374 | Each Sink Balancing Authority and each sink Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 100% but greater than or equal to 90% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 90% but greater than or equal to 80% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 80% but greater than or equal to 70% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 70% of the required Operating Reserve amount specified in Requirement R3. | M3. Each Sink Balancing Authority and each sink Reserve Sharing Group will have dated documentation demonstrating it maintained an amount of Operating Reserve, in addition to the Contingency Reserve identified in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, for the entire period of the transaction, except within the first sixty minutes following an event requiring the activation of Contingency Reserves, in accordance with Requirement 3. | 2014-10-01 |  | 2017-07-25 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1. The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-BC | [6 empty] | 30000000
BAL-002-WECC-2 (British Columbia) | 666700000010008 | R4. | 666700000010375 | Each Source Balancing Authority and each source Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve amounts identified in Requirement R1, equal to the amount and type of Operating Reserves for any Operating Reserve transactions for which it is the Source Balancing Authority or source Reserve Sharing Group. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 100% but greater than or equal to 90% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 90% but greater than or equal to 80% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 80% but greater than or equal to 70% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 70% of the required Operating Reserve amount specified in Requirement R4. | M4. Each Source Balancing Authority and each source Reserve Sharing Group will have dated documentation that demonstrates it maintained an amount of additional Operating Reserves identified in Requirement R1, greater than or equal to the amount and type of that identified in Requirement 4, for the entire period of the transaction. | 2014-10-01 |  | 2017-07-25 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1. The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-BC | [6 empty] | 40000000
BAL-002-WECC-3 | 606 | R1. | 8835 | Each Balancing Authority and each Reserve Sharing Group shall maintain a minimum amount of Contingency Reserve, except within the first sixty minutes following an event requiring the activation of Contingency Reserve, that is: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 100% but greater than or equal to 90% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 90% but greater than or equal to 80% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 80% but greater than or equal to 70% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 70% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | M1. Each Balancing Authority and each Reserve Sharing Group will have documentation demonstrating its Contingency Reserve was maintained, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. | 2021-06-28 |  |  |  | 4.1.2.1 The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.1.2.2 The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-US | [5 empty] | WECC-US | 10000000
BAL-002-WECC-3 | 606 | R2. | 8836 | Reserved. | [29 empty] | Reserved | 2021-06-28 |  |  |  | 4.1.2.1 The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.1.2.2 The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-US | [5 empty] | WECC-US | 20000000
BAL-002-WECC-3 | 606 | R3. | 8837 | Each Sink Balancing Authority and each sink Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 100% but greater than or equal to 90% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 90% but greater than or equal to 80% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 80% but greater than or equal to 70% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 70% of the required Operating Reserve amount specified in Requirement R3. | M3. Each Sink Balancing Authority and each sink Reserve Sharing Group will have dated documentation demonstrating it maintained an amount of Operating Reserve, in addition to the Contingency Reserve identified in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, for the entire period of the transaction, except within the first sixty minutes following an event requiring the activation of Contingency Reserves, in accordance with Requirement 3. | 2021-06-28 |  |  |  | 4.1.2.1 The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.1.2.2 The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-US | [5 empty] | WECC-US | 30000000
BAL-002-WECC-3 | 606 | R4. | 8838 | Each Source Balancing Authority and each source Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve amounts identified in Requirement R1, equal to the amount and type of Operating Reserves for any Operating Reserve transactions for which it is the Source Balancing Authority or source Reserve Sharing Group. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 100% but greater than or equal to 90% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 90% but greater than or equal to 80% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 80% but greater than or equal to 70% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 70% of the required Operating Reserve amount specified in Requirement R4. | M4. Each Source Balancing Authority and each source Reserve Sharing Group will have dated documentation that demonstrates it maintained an amount of additional Operating Reserves identified in Requirement R1, greater than or equal to the amount and type of that identified in Requirement 4, for the entire period of the transaction. | 2021-06-28 |  |  |  | 4.1.2.1 The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.1.2.2 The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-US | [5 empty] | WECC-US | 40000000
BAL-002-WECC-3 (British Columbia) | 666700000010335 | R1. | 666700000014827 | Each Balancing Authority and each Reserve Sharing Group shall maintain a minimum amount of Contingency Reserve, except within the first sixty minutes following an event requiring the activation of Contingency Reserve, that is: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 100% but greater than or equal to 90% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 90% but greater than or equal to 80% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 80% but greater than or equal to 70% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 70% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | M1. Each Balancing Authority and each Reserve Sharing Group will have documentation demonstrating its Contingency Reserve was maintained, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. | 2022-10-29 |  |  |  | 4.1.2.1 The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.1.2.2 The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-BC | [6 empty] | 10000000
BAL-002-WECC-3 (British Columbia) | 666700000010335 | R2. | 666700000014828 | Reserved. | [29 empty] | Reserved | 2022-10-29 |  |  |  | 4.1.2.1 The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.1.2.2 The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-BC | [6 empty] | 20000000
BAL-002-WECC-3 (British Columbia) | 666700000010335 | R3. | 666700000014829 | Each Sink Balancing Authority and each sink Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 100% but greater than or equal to 90% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 90% but greater than or equal to 80% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 80% but greater than or equal to 70% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 70% of the required Operating Reserve amount specified in Requirement R3. | M3. Each Sink Balancing Authority and each sink Reserve Sharing Group will have dated documentation demonstrating it maintained an amount of Operating Reserve, in addition to the Contingency Reserve identified in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, for the entire period of the transaction, except within the first sixty minutes following an event requiring the activation of Contingency Reserves, in accordance with Requirement 3. | 2022-10-29 |  |  |  | 4.1.2.1 The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.1.2.2 The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-BC | [6 empty] | 30000000
BAL-002-WECC-3 (British Columbia) | 666700000010335 | R4. | 666700000014830 | Each Source Balancing Authority and each source Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve amounts identified in Requirement R1, equal to the amount and type of Operating Reserves for any Operating Reserve transactions for which it is the Source Balancing Authority or source Reserve Sharing Group. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Real-Time Operations | High | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 100% but greater than or equal to 90% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 90% but greater than or equal to 80% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 80% but greater than or equal to 70% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 70% of the required Operating Reserve amount specified in Requirement R4. | M4. Each Source Balancing Authority and each source Reserve Sharing Group will have dated documentation that demonstrates it maintained an amount of additional Operating Reserves identified in Requirement R1, greater than or equal to the amount and type of that identified in Requirement 4, for the entire period of the transaction. | 2022-10-29 |  |  |  | 4.1.2.1 The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.1.2.2 The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | WECC-BC | [6 empty] | 40000000
BAL-002-WECC-AB1-2 (Alberta) | 656600000009002 | R1. | 656600000009067 | The ISO must have held, at a minimum, an average amount of contingency reserve that is: |  | ISO | [28 empty] | 2015-07-26 | [5 empty] | WECC-AB | [6 empty] | 10000000
BAL-002-WECC-AB1-2 (Alberta) | 656600000009002 | R2. | 656600000009068 | The ISO must maintain at least fifty percent (50%) of its minimum amount of contingency reserve required in requirement R1 as spinning reserve that is immediately and automatically responsive to frequency deviations through the action of a governor or other control system. |  | ISO | [28 empty] | 2015-07-26 | [5 empty] | WECC-AB | [6 empty] | 20000000
BAL-002-WECC-AB1-2 (Alberta) | 656600000009002 | R3. | 656600000009069 | The ISO must, when operating as a sink balancing authority, maintain an amount of operating reserve, in addition to the minimum contingency reserve required in requirement R1, equal to the amount of supplemental reserve for any interchange transaction designated as part of the supplemental reserve of the source balancing authority or source reserve sharing group, except within the first sixty (60) minutes following an event requiring the activation of contingency reserve or except following the deployment of contingency reserve during implementation of the ISOs capacity and energy emergency plan. |  | ISO | [28 empty] | 2015-07-26 | [5 empty] | WECC-AB | [6 empty] | 30000000
BAL-002-WECC-AB1-2 (Alberta) | 656600000009002 | R4. | 656600000009070 | The ISO must, when operating as a source balancing authority, maintain an amount of operating reserve, in addition to the minimum contingency reserve amounts required in requirement R1, equal to the amount and type of operating reserve for any operating reserve transactions for which it is the source balancing authority. |  | ISO | [28 empty] | 2015-07-26 | [5 empty] | WECC-AB | [6 empty] | 40000000
BAL-003-0 | 7 | R1. | 53 | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  | BA | BA | [21 empty] | Low | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-003-0 | 7 | R2. | 56 | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: |  | BA | BA | [21 empty] | Low | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-003-0 | 7 | R3. | 59 | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. |  | BA | BA | [21 empty] | Low | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-003-0 | 7 | R4. | 60 | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  | BA | BA | [21 empty] | Low | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-003-0 | 7 | R5. | 63 | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. |  | BA | BA | [21 empty] | Low | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
BAL-003-0 | 7 | R6. | 65 | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
BAL-003-0.1a | 282 | R1. | 3714 | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  | BA | BA | [27 empty] | 2009-05-13 |  | 2009-06-28 |  |  | BAL-003-0.1a R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-003-0.1a | 282 | R2. | 3713 | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: |  | BA | BA | [27 empty] | 2009-05-13 |  | 2009-06-28 |  |  | BAL-003-0.1a R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-003-0.1a | 282 | R3. | 3716 | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. |  | BA | BA | [27 empty] | 2009-05-13 |  | 2009-06-28 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-003-0.1a | 282 | R4. | 3715 | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  | BA | BA | [27 empty] | 2009-05-13 |  | 2009-06-28 |  |  | BAL-003-0.1a R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-003-0.1a | 282 | R5. | 3712 | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. |  | BA | BA | [27 empty] | 2009-05-13 |  | 2009-06-28 |  |  | BAL-003-0.1a R5. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
BAL-003-0.1a | 282 | R6. | 3717 | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. |  | BA | BA | [27 empty] | 2009-05-13 |  | 2009-06-28 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
BAL-003-0.1a (Ontario) | 79780000282 | R1. | 79780003714 | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  | BA | BA | [24 empty] | The Balancing Authority reviewed its Frequency Bias Settings prior January 1, but failed to recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. | The Balancing Authority failed to review its Frequency Bias Settings prior to January 1, and failed to recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  | 2009-05-13 |  | 2009-06-28 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-003-0.1a (Ontario) | 79780000282 | R2. | 79780003713 | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: |  | BA | BA | [25 empty] | The Balancing Authority established and maintained a Frequency Bias Setting that was less than, the Balancing Authority’s Frequency Response. |  | 2009-05-13 |  | 2009-06-28 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-003-0.1a (Ontario) | 79780000282 | R3. | 79780003716 | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. |  | BA | BA | [25 empty] | The Balancing Authority did not operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, during periods when such operation would not have been adverse to system or Interconnection reliability. |  | 2009-05-13 |  | 2009-06-28 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-003-0.1a (Ontario) | 79780000282 | R4. | 79780003715 | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  | BA | BA | [25 empty] | The Balancing Authority that used Dynamic Scheduling or Pseudo-ties for jointly owned units did not reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  | 2009-05-13 |  | 2009-06-28 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-003-0.1a (Ontario) | 79780000282 | R5. | 79780003712 | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. |  | BA | BA | [25 empty] | The Balancing Authority that served native load failed to have a monthly average Frequency Bias Setting that was at least 1% of the entities estimated yearly peak demand per 0.1 Hz change. |  | 2009-05-13 |  | 2009-06-28 |  |  |  | NPCC-ON | [6 empty] | 50000000
BAL-003-0.1a (Ontario) | 79780000282 | R6. | 79780003717 | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. |  | BA | BA | [23 empty] | The Balancing Authority that was performing Overlap Regulation Service changed its Frequency Bias Setting while performing Supplemental Regulation Service. | The Balancing Authority that was performing Overlap Regulation Service failed to increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. |  |  | 2009-05-13 |  | 2009-06-28 |  |  |  | NPCC-ON | [6 empty] | 60000000
BAL-003-0.1b | 8 | R1. | 66 | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  | BA | BA | [21 empty] | Low |  |  |  |  | M1. Each Balancing Authority shall perform Frequency Response surveys when called for by the Operating Committee to determine the Balancing Authority’s response to Interconnection Frequency Deviations. | 2009-06-29 |  | 2015-03-31 |  |  | BAL-003-0.1b R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-003-0.1b | 8 | R2. | 69 | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: |  | BA | BA | [21 empty] | Medium | [5 empty] | 2009-06-29 |  | 2015-03-31 |  |  | BAL-003-0.1b R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-003-0.1b | 8 | R3. | 72 | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2009-06-29 |  | 2015-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-003-0.1b | 8 | R4. | 73 | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  | BA | BA | [21 empty] | Low | [5 empty] | 2009-06-29 |  | 2015-03-31 |  |  | BAL-003-0.1b R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-003-0.1b | 8 | R5. | 76 | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2009-06-29 |  | 2015-03-31 |  |  | BAL-003-0.1b R5. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
BAL-003-0.1b | 8 | R6. | 78 | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2009-06-29 |  | 2015-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
BAL-003-0.1b (British Columbia) | 666700000010010 | R1. | 666700000010380 | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  | BA | BA | [21 empty] | Low |  |  |  |  | M1. Each Balancing Authority shall perform Frequency Response surveys when called for by the Operating Committee to determine the Balancing Authority’s response to Interconnection Frequency Deviations. | 2011-01-01 |  | 2016-03-31 |  |  |  | WECC-BC | [6 empty] | 10000000
BAL-003-0.1b (British Columbia) | 666700000010010 | R2. | 666700000010381 | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: |  | BA | BA | [21 empty] | Medium | [5 empty] | 2011-01-01 |  | 2016-03-31 |  |  |  | WECC-BC | [6 empty] | 20000000
BAL-003-0.1b (British Columbia) | 666700000010010 | R3. | 666700000010382 | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2011-01-01 |  | 2016-03-31 |  |  |  | WECC-BC | [6 empty] | 30000000
BAL-003-0.1b (British Columbia) | 666700000010010 | R4. | 666700000010383 | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  | BA | BA | [21 empty] | Low | [5 empty] | 2011-01-01 |  | 2016-03-31 |  |  |  | WECC-BC | [6 empty] | 40000000
BAL-003-0.1b (British Columbia) | 666700000010010 | R5. | 666700000010384 | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2011-01-01 |  | 2016-03-31 |  |  |  | WECC-BC | [6 empty] | 50000000
BAL-003-0.1b (British Columbia) | 666700000010010 | R6. | 666700000010385 | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2011-01-01 |  | 2016-03-31 |  |  |  | WECC-BC | [6 empty] | 60000000
BAL-003-0.1b (Manitoba) | 776600000008 | R1. | 7766000000066 | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  | BA | BA | [21 empty] | Low |  |  |  |  | M1. Each Balancing Authority shall perform Frequency Response surveys when called for by the Operating Committee to determine the Balancing Authority’s response to Interconnection Frequency Deviations. | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
BAL-003-0.1b (Manitoba) | 776600000008 | R2. | 7766000000069 | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: |  | BA | BA | [21 empty] | Medium | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
BAL-003-0.1b (Manitoba) | 776600000008 | R3. | 7766000000072 | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
BAL-003-0.1b (Manitoba) | 776600000008 | R4. | 7766000000073 | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  | BA | BA | [21 empty] | Low | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 40000000
BAL-003-0.1b (Manitoba) | 776600000008 | R5. | 7766000000076 | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 50000000
BAL-003-0.1b (Manitoba) | 776600000008 | R6. | 7766000000078 | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 60000000
BAL-003-0.1b (Ontario) | 79780000008 | R1. | 79780000066 | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  | BA | BA | [21 empty] | Low |  |  | The Balancing Authority reviewed its Frequency Bias Settings prior January 1, but failed to recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. | The Balancing Authority failed to review its Frequency Bias Settings prior to January 1, and failed to recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. | M1. Each Balancing Authority shall perform Frequency Response surveys when called for by the Operating Committee to determine the Balancing Authority’s response to Interconnection Frequency Deviations. | 2009-06-29 |  | 2015-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-003-0.1b (Ontario) | 79780000008 | R2. | 79780000069 | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: |  | BA | BA | [21 empty] | Medium | N/A | The Balancing Authority’s determination of the fixed Frequency Bias value was not based on observations and averaging the Frequency Response from Disturbances during on-peak hours. OR The Balancing Authority’s variable frequency bias maintained was not ba | N/A | The Balancing Authority did not establish and maintain a Frequency Bias Setting that was as close as practical to, or greater than, the Balancing Authority’s Frequency Response. |  | 2009-06-29 |  | 2015-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-003-0.1b (Ontario) | 79780000008 | R3. | 79780000072 | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority did not operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, during periods when such operation would not have been adverse to system or Interconnection reliability. |  | 2009-06-29 |  | 2015-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-003-0.1b (Ontario) | 79780000008 | R4. | 79780000073 | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority that used Dynamic Scheduling or Pseudo-ties for jointly owned units did not reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  | 2009-06-29 |  | 2015-03-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-003-0.1b (Ontario) | 79780000008 | R5. | 79780000076 | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority that served native load failed to have a monthly average Frequency Bias Setting that was at least 1% of the entities estimated yearly peak demand per 0.1 Hz change. |  | 2009-06-29 |  | 2015-03-31 |  |  |  | NPCC-ON | [6 empty] | 50000000
BAL-003-0.1b (Ontario) | 79780000008 | R6. | 79780000078 | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. |  | BA | BA | [21 empty] | Medium |  | The Balancing Authority that was performing Overlap Regulation Service changed its Frequency Bias Setting while performing Supplemental Regulation Service. | The Balancing Authority that was performing Overlap Regulation Service failed to increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. |  |  | 2009-06-29 |  | 2015-03-31 |  |  |  | NPCC-ON | [6 empty] | 60000000
BAL-003-0.1b (Saskatchewan) | 837500000008 | R1. | 8375000000066 | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  | BA | BA | [21 empty] | Low |  |  |  |  | M1. Each Balancing Authority shall perform Frequency Response surveys when called for by the Operating Committee to determine the Balancing Authority’s response to Interconnection Frequency Deviations. | 2010-03-30 |  | 2015-03-31 |  |  |  | MRO-SK | [6 empty] | 10000000
BAL-003-0.1b (Saskatchewan) | 837500000008 | R2. | 8375000000069 | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: |  | BA | BA | [21 empty] | Medium | [5 empty] | 2010-03-30 |  | 2015-03-31 |  |  |  | MRO-SK | [6 empty] | 20000000
BAL-003-0.1b (Saskatchewan) | 837500000008 | R3. | 8375000000072 | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2010-03-30 |  | 2015-03-31 |  |  |  | MRO-SK | [6 empty] | 30000000
BAL-003-0.1b (Saskatchewan) | 837500000008 | R4. | 8375000000073 | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  | BA | BA | [21 empty] | Low | [5 empty] | 2010-03-30 |  | 2015-03-31 |  |  |  | MRO-SK | [6 empty] | 40000000
BAL-003-0.1b (Saskatchewan) | 837500000008 | R5. | 8375000000076 | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2010-03-30 |  | 2015-03-31 |  |  |  | MRO-SK | [6 empty] | 50000000
BAL-003-0.1b (Saskatchewan) | 837500000008 | R6. | 8375000000078 | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2010-03-30 |  | 2015-03-31 |  |  |  | MRO-SK | [6 empty] | 60000000
BAL-003-0a | 9 | R1. | 79 | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  | BA | BA | [27 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-003-0a R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-003-0a | 9 | R2. | 82 | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: |  | BA | BA | [27 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-003-0a R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-003-0a | 9 | R3. | 85 | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. |  | BA | BA | [27 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-003-0a R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-003-0a | 9 | R4. | 86 | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  | BA | BA | [27 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-003-0a R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-003-0a | 9 | R5. | 89 | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. |  | BA | BA | [20 empty] | Real-Time Operations | [6 empty] | 2008-08-27 |  | 2009-05-12 | In those jurisdictions where regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after Board of Trustees adoption. Requirement R1 cannot be implemented prior to the addition of Frequency Response Sharing Group to the Compliance Registry. |  | BAL-003-0a R5. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
BAL-003-0a | 9 | R6. | 91 | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. |  | BA | BA | [20 empty] | Operations Planning | [6 empty] | 2008-08-27 |  | 2009-05-12 | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. |  | BAL-003-0a R6. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
BAL-003-0a (British Columbia) | 666700000010011 | R1. | 666700000010386 | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  | BA | BA | [27 empty] | 2010-12-31 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 10000000
BAL-003-0a (British Columbia) | 666700000010011 | R2. | 666700000010387 | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: |  | BA | BA | [27 empty] | 2010-12-31 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 20000000
BAL-003-0a (British Columbia) | 666700000010011 | R3. | 666700000010388 | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. |  | BA | BA | [27 empty] | 2010-12-31 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 30000000
BAL-003-0a (British Columbia) | 666700000010011 | R4. | 666700000010389 | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  | BA | BA | [27 empty] | 2010-12-31 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 40000000
BAL-003-0a (British Columbia) | 666700000010011 | R5. | 666700000010390 | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. |  | BA | BA | [20 empty] | Real-Time Operations | [6 empty] | 2010-12-31 |  | 2010-12-31 | In those jurisdictions where regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after Board of Trustees adoption. Requirement R1 cannot be implemented prior to the addition of Frequency Response Sharing Group to the Compliance Registry. |  |  | WECC-BC | [6 empty] | 50000000
BAL-003-0a (British Columbia) | 666700000010011 | R6. | 666700000010391 | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. |  | BA | BA | [20 empty] | Operations Planning | [6 empty] | 2010-12-31 |  | 2010-12-31 | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. |  |  | WECC-BC | [6 empty] | 60000000
BAL-003-0a (Ontario) | 79780000009 | R1. | 79780000079 | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  | BA | BA | [24 empty] | The Balancing Authority reviewed its Frequency Bias Settings prior January 1, but failed to recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. | The Balancing Authority failed to review its Frequency Bias Settings prior to January 1, and failed to recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-003-0a (Ontario) | 79780000009 | R2. | 79780000082 | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: |  | BA | BA | [25 empty] | The Balancing Authority established and maintained a Frequency Bias Setting that was less than, the Balancing Authority’s Frequency Response. |  | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-003-0a (Ontario) | 79780000009 | R3. | 79780000085 | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. |  | BA | BA | [25 empty] | The Balancing Authority did not operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, during periods when such operation would not have been adverse to system or Interconnection reliability. |  | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-003-0a (Ontario) | 79780000009 | R4. | 79780000086 | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  | BA | BA | [25 empty] | The Balancing Authority that used Dynamic Scheduling or Pseudo-ties for jointly owned units did not reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-003-0a (Ontario) | 79780000009 | R5. | 79780000089 | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. |  | BA | BA | [20 empty] | Real-Time Operations |  |  |  |  | The Balancing Authority that served native load failed to have a monthly average Frequency Bias Setting that was at least 1% of the entities estimated yearly peak demand per 0.1 Hz change. | M1. Each Frequency Response Sharing Group or Balancing Authority that is not a member of a Frequency Response Sharing Group shall have evidence such as dated data plus documented formula in either hardcopy or electronic format that it achieved an annual FRM (in accordance with the methods specified by the ERO in Attachment A with data from FRS Form 1 reported to the ERO as specified in Attachment A) that is equal to or more negative than its FRO to demonstrate compliance with Requirement R1. | 2008-08-27 |  | 2009-05-12 | In those jurisdictions where regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after Board of Trustees adoption.&lt;br/&gt;&lt;br/&gt;Requirement R1 cannot be implemented prior to the addition of Frequency Response Sharing Group to the Compliance Registry. |  |  | NPCC-ON | [6 empty] | 50000000
BAL-003-0a (Ontario) | 79780000009 | R6. | 79780000091 | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. |  | BA | BA | [20 empty] | Operations Planning |  |  | The Balancing Authority that was performing Overlap Regulation Service changed its Frequency Bias Setting while performing Supplemental Regulation Service. | The Balancing Authority that was performing Overlap Regulation Service failed to increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. |  | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | 2008-08-27 |  | 2009-05-12 | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. |  |  | NPCC-ON | [6 empty] | 60000000
BAL-003-0b | 10 | R1. | 92 | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  | BA | BA | [20 empty] | Operations Planning | [8 empty] | 2009-06-28 |  |  | BAL-003-0b R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-003-0b | 10 | R2. | 95 | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: |  | BA | BA | [29 empty] | 2009-06-28 |  |  | BAL-003-0b R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-003-0b | 10 | R3. | 98 | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability |  | BA | BA | [29 empty] | 2009-06-28 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-003-0b | 10 | R4. | 99 | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  | BA | BA | [29 empty] | 2009-06-28 |  |  | BAL-003-0b R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-003-0b | 10 | R5. | 102 | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. |  | BA | BA | [29 empty] | 2009-06-28 |  |  | BAL-003-0b R5. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
BAL-003-0b | 10 | R6. | 104 | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. |  | BA | BA | [29 empty] | 2009-06-28 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
BAL-003-0b (Ontario) | 79780000010 | R1. | 79780000092 | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  | BA | BA | [20 empty] | Operations Planning |  |  |  | The Balancing Authority reviewed its Frequency Bias Settings prior January 1, but failed to recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. | The Balancing Authority failed to review its Frequency Bias Settings prior to January 1, and failed to recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  |  |  | 2009-06-28 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-003-0b (Ontario) | 79780000010 | R2. | 79780000095 | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: |  | BA | BA | [25 empty] | The Balancing Authority established and maintained a Frequency Bias Setting that was less than, the Balancing Authority’s Frequency Response. |  |  |  | 2009-06-28 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-003-0b (Ontario) | 79780000010 | R3. | 79780000098 | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability |  | BA | BA | [25 empty] | The Balancing Authority did not operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, during periods when such operation would not have been adverse to system or Interconnection reliability. |  |  |  | 2009-06-28 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-003-0b (Ontario) | 79780000010 | R4. | 79780000099 | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  | BA | BA | [25 empty] | The Balancing Authority that used Dynamic Scheduling or Pseudo-ties for jointly owned units did not reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  |  |  | 2009-06-28 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-003-0b (Ontario) | 79780000010 | R5. | 79780000102 | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. |  | BA | BA | [25 empty] | The Balancing Authority that served native load failed to have a monthly average Frequency Bias Setting that was at least 1% of the entities estimated yearly peak demand per 0.1 Hz change. |  |  |  | 2009-06-28 |  |  |  | NPCC-ON | [6 empty] | 50000000
BAL-003-0b (Ontario) | 79780000010 | R6. | 79780000104 | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. |  | BA | BA | [23 empty] | The Balancing Authority that was performing Overlap Regulation Service changed its Frequency Bias Setting while performing Supplemental Regulation Service. | The Balancing Authority that was performing Overlap Regulation Service failed to increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. |  |  |  |  | 2009-06-28 |  |  |  | NPCC-ON | [6 empty] | 60000000
BAL-003-0 (Manitoba) | 776600000007 | R1. | 7766000000053 | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  | BA | BA | [21 empty] | Low | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 10000000
BAL-003-0 (Manitoba) | 776600000007 | R2. | 7766000000056 | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: |  | BA | BA | [21 empty] | Low | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 20000000
BAL-003-0 (Manitoba) | 776600000007 | R3. | 7766000000059 | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. |  | BA | BA | [21 empty] | Low | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 30000000
BAL-003-0 (Manitoba) | 776600000007 | R4. | 7766000000060 | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  | BA | BA | [21 empty] | Low | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 40000000
BAL-003-0 (Manitoba) | 776600000007 | R5. | 7766000000063 | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. |  | BA | BA | [21 empty] | Low | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 50000000
BAL-003-0 (Manitoba) | 776600000007 | R6. | 7766000000065 | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 60000000
BAL-003-0 (Ontario) | 79780000007 | R1. | 79780000053 | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  | BA | BA | [21 empty] | Low |  |  | The Balancing Authority reviewed its Frequency Bias Settings prior January 1, but failed to recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. | The Balancing Authority failed to review its Frequency Bias Settings prior to January 1, and failed to recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-003-0 (Ontario) | 79780000007 | R2. | 79780000056 | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority established and maintained a Frequency Bias Setting that was less than, the Balancing Authority’s Frequency Response. |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-003-0 (Ontario) | 79780000007 | R3. | 79780000059 | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority did not operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, during periods when such operation would not have been adverse to system or Interconnection reliability. |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-003-0 (Ontario) | 79780000007 | R4. | 79780000060 | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority that used Dynamic Scheduling or Pseudo-ties for jointly owned units did not reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-003-0 (Ontario) | 79780000007 | R5. | 79780000063 | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority that served native load failed to have a monthly average Frequency Bias Setting that was at least 1% of the entities estimated yearly peak demand per 0.1 Hz change. |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 50000000
BAL-003-0 (Ontario) | 79780000007 | R6. | 79780000065 | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. |  | BA | BA | [21 empty] | Medium |  | The Balancing Authority that was performing Overlap Regulation Service changed its Frequency Bias Setting while performing Supplemental Regulation Service. | The Balancing Authority that was performing Overlap Regulation Service failed to increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. |  |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 60000000
BAL-003-1 | 358 | R1. | 4531 | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Real-Time Operations | High | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO | M1. Each Frequency Response Sharing Group or Balancing Authority that is not a member of a Frequency Response Sharing Group shall have evidence such as dated data plus documented formula in either hardcopy or electronic format that it achieved an annual FRM (in accordance with the methods specified by the ERO in Attachment A with data from FRS Form 1 reported to the ERO as specified in Attachment A) that is equal to or more negative than its FRO to demonstrate compliance with Requirement R1. | 2015-04-01 |  | 2015-11-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-003-1 | 358 | R2. | 4532 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting failed to implement the validated Frequency Bias Setting value into its ACE calculation within the implementation period specified but did so within 5 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 5 calendar days but less than or equal to 15 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 15 calendar days but less than or equal to 25 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting did not implement the validated Frequency Bias Setting value into its ACE calculation in more than 25 calendar days from the implementation period specified by the ERO. | M2. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service shall have evidence such as a dated document in hard copy or electronic format showing the ERO validated Frequency Bias Setting was implemented into its ACE calculation within the implementation period specified or other evidence to demonstrate compliance with Requirement R2. | 2015-04-01 |  | 2015-11-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-003-1 | 358 | R3. | 4533 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: 1.1 Less than zero at all times, and 1.2 Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 1% but by at most 10%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 10% but by at most 20%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 20% but by at most 30%. | The Balancing Authority that is a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response obligation by more than 30%. | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | 2015-04-01 |  | 2015-11-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-003-1 | 358 | R4. | 4534 | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: • The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or • The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error less than or equal to 10% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 10% but less than or equal to 20% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 20% but less than or equal to 30% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 30% of the validated or calculated value. OR The Balancing Authority failed to change the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services. | M4. The Balancing Authority shall have evidence such as a dated operating log, database or list in hard copy or electronic format showing that when it performed Overlap Regulation Service, it modified its Frequency Bias Setting in its ACE calculation as specified in Requirement R4 to demonstrate compliance with Requirement R4. | 2015-04-01 |  | 2015-11-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-003-1.1 | 532 | R1. | 7451 | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Real-Time Operations | High | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO | M1. Each Frequency Response Sharing Group or Balancing Authority that is not a member of a Frequency Response Sharing Group shall have evidence such as dated data plus documented formula in either hardcopy or electronic format that it achieved an annual FRM (in accordance with the methods specified by the ERO in Attachment A with data from FRS Form 1 reported to the ERO as specified in Attachment A) that is equal to or more negative than its FRO to demonstrate compliance with Requirement R1. | 2016-04-01 |  | 2020-11-30 | In those jurisdictions where regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after Board of Trustees adoption. Requirement R1 cannot be implemented prior to the addition of Frequency Response Sharing Group to the Compliance Registry. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-003-1.1 | 532 | R2. | 7452 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting failed to implement the validated Frequency Bias Setting value into its ACE calculation within the implementation period specified but did so within 5 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 5 calendar days but less than or equal to 15 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more 15 calendar days but less than or equal to 25 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting did not implement the validated Frequency Bias Setting value into its ACE calculation in more than 25 calendar days from the implementation period specified by the ERO. | M2. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service shall have evidence such as a dated document in hard copy or electronic format showing the ERO validated Frequency Bias Setting was implemented into its ACE calculation within the implementation period specified or other evidence to demonstrate compliance with Requirement R2. | 2015-11-13 |  | 2020-11-30 | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-003-1.1 | 532 | R3. | 7453 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 1% but by at most 10%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 10% but by at most 20%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 20% but by at most 30%. | The Balancing Authority that is a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response obligation by more than 30%.. | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | 2015-11-13 |  | 2020-11-30 | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-003-1.1 | 532 | R4. | 7456 | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: • The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or • The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error less than or equal to 10% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 10% but less than or equal to 20% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 20% but less than or equal to 30% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 30% of the validated or calculated value. OR The Balancing Authority failed to change the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services. | M4. The Balancing Authority shall have evidence such as a dated operating log, database or list in hard copy or electronic format showing that when it performed Overlap Regulation Service, it modified its Frequency Bias Setting in its ACE calculation as specified in Requirement R4 to demonstrate compliance with Requirement R4. | 2015-11-13 |  | 2020-11-30 | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-003-1.1 (British Columbia) | 666700000010013 | R1. | 666700000010396 | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Real-Time Operations | High | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO | M1. Each Frequency Response Sharing Group or Balancing Authority that is not a member of a Frequency Response Sharing Group shall have evidence such as dated data plus documented formula in either hardcopy or electronic format that it achieved an annual FRM (in accordance with the methods specified by the ERO in Attachment A with data from FRS Form 1 reported to the ERO as specified in Attachment A) that is equal to or more negative than its FRO to demonstrate compliance with Requirement R1. | 2016-10-01 |  |  | In those jurisdictions where regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after Board of Trustees adoption. Requirement R1 cannot be implemented prior to the addition of Frequency Response Sharing Group to the Compliance Registry. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | WECC-BC | [6 empty] | 10000000
BAL-003-1.1 (British Columbia) | 666700000010013 | R2. | 666700000010397 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting failed to implement the validated Frequency Bias Setting value into its ACE calculation within the implementation period specified but did so within 5 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 5 calendar days but less than or equal to 15 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more 15 calendar days but less than or equal to 25 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting did not implement the validated Frequency Bias Setting value into its ACE calculation in more than 25 calendar days from the implementation period specified by the ERO. | M2. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service shall have evidence such as a dated document in hard copy or electronic format showing the ERO validated Frequency Bias Setting was implemented into its ACE calculation within the implementation period specified or other evidence to demonstrate compliance with Requirement R2. | 2016-10-01 |  |  | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | WECC-BC | [6 empty] | 20000000
BAL-003-1.1 (British Columbia) | 666700000010013 | R3. | 666700000010398 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 1% but by at most 10%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 10% but by at most 20%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 20% but by at most 30%. | The Balancing Authority that is a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response obligation by more than 30%.. | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | 2016-10-01 |  |  | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | WECC-BC | [6 empty] | 30000000
BAL-003-1.1 (British Columbia) | 666700000010013 | R4. | 666700000010399 | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: • The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or • The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error less than or equal to 10% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 10% but less than or equal to 20% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 20% but less than or equal to 30% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 30% of the validated or calculated value. OR The Balancing Authority failed to change the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services. | M4. The Balancing Authority shall have evidence such as a dated operating log, database or list in hard copy or electronic format showing that when it performed Overlap Regulation Service, it modified its Frequency Bias Setting in its ACE calculation as specified in Requirement R4 to demonstrate compliance with Requirement R4. | 2016-10-01 |  |  | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | WECC-BC | [6 empty] | 40000000
BAL-003-1.1 (Manitoba) | 77660000000532 | R1. | 776600000007451 | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Real-Time Operations | High | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO | M1. Each Frequency Response Sharing Group or Balancing Authority that is not a member of a Frequency Response Sharing Group shall have evidence such as dated data plus documented formula in either hardcopy or electronic format that it achieved an annual FRM (in accordance with the methods specified by the ERO in Attachment A with data from FRS Form 1 reported to the ERO as specified in Attachment A) that is equal to or more negative than its FRO to demonstrate compliance with Requirement R1. | 2017-07-01 |  | 2021-06-30 | In those jurisdictions where regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after Board of Trustees adoption. Requirement R1 cannot be implemented prior to the addition of Frequency Response Sharing Group to the Compliance Registry. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-MB | [6 empty] | 10000000
BAL-003-1.1 (Manitoba) | 77660000000532 | R2. | 776600000007452 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting failed to implement the validated Frequency Bias Setting value into its ACE calculation within the implementation period specified but did so within 5 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 5 calendar days but less than or equal to 15 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more 15 calendar days but less than or equal to 25 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting did not implement the validated Frequency Bias Setting value into its ACE calculation in more than 25 calendar days from the implementation period specified by the ERO. | M2. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service shall have evidence such as a dated document in hard copy or electronic format showing the ERO validated Frequency Bias Setting was implemented into its ACE calculation within the implementation period specified or other evidence to demonstrate compliance with Requirement R2. | 2017-07-01 |  | 2021-06-30 | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-MB | [6 empty] | 20000000
BAL-003-1.1 (Manitoba) | 77660000000532 | R3. | 776600000007453 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 1% but by at most 10%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 10% but by at most 20%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 20% but by at most 30%. | The Balancing Authority that is a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response obligation by more than 30%.. | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | 2017-07-01 |  | 2021-06-30 | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-MB | [6 empty] | 30000000
BAL-003-1.1 (Manitoba) | 77660000000532 | R4. | 776600000007456 | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: • The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or • The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error less than or equal to 10% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 10% but less than or equal to 20% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 20% but less than or equal to 30% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 30% of the validated or calculated value. OR The Balancing Authority failed to change the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services. | M4. The Balancing Authority shall have evidence such as a dated operating log, database or list in hard copy or electronic format showing that when it performed Overlap Regulation Service, it modified its Frequency Bias Setting in its ACE calculation as specified in Requirement R4 to demonstrate compliance with Requirement R4. | 2017-07-01 |  | 2021-06-30 | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-MB | [6 empty] | 40000000
BAL-003-1.1 (Nova Scotia) | 78830000000532 | R1. | 788300000007451 | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Real-Time Operations | High | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO | M1. Each Frequency Response Sharing Group or Balancing Authority that is not a member of a Frequency Response Sharing Group shall have evidence such as dated data plus documented formula in either hardcopy or electronic format that it achieved an annual FRM (in accordance with the methods specified by the ERO in Attachment A with data from FRS Form 1 reported to the ERO as specified in Attachment A) that is equal to or more negative than its FRO to demonstrate compliance with Requirement R1. | 2018-10-01 |  | 2021-06-30 | In those jurisdictions where regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after Board of Trustees adoption. Requirement R1 cannot be implemented prior to the addition of Frequency Response Sharing Group to the Compliance Registry. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | NPCC-NS | [6 empty] | 10000000
BAL-003-1.1 (Nova Scotia) | 78830000000532 | R2. | 788300000007452 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting failed to implement the validated Frequency Bias Setting value into its ACE calculation within the implementation period specified but did so within 5 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 5 calendar days but less than or equal to 15 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more 15 calendar days but less than or equal to 25 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting did not implement the validated Frequency Bias Setting value into its ACE calculation in more than 25 calendar days from the implementation period specified by the ERO. | M2. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service shall have evidence such as a dated document in hard copy or electronic format showing the ERO validated Frequency Bias Setting was implemented into its ACE calculation within the implementation period specified or other evidence to demonstrate compliance with Requirement R2. | 2017-10-01 |  | 2021-06-30 | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | NPCC-NS | [6 empty] | 20000000
BAL-003-1.1 (Nova Scotia) | 78830000000532 | R3. | 788300000007453 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 1% but by at most 10%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 10% but by at most 20%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 20% but by at most 30%. | The Balancing Authority that is a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response obligation by more than 30%.. | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | 2017-10-01 |  | 2021-06-30 | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | NPCC-NS | [6 empty] | 30000000
BAL-003-1.1 (Nova Scotia) | 78830000000532 | R4. | 788300000007456 | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: • The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or • The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error less than or equal to 10% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 10% but less than or equal to 20% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 20% but less than or equal to 30% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 30% of the validated or calculated value. OR The Balancing Authority failed to change the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services. | M4. The Balancing Authority shall have evidence such as a dated operating log, database or list in hard copy or electronic format showing that when it performed Overlap Regulation Service, it modified its Frequency Bias Setting in its ACE calculation as specified in Requirement R4 to demonstrate compliance with Requirement R4. | 2017-10-01 |  | 2021-06-30 | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | NPCC-NS | [6 empty] | 40000000
BAL-003-1.1 (Ontario) | 79780000532 | R1. | 79780007451 | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Real-Time Operations | High | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO | M1. Each Frequency Response Sharing Group or Balancing Authority that is not a member of a Frequency Response Sharing Group shall have evidence such as dated data plus documented formula in either hardcopy or electronic format that it achieved an annual FRM (in accordance with the methods specified by the ERO in Attachment A with data from FRS Form 1 reported to the ERO as specified in Attachment A) that is equal to or more negative than its FRO to demonstrate compliance with Requirement R1. | 2016-04-01 |  | 2020-11-30 | In those jurisdictions where regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after Board of Trustees adoption.&lt;br/&gt;&lt;br/&gt;Requirement R1 cannot be implemented prior to the addition of Frequency Response Sharing Group to the Compliance Registry. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | NPCC-ON | [6 empty] | 10000000
BAL-003-1.1 (Ontario) | 79780000532 | R2. | 79780007452 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting failed to implement the validated Frequency Bias Setting value into its ACE calculation within the implementation period specified but did so within 5 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 5 calendar days but less than or equal to 15 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more 15 calendar days but less than or equal to 25 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting did not implement the validated Frequency Bias Setting value into its ACE calculation in more than 25 calendar days from the implementation period specified by the ERO. | M2. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service shall have evidence such as a dated document in hard copy or electronic format showing the ERO validated Frequency Bias Setting was implemented into its ACE calculation within the implementation period specified or other evidence to demonstrate compliance with Requirement R2. | 2015-11-13 |  | 2020-11-30 | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | NPCC-ON | [6 empty] | 20000000
BAL-003-1.1 (Ontario) | 79780000532 | R3. | 79780007453 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 1% but by at most 10%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 10% but by at most 20%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 20% but by at most 30%. | The Balancing Authority that is a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response obligation by more than 30%.. | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | 2015-11-13 |  | 2020-11-30 | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | NPCC-ON | [6 empty] | 30000000
BAL-003-1.1 (Ontario) | 79780000532 | R4. | 79780007456 | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either:&lt;br/&gt;• The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or&lt;br/&gt;&lt;br/&gt;• The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error less than or equal to 10% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 10% but less than or equal to 20% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 20% but less than or equal to 30% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 30% of the validated or calculated value. OR The Balancing Authority failed to change the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services. | M4. The Balancing Authority shall have evidence such as a dated operating log, database or list in hard copy or electronic format showing that when it performed Overlap Regulation Service, it modified its Frequency Bias Setting in its ACE calculation as specified in Requirement R4 to demonstrate compliance with Requirement R4. | 2015-11-13 |  | 2020-11-30 | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | NPCC-ON | [6 empty] | 40000000
BAL-003-1.1 (Saskatchewan) | 83750000000532 | R1. | 837500000007451 | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Real-Time Operations | High | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO | M1. Each Frequency Response Sharing Group or Balancing Authority that is not a member of a Frequency Response Sharing Group shall have evidence such as dated data plus documented formula in either hardcopy or electronic format that it achieved an annual FRM (in accordance with the methods specified by the ERO in Attachment A with data from FRS Form 1 reported to the ERO as specified in Attachment A) that is equal to or more negative than its FRO to demonstrate compliance with Requirement R1. | 2017-04-01 |  | 2020-11-30 | In those jurisdictions where regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R1 of this standard shall become effective the first calendar day of the first calendar quarter 24 months after Board of Trustees adoption. Requirement R1 cannot be implemented prior to the addition of Frequency Response Sharing Group to the Compliance Registry. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-SK | [6 empty] | 10000000
BAL-003-1.1 (Saskatchewan) | 83750000000532 | R2. | 837500000007452 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting failed to implement the validated Frequency Bias Setting value into its ACE calculation within the implementation period specified but did so within 5 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 5 calendar days but less than or equal to 15 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more 15 calendar days but less than or equal to 25 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting did not implement the validated Frequency Bias Setting value into its ACE calculation in more than 25 calendar days from the implementation period specified by the ERO. | M2. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service shall have evidence such as a dated document in hard copy or electronic format showing the ERO validated Frequency Bias Setting was implemented into its ACE calculation within the implementation period specified or other evidence to demonstrate compliance with Requirement R2. | 2017-04-01 |  | 2020-11-30 | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-SK | [6 empty] | 20000000
BAL-003-1.1 (Saskatchewan) | 83750000000532 | R3. | 837500000007453 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 1% but by at most 10%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 10% but by at most 20%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 20% but by at most 30%. | The Balancing Authority that is a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response obligation by more than 30%.. | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | 2017-04-01 |  | 2020-11-30 | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-SK | [6 empty] | 30000000
BAL-003-1.1 (Saskatchewan) | 83750000000532 | R4. | 837500000007456 | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: • The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or • The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error less than or equal to 10% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 10% but less than or equal to 20% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 20% but less than or equal to 30% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 30% of the validated or calculated value. OR The Balancing Authority failed to change the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services. | M4. The Balancing Authority shall have evidence such as a dated operating log, database or list in hard copy or electronic format showing that when it performed Overlap Regulation Service, it modified its Frequency Bias Setting in its ACE calculation as specified in Requirement R4 to demonstrate compliance with Requirement R4. | 2017-04-01 |  | 2020-11-30 | In those jurisdictions where regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after applicable regulatory approval. In those jurisdictions where no regulatory approval is required, Requirements R2, R3 and R4 of this standard shall become effective the first calendar day of the first calendar quarter 12 months after Board of Trustees adoption. | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-SK | [6 empty] | 40000000
BAL-003-1 (British Columbia) | 666700000010012 | R1. | 666700000010392 | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Real-Time Operations | High | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO | M1. Each Frequency Response Sharing Group or Balancing Authority that is not a member of a Frequency Response Sharing Group shall have evidence such as dated data plus documented formula in either hardcopy or electronic format that it achieved an annual FRM (in accordance with the methods specified by the ERO in Attachment A with data from FRS Form 1 reported to the ERO as specified in Attachment A) that is equal to or more negative than its FRO to demonstrate compliance with Requirement R1. | 2015-10-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
BAL-003-1 (British Columbia) | 666700000010012 | R2. | 666700000010393 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting failed to implement the validated Frequency Bias Setting value into its ACE calculation within the implementation period specified but did so within 5 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 5 calendar days but less than or equal to 15 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 15 calendar days but less than or equal to 25 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting did not implement the validated Frequency Bias Setting value into its ACE calculation in more than 25 calendar days from the implementation period specified by the ERO. | M2. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service shall have evidence such as a dated document in hard copy or electronic format showing the ERO validated Frequency Bias Setting was implemented into its ACE calculation within the implementation period specified or other evidence to demonstrate compliance with Requirement R2. | 2015-10-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 20000000
BAL-003-1 (British Columbia) | 666700000010012 | R3. | 666700000010394 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: 1.1 Less than zero at all times, and 1.2 Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 1% but by at most 10%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 10% but by at most 20%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 20% but by at most 30%. | The Balancing Authority that is a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response obligation by more than 30%. | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | 2015-10-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 30000000
BAL-003-1 (British Columbia) | 666700000010012 | R4. | 666700000010395 | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: • The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or • The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error less than or equal to 10% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 10% but less than or equal to 20% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 20% but less than or equal to 30% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 30% of the validated or calculated value. OR The Balancing Authority failed to change the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services. | M4. The Balancing Authority shall have evidence such as a dated operating log, database or list in hard copy or electronic format showing that when it performed Overlap Regulation Service, it modified its Frequency Bias Setting in its ACE calculation as specified in Requirement R4 to demonstrate compliance with Requirement R4. | 2015-10-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 40000000
BAL-003-1 (Ontario) | 79780000358 | R1. | 79780004531 | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Real-Time Operations | High | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO | M1. Each Frequency Response Sharing Group or Balancing Authority that is not a member of a Frequency Response Sharing Group shall have evidence such as dated data plus documented formula in either hardcopy or electronic format that it achieved an annual FRM (in accordance with the methods specified by the ERO in Attachment A with data from FRS Form 1 reported to the ERO as specified in Attachment A) that is equal to or more negative than its FRO to demonstrate compliance with Requirement R1. | 2015-04-01 |  | 2015-11-12 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-003-1 (Ontario) | 79780000358 | R2. | 79780004532 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. |  | BA | BA | [20 empty] | Operations Planning | Medium | &lt;p&gt;The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting failed to implement the validated Frequency Bias Setting value into its ACE calculation within the implementation period specified but&lt;br/&gt;did so within 5 calendar days from the implementation period specified by&lt;br/&gt;the ERO.&lt;/p&gt; | &lt;p&gt;The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 5 calendar days but less than or equal to 15 calendar days from the implementation period specified by the ERO.&lt;/p&gt; | &lt;p&gt;The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 15 calendar days but less than or&lt;br/&gt;equal to 25 calendar days from the implementation period specified by&lt;br/&gt;the ERO.&lt;/p&gt; | &lt;p&gt;The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting did not implement the validated Frequency Bias Setting value into its ACE calculation in more than 25 calendar days from the&lt;br/&gt;implementation period specified by the ERO.&lt;/p&gt; | M2. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service shall have evidence such as a dated document in hard copy or electronic format showing the ERO validated Frequency Bias Setting was implemented into its ACE calculation within the implementation period specified or other evidence to demonstrate compliance with Requirement R2. | 2015-04-01 |  | 2015-11-12 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-003-1 (Ontario) | 79780000358 | R3. | 79780004533 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: 1.1 Less than zero at all times, and&lt;br/&gt;1.2 Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. |  | BA | BA | [20 empty] | Operations Planning | Medium | &lt;p&gt;The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 1% but by at most 10%.&lt;/p&gt; | &lt;p&gt;The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 10% but by at most 20%.&lt;/p&gt; | &lt;p&gt;The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 20% but by at most 30%.&lt;/p&gt; | &lt;p&gt;The Balancing Authority that is a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response obligation by more than 30%.&lt;/p&gt; | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | 2015-04-01 |  | 2015-11-12 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-003-1 (Ontario) | 79780000358 | R4. | 79780004534 | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: • The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or&lt;br/&gt;&lt;br/&gt;• The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error less than or equal to 10% of the validated or calculated value. | &lt;p&gt;The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 10% but less than or equal to 20% of the validated or calculated value.&lt;/p&gt; | &lt;p&gt;The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 20% but less than or equal to 30% of the validated or calculated value.&lt;/p&gt; | &lt;p&gt;The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 30% of the validated or calculated value. OR The Balancing Authority failed to change the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services.&lt;/p&gt; | M4. The Balancing Authority shall have evidence such as a dated operating log, database or list in hard copy or electronic format showing that when it performed Overlap Regulation Service, it modified its Frequency Bias Setting in its ACE calculation as specified in Requirement R4 to demonstrate compliance with Requirement R4. | 2015-04-01 |  | 2015-11-12 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-003-1 (Saskatchewan) | 83750000000358 | R1. | 837500000004531 | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Real-Time Operations | High | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO | M1. Each Frequency Response Sharing Group or Balancing Authority that is not a member of a Frequency Response Sharing Group shall have evidence such as dated data plus documented formula in either hardcopy or electronic format that it achieved an annual FRM (in accordance with the methods specified by the ERO in Attachment A with data from FRS Form 1 reported to the ERO as specified in Attachment A) that is equal to or more negative than its FRO to demonstrate compliance with Requirement R1. | 2015-04-01 |  | 2015-03-31 |  |  |  | MRO-SK | [6 empty] | 10000000
BAL-003-1 (Saskatchewan) | 83750000000358 | R2. | 837500000004532 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting failed to implement the validated Frequency Bias Setting value into its ACE calculation within the implementation period specified but did so within 5 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 5 calendar days but less than or equal to 15 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 15 calendar days but less than or equal to 25 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting did not implement the validated Frequency Bias Setting value into its ACE calculation in more than 25 calendar days from the implementation period specified by the ERO. | M2. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service shall have evidence such as a dated document in hard copy or electronic format showing the ERO validated Frequency Bias Setting was implemented into its ACE calculation within the implementation period specified or other evidence to demonstrate compliance with Requirement R2. | 2015-04-01 |  | 2015-03-31 |  |  |  | MRO-SK | [6 empty] | 20000000
BAL-003-1 (Saskatchewan) | 83750000000358 | R3. | 837500000004533 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: 1.1 Less than zero at all times, and 1.2 Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 1% but by at most 10%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 10% but by at most 20%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 20% but by at most 30%. | The Balancing Authority that is a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response obligation by more than 30%. | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | 2015-04-01 |  | 2015-03-31 |  |  |  | MRO-SK | [6 empty] | 30000000
BAL-003-1 (Saskatchewan) | 83750000000358 | R4. | 837500000004534 | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: • The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or • The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Operations Planning | Medium | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error less than or equal to 10% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 10% but less than or equal to 20% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 20% but less than or equal to 30% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 30% of the validated or calculated value. OR The Balancing Authority failed to change the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services. | M4. The Balancing Authority shall have evidence such as a dated operating log, database or list in hard copy or electronic format showing that when it performed Overlap Regulation Service, it modified its Frequency Bias Setting in its ACE calculation as specified in Requirement R4 to demonstrate compliance with Requirement R4. | 2015-04-01 |  | 2015-03-31 |  |  |  | MRO-SK | [6 empty] | 40000000
BAL-003-2 | 607 | R1. | 8843 | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Real-Time Operations | High | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by at most 15% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO. | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 15% but by at most 30% or 30 MW/0.1 Hz, whichever is the greater deviation from its FRO. | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% but by at most 45% or 45 MW/0.1 Hz, whichever one is the greater deviation from its FRO. | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 45% or by more than 45 MW/0.1 Hz, whichever is the greater deviation from its FRO. | M1. Each Frequency Response Sharing Group or Balancing Authority that is not a member of a Frequency Response Sharing Group shall have evidence such as dated data plus documented formula in either hardcopy or electronic format that it achieved an annual FRM (in accordance with the methods specified by the ERO in Attachment A with data from FRS Form 1 reported to the ERO as specified in Attachment A) that is equal to or more negative than its FRO to demonstrate compliance with Requirement R1. | 2020-10-01 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-003-2 | 607 | R2. | 8844 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting failed to implement the validated Frequency Bias Setting value into its ACE calculation within the implementation period specified but did so within 5 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 5 calendar days but less than or equal to 15 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 15 calendar days but less than or equal to 25 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting did not implement the validated Frequency Bias Setting value into its ACE calculation in more than 25 calendar days from the implementation period specified by the ERO. | M2. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service shall have evidence such as a dated document in hard copy or electronic format showing the ERO validated Frequency Bias Setting was implemented into its ACE calculation within the implementation period specified or other evidence to demonstrate compliance with Requirement R2. | 2020-10-01 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-003-2 | 607 | R3. | 8845 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 1% but by at most 10%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 10% but by at most 20%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 20% but by at most 30%. | The Balancing Authority that is a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response obligation by more than 30%. | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | 2020-10-01 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-003-2 | 607 | R4. | 8846 | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: • The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or • The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error less than or equal to 10% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 10% but less than or equal to 20% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 20% but less than or equal to 30% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 30% of the validated or calculated value. OR The Balancing Authority failed to change the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services. | M4.The Balancing Authority shall have evidence such as a dated operating log, database or list in hard copy or electronic format showing that when it performed Overlap Regulation Service, it modified its Frequency Bias Setting in its ACE calculation as specified in Requirement R4 to demonstrate compliance with Requirement R4. | 2020-10-01 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-003-2 (Manitoba) | 77660000000607 | R1. | 776600000008843 | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Real-Time Operations | High | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by at most 15% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO. | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 15% but by at most 30% or 30 MW/0.1 Hz, whichever is the greater deviation from its FRO. | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% but by at most 45% or 45 MW/0.1 Hz, whichever one is the greater deviation from its FRO. | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 45% or by more than 45 MW/0.1 Hz, whichever is the greater deviation from its FRO. | M1. Each Frequency Response Sharing Group or Balancing Authority that is not a member of a Frequency Response Sharing Group shall have evidence such as dated data plus documented formula in either hardcopy or electronic format that it achieved an annual FRM (in accordance with the methods specified by the ERO in Attachment A with data from FRS Form 1 reported to the ERO as specified in Attachment A) that is equal to or more negative than its FRO to demonstrate compliance with Requirement R1. | 2021-07-01 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-MB | [6 empty] | 10000000
BAL-003-2 (Manitoba) | 77660000000607 | R2. | 776600000008844 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting failed to implement the validated Frequency Bias Setting value into its ACE calculation within the implementation period specified but did so within 5 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 5 calendar days but less than or equal to 15 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 15 calendar days but less than or equal to 25 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting did not implement the validated Frequency Bias Setting value into its ACE calculation in more than 25 calendar days from the implementation period specified by the ERO. | M2. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service shall have evidence such as a dated document in hard copy or electronic format showing the ERO validated Frequency Bias Setting was implemented into its ACE calculation within the implementation period specified or other evidence to demonstrate compliance with Requirement R2. | 2021-07-01 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-MB | [6 empty] | 20000000
BAL-003-2 (Manitoba) | 77660000000607 | R3. | 776600000008845 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 1% but by at most 10%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 10% but by at most 20%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 20% but by at most 30%. | The Balancing Authority that is a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response obligation by more than 30%. | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | 2021-07-01 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-MB | [6 empty] | 30000000
BAL-003-2 (Manitoba) | 77660000000607 | R4. | 776600000008846 | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: • The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or • The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error less than or equal to 10% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 10% but less than or equal to 20% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 20% but less than or equal to 30% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 30% of the validated or calculated value. OR The Balancing Authority failed to change the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services. | M4.The Balancing Authority shall have evidence such as a dated operating log, database or list in hard copy or electronic format showing that when it performed Overlap Regulation Service, it modified its Frequency Bias Setting in its ACE calculation as specified in Requirement R4 to demonstrate compliance with Requirement R4. | 2021-07-01 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-MB | [6 empty] | 40000000
BAL-003-2 (Nova Scotia) | 78830000000607 | R1. | 788300000008843 | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Real-Time Operations | High | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by at most 15% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO. | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 15% but by at most 30% or 30 MW/0.1 Hz, whichever is the greater deviation from its FRO. | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% but by at most 45% or 45 MW/0.1 Hz, whichever one is the greater deviation from its FRO. | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 45% or by more than 45 MW/0.1 Hz, whichever is the greater deviation from its FRO. | M1. Each Frequency Response Sharing Group or Balancing Authority that is not a member of a Frequency Response Sharing Group shall have evidence such as dated data plus documented formula in either hardcopy or electronic format that it achieved an annual FRM (in accordance with the methods specified by the ERO in Attachment A with data from FRS Form 1 reported to the ERO as specified in Attachment A) that is equal to or more negative than its FRO to demonstrate compliance with Requirement R1. | 2021-07-01 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | NPCC-NS | [6 empty] | 10000000
BAL-003-2 (Nova Scotia) | 78830000000607 | R2. | 788300000008844 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting failed to implement the validated Frequency Bias Setting value into its ACE calculation within the implementation period specified but did so within 5 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 5 calendar days but less than or equal to 15 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 15 calendar days but less than or equal to 25 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting did not implement the validated Frequency Bias Setting value into its ACE calculation in more than 25 calendar days from the implementation period specified by the ERO. | M2. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service shall have evidence such as a dated document in hard copy or electronic format showing the ERO validated Frequency Bias Setting was implemented into its ACE calculation within the implementation period specified or other evidence to demonstrate compliance with Requirement R2. | 2021-07-01 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | NPCC-NS | [6 empty] | 20000000
BAL-003-2 (Nova Scotia) | 78830000000607 | R3. | 788300000008845 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 1% but by at most 10%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 10% but by at most 20%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 20% but by at most 30%. | The Balancing Authority that is a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response obligation by more than 30%. | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | 2021-07-01 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | NPCC-NS | [6 empty] | 30000000
BAL-003-2 (Nova Scotia) | 78830000000607 | R4. | 788300000008846 | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: • The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or • The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error less than or equal to 10% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 10% but less than or equal to 20% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 20% but less than or equal to 30% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 30% of the validated or calculated value. OR The Balancing Authority failed to change the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services. | M4.The Balancing Authority shall have evidence such as a dated operating log, database or list in hard copy or electronic format showing that when it performed Overlap Regulation Service, it modified its Frequency Bias Setting in its ACE calculation as specified in Requirement R4 to demonstrate compliance with Requirement R4. | 2021-07-01 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | NPCC-NS | [6 empty] | 40000000
BAL-003-2 (Ontario) | 79780000607 | R1. | 79780008843 | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Real-Time Operations | High | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by at most 15% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO. | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 15% but by at most 30% or 30 MW/0.1 Hz, whichever is the greater deviation from its FRO. | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% but by at most 45% or 45 MW/0.1 Hz, whichever one is the greater deviation from its FRO. | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 45% or by more than 45 MW/0.1 Hz, whichever is the greater deviation from its FRO. | M1. Each Frequency Response Sharing Group or Balancing Authority that is not a member of a Frequency Response Sharing Group shall have evidence such as dated data plus documented formula in either hardcopy or electronic format that it achieved an annual FRM (in accordance with the methods specified by the ERO in Attachment A with data from FRS Form 1 reported to the ERO as specified in Attachment A) that is equal to or more negative than its FRO to demonstrate compliance with Requirement R1. | 2020-10-01 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | NPCC-ON | [6 empty] | 10000000
BAL-003-2 (Ontario) | 79780000607 | R2. | 79780008844 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting failed to implement the validated Frequency Bias Setting value into its ACE calculation within the implementation period specified but did so within 5 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 5 calendar days but less than or equal to 15 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 15 calendar days but less than or equal to 25 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting did not implement the validated Frequency Bias Setting value into its ACE calculation in more than 25 calendar days from the implementation period specified by the ERO. | M2. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service shall have evidence such as a dated document in hard copy or electronic format showing the ERO validated Frequency Bias Setting was implemented into its ACE calculation within the implementation period specified or other evidence to demonstrate compliance with Requirement R2. | 2020-10-01 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | NPCC-ON | [6 empty] | 20000000
BAL-003-2 (Ontario) | 79780000607 | R3. | 79780008845 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 1% but by at most 10%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 10% but by at most 20%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 20% but by at most 30%. | The Balancing Authority that is a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response obligation by more than 30%. | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | 2020-10-01 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | NPCC-ON | [6 empty] | 30000000
BAL-003-2 (Ontario) | 79780000607 | R4. | 79780008846 | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: &lt;br/&gt;• The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or&lt;br/&gt;• The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error less than or equal to 10% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 10% but less than or equal to 20% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 20% but less than or equal to 30% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 30% of the validated or calculated value. OR The Balancing Authority failed to change the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services. | M4.The Balancing Authority shall have evidence such as a dated operating log, database or list in hard copy or electronic format showing that when it performed Overlap Regulation Service, it modified its Frequency Bias Setting in its ACE calculation as specified in Requirement R4 to demonstrate compliance with Requirement R4. | 2020-10-01 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | NPCC-ON | [6 empty] | 40000000
BAL-003-2 (Saskatchewan) | 83750000000607 | R1. | 837500000008843 | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. |  | BA, FRSG | BA |  |  | FRSG | [17 empty] | Real-Time Operations | High | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by at most 15% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO. | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 15% but by at most 30% or 30 MW/0.1 Hz, whichever is the greater deviation from its FRO. | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% but by at most 45% or 45 MW/0.1 Hz, whichever one is the greater deviation from its FRO. | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 45% or by more than 45 MW/0.1 Hz, whichever is the greater deviation from its FRO. | M1. Each Frequency Response Sharing Group or Balancing Authority that is not a member of a Frequency Response Sharing Group shall have evidence such as dated data plus documented formula in either hardcopy or electronic format that it achieved an annual FRM (in accordance with the methods specified by the ERO in Attachment A with data from FRS Form 1 reported to the ERO as specified in Attachment A) that is equal to or more negative than its FRO to demonstrate compliance with Requirement R1. | 2020-12-01 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-SK | [6 empty] | 10000000
BAL-003-2 (Saskatchewan) | 83750000000607 | R2. | 837500000008844 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting failed to implement the validated Frequency Bias Setting value into its ACE calculation within the implementation period specified but did so within 5 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 5 calendar days but less than or equal to 15 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 15 calendar days but less than or equal to 25 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting did not implement the validated Frequency Bias Setting value into its ACE calculation in more than 25 calendar days from the implementation period specified by the ERO. | M2. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service shall have evidence such as a dated document in hard copy or electronic format showing the ERO validated Frequency Bias Setting was implemented into its ACE calculation within the implementation period specified or other evidence to demonstrate compliance with Requirement R2. | 2020-12-01 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-SK | [6 empty] | 20000000
BAL-003-2 (Saskatchewan) | 83750000000607 | R3. | 837500000008845 | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 1% but by at most 10%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 10% but by at most 20%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 20% but by at most 30%. | The Balancing Authority that is a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response obligation by more than 30%. | M3. The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | 2020-12-01 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-SK | [6 empty] | 30000000
BAL-003-2 (Saskatchewan) | 83750000000607 | R4. | 837500000008846 | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: • The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or • The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error less than or equal to 10% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 10% but less than or equal to 20% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 20% but less than or equal to 30% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 30% of the validated or calculated value. OR The Balancing Authority failed to change the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services. | M4.The Balancing Authority shall have evidence such as a dated operating log, database or list in hard copy or electronic format showing that when it performed Overlap Regulation Service, it modified its Frequency Bias Setting in its ACE calculation as specified in Requirement R4 to demonstrate compliance with Requirement R4. | 2020-12-01 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | MRO-SK | [6 empty] | 40000000
BAL-003-AB1-1.1 (Alberta) | 656600000009003 | R1. | 656600000009071 | The ISO must: (a) achieve an annual frequency response measure (as calculated in accordance with Appendix A) that is equal to or more negative than its frequency response obligation; and (b) report, in accordance with Appendix A, the annual frequency response measure calculated pursuant to requirement R1(a), which obligations the ISO may meet through participation in a frequency response sharing group which the ISO has designated as its agent. |  | ISO | [28 empty] | 2019-08-01 | [5 empty] | WECC-AB | [6 empty] | 10000000
BAL-003-AB1-1.1 (Alberta) | 656600000009003 | R2. | 656600000009072 | The ISO must, if it is not receiving overlap regulation service and uses a fixed frequency bias setting: |  | ISO | [28 empty] | 2019-08-01 | [5 empty] | WECC-AB | [6 empty] | 20000000
BAL-003-AB1-1.1 (Alberta) | 656600000009003 | R3. | 656600000009073 | The ISO must, if it is not receiving overlap regulation service and is utilizing a variable frequency bias setting, maintain a frequency bias setting that is: |  | ISO | [28 empty] | 2019-08-01 | [5 empty] | WECC-AB | [6 empty] | 30000000
BAL-003-AB1-1.1 (Alberta) | 656600000009003 | R4. | 656600000009074 | The ISO must, if it is performing overlap regulation service, modify its frequency bias setting in its area control error calculation, in order to represent the frequency bias setting for the combined balancing authority area, to be equivalent to either: |  | ISO | [28 empty] | 2019-08-01 | [5 empty] | WECC-AB | [6 empty] | 40000000
BAL-004-0 | 12 | R1. | 113 | Only a Reliability Coordinator shall be eligible to act as Interconnection Time Monitor. A single Reliability Coordinator in each Interconnection shall be designated by the NERC Operating Committee to serve as Interconnection Time Monitor. |  | BA, RC | BA | [10 empty] | RC | [10 empty] | Low |  |  |  | The responsible entity has designated more than one interconnection time monitor for a single interconnection. |  | 2007-06-18 |  | 2017-04-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-004-0 | 12 | R2. | 114 | The Interconnection Time Monitor shall monitor Time Error and shall initiate or terminate corrective action orders in accordance with the NAESB Time Error Correction Procedure. |  | BA, RC | BA | [10 empty] | RC | [10 empty] | Low |  |  |  | The RC serving as the Interconnection Time Monitor failed to initiate or terminate corrective action orders in accordance with the NAESB Time Error Correction Procedure. |  | 2007-06-18 |  | 2017-04-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-004-0 | 12 | R3. | 115 | Each Balancing Authority, when requested, shall participate in a Time Error Correction by one of the following methods: |  | BA, RC | BA | [10 empty] | RC | [10 empty] | Low | The Balancing Authority participated in more than 75% and less than 100% of requested Time Error Corrections for the calendar year. | The Balancing Authority participated in more than 50% and less than or equal to 75% of requested Time Error Corrections for the calendar year. | The Balancing Authority participated in more than 25% and less than or equal to 50% of requested Time Error Corrections for the calendar year. | The Balancing Authority participated in less than or equal to 25% of requested Time Error Corrections for the calendar year. |  | 2007-06-18 |  | 2017-04-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-004-0 | 12 | R4. | 118 | Any Reliability Coordinator in an Interconnection shall have the authority to request the Interconnection Time Monitor to terminate a Time Error Correction in progress, or a scheduled Time Error Correction that has not begun, for reliability considerations. |  | BA, RC | BA | [10 empty] | RC | [10 empty] | Low |  |  |  | The RC serving as the Interconnection Time Monitor failed to initiate or terminate corrective action orders in accordance with the NAESB Time Error Correction Procedure. |  | 2007-06-18 |  | 2017-04-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-004-0 (British Columbia) | 666700000010014 | R1. | 666700000010400 | Only a Reliability Coordinator shall be eligible to act as Interconnection Time Monitor. A single Reliability Coordinator in each Interconnection shall be designated by the NERC Operating Committee to serve as Interconnection Time Monitor. |  | BA, RC | BA | [10 empty] | RC | [10 empty] | Low |  |  |  | The responsible entity has designated more than one interconnection time monitor for a single interconnection. |  | 2010-11-01 | [5 empty] | WECC-BC | [6 empty] | 10000000
BAL-004-0 (British Columbia) | 666700000010014 | R2. | 666700000010401 | The Interconnection Time Monitor shall monitor Time Error and shall initiate or terminate corrective action orders in accordance with the NAESB Time Error Correction Procedure. |  | BA, RC | BA | [10 empty] | RC | [10 empty] | Low |  |  |  | The RC serving as the Interconnection Time Monitor failed to initiate or terminate corrective action orders in accordance with the NAESB Time Error Correction Procedure. |  | 2010-11-01 | [5 empty] | WECC-BC | [6 empty] | 20000000
BAL-004-0 (British Columbia) | 666700000010014 | R3. | 666700000010402 | Each Balancing Authority, when requested, shall participate in a Time Error Correction by one of the following methods: |  | BA, RC | BA | [10 empty] | RC | [10 empty] | Low | The Balancing Authority participated in more than 75% and less than 100% of requested Time Error Corrections for the calendar year. | The Balancing Authority participated in more than 50% and less than or equal to 75% of requested Time Error Corrections for the calendar year. | The Balancing Authority participated in more than 25% and less than or equal to 50% of requested Time Error Corrections for the calendar year. | The Balancing Authority participated in less than or equal to 25% of requested Time Error Corrections for the calendar year. |  | 2010-11-01 | [5 empty] | WECC-BC | [6 empty] | 30000000
BAL-004-0 (British Columbia) | 666700000010014 | R4. | 666700000010403 | Any Reliability Coordinator in an Interconnection shall have the authority to request the Interconnection Time Monitor to terminate a Time Error Correction in progress, or a scheduled Time Error Correction that has not begun, for reliability considerations. |  | BA, RC | BA | [10 empty] | RC | [10 empty] | Low |  |  |  | The RC serving as the Interconnection Time Monitor failed to initiate or terminate corrective action orders in accordance with the NAESB Time Error Correction Procedure. |  | 2010-11-01 | [5 empty] | WECC-BC | [6 empty] | 40000000
BAL-004-0 (Manitoba) | 7766000000012 | R1. | 77660000000113 | Only a Reliability Coordinator shall be eligible to act as Interconnection Time Monitor. A single Reliability Coordinator in each Interconnection shall be designated by the NERC Operating Committee to serve as Interconnection Time Monitor. |  | BA, RC | BA | [10 empty] | RC | [10 empty] | Low |  |  |  | The responsible entity has designated more than one interconnection time monitor for a single interconnection. |  | 2012-04-01 |  | 2014-07-16 |  |  |  | MRO-MB | [6 empty] | 10000000
BAL-004-0 (Manitoba) | 7766000000012 | R2. | 77660000000114 | The Interconnection Time Monitor shall monitor Time Error and shall initiate or terminate corrective action orders in accordance with the NAESB Time Error Correction Procedure. |  | BA, RC | BA | [10 empty] | RC | [10 empty] | Low |  |  |  | The RC serving as the Interconnection Time Monitor failed to initiate or terminate corrective action orders in accordance with the NAESB Time Error Correction Procedure. |  | 2012-04-01 |  | 2014-07-16 |  |  |  | MRO-MB | [6 empty] | 20000000
BAL-004-0 (Manitoba) | 7766000000012 | R3. | 77660000000115 | Each Balancing Authority, when requested, shall participate in a Time Error Correction by one of the following methods: |  | BA, RC | BA | [10 empty] | RC | [10 empty] | Low | The Balancing Authority participated in more than 75% and less than 100% of requested Time Error Corrections for the calendar year. | The Balancing Authority participated in more than 50% and less than or equal to 75% of requested Time Error Corrections for the calendar year. | The Balancing Authority participated in more than 25% and less than or equal to 50% of requested Time Error Corrections for the calendar year. | The Balancing Authority participated in less than or equal to 25% of requested Time Error Corrections for the calendar year. |  | 2012-04-01 |  | 2014-07-16 |  |  |  | MRO-MB | [6 empty] | 30000000
BAL-004-0 (Manitoba) | 7766000000012 | R4. | 77660000000118 | Any Reliability Coordinator in an Interconnection shall have the authority to request the Interconnection Time Monitor to terminate a Time Error Correction in progress, or a scheduled Time Error Correction that has not begun, for reliability considerations. |  | BA, RC | BA | [10 empty] | RC | [10 empty] | Low |  |  |  | The RC serving as the Interconnection Time Monitor failed to initiate or terminate corrective action orders in accordance with the NAESB Time Error Correction Procedure. |  | 2012-04-01 |  | 2014-07-16 |  |  |  | MRO-MB | [6 empty] | 40000000
BAL-004-0 (Ontario) | 79780000012 | R1. | 79780000113 | Only a Reliability Coordinator shall be eligible to act as Interconnection Time Monitor. A single Reliability Coordinator in each Interconnection shall be designated by the NERC Operating Committee to serve as Interconnection Time Monitor. |  | RC | [11 empty] | RC | [10 empty] | Low |  |  |  | The responsible entity has designated more than one interconnection time monitor for a single interconnection. |  | 2007-06-18 |  | 2017-04-01 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-004-0 (Ontario) | 79780000012 | R2. | 79780000114 | The Interconnection Time Monitor shall monitor Time Error and shall initiate or terminate corrective action orders in accordance with the NAESB Time Error Correction Procedure. |  | RC | [11 empty] | RC | [10 empty] | Low |  |  |  | The RC serving as the Interconnection Time Monitor failed to initiate or terminate corrective action orders in accordance with the NAESB Time Error Correction Procedure. |  | 2007-06-18 |  | 2017-04-01 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-004-0 (Ontario) | 79780000012 | R3. | 79780000115 | Each Balancing Authority, when requested, shall participate in a Time Error Correction by one of the following methods: |  | BA | BA | [21 empty] | Low | The Balancing Authority participated in more than 75% and less than 100% of requested Time Error Corrections for the calendar year. | The Balancing Authority participated in more than 50% and less than or equal to 75% of requested Time Error Corrections for the calendar year. | The Balancing Authority participated in more than 25% and less than or equal to 50% of requested Time Error Corrections for the calendar year. | The Balancing Authority participated in less than or equal to 25% of requested Time Error Corrections for the calendar year. |  | 2007-06-18 |  | 2017-04-01 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-004-0 (Ontario) | 79780000012 | R4. | 79780000118 | Any Reliability Coordinator in an Interconnection shall have the authority to request the Interconnection Time Monitor to terminate a Time Error Correction in progress, or a scheduled Time Error Correction that has not begun, for reliability considerations. |  | BA, RC | BA | [10 empty] | RC | [10 empty] | Low |  |  |  | The RC serving as the Interconnection Time Monitor failed to initiate or terminate corrective action orders in accordance with the NAESB Time Error Correction Procedure. |  | 2007-06-18 |  | 2017-04-01 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-004-1 | 13 | R1. | 120 | Only a Reliability Coordinator shall be eligible to act as Interconnection Time Monitor. |  | BA, RC | BA | [10 empty] | RC | [18 empty] | 2012-08-16 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-004-1 | 13 | R2. | 121 | Each Balancing Authority, when requested, shall participate in a Time Error Correction by one of the following methods: |  | BA, RC | BA | [10 empty] | RC | [18 empty] | 2012-08-16 |  |  | BAL-004-1 R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-004-1 | 13 | R3. | 124 | Any Reliability Coordinator in an Interconnection shall have the authority to request the Interconnection Time Monitor to terminate a Time Error Correction in progress, or a scheduled Time Error Correction that has not begun, for reliability considerations. |  | BA, RC | BA | [10 empty] | RC | [18 empty] | 2012-08-16 |  |  | BAL-004-0 R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-004-1 (Ontario) | 79780000013 | R1. | 79780000120 | Only a Reliability Coordinator shall be eligible to act as Interconnection Time Monitor. |  | RC | [11 empty] | RC | [18 empty] | 2012-08-16 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-004-1 (Ontario) | 79780000013 | R2. | 79780000121 | Each Balancing Authority, when requested, shall participate in a Time Error Correction by one of the following methods: |  | BA | BA | [29 empty] | 2012-08-16 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-004-1 (Ontario) | 79780000013 | R3. | 79780000124 | Any Reliability Coordinator in an Interconnection shall have the authority to request the Interconnection Time Monitor to terminate a Time Error Correction in progress, or a scheduled Time Error Correction that has not begun, for reliability considerations. |  | RC | [11 empty] | RC | [18 empty] | 2012-08-16 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-004-WECC-01 | 14 | R1. | 126 | Each BA that operates synchronously to the Western Interconnection shall continuously operate utilizing Automatic Time Error Correction (ATEC) in its Automatic Generation Control (AGC) system. (See standard for formulas.) |  | BA | BA | [21 empty] | Low | [5 empty] | 2009-07-01 |  | 2014-03-31 |  |  |  | WECC-US | [5 empty] | WECC-US | 10000000
BAL-004-WECC-01 | 14 | R2. | 129 | Each BA that is synchronously connected to the Western Interconnection and operates in any AGC operating mode other than ATEC shall notify all other BAs of its operating mode through the designated Interconnection communication system. Each BA while synchronously connected to the Western Interconnection will be allowed to have ATEC out of service for a maximum of 24 hours per calendar quarter, for reasons including maintenance and testing. [Risk Factor: Lower] |  | BA | BA | [20 empty] | Operations Assessment | Low | [5 empty] | 2009-07-01 |  | 2014-03-31 |  |  |  | WECC-US | [5 empty] | WECC-US | 20000000
BAL-004-WECC-01 | 14 | R3. | 130 | BAs in the Western Interconnection shall be able to change their AGC operating mode between Flat Frequency (for blackout restoration); Flat Tie Line (for loss of frequency telemetry); Tie Line Bias; Tie Line Bias plus Time Error control (used in ATEC mode). The ACE used for NERC reports shall be the same ACE as the AGC operating mode in use. |  | BA | BA | [20 empty] | Operations Assessment | Low |  |  |  |  | For Requirement R3, a BA in the Western Interconnection must be able to demonstrate its ability to change its AGC operating mode when requested or during compliance audits and readiness reviews. | 2009-07-01 |  | 2014-03-31 |  |  |  | WECC-US | [5 empty] | WECC-US | 30000000
BAL-004-WECC-01 | 14 | R4. | 131 | Regardless of the AGC operating mode each BA in the Western Interconnection shall compute its hourly Primary Inadvertent Interchange when hourly checkout is complete. If hourly checkout is not complete by 50 minutes after the hour, compute Primary Inadvertent Interchange with best available data. This hourly value shall be added to the appropriate accumulated Primary Inadvertent Interchange balance for either On-Peak or Off-Peak periods. |  | BA | BA | [20 empty] | Same-Day Operations | Low |  |  |  |  | For Requirement R4, a BA in the Western Interconnection must record its hourly Primary Inadvertent Interchange and keep an accurate record of its accumulation of Primary Inadvertent Interchange for both On-Peak and Off-Peak accounts. These records must be available for review when requested or during compliance audits and readiness reviews. | 2009-07-01 |  | 2014-03-31 |  |  |  | WECC-US | [5 empty] | WECC-US | 40000000
BAL-004-WECC-01 (British Columbia) | 666700000010015 | R1. | 666700000010404 | Each BA that operates synchronously to the Western Interconnection shall continuously operate utilizing Automatic Time Error Correction (ATEC) in its Automatic Generation Control (AGC) system. (See standard for formulas.) |  | BA | BA | [21 empty] | Low | [5 empty] | 2011-01-01 |  | 2014-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
BAL-004-WECC-01 (British Columbia) | 666700000010015 | R2. | 666700000010405 | Each BA that is synchronously connected to the Western Interconnection and operates in any AGC operating mode other than ATEC shall notify all other BAs of its operating mode through the designated Interconnection communication system. Each BA while synchronously connected to the Western Interconnection will be allowed to have ATEC out of service for a maximum of 24 hours per calendar quarter, for reasons including maintenance and testing. [Risk Factor: Lower] |  | BA | BA | [20 empty] | Operations Assessment | Low | [5 empty] | 2011-01-01 |  | 2014-09-30 |  |  |  | WECC-BC | [6 empty] | 20000000
BAL-004-WECC-01 (British Columbia) | 666700000010015 | R3. | 666700000010406 | BAs in the Western Interconnection shall be able to change their AGC operating mode between Flat Frequency (for blackout restoration); Flat Tie Line (for loss of frequency telemetry); Tie Line Bias; Tie Line Bias plus Time Error control (used in ATEC mode). The ACE used for NERC reports shall be the same ACE as the AGC operating mode in use. |  | BA | BA | [20 empty] | Operations Assessment | Low |  |  |  |  | For Requirement R3, a BA in the Western Interconnection must be able to demonstrate its ability to change its AGC operating mode when requested or during compliance audits and readiness reviews. | 2011-01-01 |  | 2014-09-30 |  |  |  | WECC-BC | [6 empty] | 30000000
BAL-004-WECC-01 (British Columbia) | 666700000010015 | R4. | 666700000010407 | Regardless of the AGC operating mode each BA in the Western Interconnection shall compute its hourly Primary Inadvertent Interchange when hourly checkout is complete. If hourly checkout is not complete by 50 minutes after the hour, compute Primary Inadvertent Interchange with best available data. This hourly value shall be added to the appropriate accumulated Primary Inadvertent Interchange balance for either On-Peak or Off-Peak periods. |  | BA | BA | [20 empty] | Same-Day Operations | Low |  |  |  |  | For Requirement R4, a BA in the Western Interconnection must record its hourly Primary Inadvertent Interchange and keep an accurate record of its accumulation of Primary Inadvertent Interchange for both On-Peak and Off-Peak accounts. These records must be available for review when requested or during compliance audits and readiness reviews. | 2011-01-01 |  | 2014-09-30 |  |  |  | WECC-BC | [6 empty] | 40000000
BAL-004-WECC-02 | 357 | R1. | 4519 | Following the conclusion of each month each Balancing Authority shall verify that the absolute value of its Accumulated Primary Inadvertent Interchange (PII-accum) for both the monthly On-Peak period and the monthly Off-Peak period are each individually less than or equal to: |  | BA | BA | [20 empty] | Operations Assessment | Medium | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 150%, but was less than or equal to 160% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 160%, but was less than or equal to 170% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 170%, but was less than or equal to 180% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 180% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. | M1. Forms of acceptable evidence of compliance with Requirement R1include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT), • Data, screen shots from the internal Balancing Authority tool, or • Production of data from any other databases, spreadsheets, displays. | 2014-04-01 |  | 2018-09-30 |  |  |  | WECC-US | [5 empty] | WECC-US | 10000000
BAL-004-WECC-02 | 357 | R2. | 4520 | Each Balancing Authority shall, upon discovery of an error in the calculation of PII-hourly, recalculate within 90 days, the value of PII-hourly and adjust the PII-accum from the time of the error. |  | BA | BA | [20 empty] | Operations Assessment | Medium | The Balancing Authority did not recalculate PIIhourly and adjust the PIIaccum within 90 days of the discovery of the error; but made the required recalculations and adjustments within 120 days. | The Balancing Authority did not recalculate PIIhourly and adjust the PIIaccum within 120 days of the discovery of the error; but made the required recalculations and adjustments within 150 days. | The Balancing Authority did not recalculate PIIhourly and adjust the PIIaccum within 150 days of the discovery of the error; but made the required recalculations and adjustments within 180 days. | The Balancing Authority did not recalculate PIIhourly and adjust PIIaccum within 180 days of the discovery of the error. | M2. Forms of acceptable evidence of compliance with Requirement R2 include but are not limited to any one of the following: • Data, screen shots from the WIT, • Data, screen shots from the internal Balancing Authority tool, or • Production of data from any other databases, spreadsheets, displays. | 2014-04-01 |  | 2018-09-30 |  |  |  | WECC-US | [5 empty] | WECC-US | 20000000
BAL-004-WECC-02 | 357 | R3. | 4521 | Each Balancing Authority shall keep its Automatic Time Error Correction (ATEC) in service, with an allowable exception period of less than or equal to an accumulated 24 hours per calendar quarter for ATEC to be out of service. |  | BA | BA | [20 empty] | Same-Day Operations | Medium | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 24 hours, but less than or equal to 72 hours. | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 72 hours, but less than or equal to 120 hours. | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 120 hours, but less than or equal to 168 hours | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 168 hours. | M3. Forms of acceptable evidence of compliance with Requirement R3 may include, but are not limited to: • Dated archived files, • Historical data, • Other data that demonstrates the ATEC was out of service for less than 24 hours per calendar quarter. | 2014-04-01 |  | 2018-09-30 |  |  |  | WECC-US | [5 empty] | WECC-US | 30000000
BAL-004-WECC-02 | 357 | R4. | 4522 | Each Balancing Authority shall compute the following by 50 minutes after each hour: |  | BA | BA | [20 empty] | Operations Assessment | Medium | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within 50 minutes, but made the required calculations in less than or equal to two hours. | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within two hours, but made the required calculations in less than or equal to four hours. | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within four hours, but made the required calculations in less than or equal to six hours. | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within six hours. | M4. Forms of acceptable evidence of compliance with Requirement R4 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool that demonstrate compliance, • Data, screen shots from internal Balancing Authority tool that demonstrate compliance, or • Data from any other databases, spreadsheets, displays that demonstrate compliance. | 2014-04-01 |  | 2018-09-30 |  |  |  | WECC-US | [5 empty] | WECC-US | 40000000
BAL-004-WECC-02 | 357 | R5. | 4523 | Each Balancing Authority shall be able to change its Automatic Generation Control operating mode between Flat Frequency (for blackout restoration); Flat Tie Line (for loss of frequency telemetry); Tie Line Bias; and Tie Line Bias plus Time Error Control (used in ATEC mode), to correspond to current operating conditions. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Balancing Authority is not able to change its AGC operating mode between Flat Frequency (for blackout restoration; Flat Tie Line (for loss of frequency telemetry); Tie Line Bias; or Tie Line Bias plus Time Error control (used in ATEC mode). | M5. Forms of acceptable evidence of compliance with Requirement R5 include but are not limited to any one of the following: • Screen shots from Energy Management System, • Demonstration using an off-line system. | 2014-04-01 |  | 2018-09-30 |  |  |  | WECC-US | [5 empty] | WECC-US | 50000000
BAL-004-WECC-02 | 357 | R6. | 4524 | Each Balancing Authority shall recalculate the PIIhourly and PIIaccum for the On-Peak and Off-Peak periods whenever adjustments are made to hourly Inadvertent Interchange or ?TE. |  | BA | BA | [20 empty] | Operations Assessment | Medium | N/A | N/A | N/A | When making adjustments to hourly Inadvertent Interchange or ?TE, the Balancing Authority did not recalculate the PIIhourly and the PIIaccum for the On-Peak and Off-Peak periods. | M6. Forms of acceptable evidence of compliance with Requirement R6 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool that demonstrate compliance, • Data, screen shots from an internal Balancing Authority tool that demonstrate compliance with, or • Data from any other databases, spreadsheets, displays that demonstrate compliance. | 2014-04-01 |  | 2018-09-30 |  |  |  | WECC-US | [5 empty] | WECC-US | 60000000
BAL-004-WECC-02 | 357 | R7. | 4525 | Each Balancing Authority shall make the same adjustment to the PII-accum as it did for any month-end meter reading adjustments to Inadvertent Interchange. |  | BA | BA | [20 empty] | Operations Assessment | Medium | N/A | N/A | N/A | When making any month-end meter reading adjustments to Inadvertent Interchange, the Balancing Authority did not make the same adjustment to the PIIaccum. | M7. Forms of acceptable evidence of compliance with Requirement R7 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool that demonstrate compliance, • Data, screen shots from an internal Balancing Authority tool that demonstrate compliance, • Production of data from any other databases, spreadsheets, displays that demonstrate compliance. | 2014-04-01 |  | 2018-09-30 |  |  |  | WECC-US | [5 empty] | WECC-US | 70000000
BAL-004-WECC-02 | 357 | R8. | 4526 | Each Balancing Authority shall payback Inadvertent Interchange using ATEC rather than bilateral and unilateral payback. |  | BA | BA | [20 empty] | Operations Assessment | Medium | N/A | N/A | N/A | The Balancing Authority paid back Inadvertent Interchange using bilateral and unilateral payback rather than using ATEC. | M8. Forms of acceptable evidence of compliance with Requirement R8 include but are not limited to historical On-Peak and Off-Peak Inadvertent Interchange data, data from the WECC Interchange Tool, and ACE data. | 2014-04-01 |  | 2018-09-30 |  |  |  | WECC-US | [5 empty] | WECC-US | 80000000
BAL-004-WECC-02 (British Columbia) | 666700000010016 | R1. | 666700000010408 | Following the conclusion of each month each Balancing Authority shall verify that the absolute value of its Accumulated Primary Inadvertent Interchange (PII-accum) for both the monthly On-Peak period and the monthly Off-Peak period are each individually less than or equal to: |  | BA | BA | [20 empty] | Operations Assessment | Medium | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 150%, but was less than or equal to 160% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 160%, but was less than or equal to 170% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 170%, but was less than or equal to 180% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 180% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. | M1. Forms of acceptable evidence of compliance with Requirement R1include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT), • Data, screen shots from the internal Balancing Authority tool, or • Production of data from any other databases, spreadsheets, displays. | 2014-10-01 |  | 2019-12-31 |  |  |  | WECC-BC | [6 empty] | 10000000
BAL-004-WECC-02 (British Columbia) | 666700000010016 | R2. | 666700000010409 | Each Balancing Authority shall, upon discovery of an error in the calculation of PII-hourly, recalculate within 90 days, the value of PII-hourly and adjust the PII-accum from the time of the error. |  | BA | BA | [20 empty] | Operations Assessment | Medium | The Balancing Authority did not recalculate PIIhourly and adjust the PIIaccum within 90 days of the discovery of the error; but made the required recalculations and adjustments within 120 days. | The Balancing Authority did not recalculate PIIhourly and adjust the PIIaccum within 120 days of the discovery of the error; but made the required recalculations and adjustments within 150 days. | The Balancing Authority did not recalculate PIIhourly and adjust the PIIaccum within 150 days of the discovery of the error; but made the required recalculations and adjustments within 180 days. | The Balancing Authority did not recalculate PIIhourly and adjust PIIaccum within 180 days of the discovery of the error. | M2. Forms of acceptable evidence of compliance with Requirement R2 include but are not limited to any one of the following: • Data, screen shots from the WIT, • Data, screen shots from the internal Balancing Authority tool, or • Production of data from any other databases, spreadsheets, displays. | 2014-10-01 |  | 2019-12-31 |  |  |  | WECC-BC | [6 empty] | 20000000
BAL-004-WECC-02 (British Columbia) | 666700000010016 | R3. | 666700000010410 | Each Balancing Authority shall keep its Automatic Time Error Correction (ATEC) in service, with an allowable exception period of less than or equal to an accumulated 24 hours per calendar quarter for ATEC to be out of service. |  | BA | BA | [20 empty] | Same-Day Operations | Medium | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 24 hours, but less than or equal to 72 hours. | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 72 hours, but less than or equal to 120 hours. | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 120 hours, but less than or equal to 168 hours | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 168 hours. | M3. Forms of acceptable evidence of compliance with Requirement R3 may include, but are not limited to: • Dated archived files, • Historical data, • Other data that demonstrates the ATEC was out of service for less than 24 hours per calendar quarter. | 2014-10-01 |  | 2019-12-31 |  |  |  | WECC-BC | [6 empty] | 30000000
BAL-004-WECC-02 (British Columbia) | 666700000010016 | R4. | 666700000010411 | Each Balancing Authority shall compute the following by 50 minutes after each hour: |  | BA | BA | [20 empty] | Operations Assessment | Medium | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within 50 minutes, but made the required calculations in less than or equal to two hours. | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within two hours, but made the required calculations in less than or equal to four hours. | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within four hours, but made the required calculations in less than or equal to six hours. | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within six hours. | M4. Forms of acceptable evidence of compliance with Requirement R4 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool that demonstrate compliance, • Data, screen shots from internal Balancing Authority tool that demonstrate compliance, or • Data from any other databases, spreadsheets, displays that demonstrate compliance. | 2014-10-01 |  | 2019-12-31 |  |  |  | WECC-BC | [6 empty] | 40000000
BAL-004-WECC-02 (British Columbia) | 666700000010016 | R5. | 666700000010412 | Each Balancing Authority shall be able to change its Automatic Generation Control operating mode between Flat Frequency (for blackout restoration); Flat Tie Line (for loss of frequency telemetry); Tie Line Bias; and Tie Line Bias plus Time Error Control (used in ATEC mode), to correspond to current operating conditions. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Balancing Authority is not able to change its AGC operating mode between Flat Frequency (for blackout restoration; Flat Tie Line (for loss of frequency telemetry); Tie Line Bias; or Tie Line Bias plus Time Error control (used in ATEC mode). | M5. Forms of acceptable evidence of compliance with Requirement R5 include but are not limited to any one of the following: • Screen shots from Energy Management System, • Demonstration using an off-line system. | 2014-10-01 |  | 2019-12-31 |  |  |  | WECC-BC | [6 empty] | 50000000
BAL-004-WECC-02 (British Columbia) | 666700000010016 | R6. | 666700000010413 | Each Balancing Authority shall recalculate the PIIhourly and PIIaccum for the On-Peak and Off-Peak periods whenever adjustments are made to hourly Inadvertent Interchange or ?TE. |  | BA | BA | [20 empty] | Operations Assessment | Medium | N/A | N/A | N/A | When making adjustments to hourly Inadvertent Interchange or ?TE, the Balancing Authority did not recalculate the PIIhourly and the PIIaccum for the On-Peak and Off-Peak periods. | M6. Forms of acceptable evidence of compliance with Requirement R6 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool that demonstrate compliance, • Data, screen shots from an internal Balancing Authority tool that demonstrate compliance with, or • Data from any other databases, spreadsheets, displays that demonstrate compliance. | 2014-10-01 |  | 2019-12-31 |  |  |  | WECC-BC | [6 empty] | 60000000
BAL-004-WECC-02 (British Columbia) | 666700000010016 | R7. | 666700000010414 | Each Balancing Authority shall make the same adjustment to the PII-accum as it did for any month-end meter reading adjustments to Inadvertent Interchange. |  | BA | BA | [20 empty] | Operations Assessment | Medium | N/A | N/A | N/A | When making any month-end meter reading adjustments to Inadvertent Interchange, the Balancing Authority did not make the same adjustment to the PIIaccum. | M7. Forms of acceptable evidence of compliance with Requirement R7 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool that demonstrate compliance, • Data, screen shots from an internal Balancing Authority tool that demonstrate compliance, • Production of data from any other databases, spreadsheets, displays that demonstrate compliance. | 2014-10-01 |  | 2019-12-31 |  |  |  | WECC-BC | [6 empty] | 70000000
BAL-004-WECC-02 (British Columbia) | 666700000010016 | R8. | 666700000010415 | Each Balancing Authority shall payback Inadvertent Interchange using ATEC rather than bilateral and unilateral payback. |  | BA | BA | [20 empty] | Operations Assessment | Medium | N/A | N/A | N/A | The Balancing Authority paid back Inadvertent Interchange using bilateral and unilateral payback rather than using ATEC. | M8. Forms of acceptable evidence of compliance with Requirement R8 include but are not limited to historical On-Peak and Off-Peak Inadvertent Interchange data, data from the WECC Interchange Tool, and ACE data. | 2014-10-01 |  | 2019-12-31 |  |  |  | WECC-BC | [6 empty] | 80000000
BAL-004-WECC-3 | 581 | R1. | 8375 | Each Balancing Authority shall operate its system such that, following the conclusion of each month, the month-end absolute value of its On-Peak and Off-Peak, Accumulated Primary Inadvertent Interchange (PIIaccum), as calculated by the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, are each individually less than or equal to: |  | BA | BA | [20 empty] | Operations Assessment | Medium | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 150%, but was less than or equal to 160% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 160%, but was less than or equal to 170% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 170%, but was less than or equal to 180% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 180% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. | M1. Each Balancing Authority will have evidence that it operated its system such that, following the conclusion of each month, the month-end absolute value of its On-Peak and Off-Peak, Accumulated Primary Inadvertent Interchange (PIIaccum), as calculated by the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, meets all criteria stated in Requirement R1. | 2018-10-01 | [5 empty] | WECC-US | [5 empty] | WECC-US | 10000000
BAL-004-WECC-3 | 581 | R2. | 8378 | Each Balancing Authority shall, upon discovery of an error in the calculation of PIIhourly, recalculate within 90 days, the value of PIIhourly and adjust the PIIaccum from the time of the error. |  | BA | BA | [20 empty] | Operations Assessment | Medium | The Balancing Authority did not recalculate PIIhourly and adjust the PIIaccum within 90 days of the discovery of the error; but made the required recalculations and adjustments within 120 days. | The Balancing Authority did not recalculate PIIhourly and adjust the PIIaccum within 120 days of the discovery of the error; but made the required recalculations and adjustments within 150 days. | The Balancing Authority did not recalculate PIIhourly and adjust the PIIaccum within 150 days of the discovery of the error; but made the required recalculations and adjustments within 180 days. | The Balancing Authority did not recalculate PIIhourly and adjust the PIIaccum within 150 days of the discovery of the error. | M2. Forms of acceptable evidence of compliance with Requirement R2 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, • Data, screen shots from the internal Balancing Authority tool, or • Production of data from any other databases, spreadsheets, displays. | 2018-10-01 | [5 empty] | WECC-US | [5 empty] | WECC-US | 20000000
BAL-004-WECC-3 | 581 | R3. | 8379 | Each Balancing Authority shall keep its Automatic Time Error Correction (ATEC) in service, with an allowable exception period of less than or equal to an accumulated 24 hours per calendar quarter for ATEC to be out of service. |  | BA | BA | [20 empty] | Same-Day Operations | Medium | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 24 hours, but less than or equal to 72 hours. | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 72 hours, but less than or equal to 120 hours. | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 120 hours, but less than or equal to 168 hours | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 168 hours. | M3. Forms of acceptable evidence of compliance with Requirement R3 may include, but are not limited to: • Dated archived files, • Historical data, • Other data that demonstrates the ATEC was out of service for less than 24 hours per calendar quarter. | 2018-10-01 | [5 empty] | WECC-US | [5 empty] | WECC-US | 30000000
BAL-004-WECC-3 | 581 | R4. | 8380 | Each Balancing Authority shall compute each of the following using the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, no later than 50 minutes after each hour, |  | BA | BA | [20 empty] | Operations Assessment | Medium | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within 50 minutes, but made the required calculations in less than or equal to two hours. | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within two hours, but made the required calculations in less than or equal to four hours. | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within four hours, but made the required calculations in less than or equal to six hours. | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within six hours. | M4. Forms of acceptable evidence of compliance with Requirement R4 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, that demonstrate compliance; • Data, screen shots from internal Balancing Authority tool that demonstrate compliance; or, • Data from any other databases, spreadsheets, displays that demonstrate compliance. | 2018-10-01 | [5 empty] | WECC-US | [5 empty] | WECC-US | 40000000
BAL-004-WECC-3 | 581 | R5. | 8384 | Each Balancing Authority shall be able to change its Automatic Generation Control operating mode between Flat Frequency (for blackout restoration); Flat Tie Line (for loss of frequency telemetry); Tie Line Bias; and Tie Line Bias plus Time Error Control (used in ATEC mode), to correspond to current operating conditions. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Balancing Authority is not able to change its AGC operating mode between Flat Frequency (for blackout restoration; Flat Tie Line (for loss of frequency telemetry); Tie Line Bias; or Tie Line Bias plus Time Error control (used in ATEC mode). | M5. Forms of acceptable evidence of compliance with Requirement R5 include but are not limited to any one of the following: • Screen shots from Energy Management System, • Demonstration using an off-line system. | 2018-10-01 | [5 empty] | WECC-US | [5 empty] | WECC-US | 50000000
BAL-004-WECC-3 | 581 | R6. | 8385 | Each Balancing Authority shall recalculate the PIIhourly and PIIaccum for the On-Peak and Off-Peak periods whenever adjustments are made to hourly Inadvertent Interchange or ?TE. |  | BA | BA | [20 empty] | Operations Assessment | Medium | N/A | N/A | N/A | When making adjustments to hourly Inadvertent Interchange or ?TE, the Balancing Authority did not recalculate the PIIhourly and the PIIaccum for the On-Peak and Off-Peak periods. | M6. Forms of acceptable evidence of compliance with Requirement R6 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, that demonstrate compliance; • Data, screen shots from an internal Balancing Authority tool that demonstrate compliance with; or, • Data from any other databases, spreadsheets, displays that demonstrate compliance. | 2018-10-01 | [5 empty] | WECC-US | [5 empty] | WECC-US | 60000000
BAL-004-WECC-3 | 581 | R7. | 8386 | Each Balancing Authority shall make the same adjustment to the PIIaccum as it did for any month-end meter reading adjustments to Inadvertent Interchange. |  | BA | BA | [20 empty] | Operations Assessment | Medium | N/A | N/A | N/A | When making any month-end meter reading adjustments to Inadvertent Interchange, the Balancing Authority did not make the same adjustment to the PIIaccum. | M7. Forms of acceptable evidence of compliance with Requirement R7 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, that demonstrate compliance; • Data, screen shots from an internal Balancing Authority tool that demonstrate compliance; or, • Production of data from any other databases, spreadsheets, displays that demonstrate compliance. | 2018-10-01 | [5 empty] | WECC-US | [5 empty] | WECC-US | 70000000
BAL-004-WECC-3 | 581 | R8. | 8387 | Each Balancing Authority shall payback Inadvertent Interchange using ATEC rather than bilateral and unilateral payback. |  | BA | BA | [20 empty] | Operations Assessment | Medium | N/A | N/A | N/A | The Balancing Authority paid back Inadvertent Interchange using bilateral and unilateral payback rather than using ATEC. | M8. Forms of acceptable evidence of compliance with Requirement R8 include but are not limited to historical On-Peak and Off-Peak Inadvertent Interchange data, data from the WECC Interchange Tool, and ACE data. | 2018-10-01 | [5 empty] | WECC-US | [5 empty] | WECC-US | 80000000
BAL-004-WECC-3 (British Columbia) | 666700000010017 | R1. | 666700000010416 | Each Balancing Authority shall operate its system such that, following the conclusion of each month, the month-end absolute value of its On-Peak and Off-Peak, Accumulated Primary Inadvertent Interchange (PIIaccum), as calculated by the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, are each individually less than or equal to: |  | BA | BA | [20 empty] | Operations Assessment | Medium | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 150%, but was less than or equal to 160% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 160%, but was less than or equal to 170% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 170%, but was less than or equal to 180% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 180% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. | M1. Each Balancing Authority will have evidence that it operated its system such that, following the conclusion of each month, the month-end absolute value of its On-Peak and Off-Peak, Accumulated Primary Inadvertent Interchange (PIIaccum), as calculated by the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, meets all criteria stated in Requirement R1. | 2020-01-01 | [5 empty] | WECC-BC | [6 empty] | 10000000
BAL-004-WECC-3 (British Columbia) | 666700000010017 | R2. | 666700000010417 | Each Balancing Authority shall, upon discovery of an error in the calculation of PIIhourly, recalculate within 90 days, the value of PIIhourly and adjust the PIIaccum from the time of the error. |  | BA | BA | [20 empty] | Operations Assessment | Medium | The Balancing Authority did not recalculate PIIhourly and adjust the PIIaccum within 90 days of the discovery of the error; but made the required recalculations and adjustments within 120 days. | The Balancing Authority did not recalculate PIIhourly and adjust the PIIaccum within 120 days of the discovery of the error; but made the required recalculations and adjustments within 150 days. | The Balancing Authority did not recalculate PIIhourly and adjust the PIIaccum within 150 days of the discovery of the error; but made the required recalculations and adjustments within 180 days. | The Balancing Authority did not recalculate PIIhourly and adjust the PIIaccum within 150 days of the discovery of the error. | M2. Forms of acceptable evidence of compliance with Requirement R2 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, • Data, screen shots from the internal Balancing Authority tool, or • Production of data from any other databases, spreadsheets, displays. | 2020-01-01 | [5 empty] | WECC-BC | [6 empty] | 20000000
BAL-004-WECC-3 (British Columbia) | 666700000010017 | R3. | 666700000010418 | Each Balancing Authority shall keep its Automatic Time Error Correction (ATEC) in service, with an allowable exception period of less than or equal to an accumulated 24 hours per calendar quarter for ATEC to be out of service. |  | BA | BA | [20 empty] | Same-Day Operations | Medium | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 24 hours, but less than or equal to 72 hours. | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 72 hours, but less than or equal to 120 hours. | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 120 hours, but less than or equal to 168 hours | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 168 hours. | M3. Forms of acceptable evidence of compliance with Requirement R3 may include, but are not limited to: • Dated archived files, • Historical data, • Other data that demonstrates the ATEC was out of service for less than 24 hours per calendar quarter. | 2020-01-01 | [5 empty] | WECC-BC | [6 empty] | 30000000
BAL-004-WECC-3 (British Columbia) | 666700000010017 | R4. | 666700000010419 | Each Balancing Authority shall compute each of the following using the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, no later than 50 minutes after each hour, |  | BA | BA | [20 empty] | Operations Assessment | Medium | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within 50 minutes, but made the required calculations in less than or equal to two hours. | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within two hours, but made the required calculations in less than or equal to four hours. | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within four hours, but made the required calculations in less than or equal to six hours. | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within six hours. | M4. Forms of acceptable evidence of compliance with Requirement R4 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, that demonstrate compliance; • Data, screen shots from internal Balancing Authority tool that demonstrate compliance; or, • Data from any other databases, spreadsheets, displays that demonstrate compliance. | 2020-01-01 | [5 empty] | WECC-BC | [6 empty] | 40000000
BAL-004-WECC-3 (British Columbia) | 666700000010017 | R5. | 666700000010420 | Each Balancing Authority shall be able to change its Automatic Generation Control operating mode between Flat Frequency (for blackout restoration); Flat Tie Line (for loss of frequency telemetry); Tie Line Bias; and Tie Line Bias plus Time Error Control (used in ATEC mode), to correspond to current operating conditions. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Balancing Authority is not able to change its AGC operating mode between Flat Frequency (for blackout restoration; Flat Tie Line (for loss of frequency telemetry); Tie Line Bias; or Tie Line Bias plus Time Error control (used in ATEC mode). | M5. Forms of acceptable evidence of compliance with Requirement R5 include but are not limited to any one of the following: • Screen shots from Energy Management System, • Demonstration using an off-line system. | 2020-01-01 | [5 empty] | WECC-BC | [6 empty] | 50000000
BAL-004-WECC-3 (British Columbia) | 666700000010017 | R6. | 666700000010421 | Each Balancing Authority shall recalculate the PIIhourly and PIIaccum for the On-Peak and Off-Peak periods whenever adjustments are made to hourly Inadvertent Interchange or ?TE. |  | BA | BA | [20 empty] | Operations Assessment | Medium | N/A | N/A | N/A | When making adjustments to hourly Inadvertent Interchange or ?TE, the Balancing Authority did not recalculate the PIIhourly and the PIIaccum for the On-Peak and Off-Peak periods. | M6. Forms of acceptable evidence of compliance with Requirement R6 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, that demonstrate compliance; • Data, screen shots from an internal Balancing Authority tool that demonstrate compliance with; or, • Data from any other databases, spreadsheets, displays that demonstrate compliance. | 2020-01-01 | [5 empty] | WECC-BC | [6 empty] | 60000000
BAL-004-WECC-3 (British Columbia) | 666700000010017 | R7. | 666700000010422 | Each Balancing Authority shall make the same adjustment to the PIIaccum as it did for any month-end meter reading adjustments to Inadvertent Interchange. |  | BA | BA | [20 empty] | Operations Assessment | Medium | N/A | N/A | N/A | When making any month-end meter reading adjustments to Inadvertent Interchange, the Balancing Authority did not make the same adjustment to the PIIaccum. | M7. Forms of acceptable evidence of compliance with Requirement R7 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, that demonstrate compliance; • Data, screen shots from an internal Balancing Authority tool that demonstrate compliance; or, • Production of data from any other databases, spreadsheets, displays that demonstrate compliance. | 2020-01-01 | [5 empty] | WECC-BC | [6 empty] | 70000000
BAL-004-WECC-3 (British Columbia) | 666700000010017 | R8. | 666700000010423 | Each Balancing Authority shall payback Inadvertent Interchange using ATEC rather than bilateral and unilateral payback. |  | BA | BA | [20 empty] | Operations Assessment | Medium | N/A | N/A | N/A | The Balancing Authority paid back Inadvertent Interchange using bilateral and unilateral payback rather than using ATEC. | M8. Forms of acceptable evidence of compliance with Requirement R8 include but are not limited to historical On-Peak and Off-Peak Inadvertent Interchange data, data from the WECC Interchange Tool, and ACE data. | 2020-01-01 | [5 empty] | WECC-BC | [6 empty] | 80000000
BAL-004-WECC-AB-2 (Alberta) | 656600000009004 | R1. | 656600000009075 | Following the conclusion of each month, the ISO must verify that the absolute value of its accumulated primary inadvertent interchange for both the monthly on peak period and the monthly off peak period are each individually less than or equal to 150% of the previous calendar year's peak demand, where peak demand is the highest hourly integrated net energy for load. |  | ISO | [28 empty] | 2016-12-19 | [5 empty] | WECC-AB | [6 empty] | 10000000
BAL-004-WECC-AB-2 (Alberta) | 656600000009004 | R2. | 656600000009076 | The ISO must, within ninety (90) days of discovery of an error in the calculation of hourly primary inadvertent interchange, recalculate the value of hourly primary inadvertent interchange and adjust the accumulated primary inadvertent interchange from the time of the error. |  | ISO | [28 empty] | 2016-12-19 | [5 empty] | WECC-AB | [6 empty] | 20000000
BAL-004-WECC-AB-2 (Alberta) | 656600000009004 | R3. | 656600000009077 | The ISO must, while synchronously connected to the western interconnection, keep its automatic time error correction in service, with an allowable exception period of less than or equal to an accumulated twenty-four (24) hours per calendar quarter for automatic time error correction to be out of service. |  | ISO | [28 empty] | 2016-12-19 | [5 empty] | WECC-AB | [6 empty] | 30000000
BAL-004-WECC-AB-2 (Alberta) | 656600000009004 | R4. | 656600000009078 | The ISO must compute the following by fifty (50) minutes after each hour: |  | ISO | [28 empty] | 2016-12-19 | [5 empty] | WECC-AB | [6 empty] | 40000000
BAL-004-WECC-AB-2 (Alberta) | 656600000009004 | R5. | 656600000009079 | The ISO must be able to change its automatic generation control operating mode between flat frequency, flat tie line, tie line bias, and tie line bias plus time error control, to correspond to current operating conditions. |  | ISO | [28 empty] | 2016-12-19 | [5 empty] | WECC-AB | [6 empty] | 50000000
BAL-004-WECC-AB-2 (Alberta) | 656600000009004 | R6. | 656600000009080 | The ISO must recalculate the hourly primary inadvertent interchange and accumulated primary inadvertent interchange for the on peak and off peak periods whenever adjustments are made to hourly inadvertent interchange or the hourly change in system time error, as distributed by the Interconnection time monitor. |  | ISO | [28 empty] | 2016-12-19 | [5 empty] | WECC-AB | [6 empty] | 60000000
BAL-004-WECC-AB-2 (Alberta) | 656600000009004 | R7. | 656600000009081 | The ISO must make the same adjustment to the accumulated primary inadvertent interchange as it did for any month-end meter reading adjustments to inadvertent interchange. |  | ISO | [28 empty] | 2016-12-19 | [5 empty] | WECC-AB | [6 empty] | 70000000
BAL-004-WECC-AB-2 (Alberta) | 656600000009004 | R8. | 656600000009082 | The ISO must payback inadvertent interchange using automatic time error correction rather than bilateral and unilateral payback. |  | ISO | [28 empty] | 2016-12-19 | [5 empty] | WECC-AB | [6 empty] | 80000000
BAL-005-0 | 15 | R1. | 136 | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | N/A | N/A | N/A | N/A |  | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-005-0 | 15 | R10. | 140 | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | High | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 100000000
BAL-005-0 | 15 | R11. | 141 | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 110000000
BAL-005-0 | 15 | R12. | 142 | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 120000000
BAL-005-0 | 15 | R13. | 146 | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 130000000
BAL-005-0 | 15 | R14. | 147 | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 140000000
BAL-005-0 | 15 | R15. | 148 | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 150000000
BAL-005-0 | 15 | R16. | 149 | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 160000000
BAL-005-0 | 15 | R17. | 150 | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See standard for formula. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 170000000
BAL-005-0 | 15 | R2. | 151 | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-005-0 | 15 | R3. | 152 | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-005-0 | 15 | R4. | 153 | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-005-0 | 15 | R5. | 154 | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
BAL-005-0 | 15 | R6. | 155 | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
BAL-005-0 | 15 | R7. | 156 | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
BAL-005-0 | 15 | R8. | 157 | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
BAL-005-0 | 15 | R9. | 159 | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
BAL-005-0.1b | 16 | R1. | 161 | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [9 empty] | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-005-0.1b | 16 | R10. | 165 | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | High | [5 empty] | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R10. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 100000000
BAL-005-0.1b | 16 | R11. | 166 | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R11. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 110000000
BAL-005-0.1b | 16 | R12. | 167 | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R12. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 120000000
BAL-005-0.1b | 16 | R13. | 171 | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R13. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 130000000
BAL-005-0.1b | 16 | R14. | 172 | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R14. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 140000000
BAL-005-0.1b | 16 | R15. | 173 | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R15. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 150000000
BAL-005-0.1b | 16 | R16. | 174 | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R16. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 160000000
BAL-005-0.1b | 16 | R17. | 175 | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See Standard for Values |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R17. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 170000000
BAL-005-0.1b | 16 | R2. | 176 | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | High | [5 empty] | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-005-0.1b | 16 | R3. | 177 | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-005-0.1b | 16 | R4. | 178 | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-005-0.1b | 16 | R5. | 179 | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R5. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
BAL-005-0.1b | 16 | R6. | 180 | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R6. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
BAL-005-0.1b | 16 | R7. | 181 | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R7. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
BAL-005-0.1b | 16 | R8. | 182 | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R8. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
BAL-005-0.1b | 16 | R9. | 184 | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R9. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
BAL-005-0.1b (British Columbia) | 666700000010018 | R1. | 666700000010424 | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [9 empty] | 2011-01-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 10000000
BAL-005-0.1b (British Columbia) | 666700000010018 | R10. | 666700000010425 | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | High | [5 empty] | 2011-01-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 100000000
BAL-005-0.1b (British Columbia) | 666700000010018 | R11. | 666700000010426 | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-01-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 110000000
BAL-005-0.1b (British Columbia) | 666700000010018 | R12. | 666700000010427 | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-01-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 120000000
BAL-005-0.1b (British Columbia) | 666700000010018 | R13. | 666700000010428 | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2011-01-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 130000000
BAL-005-0.1b (British Columbia) | 666700000010018 | R14. | 666700000010429 | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2011-01-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 140000000
BAL-005-0.1b (British Columbia) | 666700000010018 | R15. | 666700000010430 | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2011-01-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 150000000
BAL-005-0.1b (British Columbia) | 666700000010018 | R16. | 666700000010431 | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-01-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 160000000
BAL-005-0.1b (British Columbia) | 666700000010018 | R17. | 666700000010432 | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See Standard for Values |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-01-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 170000000
BAL-005-0.1b (British Columbia) | 666700000010018 | R2. | 666700000010433 | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | High | [5 empty] | 2011-01-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 20000000
BAL-005-0.1b (British Columbia) | 666700000010018 | R3. | 666700000010434 | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-01-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 30000000
BAL-005-0.1b (British Columbia) | 666700000010018 | R4. | 666700000010435 | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-01-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 40000000
BAL-005-0.1b (British Columbia) | 666700000010018 | R5. | 666700000010436 | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-01-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 50000000
BAL-005-0.1b (British Columbia) | 666700000010018 | R6. | 666700000010437 | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-01-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 60000000
BAL-005-0.1b (British Columbia) | 666700000010018 | R7. | 666700000010438 | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-01-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 70000000
BAL-005-0.1b (British Columbia) | 666700000010018 | R8. | 666700000010439 | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-01-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 80000000
BAL-005-0.1b (British Columbia) | 666700000010018 | R9. | 666700000010440 | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2011-01-01 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 90000000
BAL-005-0.1b (Ontario) | 79780000016 | R1. | 79780000161 | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  | GOP, LSE, TOP | [5 empty] | GOP |  | LSE | [10 empty] | TOP | [9 empty] | 2009-05-13 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-005-0.1b (Ontario) | 79780000016 | R10. | 79780000165 | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA | BA | [21 empty] | High |  |  |  | The Balancing Authority failed to include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | 2009-05-13 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 100000000
BAL-005-0.1b (Ontario) | 79780000016 | R11. | 79780000166 | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority failed to include the effect of Ramp rates in the Scheduled Interchange values to calculate ACE. |  | 2009-05-13 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 110000000
BAL-005-0.1b (Ontario) | 79780000016 | R12. | 79780000167 | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority failed to include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | 2009-05-13 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 120000000
BAL-005-0.1b (Ontario) | 79780000016 | R13. | 79780000171 | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority failed to perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment OR the Balancing Authority failed to adjust the component (e.g., Tie Line |  | 2009-05-13 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 130000000
BAL-005-0.1b (Ontario) | 79780000016 | R14. | 79780000172 | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority failed to provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. |  | 2009-05-13 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 140000000
BAL-005-0.1b (Ontario) | 79780000016 | R15. | 79780000173 | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | BA | BA | [21 empty] | Low |  |  | The Balancing Authority failed to periodically test backup power supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power sup | The Balancing Authority failed to provide adequate and reliable backup power supplies to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | 2009-05-13 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 150000000
BAL-005-0.1b (Ontario) | 79780000016 | R16. | 79780000174 | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  | BA | BA | [21 empty] | Medium | The Balancing Authority failed to collect coincident data to the greatest practical extent. |  | The Balancing Authority failed to flag missing or bad data for operator display and archival purposes. | The Balancing Authority failed to sample data at least at the same periodicity with which ACE is calculated. |  | 2009-05-13 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 160000000
BAL-005-0.1b (Ontario) | 79780000016 | R17. | 79780000175 | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See Standard for Values |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority failed to at least annually check and calibrate its time error and frequency devices against a common reference. |  | 2009-05-13 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 170000000
BAL-005-0.1b (Ontario) | 79780000016 | R2. | 79780000176 | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. |  | BA | BA | [21 empty] | High |  |  |  | The Balancing Authority failed to maintain Regulating Reserve that can be controlled by AGC to meet Control Performance Standard. |  | 2009-05-13 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-005-0.1b (Ontario) | 79780000016 | R3. | 79780000177 | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority providing Regulation Service failed to ensure adequate metering, communications, and control equipment was provided. |  | 2009-05-13 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-005-0.1b (Ontario) | 79780000016 | R4. | 79780000178 | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority providing Regulation Service failed to notify the Host Balancing Authority for whom it is controlling if it was unable to provide the service, as well as any Intermediate Balancing Authorities. |  | 2009-05-13 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-005-0.1b (Ontario) | 79780000016 | R5. | 79780000179 | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority receiving Regulation Service failed to ensure that back-up plans were in place to provide replacement Regulation Service. |  | 2009-05-13 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 50000000
BAL-005-0.1b (Ontario) | 79780000016 | R6. | 79780000180 | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  | BA | BA | [21 empty] | Medium | The Balancing Authority failed to notify the Reliability Coordinator within 30 minutes of its inability to calculate ACE. | The Balancing Authority failed to calculate ACE as specified in the requirement. |  | The Balancing Authority failed to notify the Reliability Coordinator within 30 minutes of its inability to calculate ACE and failed to use the ACE calculation specified in the requirement in its attempt to calculate ACE. |  | 2009-05-13 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 60000000
BAL-005-0.1b (Ontario) | 79780000016 | R7. | 79780000181 | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority failed to operate AGC continuously when there were no adverse impacts OR if their AGC was inoperative the Balancing Authority failed to use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | 2009-05-13 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 70000000
BAL-005-0.1b (Ontario) | 79780000016 | R8. | 79780000182 | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority failed to ensure that data acquisition for and calculation of ACE occurred at least every six seconds. |  | 2009-05-13 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 80000000
BAL-005-0.1b (Ontario) | 79780000016 | R9. | 79780000184 | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority failed to include all Interchanged Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | 2009-05-13 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 90000000
BAL-005-0.1b (Saskatchewan) | 8375000000016 | R1. | 83750000000161 | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [9 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 10000000
BAL-005-0.1b (Saskatchewan) | 8375000000016 | R10. | 83750000000165 | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | High | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 100000000
BAL-005-0.1b (Saskatchewan) | 8375000000016 | R11. | 83750000000166 | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 110000000
BAL-005-0.1b (Saskatchewan) | 8375000000016 | R12. | 83750000000167 | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 120000000
BAL-005-0.1b (Saskatchewan) | 8375000000016 | R13. | 83750000000171 | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 130000000
BAL-005-0.1b (Saskatchewan) | 8375000000016 | R14. | 83750000000172 | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 140000000
BAL-005-0.1b (Saskatchewan) | 8375000000016 | R15. | 83750000000173 | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 150000000
BAL-005-0.1b (Saskatchewan) | 8375000000016 | R16. | 83750000000174 | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 160000000
BAL-005-0.1b (Saskatchewan) | 8375000000016 | R17. | 83750000000175 | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See Standard for Values |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 170000000
BAL-005-0.1b (Saskatchewan) | 8375000000016 | R2. | 83750000000176 | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | High | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 20000000
BAL-005-0.1b (Saskatchewan) | 8375000000016 | R3. | 83750000000177 | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 30000000
BAL-005-0.1b (Saskatchewan) | 8375000000016 | R4. | 83750000000178 | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 40000000
BAL-005-0.1b (Saskatchewan) | 8375000000016 | R5. | 83750000000179 | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 50000000
BAL-005-0.1b (Saskatchewan) | 8375000000016 | R6. | 83750000000180 | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 60000000
BAL-005-0.1b (Saskatchewan) | 8375000000016 | R7. | 83750000000181 | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 70000000
BAL-005-0.1b (Saskatchewan) | 8375000000016 | R8. | 83750000000182 | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 80000000
BAL-005-0.1b (Saskatchewan) | 8375000000016 | R9. | 83750000000184 | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 90000000
BAL-005-0.2b | 315 | R1. | 4105 | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [9 empty] | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-005-0.2b | 315 | R10. | 4108 | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | High |  |  |  | The Balancing Authority failed to include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R10. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 100000000
BAL-005-0.2b | 315 | R11. | 4110 | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority failed to include the effect of Ramp rates in the Scheduled Interchange values to calculate ACE. |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R11. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 110000000
BAL-005-0.2b | 315 | R12. | 4111 | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority failed to include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R12. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 120000000
BAL-005-0.2b | 315 | R13. | 4107 | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low |  |  |  | The Balancing Authority failed to perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment OR the Balancing Authority failed to adjust the component (e.g., Tie Line |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R13. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 130000000
BAL-005-0.2b | 315 | R14. | 4101 | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | N/A | The responsible entity did not provide its operating personnel with real-time values for one of the following: ACE, Interconnection frequency or Net Actual Interchange. | The responsible entity did not provide its operating personnel with real-time values for two of the following: ACE, Interconnection frequency or Net Actual Interchange. | The responsible entity did not provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. OR The respo |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R14. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 140000000
BAL-005-0.2b | 315 | R15. | 4113 | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low |  |  | The Balancing Authority failed to periodically test backup power supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power sup | The Balancing Authority failed to provide adequate and reliable backup power supplies to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R15. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 150000000
BAL-005-0.2b | 315 | R16. | 4115 | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | The Balancing Authority failed to collect coincident data to the greatest practical extent. |  | The Balancing Authority failed to flag missing or bad data for operator display and archival purposes. | The Balancing Authority failed to sample data at least at the same periodicity with which ACE is calculated. |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R16. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 160000000
BAL-005-0.2b | 315 | R17. | 4112 | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See Standard for Values |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority failed to at least annually check and calibrate its time error and frequency devices against a common reference. |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R17. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 170000000
BAL-005-0.2b | 315 | R2. | 4100 | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. (Retirement approved by FERC effective January 21, 2014.) |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | High |  |  |  | The Balancing Authority failed to maintain Regulating Reserve that can be controlled by AGC to meet Control Performance Standard. |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-005-0.2b | 315 | R3. | 4102 | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority providing Regulation Service failed to ensure adequate metering, communications, and control equipment was provided. |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-005-0.2b | 315 | R4. | 4099 | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority providing Regulation Service failed to notify the Host Balancing Authority for whom it is controlling if it was unable to provide the service, as well as any Intermediate Balancing Authorities. |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-005-0.2b | 315 | R5. | 4106 | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority receiving Regulation Service failed to ensure that back-up plans were in place to provide replacement Regulation Service. |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R5. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
BAL-005-0.2b | 315 | R6. | 4103 | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | The Balancing Authority failed to notify the Reliability Coordinator within 30 minutes of its inability to calculate ACE. | The Balancing Authority failed to calculate ACE as specified in the requirement. |  | The Balancing Authority failed to notify the Reliability Coordinator within 30 minutes of its inability to calculate ACE and failed to use the ACE calculation specified in the requirement in its attempt to calculate ACE. |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R6. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
BAL-005-0.2b | 315 | R7. | 4104 | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority failed to operate AGC continuously when there were no adverse impacts OR if their AGC was inoperative the Balancing Authority failed to use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R7. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
BAL-005-0.2b | 315 | R8. | 4109 | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority failed to ensure that data acquisition for and calculation of ACE occurred at least every six seconds. |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R8. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
BAL-005-0.2b | 315 | R9. | 4114 | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low |  |  |  | The Balancing Authority failed to include all Interchanged Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R9. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
BAL-005-0.2b (British Columbia) | 666700000010019 | R1. | 666700000010441 | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [9 empty] | 2013-12-12 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
BAL-005-0.2b (British Columbia) | 666700000010019 | R10. | 666700000010442 | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | High |  |  |  | The Balancing Authority failed to include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | 2013-12-12 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 100000000
BAL-005-0.2b (British Columbia) | 666700000010019 | R11. | 666700000010443 | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority failed to include the effect of Ramp rates in the Scheduled Interchange values to calculate ACE. |  | 2013-12-12 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 110000000
BAL-005-0.2b (British Columbia) | 666700000010019 | R12. | 666700000010444 | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority failed to include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | 2013-12-12 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 120000000
BAL-005-0.2b (British Columbia) | 666700000010019 | R13. | 666700000010445 | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low |  |  |  | The Balancing Authority failed to perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment OR the Balancing Authority failed to adjust the component (e.g., Tie Line |  | 2013-12-12 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 130000000
BAL-005-0.2b (British Columbia) | 666700000010019 | R14. | 666700000010446 | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | N/A | The responsible entity did not provide its operating personnel with real-time values for one of the following: ACE, Interconnection frequency or Net Actual Interchange. | The responsible entity did not provide its operating personnel with real-time values for two of the following: ACE, Interconnection frequency or Net Actual Interchange. | The responsible entity did not provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. OR The respo |  | 2013-12-12 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 140000000
BAL-005-0.2b (British Columbia) | 666700000010019 | R15. | 666700000010447 | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low |  |  | The Balancing Authority failed to periodically test backup power supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power sup | The Balancing Authority failed to provide adequate and reliable backup power supplies to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | 2013-12-12 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 150000000
BAL-005-0.2b (British Columbia) | 666700000010019 | R16. | 666700000010448 | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | The Balancing Authority failed to collect coincident data to the greatest practical extent. |  | The Balancing Authority failed to flag missing or bad data for operator display and archival purposes. | The Balancing Authority failed to sample data at least at the same periodicity with which ACE is calculated. |  | 2013-12-12 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 160000000
BAL-005-0.2b (British Columbia) | 666700000010019 | R17. | 666700000010449 | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See Standard for Values |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority failed to at least annually check and calibrate its time error and frequency devices against a common reference. |  | 2013-12-12 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 170000000
BAL-005-0.2b (British Columbia) | 666700000010019 | R2. | 666700000010450 | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. (Retirement approved by FERC effective January 21, 2014.) |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | High |  |  |  | The Balancing Authority failed to maintain Regulating Reserve that can be controlled by AGC to meet Control Performance Standard. |  | 2013-12-12 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 20000000
BAL-005-0.2b (British Columbia) | 666700000010019 | R3. | 666700000010451 | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority providing Regulation Service failed to ensure adequate metering, communications, and control equipment was provided. |  | 2013-12-12 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 30000000
BAL-005-0.2b (British Columbia) | 666700000010019 | R4. | 666700000010452 | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority providing Regulation Service failed to notify the Host Balancing Authority for whom it is controlling if it was unable to provide the service, as well as any Intermediate Balancing Authorities. |  | 2013-12-12 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 40000000
BAL-005-0.2b (British Columbia) | 666700000010019 | R5. | 666700000010453 | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority receiving Regulation Service failed to ensure that back-up plans were in place to provide replacement Regulation Service. |  | 2013-12-12 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 50000000
BAL-005-0.2b (British Columbia) | 666700000010019 | R6. | 666700000010454 | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | The Balancing Authority failed to notify the Reliability Coordinator within 30 minutes of its inability to calculate ACE. | The Balancing Authority failed to calculate ACE as specified in the requirement. |  | The Balancing Authority failed to notify the Reliability Coordinator within 30 minutes of its inability to calculate ACE and failed to use the ACE calculation specified in the requirement in its attempt to calculate ACE. |  | 2013-12-12 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 60000000
BAL-005-0.2b (British Columbia) | 666700000010019 | R7. | 666700000010455 | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority failed to operate AGC continuously when there were no adverse impacts OR if their AGC was inoperative the Balancing Authority failed to use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | 2013-12-12 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 70000000
BAL-005-0.2b (British Columbia) | 666700000010019 | R8. | 666700000010456 | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority failed to ensure that data acquisition for and calculation of ACE occurred at least every six seconds. |  | 2013-12-12 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 80000000
BAL-005-0.2b (British Columbia) | 666700000010019 | R9. | 666700000010457 | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low |  |  |  | The Balancing Authority failed to include all Interchanged Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | 2013-12-12 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 90000000
BAL-005-0.2b (Manitoba) | 77660000000315 | R1. | 776600000004105 | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [9 empty] | 2016-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 10000000
BAL-005-0.2b (Manitoba) | 77660000000315 | R10. | 776600000004108 | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | High |  |  |  | The Balancing Authority failed to include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | 2016-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 100000000
BAL-005-0.2b (Manitoba) | 77660000000315 | R11. | 776600000004110 | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority failed to include the effect of Ramp rates in the Scheduled Interchange values to calculate ACE. |  | 2016-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 110000000
BAL-005-0.2b (Manitoba) | 77660000000315 | R12. | 776600000004111 | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority failed to include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | 2016-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 120000000
BAL-005-0.2b (Manitoba) | 77660000000315 | R13. | 776600000004107 | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low |  |  |  | The Balancing Authority failed to perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment OR the Balancing Authority failed to adjust the component (e.g., Tie Line |  | 2016-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 130000000
BAL-005-0.2b (Manitoba) | 77660000000315 | R14. | 776600000004101 | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | N/A | The responsible entity did not provide its operating personnel with real-time values for one of the following: ACE, Interconnection frequency or Net Actual Interchange. | The responsible entity did not provide its operating personnel with real-time values for two of the following: ACE, Interconnection frequency or Net Actual Interchange. | The responsible entity did not provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. OR The respo |  | 2016-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 140000000
BAL-005-0.2b (Manitoba) | 77660000000315 | R15. | 776600000004113 | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low |  |  | The Balancing Authority failed to periodically test backup power supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power sup | The Balancing Authority failed to provide adequate and reliable backup power supplies to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | 2016-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 150000000
BAL-005-0.2b (Manitoba) | 77660000000315 | R16. | 776600000004115 | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | The Balancing Authority failed to collect coincident data to the greatest practical extent. |  | The Balancing Authority failed to flag missing or bad data for operator display and archival purposes. | The Balancing Authority failed to sample data at least at the same periodicity with which ACE is calculated. |  | 2016-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 160000000
BAL-005-0.2b (Manitoba) | 77660000000315 | R17. | 776600000004112 | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See Standard for Values |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority failed to at least annually check and calibrate its time error and frequency devices against a common reference. |  | 2016-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 170000000
BAL-005-0.2b (Manitoba) | 77660000000315 | R2. | 776600000004100 | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. (Retirement approved by FERC effective January 21, 2014.) |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | High |  |  |  | The Balancing Authority failed to maintain Regulating Reserve that can be controlled by AGC to meet Control Performance Standard. |  | 2016-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 20000000
BAL-005-0.2b (Manitoba) | 77660000000315 | R3. | 776600000004102 | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority providing Regulation Service failed to ensure adequate metering, communications, and control equipment was provided. |  | 2016-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 30000000
BAL-005-0.2b (Manitoba) | 77660000000315 | R4. | 776600000004099 | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority providing Regulation Service failed to notify the Host Balancing Authority for whom it is controlling if it was unable to provide the service, as well as any Intermediate Balancing Authorities. |  | 2016-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 40000000
BAL-005-0.2b (Manitoba) | 77660000000315 | R5. | 776600000004106 | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority receiving Regulation Service failed to ensure that back-up plans were in place to provide replacement Regulation Service. |  | 2016-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 50000000
BAL-005-0.2b (Manitoba) | 77660000000315 | R6. | 776600000004103 | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | The Balancing Authority failed to notify the Reliability Coordinator within 30 minutes of its inability to calculate ACE. | The Balancing Authority failed to calculate ACE as specified in the requirement. |  | The Balancing Authority failed to notify the Reliability Coordinator within 30 minutes of its inability to calculate ACE and failed to use the ACE calculation specified in the requirement in its attempt to calculate ACE. |  | 2016-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 60000000
BAL-005-0.2b (Manitoba) | 77660000000315 | R7. | 776600000004104 | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority failed to operate AGC continuously when there were no adverse impacts OR if their AGC was inoperative the Balancing Authority failed to use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | 2016-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 70000000
BAL-005-0.2b (Manitoba) | 77660000000315 | R8. | 776600000004109 | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority failed to ensure that data acquisition for and calculation of ACE occurred at least every six seconds. |  | 2016-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 80000000
BAL-005-0.2b (Manitoba) | 77660000000315 | R9. | 776600000004114 | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low |  |  |  | The Balancing Authority failed to include all Interchanged Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | 2016-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 90000000
BAL-005-0.2b (Ontario) | 79780000315 | R1. | 79780004105 | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  | GOP, LSE, TOP | [5 empty] | GOP |  | LSE | [10 empty] | TOP | [9 empty] | 2012-09-13 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-005-0.2b (Ontario) | 79780000315 | R10. | 79780004108 | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA | BA | [21 empty] | High |  |  |  | The Balancing Authority failed to include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | 2012-09-13 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 100000000
BAL-005-0.2b (Ontario) | 79780000315 | R11. | 79780004110 | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority failed to include the effect of Ramp rates in the Scheduled Interchange values to calculate ACE. |  | 2012-09-13 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 110000000
BAL-005-0.2b (Ontario) | 79780000315 | R12. | 79780004111 | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority failed to include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | 2012-09-13 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 120000000
BAL-005-0.2b (Ontario) | 79780000315 | R13. | 79780004107 | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority failed to perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment OR the Balancing Authority failed to adjust the component (e.g., Tie Line |  | 2012-09-13 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 130000000
BAL-005-0.2b (Ontario) | 79780000315 | R14. | 79780004101 | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  | BA | BA | [21 empty] | Low | N/A | The responsible entity did not provide its operating personnel with real-time values for one of the following: ACE, Interconnection frequency or Net Actual Interchange. | The responsible entity did not provide its operating personnel with real-time values for two of the following: ACE, Interconnection frequency or Net Actual Interchange. | The responsible entity did not provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. OR The respo |  | 2012-09-13 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 140000000
BAL-005-0.2b (Ontario) | 79780000315 | R15. | 79780004113 | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | BA | BA | [21 empty] | Low |  |  | The Balancing Authority failed to periodically test backup power supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power sup | The Balancing Authority failed to provide adequate and reliable backup power supplies to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | 2012-09-13 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 150000000
BAL-005-0.2b (Ontario) | 79780000315 | R16. | 79780004115 | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  | BA | BA | [21 empty] | Medium | The Balancing Authority failed to collect coincident data to the greatest practical extent. |  | The Balancing Authority failed to flag missing or bad data for operator display and archival purposes. | The Balancing Authority failed to sample data at least at the same periodicity with which ACE is calculated. |  | 2012-09-13 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 160000000
BAL-005-0.2b (Ontario) | 79780000315 | R17. | 79780004112 | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See Standard for Values |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority failed to at least annually check and calibrate its time error and frequency devices against a common reference. |  | 2012-09-13 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 170000000
BAL-005-0.2b (Ontario) | 79780000315 | R2. | 79780004100 | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. |  | BA | BA | [21 empty] | High |  |  |  | The Balancing Authority failed to maintain Regulating Reserve that can be controlled by AGC to meet Control Performance Standard. |  | 2012-09-13 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-005-0.2b (Ontario) | 79780000315 | R3. | 79780004102 | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority providing Regulation Service failed to ensure adequate metering, communications, and control equipment was provided. |  | 2012-09-13 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-005-0.2b (Ontario) | 79780000315 | R4. | 79780004099 | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority providing Regulation Service failed to notify the Host Balancing Authority for whom it is controlling if it was unable to provide the service, as well as any Intermediate Balancing Authorities. |  | 2012-09-13 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-005-0.2b (Ontario) | 79780000315 | R5. | 79780004106 | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority receiving Regulation Service failed to ensure that back-up plans were in place to provide replacement Regulation Service. |  | 2012-09-13 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 50000000
BAL-005-0.2b (Ontario) | 79780000315 | R6. | 79780004103 | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  | BA | BA | [21 empty] | Medium | The Balancing Authority failed to notify the Reliability Coordinator within 30 minutes of its inability to calculate ACE. | The Balancing Authority failed to calculate ACE as specified in the requirement. |  | The Balancing Authority failed to notify the Reliability Coordinator within 30 minutes of its inability to calculate ACE and failed to use the ACE calculation specified in the requirement in its attempt to calculate ACE. |  | 2012-09-13 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 60000000
BAL-005-0.2b (Ontario) | 79780000315 | R7. | 79780004104 | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority failed to operate AGC continuously when there were no adverse impacts OR if their AGC was inoperative the Balancing Authority failed to use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | 2012-09-13 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 70000000
BAL-005-0.2b (Ontario) | 79780000315 | R8. | 79780004109 | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority failed to ensure that data acquisition for and calculation of ACE occurred at least every six seconds. |  | 2012-09-13 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 80000000
BAL-005-0.2b (Ontario) | 79780000315 | R9. | 79780004114 | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority failed to include all Interchanged Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | 2012-09-13 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 90000000
BAL-005-0.2b (Saskatchewan) | 83750000000315 | R1. | 837500000004105 | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [9 empty] | 2014-04-01 |  | 2018-12-31 |  |  |  | MRO-SK | [6 empty] | 10000000
BAL-005-0.2b (Saskatchewan) | 83750000000315 | R10. | 837500000004108 | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | High |  |  |  | The Balancing Authority failed to include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | 2014-04-01 |  | 2018-12-31 |  |  |  | MRO-SK | [6 empty] | 100000000
BAL-005-0.2b (Saskatchewan) | 83750000000315 | R11. | 837500000004110 | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority failed to include the effect of Ramp rates in the Scheduled Interchange values to calculate ACE. |  | 2014-04-01 |  | 2018-12-31 |  |  |  | MRO-SK | [6 empty] | 110000000
BAL-005-0.2b (Saskatchewan) | 83750000000315 | R12. | 837500000004111 | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority failed to include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | 2014-04-01 |  | 2018-12-31 |  |  |  | MRO-SK | [6 empty] | 120000000
BAL-005-0.2b (Saskatchewan) | 83750000000315 | R13. | 837500000004107 | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low |  |  |  | The Balancing Authority failed to perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment OR the Balancing Authority failed to adjust the component (e.g., Tie Line |  | 2014-04-01 |  | 2018-12-31 |  |  |  | MRO-SK | [6 empty] | 130000000
BAL-005-0.2b (Saskatchewan) | 83750000000315 | R14. | 837500000004101 | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | N/A | The responsible entity did not provide its operating personnel with real-time values for one of the following: ACE, Interconnection frequency or Net Actual Interchange. | The responsible entity did not provide its operating personnel with real-time values for two of the following: ACE, Interconnection frequency or Net Actual Interchange. | The responsible entity did not provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. OR The respo |  | 2014-04-01 |  | 2018-12-31 |  |  |  | MRO-SK | [6 empty] | 140000000
BAL-005-0.2b (Saskatchewan) | 83750000000315 | R15. | 837500000004113 | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low |  |  | The Balancing Authority failed to periodically test backup power supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power sup | The Balancing Authority failed to provide adequate and reliable backup power supplies to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | 2014-04-01 |  | 2018-12-31 |  |  |  | MRO-SK | [6 empty] | 150000000
BAL-005-0.2b (Saskatchewan) | 83750000000315 | R16. | 837500000004115 | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | The Balancing Authority failed to collect coincident data to the greatest practical extent. |  | The Balancing Authority failed to flag missing or bad data for operator display and archival purposes. | The Balancing Authority failed to sample data at least at the same periodicity with which ACE is calculated. |  | 2014-04-01 |  | 2018-12-31 |  |  |  | MRO-SK | [6 empty] | 160000000
BAL-005-0.2b (Saskatchewan) | 83750000000315 | R17. | 837500000004112 | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See Standard for Values |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority failed to at least annually check and calibrate its time error and frequency devices against a common reference. |  | 2014-04-01 |  | 2018-12-31 |  |  |  | MRO-SK | [6 empty] | 170000000
BAL-005-0.2b (Saskatchewan) | 83750000000315 | R2. | 837500000004100 | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. (Retirement approved by FERC effective January 21, 2014.) |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | High |  |  |  | The Balancing Authority failed to maintain Regulating Reserve that can be controlled by AGC to meet Control Performance Standard. |  | 2014-04-01 |  | 2018-12-31 |  |  |  | MRO-SK | [6 empty] | 20000000
BAL-005-0.2b (Saskatchewan) | 83750000000315 | R3. | 837500000004102 | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority providing Regulation Service failed to ensure adequate metering, communications, and control equipment was provided. |  | 2014-04-01 |  | 2018-12-31 |  |  |  | MRO-SK | [6 empty] | 30000000
BAL-005-0.2b (Saskatchewan) | 83750000000315 | R4. | 837500000004099 | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority providing Regulation Service failed to notify the Host Balancing Authority for whom it is controlling if it was unable to provide the service, as well as any Intermediate Balancing Authorities. |  | 2014-04-01 |  | 2018-12-31 |  |  |  | MRO-SK | [6 empty] | 40000000
BAL-005-0.2b (Saskatchewan) | 83750000000315 | R5. | 837500000004106 | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority receiving Regulation Service failed to ensure that back-up plans were in place to provide replacement Regulation Service. |  | 2014-04-01 |  | 2018-12-31 |  |  |  | MRO-SK | [6 empty] | 50000000
BAL-005-0.2b (Saskatchewan) | 83750000000315 | R6. | 837500000004103 | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | The Balancing Authority failed to notify the Reliability Coordinator within 30 minutes of its inability to calculate ACE. | The Balancing Authority failed to calculate ACE as specified in the requirement. |  | The Balancing Authority failed to notify the Reliability Coordinator within 30 minutes of its inability to calculate ACE and failed to use the ACE calculation specified in the requirement in its attempt to calculate ACE. |  | 2014-04-01 |  | 2018-12-31 |  |  |  | MRO-SK | [6 empty] | 60000000
BAL-005-0.2b (Saskatchewan) | 83750000000315 | R7. | 837500000004104 | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority failed to operate AGC continuously when there were no adverse impacts OR if their AGC was inoperative the Balancing Authority failed to use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | 2014-04-01 |  | 2018-12-31 |  |  |  | MRO-SK | [6 empty] | 70000000
BAL-005-0.2b (Saskatchewan) | 83750000000315 | R8. | 837500000004109 | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium |  |  |  | The Balancing Authority failed to ensure that data acquisition for and calculation of ACE occurred at least every six seconds. |  | 2014-04-01 |  | 2018-12-31 |  |  |  | MRO-SK | [6 empty] | 80000000
BAL-005-0.2b (Saskatchewan) | 83750000000315 | R9. | 837500000004114 | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low |  |  |  | The Balancing Authority failed to include all Interchanged Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | 2014-04-01 |  | 2018-12-31 |  |  |  | MRO-SK | [6 empty] | 90000000
BAL-005-0a | 279 | R1. | 3684 | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [11 empty] | 2008-04-15 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-005-0a | 279 | R10. | 3687 | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | High | [7 empty] | 2008-04-15 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 100000000
BAL-005-0a | 279 | R11. | 3689 | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [7 empty] | 2008-04-15 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 110000000
BAL-005-0a | 279 | R12. | 3690 | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [7 empty] | 2008-04-15 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 120000000
BAL-005-0a | 279 | R13. | 3686 | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [7 empty] | 2008-04-15 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 130000000
BAL-005-0a | 279 | R14. | 3680 | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [7 empty] | 2008-04-15 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 140000000
BAL-005-0a | 279 | R15. | 3692 | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [7 empty] | 2008-04-15 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 150000000
BAL-005-0a | 279 | R16. | 3694 | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [7 empty] | 2008-04-15 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 160000000
BAL-005-0a | 279 | R17. | 3691 | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See standard for formula. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [7 empty] | 2008-04-15 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 170000000
BAL-005-0a | 279 | R2. | 3679 | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | High | [7 empty] | 2008-04-15 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-005-0a | 279 | R3. | 3681 | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [7 empty] | 2008-04-15 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-005-0a | 279 | R4. | 3678 | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [7 empty] | 2008-04-15 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-005-0a | 279 | R5. | 3685 | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [7 empty] | 2008-04-15 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
BAL-005-0a | 279 | R6. | 3682 | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [7 empty] | 2008-04-15 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
BAL-005-0a | 279 | R7. | 3683 | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [7 empty] | 2008-04-15 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
BAL-005-0a | 279 | R8. | 3688 | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [7 empty] | 2008-04-15 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
BAL-005-0a | 279 | R9. | 3693 | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [7 empty] | 2008-04-15 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
BAL-005-0a (Ontario) | 79780000279 | R1. | 79780003684 | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  | GOP, LSE, TOP | [5 empty] | GOP |  | LSE | [10 empty] | TOP |  |  |  |  | N/A | N/A | N/A | N/A |  |  |  | 2008-04-15 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-005-0a (Ontario) | 79780000279 | R10. | 79780003687 | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA | BA | [21 empty] | High | N/A | N/A | N/A | The Balancing Authority failed to include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  |  |  | 2008-04-15 |  |  |  | NPCC-ON | [6 empty] | 100000000
BAL-005-0a (Ontario) | 79780000279 | R11. | 79780003689 | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  | BA | BA | [21 empty] | Medium | N/A | N/A | N/A | The Balancing Authority failed to include the effect of Ramp rates in the Scheduled Interchange values to calculate ACE. |  |  |  | 2008-04-15 |  |  |  | NPCC-ON | [6 empty] | 110000000
BAL-005-0a (Ontario) | 79780000279 | R12. | 79780003690 | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | BA | BA | [21 empty] | Medium | N/A | N/A | N/A | The Balancing Authority failed to include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  |  |  | 2008-04-15 |  |  |  | NPCC-ON | [6 empty] | 120000000
BAL-005-0a (Ontario) | 79780000279 | R13. | 79780003686 | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  | BA | BA | [21 empty] | Low | N/A | N/A | N/A | The Balancing Authority failed to perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment OR the Balancing Authority failed to adjust the component (e.g., Tie Line |  |  |  | 2008-04-15 |  |  |  | NPCC-ON | [6 empty] | 130000000
BAL-005-0a (Ontario) | 79780000279 | R14. | 79780003680 | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  | BA | BA | [21 empty] | Low | N/A | N/A | N/A | The Balancing Authority failed to provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. |  |  |  | 2008-04-15 |  |  |  | NPCC-ON | [6 empty] | 140000000
BAL-005-0a (Ontario) | 79780000279 | R15. | 79780003692 | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | BA | BA | [21 empty] | Low | N/A | N/A | The Balancing Authority failed to periodically test backup power supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power sup | The Balancing Authority failed to provide adequate and reliable backup power supplies to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  |  |  | 2008-04-15 |  |  |  | NPCC-ON | [6 empty] | 150000000
BAL-005-0a (Ontario) | 79780000279 | R16. | 79780003694 | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  | BA | BA | [21 empty] | Medium | The Balancing Authority failed to collect coincident data to the greatest practical extent. | N/A | The Balancing Authority failed to flag missing or bad data for operator display and archival purposes. | The Balancing Authority failed to sample data at least at the same periodicity with which ACE is calculated. |  |  |  | 2008-04-15 |  |  |  | NPCC-ON | [6 empty] | 160000000
BAL-005-0a (Ontario) | 79780000279 | R17. | 79780003691 | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See standard for formula. |  | BA | BA | [21 empty] | Medium | N/A | N/A | N/A | The Balancing Authority failed to at least annually check and calibrate its time error and frequency devices against a common reference. |  |  |  | 2008-04-15 |  |  |  | NPCC-ON | [6 empty] | 170000000
BAL-005-0a (Ontario) | 79780000279 | R2. | 79780003679 | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. |  | BA | BA | [21 empty] | High | N/A | N/A | N/A | The Balancing Authority failed to maintain Regulating Reserve that can be controlled by AGC to meet Control Performance Standard. |  |  |  | 2008-04-15 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-005-0a (Ontario) | 79780000279 | R3. | 79780003681 | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  | BA | BA | [21 empty] | Medium | N/A | N/A | N/A | The Balancing Authority providing Regulation Service failed to ensure adequate metering, communications, and control equipment was provided. |  |  |  | 2008-04-15 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-005-0a (Ontario) | 79780000279 | R4. | 79780003678 | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  | BA | BA | [21 empty] | Medium | N/A | N/A | N/A | The Balancing Authority providing Regulation Service failed to notify the Host Balancing Authority for whom it is controlling if it was unable to provide the service, as well as any Intermediate Balancing Authorities. |  |  |  | 2008-04-15 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-005-0a (Ontario) | 79780000279 | R5. | 79780003685 | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  | BA | BA | [21 empty] | Medium | N/A | N/A | N/A | The Balancing Authority receiving Regulation Service failed to ensure that back-up plans were in place to provide replacement Regulation Service. |  |  |  | 2008-04-15 |  |  |  | NPCC-ON | [6 empty] | 50000000
BAL-005-0a (Ontario) | 79780000279 | R6. | 79780003682 | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  | BA | BA | [21 empty] | Medium | The Balancing Authority failed to notify the Reliability Coordinator within 30 minutes of its inability to calculate ACE. | The Balancing Authority failed to calculate ACE as specified in the requirement. | N/A | The Balancing Authority failed to notify the Reliability Coordinator within 30 minutes of its inability to calculate ACE and failed to use the ACE calculation specified in the requirement in its attempt to calculate ACE. |  |  |  | 2008-04-15 |  |  |  | NPCC-ON | [6 empty] | 60000000
BAL-005-0a (Ontario) | 79780000279 | R7. | 79780003683 | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | BA | BA | [21 empty] | Medium | N/A | N/A | N/A | The Balancing Authority failed to operate AGC continuously when there were no adverse impacts OR if their AGC was inoperative the Balancing Authority failed to use manual control to adjust generation to maintain the Net Scheduled Interchange. |  |  |  | 2008-04-15 |  |  |  | NPCC-ON | [6 empty] | 70000000
BAL-005-0a (Ontario) | 79780000279 | R8. | 79780003688 | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  | BA | BA | [21 empty] | Medium | N/A | N/A | N/A | The Balancing Authority failed to ensure that data acquisition for and calculation of ACE occurred at least every six seconds. |  |  |  | 2008-04-15 |  |  |  | NPCC-ON | [6 empty] | 80000000
BAL-005-0a (Ontario) | 79780000279 | R9. | 79780003693 | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA | BA | [21 empty] | Low | N/A | N/A | N/A | The Balancing Authority failed to include all Interchanged Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  |  |  | 2008-04-15 |  |  |  | NPCC-ON | [6 empty] | 90000000
BAL-005-0b | 17 | R1. | 186 | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [9 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-005-0b | 17 | R10. | 190 | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | High | [5 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R10. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 100000000
BAL-005-0b | 17 | R11. | 191 | Balancing Authorities shall include the effect of Ramp Rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R11. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 110000000
BAL-005-0b | 17 | R12. | 192 | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R12. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 120000000
BAL-005-0b | 17 | R13. | 196 | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R13. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 130000000
BAL-005-0b | 17 | R14. | 197 | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R14. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 140000000
BAL-005-0b | 17 | R15. | 198 | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R15. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 150000000
BAL-005-0b | 17 | R16. | 199 | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R16. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 160000000
BAL-005-0b | 17 | R17. | 200 | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See Standard for Values |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 170000000
BAL-005-0b | 17 | R2. | 201 | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  | Real-Time Operations | High | [5 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-005-0b | 17 | R3. | 202 | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  | Real-Time Operations | Medium | [5 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-005-0b | 17 | R4. | 203 | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  | Real-Time Operations | Medium | [5 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-005-0b | 17 | R5. | 204 | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  | Real-Time Operations | Medium | [5 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R5. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
BAL-005-0b | 17 | R6. | 205 | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  | Real-Time Operations | Medium | [5 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R6. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
BAL-005-0b | 17 | R7. | 206 | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  | Operations Assessment | Medium | [5 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R7. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
BAL-005-0b | 17 | R8. | 207 | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  | Same-Day Operations | Medium | [5 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R8. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
BAL-005-0b | 17 | R9. | 209 | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  | Operations Planning | Low | [5 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R9. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
BAL-005-0b (British Columbia) | 666700000010020 | R1. | 666700000010458 | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [9 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 10000000
BAL-005-0b (British Columbia) | 666700000010020 | R10. | 666700000010459 | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | High | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 100000000
BAL-005-0b (British Columbia) | 666700000010020 | R11. | 666700000010460 | Balancing Authorities shall include the effect of Ramp Rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 110000000
BAL-005-0b (British Columbia) | 666700000010020 | R12. | 666700000010461 | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 120000000
BAL-005-0b (British Columbia) | 666700000010020 | R13. | 666700000010462 | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 130000000
BAL-005-0b (British Columbia) | 666700000010020 | R14. | 666700000010463 | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 140000000
BAL-005-0b (British Columbia) | 666700000010020 | R15. | 666700000010464 | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 150000000
BAL-005-0b (British Columbia) | 666700000010020 | R16. | 666700000010465 | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 160000000
BAL-005-0b (British Columbia) | 666700000010020 | R17. | 666700000010466 | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See Standard for Values |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 170000000
BAL-005-0b (British Columbia) | 666700000010020 | R2. | 666700000010467 | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  | Real-Time Operations | High | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 20000000
BAL-005-0b (British Columbia) | 666700000010020 | R3. | 666700000010468 | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  | Real-Time Operations | Medium | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 30000000
BAL-005-0b (British Columbia) | 666700000010020 | R4. | 666700000010469 | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  | Real-Time Operations | Medium | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 40000000
BAL-005-0b (British Columbia) | 666700000010020 | R5. | 666700000010470 | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  | Real-Time Operations | Medium | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 50000000
BAL-005-0b (British Columbia) | 666700000010020 | R6. | 666700000010471 | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  | Real-Time Operations | Medium | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 60000000
BAL-005-0b (British Columbia) | 666700000010020 | R7. | 666700000010472 | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  | Operations Assessment | Medium | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 70000000
BAL-005-0b (British Columbia) | 666700000010020 | R8. | 666700000010473 | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  | Same-Day Operations | Medium | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 80000000
BAL-005-0b (British Columbia) | 666700000010020 | R9. | 666700000010474 | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  | Operations Planning | Low | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 90000000
BAL-005-0b (Ontario) | 79780000017 | R1. | 79780000186 | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  | GOP, LSE, TOP | [5 empty] | GOP |  | LSE | [10 empty] | TOP | [9 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-005-0b (Ontario) | 79780000017 | R10. | 79780000190 | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA | BA | [21 empty] | High |  |  |  | The Balancing Authority failed to include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 100000000
BAL-005-0b (Ontario) | 79780000017 | R11. | 79780000191 | Balancing Authorities shall include the effect of Ramp Rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority failed to include the effect of Ramp rates in the Scheduled Interchange values to calculate ACE. |  | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 110000000
BAL-005-0b (Ontario) | 79780000017 | R12. | 79780000192 | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority failed to include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 120000000
BAL-005-0b (Ontario) | 79780000017 | R13. | 79780000196 | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority failed to perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment OR the Balancing Authority failed to adjust the component (e.g., Tie Line |  | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 130000000
BAL-005-0b (Ontario) | 79780000017 | R14. | 79780000197 | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority failed to provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. |  | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 140000000
BAL-005-0b (Ontario) | 79780000017 | R15. | 79780000198 | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | BA | BA | [21 empty] | Low |  |  | The Balancing Authority failed to periodically test backup power supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power sup | The Balancing Authority failed to provide adequate and reliable backup power supplies to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 150000000
BAL-005-0b (Ontario) | 79780000017 | R16. | 79780000199 | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  | BA | BA | [21 empty] | Medium | The Balancing Authority failed to collect coincident data to the greatest practical extent. |  | The Balancing Authority failed to flag missing or bad data for operator display and archival purposes. | The Balancing Authority failed to sample data at least at the same periodicity with which ACE is calculated. |  | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 160000000
BAL-005-0b (Ontario) | 79780000017 | R17. | 79780000200 | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See Standard for Values |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority failed to at least annually check and calibrate its time error and frequency devices against a common reference. |  | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 170000000
BAL-005-0b (Ontario) | 79780000017 | R2. | 79780000201 | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. |  | BA | BA | [20 empty] | Real-Time Operations | High |  |  |  | The Balancing Authority failed to maintain Regulating Reserve that can be controlled by AGC to meet Control Performance Standard. | M2. Each Balancing Authority will have dated records to show when it was unable to calculate Reporting ACE for more than 30 consecutive minutes and that it notified its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. Such evidence may include, but is not limited to, dated voice recordings, operating logs, or other communication documentation. | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-005-0b (Ontario) | 79780000017 | R3. | 79780000202 | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  | BA | BA | [20 empty] | Real-Time Operations | Medium |  |  |  | The Balancing Authority providing Regulation Service failed to ensure adequate metering, communications, and control equipment was provided. | M3. The Balancing Authority shall have evidence such as dated documents or other evidence in hard copy or electronic format showing the frequency metering equipment used for the calculation of Reporting ACE had a minimum availability of 99.95% for each calendar year and had a minimum accuracy of 0.001 Hz to demonstrate compliance with Requirement R3. | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-005-0b (Ontario) | 79780000017 | R4. | 79780000203 | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  | BA | BA | [20 empty] | Real-Time Operations | Medium |  |  |  | The Balancing Authority providing Regulation Service failed to notify the Host Balancing Authority for whom it is controlling if it was unable to provide the service, as well as any Intermediate Balancing Authorities. |  | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-005-0b (Ontario) | 79780000017 | R5. | 79780000204 | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  | BA | BA | [20 empty] | Real-Time Operations | Medium |  |  |  | The Balancing Authority receiving Regulation Service failed to ensure that back-up plans were in place to provide replacement Regulation Service. |  | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 50000000
BAL-005-0b (Ontario) | 79780000017 | R6. | 79780000205 | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority failed to notify the Reliability Coordinator within 30 minutes of its inability to calculate ACE. | The Balancing Authority failed to calculate ACE as specified in the requirement. |  | The Balancing Authority failed to notify the Reliability Coordinator within 30 minutes of its inability to calculate ACE and failed to use the ACE calculation specified in the requirement in its attempt to calculate ACE. | M4. Each Balancing Authority Area shall have evidence such as a graphical display or dated alarm log that provides indication of data validity for the real-time Reporting ACE based on both the calculated result and all of the associated inputs therein. | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 60000000
BAL-005-0b (Ontario) | 79780000017 | R7. | 79780000206 | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | BA | BA | [20 empty] | Operations Assessment | Medium |  |  |  | The Balancing Authority failed to operate AGC continuously when there were no adverse impacts OR if their AGC was inoperative the Balancing Authority failed to use manual control to adjust generation to maintain the Net Scheduled Interchange. | M5.. Each Balancing Authority will have dated documentation demonstrating that the system necessary to calculate Reporting ACE has a minimum availability of 99.5% for each calendar year. Acceptable evidence may include historical data, dated archive files; or data from other databases, spreadsheets, or displays that demonstrate compliance. | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 70000000
BAL-005-0b (Ontario) | 79780000017 | R8. | 79780000207 | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  | BA | BA | [20 empty] | Same-Day Operations | Medium |  |  |  | The Balancing Authority failed to ensure that data acquisition for and calculation of ACE occurred at least every six seconds. | M6. Each Balancing Authority shall have a current Operating Process meeting the provisions of Requirement R6 and evidence to show that the process was implemented, such as dated communications or incorporation in System Operator task verification. | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 80000000
BAL-005-0b (Ontario) | 79780000017 | R9. | 79780000209 | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA | BA | [20 empty] | Operations Planning | Low |  |  |  | The Balancing Authority failed to include all Interchanged Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 90000000
BAL-005-0 (Manitoba) | 7766000000015 | R1. | 77660000000136 | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | N/A | N/A | N/A | N/A |  | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
BAL-005-0 (Manitoba) | 7766000000015 | R10. | 77660000000140 | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | High | [5 empty] | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 100000000
BAL-005-0 (Manitoba) | 7766000000015 | R11. | 77660000000141 | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 110000000
BAL-005-0 (Manitoba) | 7766000000015 | R12. | 77660000000142 | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 120000000
BAL-005-0 (Manitoba) | 7766000000015 | R13. | 77660000000146 | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 130000000
BAL-005-0 (Manitoba) | 7766000000015 | R14. | 77660000000147 | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 140000000
BAL-005-0 (Manitoba) | 7766000000015 | R15. | 77660000000148 | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 150000000
BAL-005-0 (Manitoba) | 7766000000015 | R16. | 77660000000149 | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 160000000
BAL-005-0 (Manitoba) | 7766000000015 | R17. | 77660000000150 | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See standard for formula. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 170000000
BAL-005-0 (Manitoba) | 7766000000015 | R2. | 77660000000151 | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
BAL-005-0 (Manitoba) | 7766000000015 | R3. | 77660000000152 | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
BAL-005-0 (Manitoba) | 7766000000015 | R4. | 77660000000153 | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 40000000
BAL-005-0 (Manitoba) | 7766000000015 | R5. | 77660000000154 | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 50000000
BAL-005-0 (Manitoba) | 7766000000015 | R6. | 77660000000155 | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 60000000
BAL-005-0 (Manitoba) | 7766000000015 | R7. | 77660000000156 | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 70000000
BAL-005-0 (Manitoba) | 7766000000015 | R8. | 77660000000157 | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 80000000
BAL-005-0 (Manitoba) | 7766000000015 | R9. | 77660000000159 | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | Low | [5 empty] | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 90000000
BAL-005-0 (Ontario) | 79780000015 | R1. | 79780000136 | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  | GOP, LSE, TOP | [5 empty] | GOP |  | LSE | [10 empty] | TOP |  |  |  | Medium | N/A | N/A | N/A | N/A |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-005-0 (Ontario) | 79780000015 | R10. | 79780000140 | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA | BA | [21 empty] | High | N/A | N/A | N/A | The Balancing Authority failed to include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 100000000
BAL-005-0 (Ontario) | 79780000015 | R11. | 79780000141 | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  | BA | BA | [21 empty] | Medium | N/A | N/A | N/A | The Balancing Authority failed to include the effect of Ramp rates in the Scheduled Interchange values to calculate ACE. |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 110000000
BAL-005-0 (Ontario) | 79780000015 | R12. | 79780000142 | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | BA | BA | [21 empty] | Medium | N/A | N/A | N/A | The Balancing Authority failed to include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 120000000
BAL-005-0 (Ontario) | 79780000015 | R13. | 79780000146 | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  | BA | BA | [21 empty] | Low | N/A | N/A | N/A | The Balancing Authority failed to perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment OR the Balancing Authority failed to adjust the component (e.g., Tie Line |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 130000000
BAL-005-0 (Ontario) | 79780000015 | R14. | 79780000147 | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  | BA | BA | [21 empty] | Low | N/A | N/A | N/A | The Balancing Authority failed to provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 140000000
BAL-005-0 (Ontario) | 79780000015 | R15. | 79780000148 | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | BA | BA | [21 empty] | Low | N/A | N/A | The Balancing Authority failed to periodically test backup power supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power sup | The Balancing Authority failed to provide adequate and reliable backup power supplies to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 150000000
BAL-005-0 (Ontario) | 79780000015 | R16. | 79780000149 | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  | BA | BA | [21 empty] | Medium | The Balancing Authority failed to collect coincident data to the greatest practical extent. | N/A | The Balancing Authority failed to flag missing or bad data for operator display and archival purposes. | The Balancing Authority failed to sample data at least at the same periodicity with which ACE is calculated. |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 160000000
BAL-005-0 (Ontario) | 79780000015 | R17. | 79780000150 | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See standard for formula. |  | BA | BA | [21 empty] | Low | N/A | N/A | N/A | The Balancing Authority failed to at least annually check and calibrate its time error and frequency devices against a common reference. |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 170000000
BAL-005-0 (Ontario) | 79780000015 | R2. | 79780000151 | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. |  | BA | BA | [21 empty] | Low | N/A | N/A | N/A | The Balancing Authority failed to maintain Regulating Reserve that can be controlled by AGC to meet Control Performance Standard. |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-005-0 (Ontario) | 79780000015 | R3. | 79780000152 | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  | BA | BA | [21 empty] | Medium | N/A | N/A | N/A | The Balancing Authority providing Regulation Service failed to ensure adequate metering, communications, and control equipment was provided. |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-005-0 (Ontario) | 79780000015 | R4. | 79780000153 | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  | BA | BA | [21 empty] | Medium | N/A | N/A | N/A | The Balancing Authority providing Regulation Service failed to notify the Host Balancing Authority for whom it is controlling if it was unable to provide the service, as well as any Intermediate Balancing Authorities. |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-005-0 (Ontario) | 79780000015 | R5. | 79780000154 | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  | BA | BA | [21 empty] | Medium | N/A | N/A | N/A | The Balancing Authority receiving Regulation Service failed to ensure that back-up plans were in place to provide replacement Regulation Service. |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 50000000
BAL-005-0 (Ontario) | 79780000015 | R6. | 79780000155 | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  | BA | BA | [21 empty] | Medium | The Balancing Authority failed to notify the Reliability Coordinator within 30 minutes of its inability to calculate ACE. | The Balancing Authority failed to calculate ACE as specified in the requirement. | N/A | The Balancing Authority failed to notify the Reliability Coordinator within 30 minutes of its inability to calculate ACE and failed to use the ACE calculation specified in the requirement in its attempt to calculate ACE. |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 60000000
BAL-005-0 (Ontario) | 79780000015 | R7. | 79780000156 | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | BA | BA | [21 empty] | Low | N/A | N/A | N/A | The Balancing Authority failed to operate AGC continuously when there were no adverse impacts OR if their AGC was inoperative the Balancing Authority failed to use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 70000000
BAL-005-0 (Ontario) | 79780000015 | R8. | 79780000157 | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  | BA | BA | [21 empty] | Medium | N/A | N/A | N/A | The Balancing Authority failed to ensure that data acquisition for and calculation of ACE occurred at least every six seconds. |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 80000000
BAL-005-0 (Ontario) | 79780000015 | R9. | 79780000159 | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA | BA | [21 empty] | Low | N/A | N/A | N/A | The Balancing Authority failed to include all Interchanged Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 90000000
BAL-005-1 | 544 | R1. | 7614 | The Balancing Authority shall use a design scan rate of no more than six seconds in acquiring data necessary to calculate Reporting ACE. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | Balancing Authority was using a design scan rate of greater than six seconds to acquire the data necessary to calculate Reporting ACE. | M1. Each Balancing Authority will have dated documentation demonstrating that the data necessary to calculate Reporting ACE was designed to be scanned at a rate of no more than six seconds. Acceptable evidence may include historical data, dated archive files; or data from other databases, spreadsheets, or displays that demonstrate compliance. | 2019-01-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-005-1 | 544 | R2. | 7615 | A Balancing Authority that is unable to calculate Reporting ACE for more than 30-consecutive minutes shall notify its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority failed to notify its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE but notified its Reliability Coordinator in less than or equal to 50 minutes from the beginning of the inability to calculate Reporting ACE. | The Balancing Authority failed to notify its Reliability Coordinator within 50 minutes of the beginning of an inability to calculate Reporting ACE but notified its Reliability Coordinator in less than or equal to 55 minutes from the beginning of an inability to calculate Reporting ACE. | The Balancing Authority failed to notify its Reliability Coordinator within 55 minutes of the beginning of an inability to calculate Reporting ACE but notified its Reliability Coordinator in less than or equal to 60 minutes from the beginning of an inability to calculate Reporting ACE. | The Balancing Authority failed to notify its Reliability Coordinator within 60 minutes of the beginning of an inability to calculate Reporting ACE. | M2. Each Balancing Authority will have dated records to show when it was unable to calculate Reporting ACE for more than 30 consecutive minutes and that it notified its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. Such evidence may include, but is not limited to, dated voice recordings, operating logs, or other communication documentation. | 2019-01-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-005-1 | 544 | R3. | 7616 | Each Balancing Authority shall use frequency metering equipment for the calculation of Reporting ACE: |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.95% of the calendar year but was available greater than or equal to 99.94 % of the calendar year. | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.94% of the calendar year but was available greater than or equal to 99.93 % of the calendar year. | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.93% of the calendar year but was available greater than or equal to 99.92 % of the calendar year. | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.92% of the calendar year OR The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE failed to have a minimum accuracy of 0.001 Hz. | M3. The Balancing Authority shall have evidence such as dated documents or other evidence in hard copy or electronic format showing the frequency metering equipment used for the calculation of Reporting ACE had a minimum availability of 99.95% for each calendar year and had a minimum accuracy of 0.001 Hz to demonstrate compliance with Requirement R3. | 2019-01-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-005-1 | 544 | R4. | 7617 | The Balancing Authority shall make available to the operator information associated with Reporting ACE including, but not limited to, quality flags indicating missing or invalid data. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Balancing Authority failed to make available information indicating missing or invalid data associated with Reporting ACE to its operators. | M4. Each Balancing Authority Area shall have evidence such as a graphical display or dated alarm log that provides indication of data validity for the real-time Reporting ACE based on both the calculated result and all of the associated inputs therein. | 2019-01-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-005-1 | 544 | R5. | 7618 | Each Balancing Authority’s system used to calculate Reporting ACE shall be available a minimum of 99.5% of each calendar year. |  | BA | BA | [20 empty] | Operations Assessment | Medium | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.5% of the calendar year but was available greater than or equal to 99.4 % of the calendar year. | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.4% of the calendar year but was available greater than or equal to 99.3 % of the calendar year. | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.3% of the calendar year but was available greater than or equal to 99.2 % of the calendar year. | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.2% of the calendar year. | M5.. Each Balancing Authority will have dated documentation demonstrating that the system necessary to calculate Reporting ACE has a minimum availability of 99.5% for each calendar year. Acceptable evidence may include historical data, dated archive files; or data from other databases, spreadsheets, or displays that demonstrate compliance. | 2019-01-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
BAL-005-1 | 544 | R6. | 7619 | Each Balancing Authority that is within a multiple Balancing Authority Interconnection shall implement an Operating Process to identify and mitigate errors affecting the accuracy of scan rate data used in the calculation of Reporting ACE for each Balancing Authority Area. |  | BA | BA | [20 empty] | Same-Day Operations | Medium | N/A | N/A | N/A | The Balancing Authority failed to implement an Operating Process to identify and mitigate errors affecting the scan-rate accuracy of data used in the calculation of Reporting ACE. | M6. Each Balancing Authority shall have a current Operating Process meeting the provisions of Requirement R6 and evidence to show that the process was implemented, such as dated communications or incorporation in System Operator task verification. | 2019-01-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
BAL-005-1 | 544 | R7. | 7620 | Each Balancing Authority shall ensure that each Tie-Line, Pseudo-Tie, and Dynamic Schedule with an Adjacent Balancing Authority is equipped with: |  | BA | BA | [20 empty] | Operations Planning | Medium | N/A | N/A | N/A | The Balancing Authority failed to use a common source for Tie-Lines, Pseudo-ties and Dynamic Schedules with its Adjacent Balancing Authorities OR The Balancing Authority failed to use a time synchronized common source for hourly megawatt hour values that are agreed-upon to aid in the identification and mitigation of errors. | M7. The Balancing Authority shall have dated evidence such as voice recordings or transcripts, operator logs, electronic communications, or other equivalent evidence that will be used to demonstrate a common source for the components used in the calculation of Reporting ACE with its Adjacent Balancing Authority. | 2019-01-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
BAL-005-1 (British Columbia) | 666700000010021 | R1. | 666700000010475 | The Balancing Authority shall use a design scan rate of no more than six seconds in acquiring data necessary to calculate Reporting ACE. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | Balancing Authority was using a design scan rate of greater than six seconds to acquire the data necessary to calculate Reporting ACE. | M1. Each Balancing Authority will have dated documentation demonstrating that the data necessary to calculate Reporting ACE was designed to be scanned at a rate of no more than six seconds. Acceptable evidence may include historical data, dated archive files; or data from other databases, spreadsheets, or displays that demonstrate compliance. | 2019-10-01 | [5 empty] | WECC-BC | [6 empty] | 10000000
BAL-005-1 (British Columbia) | 666700000010021 | R2. | 666700000010476 | A Balancing Authority that is unable to calculate Reporting ACE for more than 30-consecutive minutes shall notify its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority failed to notify its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE but notified its Reliability Coordinator in less than or equal to 50 minutes from the beginning of the inability to calculate Reporting ACE. | The Balancing Authority failed to notify its Reliability Coordinator within 50 minutes of the beginning of an inability to calculate Reporting ACE but notified its Reliability Coordinator in less than or equal to 55 minutes from the beginning of an inability to calculate Reporting ACE. | The Balancing Authority failed to notify its Reliability Coordinator within 55 minutes of the beginning of an inability to calculate Reporting ACE but notified its Reliability Coordinator in less than or equal to 60 minutes from the beginning of an inability to calculate Reporting ACE. | The Balancing Authority failed to notify its Reliability Coordinator within 60 minutes of the beginning of an inability to calculate Reporting ACE. | M2. Each Balancing Authority will have dated records to show when it was unable to calculate Reporting ACE for more than 30 consecutive minutes and that it notified its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. Such evidence may include, but is not limited to, dated voice recordings, operating logs, or other communication documentation. | 2019-10-01 | [5 empty] | WECC-BC | [6 empty] | 20000000
BAL-005-1 (British Columbia) | 666700000010021 | R3. | 666700000010477 | Each Balancing Authority shall use frequency metering equipment for the calculation of Reporting ACE: |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.95% of the calendar year but was available greater than or equal to 99.94 % of the calendar year. | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.94% of the calendar year but was available greater than or equal to 99.93 % of the calendar year. | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.93% of the calendar year but was available greater than or equal to 99.92 % of the calendar year. | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.92% of the calendar year OR The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE failed to have a minimum accuracy of 0.001 Hz. | M3. The Balancing Authority shall have evidence such as dated documents or other evidence in hard copy or electronic format showing the frequency metering equipment used for the calculation of Reporting ACE had a minimum availability of 99.95% for each calendar year and had a minimum accuracy of 0.001 Hz to demonstrate compliance with Requirement R3. | 2019-10-01 | [5 empty] | WECC-BC | [6 empty] | 30000000
BAL-005-1 (British Columbia) | 666700000010021 | R4. | 666700000010478 | The Balancing Authority shall make available to the operator information associated with Reporting ACE including, but not limited to, quality flags indicating missing or invalid data. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Balancing Authority failed to make available information indicating missing or invalid data associated with Reporting ACE to its operators. | M4. Each Balancing Authority Area shall have evidence such as a graphical display or dated alarm log that provides indication of data validity for the real-time Reporting ACE based on both the calculated result and all of the associated inputs therein. | 2019-10-01 | [5 empty] | WECC-BC | [6 empty] | 40000000
BAL-005-1 (British Columbia) | 666700000010021 | R5. | 666700000010479 | Each Balancing Authority’s system used to calculate Reporting ACE shall be available a minimum of 99.5% of each calendar year. |  | BA | BA | [20 empty] | Operations Assessment | Medium | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.5% of the calendar year but was available greater than or equal to 99.4 % of the calendar year. | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.4% of the calendar year but was available greater than or equal to 99.3 % of the calendar year. | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.3% of the calendar year but was available greater than or equal to 99.2 % of the calendar year. | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.2% of the calendar year. | M5.. Each Balancing Authority will have dated documentation demonstrating that the system necessary to calculate Reporting ACE has a minimum availability of 99.5% for each calendar year. Acceptable evidence may include historical data, dated archive files; or data from other databases, spreadsheets, or displays that demonstrate compliance. | 2019-10-01 | [5 empty] | WECC-BC | [6 empty] | 50000000
BAL-005-1 (British Columbia) | 666700000010021 | R6. | 666700000010480 | Each Balancing Authority that is within a multiple Balancing Authority Interconnection shall implement an Operating Process to identify and mitigate errors affecting the accuracy of scan rate data used in the calculation of Reporting ACE for each Balancing Authority Area. |  | BA | BA | [20 empty] | Same-Day Operations | Medium | N/A | N/A | N/A | The Balancing Authority failed to implement an Operating Process to identify and mitigate errors affecting the scan-rate accuracy of data used in the calculation of Reporting ACE. | M6. Each Balancing Authority shall have a current Operating Process meeting the provisions of Requirement R6 and evidence to show that the process was implemented, such as dated communications or incorporation in System Operator task verification. | 2019-10-01 | [5 empty] | WECC-BC | [6 empty] | 60000000
BAL-005-1 (British Columbia) | 666700000010021 | R7. | 666700000010481 | Each Balancing Authority shall ensure that each Tie-Line, Pseudo-Tie, and Dynamic Schedule with an Adjacent Balancing Authority is equipped with: |  | BA | BA | [20 empty] | Operations Planning | Medium | N/A | N/A | N/A | The Balancing Authority failed to use a common source for Tie-Lines, Pseudo-ties and Dynamic Schedules with its Adjacent Balancing Authorities OR The Balancing Authority failed to use a time synchronized common source for hourly megawatt hour values that are agreed-upon to aid in the identification and mitigation of errors. | M7. The Balancing Authority shall have dated evidence such as voice recordings or transcripts, operator logs, electronic communications, or other equivalent evidence that will be used to demonstrate a common source for the components used in the calculation of Reporting ACE with its Adjacent Balancing Authority. | 2019-10-01 | [5 empty] | WECC-BC | [6 empty] | 70000000
BAL-005-1 (Manitoba) | 77660000000544 | R1. | 776600000007614 | The Balancing Authority shall use a design scan rate of no more than six seconds in acquiring data necessary to calculate Reporting ACE. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | Balancing Authority was using a design scan rate of greater than six seconds to acquire the data necessary to calculate Reporting ACE. | M1. Each Balancing Authority will have dated documentation demonstrating that the data necessary to calculate Reporting ACE was designed to be scanned at a rate of no more than six seconds. Acceptable evidence may include historical data, dated archive files; or data from other databases, spreadsheets, or displays that demonstrate compliance. | 2021-01-01 | [5 empty] | MRO-MB | [6 empty] | 10000000
BAL-005-1 (Manitoba) | 77660000000544 | R2. | 776600000007615 | A Balancing Authority that is unable to calculate Reporting ACE for more than 30-consecutive minutes shall notify its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority failed to notify its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE but notified its Reliability Coordinator in less than or equal to 50 minutes from the beginning of the inability to calculate Reporting ACE. | The Balancing Authority failed to notify its Reliability Coordinator within 50 minutes of the beginning of an inability to calculate Reporting ACE but notified its Reliability Coordinator in less than or equal to 55 minutes from the beginning of an inability to calculate Reporting ACE. | The Balancing Authority failed to notify its Reliability Coordinator within 55 minutes of the beginning of an inability to calculate Reporting ACE but notified its Reliability Coordinator in less than or equal to 60 minutes from the beginning of an inability to calculate Reporting ACE. | The Balancing Authority failed to notify its Reliability Coordinator within 60 minutes of the beginning of an inability to calculate Reporting ACE. | M2. Each Balancing Authority will have dated records to show when it was unable to calculate Reporting ACE for more than 30 consecutive minutes and that it notified its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. Such evidence may include, but is not limited to, dated voice recordings, operating logs, or other communication documentation. | 2021-01-01 | [5 empty] | MRO-MB | [6 empty] | 20000000
BAL-005-1 (Manitoba) | 77660000000544 | R3. | 776600000007616 | Each Balancing Authority shall use frequency metering equipment for the calculation of Reporting ACE: |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.95% of the calendar year but was available greater than or equal to 99.94 % of the calendar year. | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.94% of the calendar year but was available greater than or equal to 99.93 % of the calendar year. | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.93% of the calendar year but was available greater than or equal to 99.92 % of the calendar year. | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.92% of the calendar year OR The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE failed to have a minimum accuracy of 0.001 Hz. | M3. The Balancing Authority shall have evidence such as dated documents or other evidence in hard copy or electronic format showing the frequency metering equipment used for the calculation of Reporting ACE had a minimum availability of 99.95% for each calendar year and had a minimum accuracy of 0.001 Hz to demonstrate compliance with Requirement R3. | 2021-01-01 | [5 empty] | MRO-MB | [6 empty] | 30000000
BAL-005-1 (Manitoba) | 77660000000544 | R4. | 776600000007617 | The Balancing Authority shall make available to the operator information associated with Reporting ACE including, but not limited to, quality flags indicating missing or invalid data. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Balancing Authority failed to make available information indicating missing or invalid data associated with Reporting ACE to its operators. | M4. Each Balancing Authority Area shall have evidence such as a graphical display or dated alarm log that provides indication of data validity for the real-time Reporting ACE based on both the calculated result and all of the associated inputs therein. | 2021-01-01 | [5 empty] | MRO-MB | [6 empty] | 40000000
BAL-005-1 (Manitoba) | 77660000000544 | R5. | 776600000007618 | Each Balancing Authority’s system used to calculate Reporting ACE shall be available a minimum of 99.5% of each calendar year. |  | BA | BA | [20 empty] | Operations Assessment | Medium | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.5% of the calendar year but was available greater than or equal to 99.4 % of the calendar year. | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.4% of the calendar year but was available greater than or equal to 99.3 % of the calendar year. | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.3% of the calendar year but was available greater than or equal to 99.2 % of the calendar year. | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.2% of the calendar year. | M5.. Each Balancing Authority will have dated documentation demonstrating that the system necessary to calculate Reporting ACE has a minimum availability of 99.5% for each calendar year. Acceptable evidence may include historical data, dated archive files; or data from other databases, spreadsheets, or displays that demonstrate compliance. | 2021-01-01 | [5 empty] | MRO-MB | [6 empty] | 50000000
BAL-005-1 (Manitoba) | 77660000000544 | R6. | 776600000007619 | Each Balancing Authority that is within a multiple Balancing Authority Interconnection shall implement an Operating Process to identify and mitigate errors affecting the accuracy of scan rate data used in the calculation of Reporting ACE for each Balancing Authority Area. |  | BA | BA | [20 empty] | Same-Day Operations | Medium | N/A | N/A | N/A | The Balancing Authority failed to implement an Operating Process to identify and mitigate errors affecting the scan-rate accuracy of data used in the calculation of Reporting ACE. | M6. Each Balancing Authority shall have a current Operating Process meeting the provisions of Requirement R6 and evidence to show that the process was implemented, such as dated communications or incorporation in System Operator task verification. | 2021-01-01 | [5 empty] | MRO-MB | [6 empty] | 60000000
BAL-005-1 (Manitoba) | 77660000000544 | R7. | 776600000007620 | Each Balancing Authority shall ensure that each Tie-Line, Pseudo-Tie, and Dynamic Schedule with an Adjacent Balancing Authority is equipped with: |  | BA | BA | [20 empty] | Operations Planning | Medium | N/A | N/A | N/A | The Balancing Authority failed to use a common source for Tie-Lines, Pseudo-ties and Dynamic Schedules with its Adjacent Balancing Authorities OR The Balancing Authority failed to use a time synchronized common source for hourly megawatt hour values that are agreed-upon to aid in the identification and mitigation of errors. | M7. The Balancing Authority shall have dated evidence such as voice recordings or transcripts, operator logs, electronic communications, or other equivalent evidence that will be used to demonstrate a common source for the components used in the calculation of Reporting ACE with its Adjacent Balancing Authority. | 2021-01-01 | [5 empty] | MRO-MB | [6 empty] | 70000000
BAL-005-1 (Nova Scotia) | 78830000000544 | R1. | 788300000007614 | The Balancing Authority shall use a design scan rate of no more than six seconds in acquiring data necessary to calculate Reporting ACE. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | Balancing Authority was using a design scan rate of greater than six seconds to acquire the data necessary to calculate Reporting ACE. | M1. Each Balancing Authority will have dated documentation demonstrating that the data necessary to calculate Reporting ACE was designed to be scanned at a rate of no more than six seconds. Acceptable evidence may include historical data, dated archive files; or data from other databases, spreadsheets, or displays that demonstrate compliance. | 2019-04-01 | [5 empty] | NPCC-NS | [6 empty] | 10000000
BAL-005-1 (Nova Scotia) | 78830000000544 | R2. | 788300000007615 | A Balancing Authority that is unable to calculate Reporting ACE for more than 30-consecutive minutes shall notify its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority failed to notify its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE but notified its Reliability Coordinator in less than or equal to 50 minutes from the beginning of the inability to calculate Reporting ACE. | The Balancing Authority failed to notify its Reliability Coordinator within 50 minutes of the beginning of an inability to calculate Reporting ACE but notified its Reliability Coordinator in less than or equal to 55 minutes from the beginning of an inability to calculate Reporting ACE. | The Balancing Authority failed to notify its Reliability Coordinator within 55 minutes of the beginning of an inability to calculate Reporting ACE but notified its Reliability Coordinator in less than or equal to 60 minutes from the beginning of an inability to calculate Reporting ACE. | The Balancing Authority failed to notify its Reliability Coordinator within 60 minutes of the beginning of an inability to calculate Reporting ACE. | M2. Each Balancing Authority will have dated records to show when it was unable to calculate Reporting ACE for more than 30 consecutive minutes and that it notified its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. Such evidence may include, but is not limited to, dated voice recordings, operating logs, or other communication documentation. | 2019-04-01 | [5 empty] | NPCC-NS | [6 empty] | 20000000
BAL-005-1 (Nova Scotia) | 78830000000544 | R3. | 788300000007616 | Each Balancing Authority shall use frequency metering equipment for the calculation of Reporting ACE: |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.95% of the calendar year but was available greater than or equal to 99.94 % of the calendar year. | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.94% of the calendar year but was available greater than or equal to 99.93 % of the calendar year. | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.93% of the calendar year but was available greater than or equal to 99.92 % of the calendar year. | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.92% of the calendar year OR The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE failed to have a minimum accuracy of 0.001 Hz. | M3. The Balancing Authority shall have evidence such as dated documents or other evidence in hard copy or electronic format showing the frequency metering equipment used for the calculation of Reporting ACE had a minimum availability of 99.95% for each calendar year and had a minimum accuracy of 0.001 Hz to demonstrate compliance with Requirement R3. | 2019-04-01 | [5 empty] | NPCC-NS | [6 empty] | 30000000
BAL-005-1 (Nova Scotia) | 78830000000544 | R4. | 788300000007617 | The Balancing Authority shall make available to the operator information associated with Reporting ACE including, but not limited to, quality flags indicating missing or invalid data. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Balancing Authority failed to make available information indicating missing or invalid data associated with Reporting ACE to its operators. | M4. Each Balancing Authority Area shall have evidence such as a graphical display or dated alarm log that provides indication of data validity for the real-time Reporting ACE based on both the calculated result and all of the associated inputs therein. | 2019-04-01 | [5 empty] | NPCC-NS | [6 empty] | 40000000
BAL-005-1 (Nova Scotia) | 78830000000544 | R5. | 788300000007618 | Each Balancing Authority’s system used to calculate Reporting ACE shall be available a minimum of 99.5% of each calendar year. |  | BA | BA | [20 empty] | Operations Assessment | Medium | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.5% of the calendar year but was available greater than or equal to 99.4 % of the calendar year. | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.4% of the calendar year but was available greater than or equal to 99.3 % of the calendar year. | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.3% of the calendar year but was available greater than or equal to 99.2 % of the calendar year. | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.2% of the calendar year. | M5.. Each Balancing Authority will have dated documentation demonstrating that the system necessary to calculate Reporting ACE has a minimum availability of 99.5% for each calendar year. Acceptable evidence may include historical data, dated archive files; or data from other databases, spreadsheets, or displays that demonstrate compliance. | 2019-04-01 | [5 empty] | NPCC-NS | [6 empty] | 50000000
BAL-005-1 (Nova Scotia) | 78830000000544 | R6. | 788300000007619 | Each Balancing Authority that is within a multiple Balancing Authority Interconnection shall implement an Operating Process to identify and mitigate errors affecting the accuracy of scan rate data used in the calculation of Reporting ACE for each Balancing Authority Area. |  | BA | BA | [20 empty] | Same-Day Operations | Medium | N/A | N/A | N/A | The Balancing Authority failed to implement an Operating Process to identify and mitigate errors affecting the scan-rate accuracy of data used in the calculation of Reporting ACE. | M6. Each Balancing Authority shall have a current Operating Process meeting the provisions of Requirement R6 and evidence to show that the process was implemented, such as dated communications or incorporation in System Operator task verification. | 2019-04-01 | [5 empty] | NPCC-NS | [6 empty] | 60000000
BAL-005-1 (Nova Scotia) | 78830000000544 | R7. | 788300000007620 | Each Balancing Authority shall ensure that each Tie-Line, Pseudo-Tie, and Dynamic Schedule with an Adjacent Balancing Authority is equipped with: |  | BA | BA | [20 empty] | Operations Planning | Medium | N/A | N/A | N/A | The Balancing Authority failed to use a common source for Tie-Lines, Pseudo-ties and Dynamic Schedules with its Adjacent Balancing Authorities OR The Balancing Authority failed to use a time synchronized common source for hourly megawatt hour values that are agreed-upon to aid in the identification and mitigation of errors. | M7. The Balancing Authority shall have dated evidence such as voice recordings or transcripts, operator logs, electronic communications, or other equivalent evidence that will be used to demonstrate a common source for the components used in the calculation of Reporting ACE with its Adjacent Balancing Authority. | 2019-04-01 | [5 empty] | NPCC-NS | [6 empty] | 70000000
BAL-005-1 (Ontario) | 79780000544 | R1. | 79780007614 | The Balancing Authority shall use a design scan rate of no more than six seconds in acquiring data necessary to calculate Reporting ACE. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | Balancing Authority was using a design scan rate of greater than six seconds to acquire the data necessary to calculate Reporting ACE. | M1. Each Balancing Authority will have dated documentation demonstrating that the data necessary to calculate Reporting ACE was designed to be scanned at a rate of no more than six seconds. Acceptable evidence may include historical data, dated archive files; or data from other databases, spreadsheets, or displays that demonstrate compliance. | 2019-01-01 | [5 empty] | NPCC-ON | [6 empty] | 10000000
BAL-005-1 (Ontario) | 79780000544 | R2. | 79780007615 | A Balancing Authority that is unable to calculate Reporting ACE for more than 30-consecutive minutes shall notify its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority failed to notify its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE but notified its Reliability Coordinator in less than or equal to 50 minutes from the beginning of the inability to calculate Reporting ACE. | The Balancing Authority failed to notify its Reliability Coordinator within 50 minutes of the beginning of an inability to calculate Reporting ACE but notified its Reliability Coordinator in less than or equal to 55 minutes from the beginning of an inability to calculate Reporting ACE. | The Balancing Authority failed to notify its Reliability Coordinator within 55 minutes of the beginning of an inability to calculate Reporting ACE but notified its Reliability Coordinator in less than or equal to 60 minutes from the beginning of an inability to calculate Reporting ACE. | The Balancing Authority failed to notify its Reliability Coordinator within 60 minutes of the beginning of an inability to calculate Reporting ACE. | M2. Each Balancing Authority will have dated records to show when it was unable to calculate Reporting ACE for more than 30 consecutive minutes and that it notified its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. Such evidence may include, but is not limited to, dated voice recordings, operating logs, or other communication documentation. | 2019-01-01 | [5 empty] | NPCC-ON | [6 empty] | 20000000
BAL-005-1 (Ontario) | 79780000544 | R3. | 79780007616 | Each Balancing Authority shall use frequency metering equipment for the calculation of Reporting ACE: 3.1. that is available a minimum of 99.95% for each calendar year; and, 3.2. with a minimum accuracy of 0.001 Hz. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.95% of the calendar year but was available greater than or equal to 99.94 % of the calendar year. | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.94% of the calendar year but was available greater than or equal to 99.93 % of the calendar year. | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.93% of the calendar year but was available greater than or equal to 99.92 % of the calendar year. | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.92% of the calendar year OR The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE failed to have a minimum accuracy of 0.001 Hz. | M3. The Balancing Authority shall have evidence such as dated documents or other evidence in hard copy or electronic format showing the frequency metering equipment used for the calculation of Reporting ACE had a minimum availability of 99.95% for each calendar year and had a minimum accuracy of 0.001 Hz to demonstrate compliance with Requirement R3. | 2019-01-01 | [5 empty] | NPCC-ON | [6 empty] | 30000000
BAL-005-1 (Ontario) | 79780000544 | R4. | 79780007617 | The Balancing Authority shall make available to the operator information associated with Reporting ACE including, but not limited to, quality flags indicating missing or invalid data. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Balancing Authority failed to make available information indicating missing or invalid data associated with Reporting ACE to its operators. | M4. Each Balancing Authority Area shall have evidence such as a graphical display or dated alarm log that provides indication of data validity for the real-time Reporting ACE based on both the calculated result and all of the associated inputs therein. | 2019-01-01 | [5 empty] | NPCC-ON | [6 empty] | 40000000
BAL-005-1 (Ontario) | 79780000544 | R5. | 79780007618 | Each Balancing Authority’s system used to calculate Reporting ACE shall be available a minimum of 99.5% of each calendar year. |  | BA | BA | [20 empty] | Operations Assessment | Medium | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.5% of the calendar year but was available greater than or equal to 99.4 % of the calendar year. | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.4% of the calendar year but was available greater than or equal to 99.3 % of the calendar year. | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.3% of the calendar year but was available greater than or equal to 99.2 % of the calendar year. | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.2% of the calendar year. | M5.. Each Balancing Authority will have dated documentation demonstrating that the system necessary to calculate Reporting ACE has a minimum availability of 99.5% for each calendar year. Acceptable evidence may include historical data, dated archive files; or data from other databases, spreadsheets, or displays that demonstrate compliance. | 2019-01-01 | [5 empty] | NPCC-ON | [6 empty] | 50000000
BAL-005-1 (Ontario) | 79780000544 | R6. | 79780007619 | Each Balancing Authority that is within a multiple Balancing Authority Interconnection shall implement an Operating Process to identify and mitigate errors affecting the accuracy of scan rate data used in the calculation of Reporting ACE for each Balancing Authority Area. |  | BA | BA | [20 empty] | Same-Day Operations | Medium | N/A | N/A | N/A | The Balancing Authority failed to implement an Operating Process to identify and mitigate errors affecting the scan-rate accuracy of data used in the calculation of Reporting ACE. | M6. Each Balancing Authority shall have a current Operating Process meeting the provisions of Requirement R6 and evidence to show that the process was implemented, such as dated communications or incorporation in System Operator task verification. | 2019-01-01 | [5 empty] | NPCC-ON | [6 empty] | 60000000
BAL-005-1 (Ontario) | 79780000544 | R7. | 79780007620 | Each Balancing Authority shall ensure that each Tie-Line, Pseudo-Tie, and Dynamic Schedule with an Adjacent Balancing Authority is equipped with: |  | BA | BA | [20 empty] | Operations Planning | Medium | N/A | N/A | N/A | The Balancing Authority failed to use a common source for Tie-Lines, Pseudo-ties and Dynamic Schedules with its Adjacent Balancing Authorities OR The Balancing Authority failed to use a time synchronized common source for hourly megawatt hour values that are agreed-upon to aid in the identification and mitigation of errors. | M7. The Balancing Authority shall have dated evidence such as voice recordings or transcripts, operator logs, electronic communications, or other equivalent evidence that will be used to demonstrate a common source for the components used in the calculation of Reporting ACE with its Adjacent Balancing Authority. | 2019-01-01 | [5 empty] | NPCC-ON | [6 empty] | 70000000
BAL-005-1 (Saskatchewan) | 83750000000544 | R1. | 837500000007614 | The Balancing Authority shall use a design scan rate of no more than six seconds in acquiring data necessary to calculate Reporting ACE. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | Balancing Authority was using a design scan rate of greater than six seconds to acquire the data necessary to calculate Reporting ACE. | M1. Each Balancing Authority will have dated documentation demonstrating that the data necessary to calculate Reporting ACE was designed to be scanned at a rate of no more than six seconds. Acceptable evidence may include historical data, dated archive files; or data from other databases, spreadsheets, or displays that demonstrate compliance. | 2019-01-01 | [5 empty] | MRO-SK | [6 empty] | 10000000
BAL-005-1 (Saskatchewan) | 83750000000544 | R2. | 837500000007615 | A Balancing Authority that is unable to calculate Reporting ACE for more than 30-consecutive minutes shall notify its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority failed to notify its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE but notified its Reliability Coordinator in less than or equal to 50 minutes from the beginning of the inability to calculate Reporting ACE. | The Balancing Authority failed to notify its Reliability Coordinator within 50 minutes of the beginning of an inability to calculate Reporting ACE but notified its Reliability Coordinator in less than or equal to 55 minutes from the beginning of an inability to calculate Reporting ACE. | The Balancing Authority failed to notify its Reliability Coordinator within 55 minutes of the beginning of an inability to calculate Reporting ACE but notified its Reliability Coordinator in less than or equal to 60 minutes from the beginning of an inability to calculate Reporting ACE. | The Balancing Authority failed to notify its Reliability Coordinator within 60 minutes of the beginning of an inability to calculate Reporting ACE. | M2. Each Balancing Authority will have dated records to show when it was unable to calculate Reporting ACE for more than 30 consecutive minutes and that it notified its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. Such evidence may include, but is not limited to, dated voice recordings, operating logs, or other communication documentation. | 2019-01-01 | [5 empty] | MRO-SK | [6 empty] | 20000000
BAL-005-1 (Saskatchewan) | 83750000000544 | R3. | 837500000007616 | Each Balancing Authority shall use frequency metering equipment for the calculation of Reporting ACE: |  | BA | BA | [20 empty] | Real-Time Operations | Medium | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.95% of the calendar year but was available greater than or equal to 99.94 % of the calendar year. | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.94% of the calendar year but was available greater than or equal to 99.93 % of the calendar year. | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.93% of the calendar year but was available greater than or equal to 99.92 % of the calendar year. | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.92% of the calendar year OR The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE failed to have a minimum accuracy of 0.001 Hz. | M3. The Balancing Authority shall have evidence such as dated documents or other evidence in hard copy or electronic format showing the frequency metering equipment used for the calculation of Reporting ACE had a minimum availability of 99.95% for each calendar year and had a minimum accuracy of 0.001 Hz to demonstrate compliance with Requirement R3. | 2019-01-01 | [5 empty] | MRO-SK | [6 empty] | 30000000
BAL-005-1 (Saskatchewan) | 83750000000544 | R4. | 837500000007617 | The Balancing Authority shall make available to the operator information associated with Reporting ACE including, but not limited to, quality flags indicating missing or invalid data. |  | BA | BA | [20 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Balancing Authority failed to make available information indicating missing or invalid data associated with Reporting ACE to its operators. | M4. Each Balancing Authority Area shall have evidence such as a graphical display or dated alarm log that provides indication of data validity for the real-time Reporting ACE based on both the calculated result and all of the associated inputs therein. | 2019-01-01 | [5 empty] | MRO-SK | [6 empty] | 40000000
BAL-005-1 (Saskatchewan) | 83750000000544 | R5. | 837500000007618 | Each Balancing Authority’s system used to calculate Reporting ACE shall be available a minimum of 99.5% of each calendar year. |  | BA | BA | [20 empty] | Operations Assessment | Medium | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.5% of the calendar year but was available greater than or equal to 99.4 % of the calendar year. | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.4% of the calendar year but was available greater than or equal to 99.3 % of the calendar year. | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.3% of the calendar year but was available greater than or equal to 99.2 % of the calendar year. | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.2% of the calendar year. | M5.. Each Balancing Authority will have dated documentation demonstrating that the system necessary to calculate Reporting ACE has a minimum availability of 99.5% for each calendar year. Acceptable evidence may include historical data, dated archive files; or data from other databases, spreadsheets, or displays that demonstrate compliance. | 2019-01-01 | [5 empty] | MRO-SK | [6 empty] | 50000000
BAL-005-1 (Saskatchewan) | 83750000000544 | R6. | 837500000007619 | Each Balancing Authority that is within a multiple Balancing Authority Interconnection shall implement an Operating Process to identify and mitigate errors affecting the accuracy of scan rate data used in the calculation of Reporting ACE for each Balancing Authority Area. |  | BA | BA | [20 empty] | Same-Day Operations | Medium | N/A | N/A | N/A | The Balancing Authority failed to implement an Operating Process to identify and mitigate errors affecting the scan-rate accuracy of data used in the calculation of Reporting ACE. | M6. Each Balancing Authority shall have a current Operating Process meeting the provisions of Requirement R6 and evidence to show that the process was implemented, such as dated communications or incorporation in System Operator task verification. | 2019-01-01 | [5 empty] | MRO-SK | [6 empty] | 60000000
BAL-005-1 (Saskatchewan) | 83750000000544 | R7. | 837500000007620 | Each Balancing Authority shall ensure that each Tie-Line, Pseudo-Tie, and Dynamic Schedule with an Adjacent Balancing Authority is equipped with: |  | BA | BA | [20 empty] | Operations Planning | Medium | N/A | N/A | N/A | The Balancing Authority failed to use a common source for Tie-Lines, Pseudo-ties and Dynamic Schedules with its Adjacent Balancing Authorities OR The Balancing Authority failed to use a time synchronized common source for hourly megawatt hour values that are agreed-upon to aid in the identification and mitigation of errors. | M7. The Balancing Authority shall have dated evidence such as voice recordings or transcripts, operator logs, electronic communications, or other equivalent evidence that will be used to demonstrate a common source for the components used in the calculation of Reporting ACE with its Adjacent Balancing Authority. | 2019-01-01 | [5 empty] | MRO-SK | [6 empty] | 70000000
BAL-005-AB-1 (Alberta) | 656600000009005 | R1. | 656600000009083 | The ISO must use a design scan rate of no more than 9 seconds in acquiring data necessary to calculate reporting area control error. |  | ISO | [28 empty] | 2019-07-01 | [5 empty] | WECC-AB | [6 empty] | 10000000
BAL-005-AB-1 (Alberta) | 656600000009005 | R2. | 656600000009084 | Intentionally left blank. |  | ISO | [28 empty] | 2019-07-01 | [5 empty] | WECC-AB | [6 empty] | 20000000
BAL-005-AB-1 (Alberta) | 656600000009005 | R3. | 656600000009085 | The ISO must use frequency metering equipment for the calculation of reporting area control error: |  | ISO | [28 empty] | 2019-07-01 | [5 empty] | WECC-AB | [6 empty] | 30000000
BAL-005-AB-1 (Alberta) | 656600000009005 | R4. | 656600000009086 | The ISO must make available to its operating personnel information associated with reporting area control error including quality flags indicating missing or invalid data. |  | ISO | [28 empty] | 2019-07-01 | [5 empty] | WECC-AB | [6 empty] | 40000000
BAL-005-AB-1 (Alberta) | 656600000009005 | R5. | 656600000009087 | The ISO must ensure the system it uses to calculate reporting area control error is available a minimum of 99.5% of each calendar year. |  | ISO | [28 empty] | 2019-07-01 | [5 empty] | WECC-AB | [6 empty] | 50000000
BAL-005-AB-1 (Alberta) | 656600000009005 | R6. | 656600000009088 | The ISO must implement an operating process to identify and mitigate errors affecting the accuracy of scan rate data used in the calculation of reporting area control error for its balancing authority area. |  | ISO | [28 empty] | 2019-07-01 | [5 empty] | WECC-AB | [6 empty] | 60000000
BAL-005-AB-1 (Alberta) | 656600000009005 | R7. | 656600000009089 | The ISO must ensure that each interconnection, pseudo-tie, and dynamic schedule with an adjacent balancing authority is equipped with: |  | ISO | [28 empty] | 2019-07-01 | [5 empty] | WECC-AB | [6 empty] | 70000000
BAL-006-0 | 381 | R1. | 4794 | Each Balancing Authority shall calculate and record hourly Inadvertent Interchange. |  | BA | BA | [29 empty] | 2006-05-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-006-0 | 381 | R2. | 4795 | Each Balancing Authority shall include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. The Balancing Authority shall take into account interchange served by jointly owned generators. |  | BA | BA | [29 empty] | 2006-05-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-006-0 | 381 | R3. | 4796 | Each Balancing Authority shall ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | BA | BA | [29 empty] | 2006-05-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-006-0 | 381 | R4. | 4797 | Adjacent Balancing Authority Areas shall operate to a common Net Interchange Schedule and Actual Net Interchange value and shall record these hourly quantities, with like values but opposite sign. Each Balancing Authority shall compute its Inadvertent Interchange based on the following: |  | BA | BA | [29 empty] | 2006-05-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-006-0 | 381 | R5. | 4803 | Adjacent Balancing Authorities that cannot mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month shall, for the purposes of dispute resolution, submit a report to their respective Regional Reliability Organization Survey Contact. The report shall describe the nature and the cause of the dispute as well as a process for correcting the discrepancy. |  | BA | BA | [29 empty] | 2006-05-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
BAL-006-0 (Ontario) | 79780000381 | R1. | 79780004794 |  |  | BA | BA | [29 empty] | 2006-05-01 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-006-0 (Ontario) | 79780000381 | R2. | 79780004795 |  |  | BA | BA | [29 empty] | 2006-05-01 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-006-0 (Ontario) | 79780000381 | R3. | 79780004796 |  |  | BA | BA | [29 empty] | 2006-05-01 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-006-0 (Ontario) | 79780000381 | R4. | 79780004797 |  |  | BA | BA | [29 empty] | 2006-05-01 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-006-0 (Ontario) | 79780000381 | R5. | 79780004803 |  |  | BA | BA | [29 empty] | 2006-05-01 |  |  |  | NPCC-ON | [6 empty] | 50000000
BAL-006-1 | 18 | R1. | 211 | Each Balancing Authority shall calculate and record hourly Inadvertent Interchange. |  | BA | BA | [21 empty] | Low | [5 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-006-1 | 18 | R2. | 212 | Each Balancing Authority shall include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. The Balancing Authority shall take into account interchange served by jointly owned generators. |  | BA | BA | [21 empty] | Low |  |  | . |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-006-1 | 18 | R3. | 213 | Each Balancing Authority shall ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | BA | BA | [21 empty] | Low | [5 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-006-1 | 18 | R4. | 214 | Adjacent Balancing Authority Areas shall operate to a common Net Interchange Schedule and Actual Net Interchange value and shall record these hourly quantities, with like values but opposite sign. Each Balancing Authority shall compute its Inadvertent Interchange based on the following: |  | BA | BA | [21 empty] | Low | [5 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-006-1 | 18 | R5. | 220 | Adjacent Balancing Authorities that cannot mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month shall, for the purposes of dispute resolution, submit a report to their respective Regional Reliability Organization Survey Contact. The report shall describe the nature and the cause of the dispute as well as a process for correcting the discrepancy. |  | BA | BA | [20 empty] | Long-Term Planning | Low | [5 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
BAL-006-1.1 | 19 | R1. | 221 | Each Balancing Authority shall calculate and record hourly Inadvertent Interchange. |  | BA | BA | [20 empty] | Long-Term Planning | [6 empty] | 2009-05-13 |  | 2011-03-31 |  |  | BAL-006-1.1 R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-006-1.1 | 19 | R2. | 222 | Each Balancing Authority shall include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. The Balancing Authority shall take into account interchange served by jointly owned generators. |  | BA | BA | [20 empty] | Long-Term Planning | [6 empty] | 2009-05-13 |  | 2011-03-31 |  |  | BAL-006-1.1 R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-006-1.1 | 19 | R3. | 223 | Each Balancing Authority shall ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | BA | BA | [20 empty] | Long-Term Planning | [6 empty] | 2009-05-13 |  | 2011-03-31 |  |  | BAL-006-1.1 R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-006-1.1 | 19 | R4. | 224 | Adjacent Balancing Authority Areas shall operate to a common Net Interchange Schedule and Actual Net Interchange value and shall record these hourly quantities, with like values but opposite sign. Each Balancing Authority shall compute its Inadvertent Interchange based on the following: |  | BA | BA | [20 empty] | Long-Term Planning | [6 empty] | 2009-05-13 |  | 2011-03-31 |  |  | BAL-006-1.1 R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-006-1.1 | 19 | R5. | 230 | Adjacent Balancing Authorities that cannot mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month shall, for the purposes of dispute resolution, submit a report to their respective Regional Reliability Organization Survey Contact. The report shall describe the nature and the cause of the dispute as well as a process for correcting the discrepancy. |  | BA | BA | [20 empty] | Long-Term Planning | [6 empty] | 2009-05-13 |  | 2011-03-31 |  |  | BAL-006-1.1 R5. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
BAL-006-1.1 (British Columbia) | 666700000010023 | R1. | 666700000010487 | Each Balancing Authority shall calculate and record hourly Inadvertent Interchange. |  | BA | BA | [20 empty] | Long-Term Planning | [6 empty] | 2011-01-01 |  | 2013-04-14 |  |  |  | WECC-BC | [6 empty] | 10000000
BAL-006-1.1 (British Columbia) | 666700000010023 | R2. | 666700000010488 | Each Balancing Authority shall include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. The Balancing Authority shall take into account interchange served by jointly owned generators. |  | BA | BA | [20 empty] | Long-Term Planning | [6 empty] | 2011-01-01 |  | 2013-04-14 |  |  |  | WECC-BC | [6 empty] | 20000000
BAL-006-1.1 (British Columbia) | 666700000010023 | R3. | 666700000010489 | Each Balancing Authority shall ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | BA | BA | [20 empty] | Long-Term Planning | [6 empty] | 2011-01-01 |  | 2013-04-14 |  |  |  | WECC-BC | [6 empty] | 30000000
BAL-006-1.1 (British Columbia) | 666700000010023 | R4. | 666700000010490 | Adjacent Balancing Authority Areas shall operate to a common Net Interchange Schedule and Actual Net Interchange value and shall record these hourly quantities, with like values but opposite sign. Each Balancing Authority shall compute its Inadvertent Interchange based on the following: |  | BA | BA | [20 empty] | Long-Term Planning | [6 empty] | 2011-01-01 |  | 2013-04-14 |  |  |  | WECC-BC | [6 empty] | 40000000
BAL-006-1.1 (British Columbia) | 666700000010023 | R5. | 666700000010491 | Adjacent Balancing Authorities that cannot mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month shall, for the purposes of dispute resolution, submit a report to their respective Regional Reliability Organization Survey Contact. The report shall describe the nature and the cause of the dispute as well as a process for correcting the discrepancy. |  | BA | BA | [20 empty] | Long-Term Planning | [6 empty] | 2011-01-01 |  | 2013-04-14 |  |  |  | WECC-BC | [6 empty] | 50000000
BAL-006-1.1 (Ontario) | 79780000019 | R1. | 79780000221 | Each Balancing Authority shall calculate and record hourly Inadvertent Interchange. |  | BA | BA | [20 empty] | Long-Term Planning |  |  |  |  | Each Balancing Authority failed to calculate and record hourly Inadvertent Interchange. |  | 2009-05-13 |  | 2011-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-006-1.1 (Ontario) | 79780000019 | R2. | 79780000222 | Each Balancing Authority shall include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. The Balancing Authority shall take into account interchange served by jointly owned generators. |  | BA | BA | [20 empty] | Long-Term Planning |  |  |  | The Balancing Authority failed to include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. | The Balancing Authority failed to include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. |  | 2009-05-13 |  | 2011-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-006-1.1 (Ontario) | 79780000019 | R3. | 79780000223 | Each Balancing Authority shall ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | BA | BA | [20 empty] | Long-Term Planning |  |  |  |  | The Balancing Authority failed to ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | 2009-05-13 |  | 2011-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-006-1.1 (Ontario) | 79780000019 | R4. | 79780000224 | Adjacent Balancing Authority Areas shall operate to a common Net Interchange Schedule and Actual Net Interchange value and shall record these hourly quantities, with like values but opposite sign. Each Balancing Authority shall compute its Inadvertent Interchange based on the following: |  | BA | BA | [20 empty] | Long-Term Planning |  | The Balancing Authority failed to record Actual Net Interchange values that are equal but opposite in sign to its Adjacent Balancing Authorities. | The Balancing Authority failed to compute Inadvertent Interchange. | The Balancing Authority failed to operate to a common Net Interchange Schedule that is equal but opposite to its Adjacent Balancing Authorities. |  |  | 2009-05-13 |  | 2011-03-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-006-1.1 (Ontario) | 79780000019 | R5. | 79780000230 | Adjacent Balancing Authorities that cannot mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month shall, for the purposes of dispute resolution, submit a report to their respective Regional Reliability Organization Survey Contact. The report shall describe the nature and the cause of the dispute as well as a process for correcting the discrepancy. |  | BA | BA | [20 empty] | Long-Term Planning |  | Adjacent Balancing Authorities that could not mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities, submitted a report to their respective Regional Reliability Organizations Survey Contact describing the natu | Adjacent Balancing Authorities that could not mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month, failed to submit a report to their respective Regional Relia |  |  |  | 2009-05-13 |  | 2011-03-31 |  |  |  | NPCC-ON | [6 empty] | 50000000
BAL-006-1 (British Columbia) | 666700000010022 | R1. | 666700000010482 | Each Balancing Authority shall calculate and record hourly Inadvertent Interchange. |  | BA | BA | [21 empty] | Low | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 10000000
BAL-006-1 (British Columbia) | 666700000010022 | R2. | 666700000010483 | Each Balancing Authority shall include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. The Balancing Authority shall take into account interchange served by jointly owned generators. |  | BA | BA | [21 empty] | Low |  |  | . |  |  | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 20000000
BAL-006-1 (British Columbia) | 666700000010022 | R3. | 666700000010484 | Each Balancing Authority shall ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | BA | BA | [21 empty] | Low | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 30000000
BAL-006-1 (British Columbia) | 666700000010022 | R4. | 666700000010485 | Adjacent Balancing Authority Areas shall operate to a common Net Interchange Schedule and Actual Net Interchange value and shall record these hourly quantities, with like values but opposite sign. Each Balancing Authority shall compute its Inadvertent Interchange based on the following: |  | BA | BA | [21 empty] | Low | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 40000000
BAL-006-1 (British Columbia) | 666700000010022 | R5. | 666700000010486 | Adjacent Balancing Authorities that cannot mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month shall, for the purposes of dispute resolution, submit a report to their respective Regional Reliability Organization Survey Contact. The report shall describe the nature and the cause of the dispute as well as a process for correcting the discrepancy. |  | BA | BA | [20 empty] | Long-Term Planning | Low | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 50000000
BAL-006-1 (Ontario) | 79780000018 | R1. | 79780000211 | Each Balancing Authority shall calculate and record hourly Inadvertent Interchange. |  | BA | BA | [21 empty] | Low |  |  |  | Each Balancing Authority failed to calculate and record hourly Inadvertent Interchange. |  | 2007-06-18 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-006-1 (Ontario) | 79780000018 | R2. | 79780000212 | Each Balancing Authority shall include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. The Balancing Authority shall take into account interchange served by jointly owned generators. |  | BA | BA | [21 empty] | Low |  |  | The Balancing Authority failed to include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. | The Balancing Authority failed to include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. |  | 2007-06-18 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-006-1 (Ontario) | 79780000018 | R3. | 79780000213 | Each Balancing Authority shall ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority failed to ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | 2007-06-18 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-006-1 (Ontario) | 79780000018 | R4. | 79780000214 | Adjacent Balancing Authority Areas shall operate to a common Net Interchange Schedule and Actual Net Interchange value and shall record these hourly quantities, with like values but opposite sign. Each Balancing Authority shall compute its Inadvertent Interchange based on the following: |  | BA | BA | [21 empty] | Low | The Balancing Authority failed to record Actual Net Interchange values that are equal but opposite in sign to its Adjacent Balancing Authorities. | The Balancing Authority failed to compute Inadvertent Interchange. | The Balancing Authority failed to operate to a common Net Interchange Schedule that is equal but opposite to its Adjacent Balancing Authorities. |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-006-1 (Ontario) | 79780000018 | R5. | 79780000220 | Adjacent Balancing Authorities that cannot mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month shall, for the purposes of dispute resolution, submit a report to their respective Regional Reliability Organization Survey Contact. The report shall describe the nature and the cause of the dispute as well as a process for correcting the discrepancy. |  | BA | BA | [20 empty] | Long-Term Planning | Low | Adjacent Balancing Authorities that could not mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities, submitted a report to their respective Regional Reliability Organizations Survey Contact describing the natu | Adjacent Balancing Authorities that could not mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month, failed to submit a report to their respective Regional Relia |  |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 50000000
BAL-006-2 | 246 | R1. | 3203 | Each Balancing Authority shall calculate and record hourly Inadvertent Interchange. |  | BA | BA | [20 empty] | Long-Term Planning | Low | N/A | N/A | N/A | Each Balancing Authority failed to calculate and record hourly Inadvertent Interchange. |  | 2011-04-01 |  | 2018-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
BAL-006-2 | 246 | R2. | 3204 | Each Balancing Authority shall include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. The Balancing Authority shall take into account interchange served by jointly owned generators. |  | BA | BA | [20 empty] | Long-Term Planning | Low | N/A | N/A | The Balancing Authority failed to include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. OR Failed to take into account interchange served by jointly owned generators. | The Balancing Authority failed to include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. AND Failed to take into account interchange served by jointly owned generators. |  | 2011-04-01 |  | 2018-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
BAL-006-2 | 246 | R3. | 3205 | Each Balancing Authority shall ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | BA | BA | [20 empty] | Long-Term Planning | Low | N/A | N/A | N/A | The Balancing Authority failed to ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | 2011-04-01 |  | 2018-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
BAL-006-2 | 246 | R4. | 3206 | Adjacent Balancing Authority Areas shall operate to a common Net Interchange Schedule and Actual Net Interchange value and shall record these hourly quantities, with like values but opposite sign. Each Balancing Authority shall compute its Inadvertent Interchange based on the following: |  | BA | BA | [20 empty] | Long-Term Planning | Low | The Balancing Authority failed to record Actual Net Interchange values that are equal but opposite in sign to its Adjacent Balancing Authorities. | The Balancing Authority failed to compute Inadvertent Interchange. | The Balancing Authority failed to operate to a common Net Interchange Schedule that is equal but opposite to its Adjacent Balancing Authorities. | N/A |  | 2011-04-01 |  | 2018-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
BAL-006-2 | 246 | R5. | 3212 | Adjacent Balancing Authorities that cannot mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month shall, for the purposes of dispute resolution, submit a report to their respective Regional Reliability Organization Survey Contact. The report shall describe the nature and the cause of the dispute as well as a process for correcting the discrepancy. |  | BA | BA | [20 empty] | Long-Term Planning | Low | Adjacent Balancing Authorities that could not mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities, submitted a report to their respective Regional Reliability Organizations Survey Contact describing the nature and the cause of the dispute but failed to provide a process for correcting the discrepancy. | Adjacent Balancing Authorities that could not mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month, failed to submit a report to their respective Regional Reliability Organizations Survey Contact describing the nature and the cause of the dispute as well as a process for correcting the discrepancy. | N/A | N/A |  | 2011-04-01 |  | 2018-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
BAL-006-2 (British Columbia) | 666700000010024 | R1. | 666700000010492 | Each Balancing Authority shall calculate and record hourly Inadvertent Interchange. |  | BA | BA | [20 empty] | Long-Term Planning | Low | N/A | N/A | N/A | Each Balancing Authority failed to calculate and record hourly Inadvertent Interchange. |  | 2013-04-15 | [5 empty] | WECC-BC | [6 empty] | 10000000
BAL-006-2 (British Columbia) | 666700000010024 | R2. | 666700000010493 | Each Balancing Authority shall include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. The Balancing Authority shall take into account interchange served by jointly owned generators. |  | BA | BA | [20 empty] | Long-Term Planning | Low | N/A | N/A | The Balancing Authority failed to include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. OR Failed to take into account interchange served by jointly owned generators. | The Balancing Authority failed to include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. AND Failed to take into account interchange served by jointly owned generators. |  | 2013-04-15 | [5 empty] | WECC-BC | [6 empty] | 20000000
BAL-006-2 (British Columbia) | 666700000010024 | R3. | 666700000010494 | Each Balancing Authority shall ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | BA | BA | [20 empty] | Long-Term Planning | Low | N/A | N/A | N/A | The Balancing Authority failed to ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | 2013-04-15 | [5 empty] | WECC-BC | [6 empty] | 30000000
BAL-006-2 (British Columbia) | 666700000010024 | R4. | 666700000010495 | Adjacent Balancing Authority Areas shall operate to a common Net Interchange Schedule and Actual Net Interchange value and shall record these hourly quantities, with like values but opposite sign. Each Balancing Authority shall compute its Inadvertent Interchange based on the following: |  | BA | BA | [20 empty] | Long-Term Planning | Low | The Balancing Authority failed to record Actual Net Interchange values that are equal but opposite in sign to its Adjacent Balancing Authorities. | The Balancing Authority failed to compute Inadvertent Interchange. | The Balancing Authority failed to operate to a common Net Interchange Schedule that is equal but opposite to its Adjacent Balancing Authorities. | N/A |  | 2013-04-15 | [5 empty] | WECC-BC | [6 empty] | 40000000
BAL-006-2 (British Columbia) | 666700000010024 | R5. | 666700000010496 | Adjacent Balancing Authorities that cannot mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month shall, for the purposes of dispute resolution, submit a report to their respective Regional Reliability Organization Survey Contact. The report shall describe the nature and the cause of the dispute as well as a process for correcting the discrepancy. |  | BA | BA | [20 empty] | Long-Term Planning | Low | Adjacent Balancing Authorities that could not mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities, submitted a report to their respective Regional Reliability Organizations Survey Contact describing the nature and the cause of the dispute but failed to provide a process for correcting the discrepancy. | Adjacent Balancing Authorities that could not mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month, failed to submit a report to their respective Regional Reliability Organizations Survey Contact describing the nature and the cause of the dispute as well as a process for correcting the discrepancy. | N/A | N/A |  | 2013-04-15 | [5 empty] | WECC-BC | [6 empty] | 50000000
BAL-006-2 (Manitoba) | 77660000000246 | R1. | 776600000003203 | Each Balancing Authority shall calculate and record hourly Inadvertent Interchange. |  | BA | BA | [20 empty] | Long-Term Planning | Low | N/A | N/A | N/A | Each Balancing Authority failed to calculate and record hourly Inadvertent Interchange. |  | 2014-02-14 |  | 2017-10-12 |  |  |  | MRO-MB | [6 empty] | 10000000
BAL-006-2 (Manitoba) | 77660000000246 | R2. | 776600000003204 | Each Balancing Authority shall include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. The Balancing Authority shall take into account interchange served by jointly owned generators. |  | BA | BA | [20 empty] | Long-Term Planning | Low | N/A | N/A | The Balancing Authority failed to include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. OR Failed to take into account interchange served by jointly owned generators. | The Balancing Authority failed to include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. AND Failed to take into account interchange served by jointly owned generators. |  | 2014-02-14 |  | 2017-10-12 |  |  |  | MRO-MB | [6 empty] | 20000000
BAL-006-2 (Manitoba) | 77660000000246 | R3. | 776600000003205 | Each Balancing Authority shall ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | BA | BA | [20 empty] | Long-Term Planning | Low | N/A | N/A | N/A | The Balancing Authority failed to ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | 2014-02-14 |  | 2017-10-12 |  |  |  | MRO-MB | [6 empty] | 30000000
BAL-006-2 (Manitoba) | 77660000000246 | R4. | 776600000003206 | Adjacent Balancing Authority Areas shall operate to a common Net Interchange Schedule and Actual Net Interchange value and shall record these hourly quantities, with like values but opposite sign. Each Balancing Authority shall compute its Inadvertent Interchange based on the following: |  | BA | BA | [20 empty] | Long-Term Planning | Low | The Balancing Authority failed to record Actual Net Interchange values that are equal but opposite in sign to its Adjacent Balancing Authorities. | The Balancing Authority failed to compute Inadvertent Interchange. | The Balancing Authority failed to operate to a common Net Interchange Schedule that is equal but opposite to its Adjacent Balancing Authorities. | N/A |  | 2014-02-14 |  | 2017-10-12 |  |  |  | MRO-MB | [6 empty] | 40000000
BAL-006-2 (Manitoba) | 77660000000246 | R5. | 776600000003212 | Adjacent Balancing Authorities that cannot mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month shall, for the purposes of dispute resolution, submit a report to their respective Regional Reliability Organization Survey Contact. The report shall describe the nature and the cause of the dispute as well as a process for correcting the discrepancy. |  | BA | BA | [20 empty] | Long-Term Planning | Low | Adjacent Balancing Authorities that could not mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities, submitted a report to their respective Regional Reliability Organizations Survey Contact describing the nature and the cause of the dispute but failed to provide a process for correcting the discrepancy. | Adjacent Balancing Authorities that could not mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month, failed to submit a report to their respective Regional Reliability Organizations Survey Contact describing the nature and the cause of the dispute as well as a process for correcting the discrepancy. | N/A | N/A |  | 2014-02-14 |  | 2017-10-12 |  |  |  | MRO-MB | [6 empty] | 50000000
BAL-006-2 (Ontario) | 79780000246 | R1. | 79780003203 | Each Balancing Authority shall calculate and record hourly Inadvertent Interchange. |  | BA | BA | [20 empty] | Long-Term Planning | Low | N/A | N/A | N/A | Each Balancing Authority failed to calculate and record hourly Inadvertent Interchange. |  | 2011-04-01 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
BAL-006-2 (Ontario) | 79780000246 | R2. | 79780003204 | Each Balancing Authority shall include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. The Balancing Authority shall take into account interchange served by jointly owned generators. |  | BA | BA | [20 empty] | Long-Term Planning | Low | N/A | N/A | The Balancing Authority failed to include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. OR Failed to take into account interchange served by jointly owned generators. | The Balancing Authority failed to include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. AND Failed to take into account interchange served by jointly owned generators. |  | 2011-04-01 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
BAL-006-2 (Ontario) | 79780000246 | R3. | 79780003205 | Each Balancing Authority shall ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | BA | BA | [20 empty] | Long-Term Planning | Low | N/A | N/A | N/A | The Balancing Authority failed to ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | 2011-04-01 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
BAL-006-2 (Ontario) | 79780000246 | R4. | 79780003206 | Adjacent Balancing Authority Areas shall operate to a common Net Interchange Schedule and Actual Net Interchange value and shall record these hourly quantities, with like values but opposite sign. Each Balancing Authority shall compute its Inadvertent Interchange based on the following: |  | BA | BA | [20 empty] | Long-Term Planning | Low | The Balancing Authority failed to record Actual Net Interchange values that are equal but opposite in sign to its Adjacent Balancing Authorities. | The Balancing Authority failed to compute Inadvertent Interchange. | The Balancing Authority failed to operate to a common Net Interchange Schedule that is equal but opposite to its Adjacent Balancing Authorities. | N/A |  | 2011-04-01 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
BAL-006-2 (Ontario) | 79780000246 | R5. | 79780003212 | Adjacent Balancing Authorities that cannot mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month shall, for the purposes of dispute resolution, submit a report to their respective Regional Reliability Organization Survey Contact. The report shall describe the nature and the cause of the dispute as well as a process for correcting the discrepancy. |  | BA | BA | [20 empty] | Long-Term Planning | Low | &lt;p&gt;Adjacent Balancing Authorities that could not mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities, submitted a report to their respective Regional Reliability Organizations Survey Contact describing the nature and the cause of the dispute but failed to provide a process for correcting the discrepancy.&lt;/p&gt; | &lt;p&gt;Adjacent Balancing Authorities that could not mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month, failed to submit a report to their respective Regional Reliability Organizations Survey Contact describing the nature and the cause of the dispute as well as a process for correcting the discrepancy.&lt;/p&gt; | N/A | N/A |  | 2011-04-01 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 50000000
BAL-006-2 (Saskatchewan) | 83750000000246 | R1. | 837500000003203 | Each Balancing Authority shall calculate and record hourly Inadvertent Interchange. |  | BA | BA | [20 empty] | Long-Term Planning | Low | N/A | N/A | N/A | Each Balancing Authority failed to calculate and record hourly Inadvertent Interchange. |  | 2014-04-01 |  | 2019-01-01 |  |  |  | MRO-SK | [6 empty] | 10000000
BAL-006-2 (Saskatchewan) | 83750000000246 | R2. | 837500000003204 | Each Balancing Authority shall include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. The Balancing Authority shall take into account interchange served by jointly owned generators. |  | BA | BA | [20 empty] | Long-Term Planning | Low | N/A | N/A | The Balancing Authority failed to include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. OR Failed to take into account interchange served by jointly owned generators. | The Balancing Authority failed to include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. AND Failed to take into account interchange served by jointly owned generators. |  | 2014-04-01 |  | 2019-01-01 |  |  |  | MRO-SK | [6 empty] | 20000000
BAL-006-2 (Saskatchewan) | 83750000000246 | R3. | 837500000003205 | Each Balancing Authority shall ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | BA | BA | [20 empty] | Long-Term Planning | Low | N/A | N/A | N/A | The Balancing Authority failed to ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | 2014-04-01 |  | 2019-01-01 |  |  |  | MRO-SK | [6 empty] | 30000000
BAL-006-2 (Saskatchewan) | 83750000000246 | R4. | 837500000003206 | Adjacent Balancing Authority Areas shall operate to a common Net Interchange Schedule and Actual Net Interchange value and shall record these hourly quantities, with like values but opposite sign. Each Balancing Authority shall compute its Inadvertent Interchange based on the following: |  | BA | BA | [20 empty] | Long-Term Planning | Low | The Balancing Authority failed to record Actual Net Interchange values that are equal but opposite in sign to its Adjacent Balancing Authorities. | The Balancing Authority failed to compute Inadvertent Interchange. | The Balancing Authority failed to operate to a common Net Interchange Schedule that is equal but opposite to its Adjacent Balancing Authorities. | N/A |  | 2014-04-01 |  | 2019-01-01 |  |  |  | MRO-SK | [6 empty] | 40000000
BAL-006-2 (Saskatchewan) | 83750000000246 | R5. | 837500000003212 | Adjacent Balancing Authorities that cannot mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month shall, for the purposes of dispute resolution, submit a report to their respective Regional Reliability Organization Survey Contact. The report shall describe the nature and the cause of the dispute as well as a process for correcting the discrepancy. |  | BA | BA | [20 empty] | Long-Term Planning | Low | Adjacent Balancing Authorities that could not mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities, submitted a report to their respective Regional Reliability Organizations Survey Contact describing the nature and the cause of the dispute but failed to provide a process for correcting the discrepancy. | Adjacent Balancing Authorities that could not mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month, failed to submit a report to their respective Regional Reliability Organizations Survey Contact describing the nature and the cause of the dispute as well as a process for correcting the discrepancy. | N/A | N/A |  | 2014-04-01 |  | 2019-01-01 |  |  |  | MRO-SK | [6 empty] | 50000000
BAL-502-RF-03 | 575 | R1. | 8220 | The Planning Coordinator shall perform and document a Resource Adequacy analysis annually. The Resource Adequacy analysis shall |  | PCPA | [9 empty] | PCPA | [11 empty] | Long-Term Planning | Medium | The Planning Coordinator Resource Adequacy analysis failed to consider 1 or 2 of the Resource availability characteristics subcomponents under Requirement R1, Part 1.4 and documentation of how and why they were included in the analysis or why they were not included OR The Planning Coordinator Resource Adequacy analysis failed to consider Transmission maintenance outage schedules and document how and why they were included in the analysis or why they were not included per Requirement R1, Part 1.5 | The Planning Coordinator Resource Adequacy analysis failed to express the planning reserve margin developed from Requirement R1, Part 1.1 as a percentage of the net Median forecast peak Load per Requirement R1, Part 1.1.2 OR The Planning Coordinator Resource Adequacy analysis failed to include 1 of the Load forecast Characteristics subcomponents under Requirement R1, Part 1.3.1 and documentation of its use OR The Planning Coordinator Resource Adequacy analysis failed to include 1 of the Resource Characteristics subcomponents under Requirement R1, Part 1.3.2 and documentation of its use OR The Planning Coordinator Resource Adequacy analysis failed to document that all Load in the Planning Coordinator area is accounted for in its Resource Adequacy analysis per Requirement R1, Part 1.7 | The Planning Coordinator Resource Adequacy analysis failed to be performed or verified separately for individual years of Year One through Year Ten per Requirement R1, Part 1.2 OR The Planning Coordinator failed to perform an analysis or verification for one year in the 2 through 5 year period or one year in the 6 though 10 year period or both per Requirement R1, Part 1.2.2 OR The Planning Coordinator Resource Adequacy analysis failed to include 2 or more of the Load forecast Characteristics subcomponents under Requirement R1, Part 1.3.1 and documentation of their use OR The Planning Coordinator Resource Adequacy analysis failed to include 2 or more of the Resource Characteristics subcomponents under Requirement R1, Part 1.3.2 and documentation of their use OR The Planning Coordinator Resource Adequacy analysis failed to include Transmission limitations and documentation of its use per Requirement R1, Part 1.3.3 OR The Planning Coordinator Resource Adequacy analysis failed to include assistance from other interconnected systems OR The Planning Coordinator Resource Adequacy analysis failed to consider 3 or more Resource availability characteristics subcomponents under Requirement R1, Part 1.4 and documentation of how and why they were included in the analysis or why they were not included OR The Planning Coordinator Resource Adequacy analysis failed to document that capacity resources are appropriately accounted for in its Resource Adequacy analysis per Requirement R1, Part 1.6 | The Planning Coordinator failed to perform and document a Resource Adequacy analysis annually per R1. OR The Planning Coordinator Resource Adequacy analysis failed to calculate a Planning reserve margin that will result in the sum of the probabilities for loss of Load for the integrated peak hour for all days of each planning year analyzed for each planning period being equal to 0.1 per Requirement R1, Part 1.1 OR The Planning Coordinator failed to perform an analysis for Year One per Requirement R1, Part 1.2.1 | M1. Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 | [5 empty] | RF-US |  |  | RF-US |  |  |  | 10000000
BAL-502-RF-03 | 575 | R2. | 8259 | The Planning Coordinator shall annually document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis |  | PCPA | [9 empty] | PCPA | [11 empty] | Long-Term Planning | Low | The Planning Coordinator failed to publicly post the documents as specified per requirement Requirement R2, Part 2.1 and Requirement R2, Part 2.2 later than 30 calendar days prior to the beginning of Year One per Requirement R2, Part 2.3 | The Planning Coordinator failed to document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis for one of the years in the 2 through 10 year period per Requirement R2, Part 2.1. OR The Planning Coordinator failed to document the Planning Reserve margin calculated per requirement R1.1 for each of the three years in the analysis per Requirement R2, Part 2.2. | The Planning Coordinator failed to document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis for year 1 of the 10 year period per Requirement R2, Part 2.1. OR The Planning Coordinator failed to document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis for two or more of the years in the 2 through 10 year period per Requirement R2, Part 2.1. | The Planning Coordinator failed to document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis per Requirement R2, Part 2. | M2. Each Planning Coordinator shall possess the documentation of its projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis on an annual basis in accordance with R2. | 2018-01-01 | [5 empty] | RF-US |  |  | RF-US |  |  |  | 20000000
BAL-502-RF-03 | 575 | R3. | 8263 | The Planning Coordinator shall identify any gaps between the needed amount of planning reserves defined in Requirement R1, Part 1.1 and the projected planning reserves documented in Requirement R2 |  | PCPA | [9 empty] | PCPA | [11 empty] | Long-Term Planning | Low | None | None | None | The Planning Coordinator failed to identify any gaps between the needed amount of planning reserves and the projected planning reserves, per R3 | M3. Each Planning Coordinator shall possess the documentation identifying any gaps between the needed amounts of planning reserves and projected planning reserves in accordance with R3. | 2018-01-01 | [5 empty] | RF-US |  |  | RF-US |  |  |  | 30000000
BAL-502-RFC-02 | 247 | R1. | 3213 | The Planning Coordinator shall perform and document a Resource Adequacy analysis annually. The Resource Adequacy analysis shall: [See Standard pdf for requirements of the Resource Adequacy analysis] |  | PCPA | [9 empty] | PCPA | [12 empty] | Medium | The Planning Coordinator Resource Adequacy analysis failed to consider 1 or 2 of the Resource availability characteristics subcomponents under R1.4 and documentation of how and why they were included in the analysis or why they were not included OR The Planning Coordinator Resource Adequacy analysis failed to consider Transmission maintenance outage schedules and document how and why they were included in the analysis or why they were not included per R1.5 | The Planning Coordinator Resource Adequacy analysis failed to express the planning reserve margin developed from R1.1 as a percentage of the net Median forecast peak Load per R1.1.2 OR The Planning Coordinator Resource Adequacy analysis failed to include 1 of the Load forecast Characteristics subcomponents under R1.3.1 and documentation of its use OR The Planning Coordinator Resource Adequacy analysis failed to document that all Load in the Planning Coordinator area is accounted for in its Resource Adequacy analysis per R1.7 | The Planning Coordinator Resource Adequacy analysis failed to be performed or verified separately for individual years of Year One through Year Ten per R1.2 OR The Planning Coordinator failed to perform an analysis or verification for one year in the 2 through 5 year period or one year in the 6 though 10 year period or both per R1.2.2 OR The Planning Coordinator Resource Adequacy analysis failed to include 2 or more of the Load forecast Characteristics subcomponents under R1.3.1 and documentation of their use OR The Planning Coordinator Resource Adequacy analysis failed to include 2 or more of the Resource Characteristics subcomponents under R1.3.2 and documentation of their use OR The Planning Coordinator Resource Adequacy analysis failed to include Transmission limitations and documentation of its use per R1.3.3 OR The Planning Coordinator Resource Adequacy analysis failed to include assistance from other interconnected systems and documentation of its use per R1.3.4 OR The Planning Coordinator Resource Adequacy analysis failed to consider 3 or more Resource availability characteristics subcomponents under R1.4 and documentation of how and why they were included in the analysis or why they were not included OR The Planning Coordinator Resource Adequacy analysis failed to document that capacity resources are appropriately accounted for in its Resource Adequacy analysis per R1.6 | The Planning Coordinator failed to perform and document a Resource Adequacy analysis annually per R1 OR The Planning Coordinator Resource Adequacy analysis failed to calculate a Planning reserve margin that will result in the sum of the probabilities for loss of Load for the integrated peak hour for all days of each planning year analyzed for each planning period being equal to 0.1 per OR The Planning Coordinator failed to perform an analysis for Year One per R1.2.1 R1.1 | M1 Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2011-05-23 |  | 2017-12-31 |  |  |  | RF-US |  |  | RF-US |  |  |  | 10000000
BAL-502-RFC-02 | 247 | R2. | 3214 | The Planning Coordinator shall annually document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis. [See Standard pdf for the requirements of the documentation] |  | PCPA | [9 empty] | PCPA | [12 empty] | Low | The Planning Coordinator failed to publicly post the documents as specified per requirement R2.1 and R2.2 later than 30 calendar days prior to the beginning of Year One per R2.3 | The Planning Coordinator failed to document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis for one of the years in the 2 through 10 year period per R2.1 OR The Planning Coordinator failed to document the Planning Reserve margin calculated per requirement R1.1 for each of the three years in the analysis per R2.2. | The Planning Coordinator failed to document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis for year 1 of the 10 year period per R2.1 OR The Planning Coordinator failed to document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis for two or more of the years in the 2 through 10 year period per R2.1. | The Planning Coordinator failed to document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis per R2. | M2 Each Planning Coordinator shall possess the documentation of its projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis on an annual basis in accordance with R2. | 2011-05-23 |  | 2017-12-31 |  |  |  | RF-US |  |  | RF-US |  |  |  | 20000000
BAL-STD-002-0 | 21 | WR1. | 239 | The reliable operation of the interconnected power system requires that adequate generating capacity be available at all times to maintain scheduled frequency and avoid loss of firm load following transmission or generation contingencies. This generating capacity is necessary to: -supply requirements for load variations. -replace generating capacity and energy lost due to forced outages of generation or transmission equipment. -meet on-demand obligations. -replace energy lost due to curtailment of interruptible imports. a. Minimum Operating Reserve. Each Balancing Authority shall maintain minimum Operating Reserve which is the sum of the following: (i) Regulating reserve. Sufficient Spinning Reserve, immediately responsive to Automatic Generation Control (AGC) to provide sufficient regulating margin to allow the Balancing Authority to meet NERC’s Control Performance Criteria (see BAL-001-0). (ii) Contingency reserve. An amount of Spinning Reserve and Nonspinning Reserve (at least half of which must be Spinning Reserve), sufficient to meet the NERC Disturbance Control Standard BAL-002-0, equal to the greater of: (a) The loss of generating capacity due to forced outages of generation or transmission equipment that would result from the most severe single contingency; or (b) The sum of five percent of the load responsibility served by hydro generation and seven percent of the load responsibility served by thermal generation. The combined unit ramp rate of each Balancing Authority’s on-line, unloaded generating capacity must be capable of responding to the Spinning Reserve requirement of that Balancing Authority within ten minutes (iii) Additional reserve for interruptible imports. An amount of reserve, which can be made effective within ten minutes, equal to interruptible imports. (iv) Additional reserve for on-demand obligations. An amount of reserve, which can be made effective within ten minutes, equal to on-demand obligations to other entities or Balancing Authorities b. Acceptable types of Nonspinning Reserve. The Nonspinning Reserve obligations identified in subsections a (ii), a (iii), and a (iv), if any, can be met by use of the following: (i) interruptible load; (ii) interruptible exports; (iii) on-demand rights from other entities or Balancing Authorities; (iv) Spinning Reserve in excess of requirements in subsections a (i) and a (ii); or (v) off-line generation which qualifies as Nonspinning Reserve. c. Knowledge of Operating Reserve. Operating Reserves shall be calculated such that the amount available which can be fully activated in the next ten minutes will be known at all times. d. Restoration of Operating Reserve. After the occurrence of any event necessitating the use of Operating Reserve, that reserve shall be restored as promptly as practicable. The time taken to restore reserves shall not exceed 60 minutes (Source: WECC Criterion) |  | BA, RSG | BA | [15 empty] | RSG | [11 empty] | 2007-06-18 |  | 2014-09-30 |  |  |  | WECC-US | [5 empty] | WECC-US | 10000000
BAL-STD-002-0 (British Columbia) | 666700000010025 | WR1. | 666700000010497 | The reliable operation of the interconnected power system requires that adequate generating capacity be available at all times to maintain scheduled frequency and avoid loss of firm load following transmission or generation contingencies. This generating capacity is necessary to: -supply requirements for load variations. -replace generating capacity and energy lost due to forced outages of generation or transmission equipment. -meet on-demand obligations. -replace energy lost due to curtailment of interruptible imports. a. Minimum Operating Reserve. Each Balancing Authority shall maintain minimum Operating Reserve which is the sum of the following: (i) Regulating reserve. Sufficient Spinning Reserve, immediately responsive to Automatic Generation Control (AGC) to provide sufficient regulating margin to allow the Balancing Authority to meet NERC’s Control Performance Criteria (see BAL-001-0). (ii) Contingency reserve. An amount of Spinning Reserve and Nonspinning Reserve (at least half of which must be Spinning Reserve), sufficient to meet the NERC Disturbance Control Standard BAL-002-0, equal to the greater of: (a) The loss of generating capacity due to forced outages of generation or transmission equipment that would result from the most severe single contingency; or (b) The sum of five percent of the load responsibility served by hydro generation and seven percent of the load responsibility served by thermal generation. The combined unit ramp rate of each Balancing Authority’s on-line, unloaded generating capacity must be capable of responding to the Spinning Reserve requirement of that Balancing Authority within ten minutes (iii) Additional reserve for interruptible imports. An amount of reserve, which can be made effective within ten minutes, equal to interruptible imports. (iv) Additional reserve for on-demand obligations. An amount of reserve, which can be made effective within ten minutes, equal to on-demand obligations to other entities or Balancing Authorities b. Acceptable types of Nonspinning Reserve. The Nonspinning Reserve obligations identified in subsections a (ii), a (iii), and a (iv), if any, can be met by use of the following: (i) interruptible load; (ii) interruptible exports; (iii) on-demand rights from other entities or Balancing Authorities; (iv) Spinning Reserve in excess of requirements in subsections a (i) and a (ii); or (v) off-line generation which qualifies as Nonspinning Reserve. c. Knowledge of Operating Reserve. Operating Reserves shall be calculated such that the amount available which can be fully activated in the next ten minutes will be known at all times. d. Restoration of Operating Reserve. After the occurrence of any event necessitating the use of Operating Reserve, that reserve shall be restored as promptly as practicable. The time taken to restore reserves shall not exceed 60 minutes (Source: WECC Criterion) |  | BA, RSG | BA | [15 empty] | RSG | [11 empty] | 2010-11-01 |  | 2014-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-001-0 | 382 | R1. | 4804 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-001-0 | 382 | R2. | 4805 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-001-0 | 382 | R3. | 4806 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-001-0 | 382 | R4. | 4807 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load Serving Entity shall establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials and develop reporting procedures as appropriate to their circumstances. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-001-0 (Ontario) | 79780000382 | R1. | 79780004804 |  |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-001-0 (Ontario) | 79780000382 | R2. | 79780004805 |  |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-001-0 (Ontario) | 79780000382 | R3. | 79780004806 |  |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-001-0 (Ontario) | 79780000382 | R4. | 79780004807 |  |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-001-1 | 22 | R1. | 240 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2011-02-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-001-1 | 22 | R2. | 241 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2011-02-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-001-1 | 22 | R3. | 242 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2011-02-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-001-1 | 22 | R4. | 243 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials and develop reporting procedures as appropriate to their circumstances. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2011-02-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-001-1a | 276 | R1. | 3612 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-02-02 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-001-1a | 276 | R2. | 3613 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-02-02 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-001-1a | 276 | R3. | 3614 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-02-02 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-001-1a | 276 | R4. | 3615 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials and develop reporting procedures as appropriate to their circumstances. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-02-02 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-001-1a (Ontario) | 79780000276 | R1. | 79780003612 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | Medium |  |  | The responsible entity has procedures for the recognition of sabotage events on its facilities and multi site sabotage affecting larger portions of the Interconnection but does not have a procedure for making their operating personnel aware of said events | The responsible entity failed to have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi site sabotage affecting larger portions of the Interconnection. |  | 2011-02-02 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-001-1a (Ontario) | 79780000276 | R2. | 79780003613 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | Medium |  |  | The responsible entity has demonstrated the existence of a procedure to communicate information concerning sabotage events, but not all of the appropriate parties in the interconnection are identified. | The responsible entity failed to have a procedure for communicating information concerning sabotage events. |  | 2011-02-02 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-001-1a (Ontario) | 79780000276 | R3. | 79780003614 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | Medium |  | The responsible entity has demonstrated the existence of a response guideline for reporting disturbances due to sabotage events, but the guideline did not list all of the appropriate personnel to contact. | The responsible entity has demonstrated the existence of a response guideline for reporting disturbances due to sabotage events, including all of the appropriate personnel to contact, but the guideline was not available to its operating personnel. | The responsible entity failed to have a response guideline for reporting disturbances due to sabotage events. |  | 2011-02-02 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-001-1a (Ontario) | 79780000276 | R4. | 79780003615 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials and develop reporting procedures as appropriate to their circumstances. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | Medium |  |  | The responsible entity has established communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials, but has not developed a reporting procedure. | The responsible entity failed to establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials, nor developed a reporting procedure. |  | 2011-02-02 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-001-1 (British Columbia) | 666700000010026 | R1. | 666700000010498 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-01-01 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-001-1 (British Columbia) | 666700000010026 | R2. | 666700000010499 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-01-01 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 20000000
CIP-001-1 (British Columbia) | 666700000010026 | R3. | 666700000010500 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-01-01 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 30000000
CIP-001-1 (British Columbia) | 666700000010026 | R4. | 666700000010501 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials and develop reporting procedures as appropriate to their circumstances. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-01-01 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 40000000
CIP-001-1 (Ontario) | 79780000022 | R1. | 79780000240 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | Medium |  |  | The responsible entity has procedures for the recognition of sabotage events on its facilities and multi site sabotage affecting larger portions of the Interconnection but does not have a procedure for making their operating personnel aware of said events | The responsible entity failed to have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi site sabotage affecting larger portions of the Interconnection. |  | 2007-06-18 |  | 2011-02-01 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-001-1 (Ontario) | 79780000022 | R2. | 79780000241 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | Medium |  |  | The responsible entity has demonstrated the existence of a procedure to communicate information concerning sabotage events, but not all of the appropriate parties in the interconnection are identified. | The responsible entity failed to have a procedure for communicating information concerning sabotage events. |  | 2007-06-18 |  | 2011-02-01 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-001-1 (Ontario) | 79780000022 | R3. | 79780000242 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | Medium |  | The responsible entity has demonstrated the existence of a response guideline for reporting disturbances due to sabotage events, but the guideline did not list all of the appropriate personnel to contact. | The responsible entity has demonstrated the existence of a response guideline for reporting disturbances due to sabotage events, including all of the appropriate personnel to contact, but the guideline was not available to its operating personnel. | The responsible entity failed to have a response guideline for reporting disturbances due to sabotage events. |  | 2007-06-18 |  | 2011-02-01 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-001-1 (Ontario) | 79780000022 | R4. | 79780000243 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials and develop reporting procedures as appropriate to their circumstances. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | Medium |  |  | The responsible entity has established communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials, but has not developed a reporting procedure. | The responsible entity failed to establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials, nor developed a reporting procedure. |  | 2007-06-18 |  | 2011-02-01 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-001-2a | 283 | EA.1. | 4527 | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP | [9 empty] | 2011-10-01 |  | 2013-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 1000000
CIP-001-2a | 283 | EA.2. | 4528 | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP | [9 empty] | 2011-10-01 |  | 2013-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2000000
CIP-001-2a | 283 | EA.3. | 4529 | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP | [9 empty] | 2011-10-01 |  | 2013-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 3000000
CIP-001-2a | 283 | EA.4. | 4530 | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall establish communications contacts with local Federal Bureau of Investigation (FBI) officials and develop reporting procedures as appropriate to their circumstances. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP | [9 empty] | 2011-10-01 |  | 2013-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 4000000
CIP-001-2a | 283 | R1. | 3725 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi site sabotage affecting larger portions of the Interconnection. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Medium | [5 empty] | 2011-10-01 |  | 2013-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-001-2a | 283 | R2. | 3726 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Medium | [5 empty] | 2011-10-01 |  | 2013-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-001-2a | 283 | R3. | 3727 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Medium | [5 empty] | 2011-10-01 |  | 2013-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-001-2a | 283 | R4. | 3728 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials and develop reporting procedures as appropriate to their circumstances. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Medium | [5 empty] | 2011-10-01 |  | 2013-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-001-2a (British Columbia) | 666700000010027 | EA.1. | 666700000010502 | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP | [9 empty] | 2013-01-15 |  | 2015-07-31 |  |  |  | WECC-BC | [6 empty] | 1000000
CIP-001-2a (British Columbia) | 666700000010027 | EA.2. | 666700000010503 | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP | [9 empty] | 2013-01-15 |  | 2015-07-31 |  |  |  | WECC-BC | [6 empty] | 2000000
CIP-001-2a (British Columbia) | 666700000010027 | EA.3. | 666700000010504 | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP | [9 empty] | 2013-01-15 |  | 2015-07-31 |  |  |  | WECC-BC | [6 empty] | 3000000
CIP-001-2a (British Columbia) | 666700000010027 | EA.4. | 666700000010505 | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall establish communications contacts with local Federal Bureau of Investigation (FBI) officials and develop reporting procedures as appropriate to their circumstances. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP | [9 empty] | 2013-01-15 |  | 2015-07-31 |  |  |  | WECC-BC | [6 empty] | 4000000
CIP-001-2a (British Columbia) | 666700000010027 | R1. | 666700000010506 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi site sabotage affecting larger portions of the Interconnection. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Medium | [5 empty] | 2013-01-15 |  | 2015-07-31 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-001-2a (British Columbia) | 666700000010027 | R2. | 666700000010507 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Medium | [5 empty] | 2013-01-15 |  | 2015-07-31 |  |  |  | WECC-BC | [6 empty] | 20000000
CIP-001-2a (British Columbia) | 666700000010027 | R3. | 666700000010508 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Medium | [5 empty] | 2013-01-15 |  | 2015-07-31 |  |  |  | WECC-BC | [6 empty] | 30000000
CIP-001-2a (British Columbia) | 666700000010027 | R4. | 666700000010509 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials and develop reporting procedures as appropriate to their circumstances. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Medium | [5 empty] | 2013-01-15 |  | 2015-07-31 |  |  |  | WECC-BC | [6 empty] | 40000000
CIP-001-2a (Ontario) | 79780000283 | EA.1. | 79780004527 | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. |  | BA, GO, GOP, LSE, RC, TO | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | [10 empty] | 2011-10-01 |  | 2013-12-31 |  |  |  | NPCC-ON | [6 empty] | 1000000
CIP-001-2a (Ontario) | 79780000283 | EA.2. | 79780004528 | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP | [9 empty] | 2011-10-01 |  | 2013-12-31 |  |  |  | NPCC-ON | [6 empty] | 2000000
CIP-001-2a (Ontario) | 79780000283 | EA.3. | 79780004529 | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP | [9 empty] | 2011-10-01 |  | 2013-12-31 |  |  |  | NPCC-ON | [6 empty] | 3000000
CIP-001-2a (Ontario) | 79780000283 | EA.4. | 79780004530 | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall establish communications contacts with local Federal Bureau of Investigation (FBI) officials and develop reporting procedures as appropriate to their circumstances. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP | [9 empty] | 2011-10-01 |  | 2013-12-31 |  |  |  | NPCC-ON | [6 empty] | 4000000
CIP-001-2a (Ontario) | 79780000283 | R1. | 79780003725 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi site sabotage affecting larger portions of the Interconnection. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Medium | N/A | N/A | The responsible entity has procedures for the recognition of sabotage events on its facilities and multi site sabotage affecting larger portions of the Interconnection but does not have a procedure for making their operating personnel aware of said events | The responsible entity failed to have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi site sabotage affecting larger portions of the Interconnection. |  | 2011-10-01 |  | 2013-12-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-001-2a (Ontario) | 79780000283 | R2. | 79780003726 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Medium | N/A | N/A | The responsible entity has demonstrated the existence of a procedure to communicate information concerning sabotage events, but not all of the appropriate parties in the interconnection are identified. | The responsible entity failed to have a procedure for communicating information concerning sabotage events. |  | 2011-10-01 |  | 2013-12-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-001-2a (Ontario) | 79780000283 | R3. | 79780003727 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Medium | N/A | The responsible entity provided its operating personnel with a sabotage response guideline, but failed to include the personnel to contact for reporting disturbances due to sabotage events. | N/A | The responsible entity failed to provide its operating personnel with a sabotage response guideline. |  | 2011-10-01 |  | 2013-12-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-001-2a (Ontario) | 79780000283 | R4. | 79780003728 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials and develop reporting procedures as appropriate to their circumstances. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Medium | N/A | N/A | The responsible entity has established communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials, but has not developed a reporting procedure. | The responsible entity failed to establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials, and has not developed a reporting procedure. |  | 2011-10-01 |  | 2013-12-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-001-2a (Saskatchewan) | 83750000000283 | EA.1. | 837500000004527 | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP | [9 empty] | 2011-02-17 |  | 2014-04-01 |  |  |  | MRO-SK | [6 empty] | 1000000
CIP-001-2a (Saskatchewan) | 83750000000283 | EA.2. | 837500000004528 | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP | [9 empty] | 2011-02-17 |  | 2014-04-01 |  |  |  | MRO-SK | [6 empty] | 2000000
CIP-001-2a (Saskatchewan) | 83750000000283 | EA.3. | 837500000004529 | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP | [9 empty] | 2011-02-17 |  | 2014-04-01 |  |  |  | MRO-SK | [6 empty] | 3000000
CIP-001-2a (Saskatchewan) | 83750000000283 | EA.4. | 837500000004530 | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall establish communications contacts with local Federal Bureau of Investigation (FBI) officials and develop reporting procedures as appropriate to their circumstances. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP | [9 empty] | 2011-02-17 |  | 2014-04-01 |  |  |  | MRO-SK | [6 empty] | 4000000
CIP-001-2a (Saskatchewan) | 83750000000283 | R1. | 837500000003725 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi site sabotage affecting larger portions of the Interconnection. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Medium | [5 empty] | 2011-02-17 |  | 2014-04-01 |  |  |  | MRO-SK | [6 empty] | 10000000
CIP-001-2a (Saskatchewan) | 83750000000283 | R2. | 837500000003726 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Medium | [5 empty] | 2011-02-17 |  | 2014-04-01 |  |  |  | MRO-SK | [6 empty] | 20000000
CIP-001-2a (Saskatchewan) | 83750000000283 | R3. | 837500000003727 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Medium | [5 empty] | 2011-02-17 |  | 2014-04-01 |  |  |  | MRO-SK | [6 empty] | 30000000
CIP-001-2a (Saskatchewan) | 83750000000283 | R4. | 837500000003728 | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials and develop reporting procedures as appropriate to their circumstances. |  | BA, GO, GOP, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Medium | [5 empty] | 2011-02-17 |  | 2014-04-01 |  |  |  | MRO-SK | [6 empty] | 40000000
CIP-002-1 | 23 | R1. | 244 | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-002-1 | 23 | R2. | 254 | Critical Asset Identification - The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-002-1 | 23 | R3. | 255 | Critical Cyber Asset Identification - Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-002-1 | 23 | R4. | 259 | Annual Approval - A senior manager or delegate(s) shall approve annually the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-002-1 (British Columbia) | 666700000010028 | R1. | 666700000010510 | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-002-1 (British Columbia) | 666700000010028 | R2. | 666700000010511 | Critical Asset Identification - The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 20000000
CIP-002-1 (British Columbia) | 666700000010028 | R3. | 666700000010512 | Critical Cyber Asset Identification - Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 30000000
CIP-002-1 (British Columbia) | 666700000010028 | R4. | 666700000010513 | Annual Approval - A senior manager or delegate(s) shall approve annually the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 40000000
CIP-002-1 (Ontario) | 79780000023 | R1. | 79780000244 | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The responsible entity has not documented a risk-based assessment methodology to use to identify its Critical Assets as specified in R1. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-002-1 (Ontario) | 79780000023 | R2. | 79780000254 | Critical Asset Identification - The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | The Responsible Entity has developed a list of Critical Assets but the list has not been reviewed and updated annually as required. | The Responsible Entity did not develop a list of its identified Critical Assets even if such list is null. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-002-1 (Ontario) | 79780000023 | R3. | 79780000255 | Critical Cyber Asset Identification - Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | The Responsible Entity has developed a list of associated Critical Cyber Assets essential to the operation of the Critical Asset list as per requirement R2 but the list has not been reviewed and updated annually as required. | The Responsible Entity did not develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset list as per requirement R2 even if such list is null. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-002-1 (Ontario) | 79780000023 | R4. | 79780000259 | Annual Approval - A senior manager or delegate(s) shall approve annually the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of the list of Critical Assets. OR The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s) | The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of both the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-002-2 | 208 | R1. | 2354 | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  | CIP-002-1 R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-002-2 | 208 | R2. | 2364 | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-002-2 | 208 | R3. | 2365 | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-2, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-002-2 | 208 | R4. | 2369 | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-002-2 (Ontario) | 79780000208 | R1. | 79780002354 | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-002-2 (Ontario) | 79780000208 | R2. | 79780002364 | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-002-2 (Ontario) | 79780000208 | R3. | 79780002365 | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-2, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-002-2 (Ontario) | 79780000208 | R4. | 79780002369 | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-002-3 | 222 | R1. | 2713 | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets.. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-002-3 | 222 | R2. | 2723 | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High |  |  |  |  | M2. The Responsible Entity shall make available its list of Critical Assets as specified in Requirement R2. | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-002-3 | 222 | R3. | 2724 | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High |  |  |  |  | M3. The Responsible Entity shall make available its list of Critical Cyber Assets as specified in Requirement R3. | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-002-3 | 222 | R4. | 2728 | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M4. The Responsible Entity shall make available its approval records of annual approvals as specified in Requirement R4. | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-002-3a | 329 | R1. | 4335 | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-002-3a | 329 | R2. | 4333 | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High | [7 empty] | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-002-3a | 329 | R3. | 4334 | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High | [7 empty] | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-002-3a | 329 | R4. | 4332 | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-002-3a (Ontario) | 79780000329 | R1. | 79780004335 | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-002-3a (Ontario) | 79780000329 | R2. | 79780004333 | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High | [7 empty] | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-002-3a (Ontario) | 79780000329 | R3. | 79780004334 | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High | [7 empty] | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-002-3a (Ontario) | 79780000329 | R4. | 79780004332 | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-002-3b | 364 | R1. | 4554 | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-002-3b | 364 | R2. | 4556 | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Planning | High |  |  |  |  | M2. The Responsible Entity shall make available its list of Critical Assets as specified in Requirement R2. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-002-3b | 364 | R3. | 4553 | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Planning | High |  |  |  |  | M3. The Responsible Entity shall make available its list of Critical Cyber Assets as specified in Requirement R3. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-002-3b | 364 | R4. | 4555 | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Planning | Low |  |  |  |  | M4. The Responsible Entity shall make available its approval records of annual approvals as specified in Requirement R4. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-002-3b (Ontario) | 79780000364 | R1. | 79780004554 | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. |  |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-002-3b (Ontario) | 79780000364 | R2. | 79780004556 | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Planning | High |  |  |  |  | M2. The Responsible Entity shall make available its list of Critical Assets as specified in Requirement R2. |  |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-002-3b (Ontario) | 79780000364 | R3. | 79780004553 | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Planning | High |  |  |  |  | M3. The Responsible Entity shall make available its list of Critical Cyber Assets as specified in Requirement R3. |  |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-002-3b (Ontario) | 79780000364 | R4. | 79780004555 | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Planning | Low |  |  |  |  | M4. The Responsible Entity shall make available its approval records of annual approvals as specified in Requirement R4. |  |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-002-3 (British Columbia) | 666700000010029 | R1. | 666700000010514 | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets.. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. | 2012-07-01 |  | 2018-09-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | WECC-BC | [6 empty] | 10000000
CIP-002-3 (British Columbia) | 666700000010029 | R2. | 666700000010515 | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High |  |  |  |  | M2. The Responsible Entity shall make available its list of Critical Assets as specified in Requirement R2. | 2012-07-01 |  | 2018-09-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | WECC-BC | [6 empty] | 20000000
CIP-002-3 (British Columbia) | 666700000010029 | R3. | 666700000010516 | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High |  |  |  |  | M3. The Responsible Entity shall make available its list of Critical Cyber Assets as specified in Requirement R3. | 2012-07-01 |  | 2018-09-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | WECC-BC | [6 empty] | 30000000
CIP-002-3 (British Columbia) | 666700000010029 | R4. | 666700000010517 | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M4. The Responsible Entity shall make available its approval records of annual approvals as specified in Requirement R4. | 2012-07-01 |  | 2018-09-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | WECC-BC | [6 empty] | 40000000
CIP-002-3(i) | 469 | R1. | 5565 | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2014-11-13 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-002-3(i) | 469 | R2. | 5566 | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High | [7 empty] | 2014-11-13 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-002-3(i) | 469 | R3. | 5567 | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3(i), Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: See Standard for Requirement Parts. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High | [7 empty] | 2014-11-13 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-002-3(i) | 469 | R4. | 5568 | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2014-11-13 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-002-3(i)b | 474 | R1. | 5579 | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. See Standard for Requirement Parts |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2014-11-13 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-002-3(i)b | 474 | R2. | 5580 | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High | [7 empty] | 2014-11-13 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-002-3(i)b | 474 | R3. | 5581 | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3(i)b, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: See Standard for Requirement Parts |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High | [7 empty] | 2014-11-13 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-002-3(i)b | 474 | R4. | 5582 | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2014-11-13 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-002-3(i)b (Ontario) | 79780000474 | R1. | 79780005579 | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. See Standard for Requirement Parts |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  | Medium |  |  |  | The responsible entity has not documented a risk-based assessment methodology to use to identify its Critical Assets as specified in R1. |  |  |  | 2014-11-13 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-002-3(i)b (Ontario) | 79780000474 | R2. | 79780005580 | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  | High |  |  | The Responsible Entity has developed a list of Critical Assets but the list has not been reviewed and updated annually as required. | The Responsible Entity did not develop a list of its identified Critical Assets even if such list is null. |  |  |  | 2014-11-13 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-002-3(i)b (Ontario) | 79780000474 | R3. | 79780005581 | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3(i)b, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: See Standard for Requirement Parts |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  | High |  |  | The Responsible Entity has developed a list of associated Critical Cyber Assets essential to the operation of the Critical Asset list as per requirement R2 but the list has not been reviewed and updated annually as required. | The Responsible Entity did not develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset list as per requirement R2 even if such list is null. |  |  |  | 2014-11-13 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-002-3(i)b (Ontario) | 79780000474 | R4. | 79780005582 | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  | Low |  | The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of the risk-based assessment methodology, the list of Critical Assets or the list of Critical Cyber Assets (even if such lists are null.) | The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of two of the following: the risk-based assessment methodology, the list of Critical Assets or the list of Critical Cyber Assets (even if such lists are null.) | The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s) annual approval of 1) A risk based assessment methodology for identification of Critical Assets, 2) a signed and dated approval of the list of Critical Assets, nor 3) a signed and dated approval of the list of Critical Cyber Assets (even if such lists are null.) |  |  |  | 2014-11-13 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-002-3(i) (Ontario) | 79780000469 | R1. | 79780005565 | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  | Medium | [7 empty] | 2014-11-13 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-002-3(i) (Ontario) | 79780000469 | R2. | 79780005566 | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  | High | [7 empty] | 2014-11-13 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-002-3(i) (Ontario) | 79780000469 | R3. | 79780005567 | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3(i), Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: See Standard for Requirement Parts. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  | High | [7 empty] | 2014-11-13 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-002-3(i) (Ontario) | 79780000469 | R4. | 79780005568 | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  | Low | [7 empty] | 2014-11-13 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-002-3 (Manitoba) | 77660000000222 | R1. | 776600000002713 | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets.. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. | 2012-04-01 |  | 2018-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | MRO-MB | [6 empty] | 10000000
CIP-002-3 (Manitoba) | 77660000000222 | R2. | 776600000002723 | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High |  |  |  |  | M2. The Responsible Entity shall make available its list of Critical Assets as specified in Requirement R2. | 2012-04-01 |  | 2018-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | MRO-MB | [6 empty] | 20000000
CIP-002-3 (Manitoba) | 77660000000222 | R3. | 776600000002724 | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High |  |  |  |  | M3. The Responsible Entity shall make available its list of Critical Cyber Assets as specified in Requirement R3. | 2012-04-01 |  | 2018-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | MRO-MB | [6 empty] | 30000000
CIP-002-3 (Manitoba) | 77660000000222 | R4. | 776600000002728 | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M4. The Responsible Entity shall make available its approval records of annual approvals as specified in Requirement R4. | 2012-04-01 |  | 2018-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | MRO-MB | [6 empty] | 40000000
CIP-002-3 (Ontario) | 79780000222 | R1. | 79780002713 | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M1. The Responsible Entity shall make available its current risk-based assessment methodology documentation as specified in Requirement R1. | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | NPCC-ON | [6 empty] | 10000000
CIP-002-3 (Ontario) | 79780000222 | R2. | 79780002723 | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High |  |  |  |  | M2. The Responsible Entity shall make available its list of Critical Assets as specified in Requirement R2. | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | NPCC-ON | [6 empty] | 20000000
CIP-002-3 (Ontario) | 79780000222 | R3. | 79780002724 | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High |  |  |  |  | M3. The Responsible Entity shall make available its list of Critical Cyber Assets as specified in Requirement R3. | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | NPCC-ON | [6 empty] | 30000000
CIP-002-3 (Ontario) | 79780000222 | R4. | 79780002728 | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M4. The Responsible Entity shall make available its approval records of annual approvals as specified in Requirement R4. | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | NPCC-ON | [6 empty] | 40000000
CIP-002-4 | 248 | R1. | 3215 | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the criteria contained in CIP-002-4 Attachment 1 – Critical Asset Criteria. The Responsible Entity shall update this list as necessary, and review it at least annually. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High | N/A | N/A | The Responsible Entity has developed a list of Critical Assets but the list has not been reviewed and updated annually as required. | The Responsible Entity did not develop a list of its identified Critical Assets even if such list is null. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-002-4 | 248 | R2. | 3216 | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R1, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. The Responsible Entity shall update this list as necessary, and review it at least annually. For each group of generating units (including nuclear generation) at a single plant location identified in Attachment 1, criterion 1.1, the only Cyber Assets that must be considered are those shared Cyber Assets that could, within 15 minutes, adversely impact the reliable operation of any combination of units that in aggregate equal or exceed Attachment 1, criterion 1.1. For the purpose of Standard CIP-002-4, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: • The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, • The Cyber Asset uses a routable protocol within a control center; or, • The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High | N/A | N/A | The Responsible Entity has developed a list of associated Critical Cyber Assets essential to the operation of the Critical Asset list as per requirement R2 but the list has not been reviewed and updated annually as required. | The Responsible Entity did not develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset list as per requirement R2 even if such list is null. OR A Cyber Asset essential to the operation of the Critical Asset was identified that met at least one of the bulleted characteristics in this requirement but was not included in the Critical Cyber Asset List. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-002-4 | 248 | R3. | 3217 | Annual Approval — The senior manager or delegate(s) shall approve annually the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1 and R2 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of the list of Critical Assets. OR The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of the list of Critical Cyber Assets (even if such lists are null.) | The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of both the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-002-4a | 330 | R1. | 4348 | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the criteria contained in CIP-002-4 Attachment 1 – Critical Asset Criteria. The Responsible Entity shall update this list as necessary, and review it at least annually. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High | N/A | N/A | The Responsible Entity has developed a list of Critical Assets but the list has not been reviewed and updated annually as required. | The Responsible Entity did not develop a list of its identified Critical Assets even if such list is null. |  |  |  | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-002-4a | 330 | R2. | 4349 | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R1, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. The Responsible Entity shall update this list as necessary, and review it at least annually. For each group of generating units (including nuclear generation) at a single plant location identified in Attachment 1, criterion 1.1, the only Cyber Assets that must be considered are those shared Cyber Assets that could, within 15 minutes, adversely impact the reliable operation of any combination of units that in aggregate equal or exceed Attachment 1, criterion 1.1. For the purpose of Standard CIP-002-4, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: • The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, • The Cyber Asset uses a routable protocol within a control center; or, • The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High | N/A | N/A | The Responsible Entity has developed a list of associated Critical Cyber Assets essential to the operation of the Critical Asset list as per requirement R2 but the list has not been reviewed and updated annually as required. | The Responsible Entity did not develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset list as per requirement R2 even if such list is null. OR A Cyber Asset essential to the operation of the Critical Asset was identified that met at least one of the bulleted characteristics in this requirement but was not included in the Critical Cyber Asset List. |  |  |  | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-002-4a | 330 | R3. | 4350 | Annual Approval — The senior manager or delegate(s) shall approve annually the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1 and R2 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of the list of Critical Assets. OR The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of the list of Critical Cyber Assets (even if such lists are null.) | The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of both the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  |  |  | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-002-4a (Ontario) | 79780000330 | R1. | 79780004348 | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the criteria contained in CIP-002-4 Attachment 1 – Critical Asset Criteria. The Responsible Entity shall update this list as necessary, and review it at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High | N/A | N/A | The Responsible Entity has developed a list of Critical Assets but the list has not been reviewed and updated annually as required. | The Responsible Entity did not develop a list of its identified Critical Assets even if such list is null. |  |  |  | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-002-4a (Ontario) | 79780000330 | R2. | 79780004349 | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R1, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. The Responsible Entity shall update this list as necessary, and review it at least annually. For each group of generating units (including nuclear generation) at a single plant location identified in Attachment 1, criterion 1.1, the only Cyber Assets that must be considered are those shared Cyber Assets that could, within 15 minutes, adversely impact the reliable operation of any combination of units that in aggregate equal or exceed Attachment 1, criterion 1.1. For the purpose of Standard CIP-002-4, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: • The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, • The Cyber Asset uses a routable protocol within a control center; or, • The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High | N/A | N/A | The Responsible Entity has developed a list of associated Critical Cyber Assets essential to the operation of the Critical Asset list as per requirement R2 but the list has not been reviewed and updated annually as required. | The Responsible Entity did not develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset list as per requirement R2 even if such list is null. OR A Cyber Asset essential to the operation of the Critical Asset wa |  |  |  | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-002-4a (Ontario) | 79780000330 | R3. | 79780004350 | Annual Approval — The senior manager or delegate(s) shall approve annually the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1 and R2 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of the list of Critical Assets. OR The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’ | The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of both the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  |  |  | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-002-4a (Saskatchewan) | 83750000000330 | R1. | 837500000004348 | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the criteria contained in CIP-002-4 Attachment 1 – Critical Asset Criteria. The Responsible Entity shall update this list as necessary, and review it at least annually. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High | N/A | N/A | The Responsible Entity has developed a list of Critical Assets but the list has not been reviewed and updated annually as required. | The Responsible Entity did not develop a list of its identified Critical Assets even if such list is null. |  | 2012-05-09 |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 10000000
CIP-002-4a (Saskatchewan) | 83750000000330 | R2. | 837500000004349 | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R1, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. The Responsible Entity shall update this list as necessary, and review it at least annually. For each group of generating units (including nuclear generation) at a single plant location identified in Attachment 1, criterion 1.1, the only Cyber Assets that must be considered are those shared Cyber Assets that could, within 15 minutes, adversely impact the reliable operation of any combination of units that in aggregate equal or exceed Attachment 1, criterion 1.1. For the purpose of Standard CIP-002-4, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: • The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, • The Cyber Asset uses a routable protocol within a control center; or, • The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High | N/A | N/A | The Responsible Entity has developed a list of associated Critical Cyber Assets essential to the operation of the Critical Asset list as per requirement R2 but the list has not been reviewed and updated annually as required. | The Responsible Entity did not develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset list as per requirement R2 even if such list is null. OR A Cyber Asset essential to the operation of the Critical Asset was identified that met at least one of the bulleted characteristics in this requirement but was not included in the Critical Cyber Asset List. |  | 2012-05-09 |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 20000000
CIP-002-4a (Saskatchewan) | 83750000000330 | R3. | 837500000004350 | Annual Approval — The senior manager or delegate(s) shall approve annually the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1 and R2 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of the list of Critical Assets. OR The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of the list of Critical Cyber Assets (even if such lists are null.) | The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of both the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | 2012-05-09 |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 30000000
CIP-002-4 (Ontario) | 79780000248 | R1. | 79780003215 | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the criteria contained in CIP-002-4 Attachment 1 – Critical Asset Criteria. The Responsible Entity shall update this list as necessary, and review it at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High | N/A | N/A | The Responsible Entity has developed a list of Critical Assets but the list has not been reviewed and updated annually as required. | The Responsible Entity did not develop a list of its identified Critical Assets even if such list is null. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-002-4 (Ontario) | 79780000248 | R2. | 79780003216 | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R1, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. The Responsible Entity shall update this list as necessary, and review it at least annually. For each group of generating units (including nuclear generation) at a single plant location identified in Attachment 1, criterion 1.1, the only Cyber Assets that must be considered are those shared Cyber Assets that could, within 15 minutes, adversely impact the reliable operation of any combination of units that in aggregate equal or exceed Attachment 1, criterion 1.1. For the purpose of Standard CIP-002-4, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: • The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, • The Cyber Asset uses a routable protocol within a control center; or, • The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | High | N/A | N/A | The Responsible Entity has developed a list of associated Critical Cyber Assets essential to the operation of the Critical Asset list as per requirement R2 but the list has not been reviewed and updated annually as required. | The Responsible Entity did not develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset list as per requirement R2 even if such list is null. OR A Cyber Asset essential to the operation of the Critical Asset wa |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-002-4 (Ontario) | 79780000248 | R3. | 79780003217 | Annual Approval — The senior manager or delegate(s) shall approve annually the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1 and R2 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of the list of Critical Assets. OR The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’ | The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of both the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-002-5 | 346 | R1. | 4480 | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3:[See Standard for sub-req's] i.Control Centers and backup Control Centers; ii.Transmission stations and substations; iii.Generation resources; iv.Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v.Special Protection Systems that support the reliable operation of the Bulk Electric System; and vi.For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | High | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, five percent or fewer BES assets have not been considered according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, 2 or fewer BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than five percent but less than or equal to 10 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than two, but fewer than or equal to four BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact and BES Cyber Systems, more than five but less than or equal to 10 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than five but less than or equal to 10 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 10 percent but less than or equal to 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than four, but fewer than or equal to six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high or medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high or medium impact and BES Cyber Assets, more than 10 but less than or equal to 15 identified BES Cyber Assets have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 10 but less than or equal to 15 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of high or medium impact BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 high or medium impact BES Cyber Systems have not been identified. |  |  |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-002-5 | 346 | R2. | 4481 | The Responsible Entity shall: [See Standard for sub-req's] |  | BA, GO, GOP, IA, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Low | The Responsible Entity did not complete its review and update for the identification required for R1 within 15 calendar months but less than or equal to 16 calendar months of the previous review. (R2.1) or The Responsible Entity did not complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 15 calendar months but less than or equal to 16 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 16 calendar months but less than or equal to 17 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 16 calendar months but less than or equal to 17 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 17 calendar months but less than or equal to 18 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 17 calendar months but less than or equal to 18 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 18 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 18 calendar months of the previous approval. (R2.2) |  |  |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-002-5.1 | 425 | R1. | 5243 | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3:[See Standard for sub-req's] i. Control Centers and backup Control Centers; ii. Transmission stations and substations; iii. Generation resources; iv. Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v. Special Protection Systems that support the reliable operation of the Bulk Electric System; and vi. For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. |  | BA, DP, DP-UFLS, GO, GOP, IA, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | High | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, five percent or fewer BES assets have not been considered according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, 2 or fewer BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than five percent but less than or equal to 10 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than two, but fewer than or equal to four BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact and BES Cyber Systems, more than five but less than or equal to 10 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than five but less than or equal to 10 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 10 percent but less than or equal to 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than four, but fewer than or equal to six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high or medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high or medium impact and BES Cyber Assets, more than 10 but less than or equal to 15 identified BES Cyber Assets have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 10 but less than or equal to 15 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of high or medium impact BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 high or medium impact BES Cyber Systems have not been identified. | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | 2016-07-01 |  | 2016-12-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-002-5.1 | 425 | R2. | 5244 | The Responsible Entity shall: [See Standard for sub-req's] |  | BA, DP, DP-UFLS, GO, GOP, IA, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not complete its review and update for the identification required for R1 within 15 calendar months but less than or equal to 16 calendar months of the previous review. (R2.1) or The Responsible Entity did not complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 15 calendar months but less than or equal to 16 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 16 calendar months but less than or equal to 17 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 16 calendar months but less than or equal to 17 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 17 calendar months but less than or equal to 18 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 17 calendar months but less than or equal to 18 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 18 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 18 calendar months of the previous approval. (R2.2) | M2. Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | 2016-07-01 |  | 2016-12-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-002-5.1a | 554 | R1. | 7843 | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3: i. Control Centers and backup Control Centers; ii. Transmission stations and substations; iii. Generation resources; iv. Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v. Special Protection Systems that support the reliable operation of the Bulk Electric System; and vi. For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. |  | BA, DP, DP-UFLS, GO, GOP, IA, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | High | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, five percent or fewer BES assets have not been considered according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, 2 or fewer BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than five percent but less than or equal to 10 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than two, but fewer than or equal to four BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact and BES Cyber Systems, more than five but less than or equal to 10 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than five but less than or equal to 10 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 10 percent but less than or equal to 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than four, but fewer than or equal to six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high or medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high or medium impact and BES Cyber Assets, more than 10 but less than or equal to 15 identified BES Cyber Assets have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 10 but less than or equal to 15 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of high or medium impact BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 high or medium impact BES Cyber Systems have not been identified. | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | 2016-12-27 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-002-5.1a | 554 | R2. | 7847 | The Responsible Entity shall: |  | BA, DP, DP-UFLS, GO, GOP, IA, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not complete its review and update for the identification required for R1 within 15 calendar months but less than or equal to 16 calendar months of the previous review. (R2.1) OR The Responsible Entity did not complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 15 calendar months but less than or equal to 16 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 16 calendar months but less than or equal to 17 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 16 calendar months but less than or equal to 17 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 17 calendar months but less than or equal to 18 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 17 calendar months but less than or equal to 18 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 18 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 18 calendar months of the previous approval. (R2.2) | M2. Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | 2016-12-27 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-002-5.1a (British Columbia) | 666700000010031 | R1. | 666700000010520 | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3: i. Control Centers and backup Control Centers; ii. Transmission stations and substations; iii. Generation resources; iv. Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v. Special Protection Systems that support the reliable operation of the Bulk Electric System; and vi. For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. |  | BA, DP, DP-UFLS, GO, GOP, IA, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | High | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, five percent or fewer BES assets have not been considered according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, 2 or fewer BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than five percent but less than or equal to 10 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than two, but fewer than or equal to four BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact and BES Cyber Systems, more than five but less than or equal to 10 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than five but less than or equal to 10 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 10 percent but less than or equal to 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than four, but fewer than or equal to six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high or medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high or medium impact and BES Cyber Assets, more than 10 but less than or equal to 15 identified BES Cyber Assets have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 10 but less than or equal to 15 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of high or medium impact BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 high or medium impact BES Cyber Systems have not been identified. | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | 2018-10-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | WECC-BC | [6 empty] | 10000000
CIP-002-5.1a (British Columbia) | 666700000010031 | R2. | 666700000010521 | The Responsible Entity shall: |  | BA, DP, DP-UFLS, GO, GOP, IA, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not complete its review and update for the identification required for R1 within 15 calendar months but less than or equal to 16 calendar months of the previous review. (R2.1) OR The Responsible Entity did not complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 15 calendar months but less than or equal to 16 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 16 calendar months but less than or equal to 17 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 16 calendar months but less than or equal to 17 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 17 calendar months but less than or equal to 18 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 17 calendar months but less than or equal to 18 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 18 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 18 calendar months of the previous approval. (R2.2) | M2. Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | 2018-10-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | WECC-BC | [6 empty] | 20000000
CIP-002-5.1a (Manitoba) | 77660000000554 | R1. | 776600000007843 | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3: i. Control Centers and backup Control Centers; ii. Transmission stations and substations; iii. Generation resources; iv. Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v. Special Protection Systems that support the reliable operation of the Bulk Electric System; and vi. For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. |  | BA, DP, DP-UFLS, GO, GOP, IA, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | High | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, five percent or fewer BES assets have not been considered according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, 2 or fewer BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than five percent but less than or equal to 10 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than two, but fewer than or equal to four BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact and BES Cyber Systems, more than five but less than or equal to 10 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than five but less than or equal to 10 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 10 percent but less than or equal to 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than four, but fewer than or equal to six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high or medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high or medium impact and BES Cyber Assets, more than 10 but less than or equal to 15 identified BES Cyber Assets have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 10 but less than or equal to 15 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of high or medium impact BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 high or medium impact BES Cyber Systems have not been identified. | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | 2018-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-MB | [6 empty] | 10000000
CIP-002-5.1a (Manitoba) | 77660000000554 | R2. | 776600000007847 | The Responsible Entity shall: |  | BA, DP, DP-UFLS, GO, GOP, IA, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not complete its review and update for the identification required for R1 within 15 calendar months but less than or equal to 16 calendar months of the previous review. (R2.1) OR The Responsible Entity did not complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 15 calendar months but less than or equal to 16 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 16 calendar months but less than or equal to 17 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 16 calendar months but less than or equal to 17 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 17 calendar months but less than or equal to 18 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 17 calendar months but less than or equal to 18 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 18 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 18 calendar months of the previous approval. (R2.2) | M2. Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | 2018-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-MB | [6 empty] | 20000000
CIP-002-5.1a (Nova Scotia) | 78830000000554 | R1. | 788300000007843 | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3: i. Control Centers and backup Control Centers; ii. Transmission stations and substations; iii. Generation resources; iv. Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v. Special Protection Systems that support the reliable operation of the Bulk Electric System; and vi. For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. |  | BA, DP, DP-UFLS, GO, GOP, IA, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | High | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, five percent or fewer BES assets have not been considered according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, 2 or fewer BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than five percent but less than or equal to 10 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than two, but fewer than or equal to four BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact and BES Cyber Systems, more than five but less than or equal to 10 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than five but less than or equal to 10 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 10 percent but less than or equal to 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than four, but fewer than or equal to six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high or medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high or medium impact and BES Cyber Assets, more than 10 but less than or equal to 15 identified BES Cyber Assets have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 10 but less than or equal to 15 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of high or medium impact BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 high or medium impact BES Cyber Systems have not been identified. | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | 2016-10-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-NS | [6 empty] | 10000000
CIP-002-5.1a (Nova Scotia) | 78830000000554 | R2. | 788300000007847 | The Responsible Entity shall: |  | BA, DP, DP-UFLS, GO, GOP, IA, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not complete its review and update for the identification required for R1 within 15 calendar months but less than or equal to 16 calendar months of the previous review. (R2.1) OR The Responsible Entity did not complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 15 calendar months but less than or equal to 16 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 16 calendar months but less than or equal to 17 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 16 calendar months but less than or equal to 17 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 17 calendar months but less than or equal to 18 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 17 calendar months but less than or equal to 18 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 18 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 18 calendar months of the previous approval. (R2.2) | M2. Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | 2016-10-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-NS | [6 empty] | 20000000
CIP-002-5.1a (Ontario) | 79780000554 | R1. | 79780007843 | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3: &lt;br/&gt;i. Control Centers and backup Control Centers; &lt;br/&gt;ii. Transmission stations and substations;&lt;br/&gt;iii. Generation resources;&lt;br/&gt;iv. Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; &lt;br/&gt;v. Special Protection Systems that support the reliable operation of the Bulk Electric System; and&lt;br/&gt;vi. For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | High | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, five percent or fewer BES assets have not been considered according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, 2 or fewer BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than five percent but less than or equal to 10 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than two, but fewer than or equal to four BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact and BES Cyber Systems, more than five but less than or equal to 10 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than five but less than or equal to 10 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 10 percent but less than or equal to 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than four, but fewer than or equal to six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high or medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high or medium impact and BES Cyber Assets, more than 10 but less than or equal to 15 identified BES Cyber Assets have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 10 but less than or equal to 15 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of high or medium impact BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 high or medium impact BES Cyber Systems have not been identified. | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | 2016-12-27 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-ON | [6 empty] | 10000000
CIP-002-5.1a (Ontario) | 79780000554 | R2. | 79780007847 | The Responsible Entity shall: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not complete its review and update for the identification required for R1 within 15 calendar months but less than or equal to 16 calendar months of the previous review. (R2.1) OR The Responsible Entity did not complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 15 calendar months but less than or equal to 16 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 16 calendar months but less than or equal to 17 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 16 calendar months but less than or equal to 17 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 17 calendar months but less than or equal to 18 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 17 calendar months but less than or equal to 18 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 18 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 18 calendar months of the previous approval. (R2.2) | M2. Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | 2016-12-27 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-ON | [6 empty] | 20000000
CIP-002-5.1a (Saskatchewan) | 83750000000554 | R1. | 837500000007843 | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3: i. Control Centers and backup Control Centers; ii. Transmission stations and substations; iii. Generation resources; iv. Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v. Special Protection Systems that support the reliable operation of the Bulk Electric System; and vi. For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. |  | BA, DP, DP-UFLS, GO, GOP, IA, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | High | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, five percent or fewer BES assets have not been considered according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, 2 or fewer BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than five percent but less than or equal to 10 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than two, but fewer than or equal to four BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact and BES Cyber Systems, more than five but less than or equal to 10 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than five but less than or equal to 10 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 10 percent but less than or equal to 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than four, but fewer than or equal to six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high or medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high or medium impact and BES Cyber Assets, more than 10 but less than or equal to 15 identified BES Cyber Assets have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 10 but less than or equal to 15 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of high or medium impact BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 high or medium impact BES Cyber Systems have not been identified. | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | 2017-10-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-SK | [6 empty] | 10000000
CIP-002-5.1a (Saskatchewan) | 83750000000554 | R2. | 837500000007847 | The Responsible Entity shall: |  | BA, DP, DP-UFLS, GO, GOP, IA, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not complete its review and update for the identification required for R1 within 15 calendar months but less than or equal to 16 calendar months of the previous review. (R2.1) OR The Responsible Entity did not complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 15 calendar months but less than or equal to 16 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 16 calendar months but less than or equal to 17 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 16 calendar months but less than or equal to 17 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 17 calendar months but less than or equal to 18 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 17 calendar months but less than or equal to 18 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 18 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 18 calendar months of the previous approval. (R2.2) | M2. Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | 2017-10-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-SK | [6 empty] | 20000000
CIP-002-5.1 (British Columbia) | 666700000010030 | R1. | 666700000010518 | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3:[See Standard for sub-req's] i. Control Centers and backup Control Centers; ii. Transmission stations and substations; iii. Generation resources; iv. Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v. Special Protection Systems that support the reliable operation of the Bulk Electric System; and vi. For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. |  | BA, DP, DP-UFLS, GO, GOP, IA, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | High | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, five percent or fewer BES assets have not been considered according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, 2 or fewer BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than five percent but less than or equal to 10 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than two, but fewer than or equal to four BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact and BES Cyber Systems, more than five but less than or equal to 10 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than five but less than or equal to 10 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 10 percent but less than or equal to 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than four, but fewer than or equal to six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high or medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high or medium impact and BES Cyber Assets, more than 10 but less than or equal to 15 identified BES Cyber Assets have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 10 but less than or equal to 15 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of high or medium impact BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 high or medium impact BES Cyber Systems have not been identified. | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | 2018-10-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-002-5.1 (British Columbia) | 666700000010030 | R2. | 666700000010519 | The Responsible Entity shall: [See Standard for sub-req's] |  | BA, DP, DP-UFLS, GO, GOP, IA, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not complete its review and update for the identification required for R1 within 15 calendar months but less than or equal to 16 calendar months of the previous review. (R2.1) or The Responsible Entity did not complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 15 calendar months but less than or equal to 16 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 16 calendar months but less than or equal to 17 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 16 calendar months but less than or equal to 17 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 17 calendar months but less than or equal to 18 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 17 calendar months but less than or equal to 18 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 18 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 18 calendar months of the previous approval. (R2.2) | M2. Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | 2018-10-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 20000000
CIP-002-5.1 (Ontario) | 79780000425 | R1. | 79780005243 | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3:[See Standard for sub-req's] |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | High | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, five percent or fewer BES assets have not been considered according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, 2 or fewer BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than five percent but less than or equal to 10 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than two, but fewer than or equal to four BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact and BES Cyber Systems, more than five but less than or equal to 10 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than five but less than or equal to 10 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 10 percent but less than or equal to 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than four, but fewer than or equal to six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high or medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high or medium impact and BES Cyber Assets, more than 10 but less than or equal to 15 identified BES Cyber Assets have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 10 but less than or equal to 15 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of high or medium impact BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 high or medium impact BES Cyber Systems have not been identified. | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | 2016-07-01 |  | 2016-12-26 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-002-5.1 (Ontario) | 79780000425 | R2. | 79780005244 | The Responsible Entity shall: [See Standard for sub-req's] |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not complete its review and update for the identification required for R1 within 15 calendar months but less than or equal to 16 calendar months of the previous review. (R2.1) or The Responsible Entity did not complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 15 calendar months but less than or equal to 16 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 16 calendar months but less than or equal to 17 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 16 calendar months but less than or equal to 17 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 17 calendar months but less than or equal to 18 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 17 calendar months but less than or equal to 18 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 18 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 18 calendar months of the previous approval. (R2.2) | M2. Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | 2016-07-01 |  | 2016-12-26 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-002-5.1 (Saskatchewan) | 83750000000425 | R1. | 837500000005243 | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3:[See Standard for sub-req's] i. Control Centers and backup Control Centers; ii. Transmission stations and substations; iii. Generation resources; iv. Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v. Special Protection Systems that support the reliable operation of the Bulk Electric System; and vi. For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. |  | BA, DP, DP-UFLS, GO, GOP, IA, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | High | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, five percent or fewer BES assets have not been considered according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, 2 or fewer BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than five percent but less than or equal to 10 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than two, but fewer than or equal to four BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact and BES Cyber Systems, more than five but less than or equal to 10 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than five but less than or equal to 10 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 10 percent but less than or equal to 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than four, but fewer than or equal to six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high or medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high or medium impact and BES Cyber Assets, more than 10 but less than or equal to 15 identified BES Cyber Assets have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 10 but less than or equal to 15 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of high or medium impact BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 high or medium impact BES Cyber Systems have not been identified. | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | 2016-07-01 |  | 2017-09-30 |  |  |  | MRO-SK | [6 empty] | 10000000
CIP-002-5.1 (Saskatchewan) | 83750000000425 | R2. | 837500000005244 | The Responsible Entity shall: [See Standard for sub-req's] |  | BA, DP, DP-UFLS, GO, GOP, IA, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not complete its review and update for the identification required for R1 within 15 calendar months but less than or equal to 16 calendar months of the previous review. (R2.1) or The Responsible Entity did not complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 15 calendar months but less than or equal to 16 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 16 calendar months but less than or equal to 17 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 16 calendar months but less than or equal to 17 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 17 calendar months but less than or equal to 18 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 17 calendar months but less than or equal to 18 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 18 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 18 calendar months of the previous approval. (R2.2) | M2. Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | 2016-07-01 |  | 2017-09-30 |  |  |  | MRO-SK | [6 empty] | 20000000
CIP-002-5 (Ontario) | 79780000346 | R1. | 79780004480 | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3:[See Standard for sub-req's] |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | High | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, five percent or fewer BES assets have not been considered according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, 2 or fewer BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than five percent but less than or equal to 10 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than two, but fewer than or equal to four BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact and BES Cyber Systems, more than five but less than or equal to 10 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than five but less than or equal to 10 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 10 percent but less than or equal to 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than four, but fewer than or equal to six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high or medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high or medium impact and BES Cyber Assets, more than 10 but less than or equal to 15 identified BES Cyber Assets have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 10 but less than or equal to 15 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of high or medium impact BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 high or medium impact BES Cyber Systems have not been identified. |  |  |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-002-5 (Ontario) | 79780000346 | R2. | 79780004481 | The Responsible Entity shall: [See Standard for sub-req's] |  | BA, GO, GOP, IA, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Low | The Responsible Entity did not complete its review and update for the identification required for R1 within 15 calendar months but less than or equal to 16 calendar months of the previous review. (R2.1) or The Responsible Entity did not complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 15 calendar months but less than or equal to 16 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 16 calendar months but less than or equal to 17 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 16 calendar months but less than or equal to 17 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 17 calendar months but less than or equal to 18 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 17 calendar months but less than or equal to 18 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 18 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 18 calendar months of the previous approval. (R2.2) |  |  |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-002-6 | 624 | R1. | 9253 | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3: i. Control Centers and backup Control Centers; ii. Transmission stations and substations; iii. Generation resources; iv. Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v. Remedial Action Schemes that support the reliable operation of the Bulk Electric System; and vi. For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | High | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, five percent or fewer BES assets have not been considered according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, 2 or fewer BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact and BES Cyber Systems, more than five but less than or equal to 10 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than five but less than or equal to 10 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 100 high or medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high or medium impact and BES Cyber Assets, more than 10 but less than or equal to 15 identified BES Cyber Assets have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 10 but less than or equal to 15 high or medium BES Cyber Systems have not been identified. | Systems, more than 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of high or medium impact BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 high or medium impact BES Cyber Systems have not been identified. | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. |  |  | 2021-02-04 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-002-6 | 624 | R2. | 9257 | Each Responsible Entity shall: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not complete its review and update for the identification required for R1 within 15 calendar months but less than or equal to 16 calendar months of the previous review. (R2.1) OR The Responsible Entity did not complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 15 calendar months but less than or equal to 16 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 16 calendar months but less than or equal to 17 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 16 calendar months but less than or equal to 17 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 17 calendar months but less than or equal to 18 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 17 calendar months but less than or equal to 18 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 18 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 18 calendar months of the previous approval. (R2.2) | Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. |  |  | 2021-02-04 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-002-6 (Ontario) | 79780000624 | R1. | 79780009253 | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3: &lt;br/&gt;i. Control Centers and backup Control Centers; &lt;br/&gt;ii. Transmission stations and substations;&lt;br/&gt;iii. Generation resources;&lt;br/&gt;iv. Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; &lt;br/&gt;v. Remedial Action Schemes that support the reliable operation of the Bulk Electric System; and&lt;br/&gt;vi. For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | High | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, five percent or fewer BES assets have not been considered according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, 2 or fewer BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact and BES Cyber Systems, more than five but less than or equal to 10 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than five but less than or equal to 10 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 100 high or medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high or medium impact and BES Cyber Assets, more than 10 but less than or equal to 15 identified BES Cyber Assets have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 10 but less than or equal to 15 high or medium BES Cyber Systems have not been identified. | Systems, more than 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of high or medium impact BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 high or medium impact BES Cyber Systems have not been identified. | M1. Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. |  |  | 2021-02-04 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-002-6 (Ontario) | 79780000624 | R2. | 79780009257 | Each Responsible Entity shall: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not complete its review and update for the identification required for R1 within 15 calendar months but less than or equal to 16 calendar months of the previous review. (R2.1) OR The Responsible Entity did not complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 15 calendar months but less than or equal to 16 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 16 calendar months but less than or equal to 17 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 16 calendar months but less than or equal to 17 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 17 calendar months but less than or equal to 18 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 17 calendar months but less than or equal to 18 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 18 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 18 calendar months of the previous approval. (R2.2) | &lt;p&gt;Acceptable evidence includes, but is not limited to, electronic or physical dated&lt;br/&gt;records to demonstrate that the Responsible Entity has reviewed and updated, where&lt;br/&gt;necessary, the identifications required in Requirement R1 and its parts, and has had its&lt;br/&gt;CIP Senior Manager or delegate approve the identifications required in Requirement&lt;br/&gt;R1 and its parts at least once every 15 calendar months, even if it has none identified&lt;br/&gt;in Requirement R1 and its parts, as required by Requirement R2.&lt;/p&gt; |  |  | 2021-02-04 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-002-7 | ST-2024-05-09-0000002 | R1. | RQ-2024-05-09-0000004 | i. Control Centers and backup Control Centers; ii. Transmission stations and substations; iii. Generation resources; iv. Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v. RAS that support the reliable operation of the BES; and vi. For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | High | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, five percent or fewer BES assets have not been considered according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, 2 or fewer BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BCS, five percent or fewer of identified BCS have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BCS, five or fewer identified BCS have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BCS, five percent or fewer high or medium BCS have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BCS, five or fewer high or medium BCS have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than five percent but less than or equal to 10 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than two, but fewer than or equal to four BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BCS, more than five percent but less than or equal to 10 percent of identified BCS have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BCS, more than five but less than or equal to 10 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BCS, more than five percent but less than or equal to 10 percent high or medium BCS have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BCS, more than five but less than or equal to 10 high or medium BCS have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 10 percent but less than or equal to 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than four, but fewer than or equal to six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high or medium impact BCS, more than 10 percent but less than or equal to 15 percent of identified BCS have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high or medium impact BCS, more than 10 but less than or equal to 15 identified BCS have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BCS, more than 10 percent but less than or equal to 15 percent high or medium BCS have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BCS, more than 10 but less than or equal to 15 high or medium BCS have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BCS, more than 15 percent of identified BCS have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BCS, more than 15 identified BCS have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BCS, more than 15 percent of high or medium impact BCS have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 high or medium impact BCS have not been identified. | Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-002-7 | ST-2024-05-09-0000002 | R2. | RQ-2024-05-09-0000005 | Each Responsible Entity shall: |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not complete its review and update for the identification required for Requirement R1 within 15 calendar months but less than or equal to 16 calendar months of the previous review. (Part 2.1) OR The Responsible Entity did not complete its approval of the identifications required by Requirement R1 by the CIP Senior Manager or delegate according to Requirement R2 within 15 calendar months but less than or equal to 16 calendar months of the previous approval. (Part 2.2) | The Responsible Entity did not complete its review and update for the identification required for Requirement R1 within 16 calendar months but less than or equal to 17 calendar months of the previous review. (Part2.1) OR The Responsible Entity failed to complete its approval of the identifications required by Requirement R1 by the CIP Senior Manager or delegate according to Requirement R2 within 16 calendar months but less than or equal to 17 calendar months of the previous approval. (Part 2.2) | The Responsible Entity did not complete its review and update for the identification required for Requirement R1 within 17 calendar months but less than or equal to 18 calendar months of the previous review. (Part 2.1) OR The Responsible Entity failed to complete its approval of the identifications required by Requirement R1 by the CIP Senior Manager or delegate according to Requirement R2 within 17 calendar months but less than or equal to 18 calendar months of the previous approval. (Part 2.2) | The Responsible Entity did not complete its review and update for the identification required for Requirement R1 within 18 calendar months of the previous review. (Part 2.1) OR The Responsible Entity failed to complete its approval of the identifications required by Requirement R1 by the CIP Senior Manager or delegate according to Requirement R2 within 18 calendar months of the previous approval. (Part 2.2) | Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-002-AB-5.1 (Alberta) | 656600000009006 | R1. | 656600000009090 | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3: (i) control centres and backup control centres; (ii) transmission stations and substations; (iii) generating units and aggregated generating facilities; (iv) systems and facilities critical to system restoration, including contracted blackstart resources and cranking paths and initial switching requirements; (v) remedial action schemes that support the reliable operation of the bulk electric system; and (vi) for the legal owner of an electric distribution system or legal owner of a transmission facility, protection systems specified in Applicability subsection 4.2.1 above. |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 10000000
CIP-002-AB-5.1 (Alberta) | 656600000009006 | R2. | 656600000009091 | The Responsible Entity shall: |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 20000000
CIP-003-1 | 24 | R1. | 260 | Cyber Security Policy - The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-003-1 | 24 | R2. | 264 | Leadership - The Responsible Entity shall assign a senior manager with overall responsibility for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002 through CIP-009 |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-003-1 | 24 | R3. | 268 | Exceptions - Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-003-1 | 24 | R4. | 272 | Information Protection - The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-003-1 | 24 | R5. | 276 | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-003-1 | 24 | R6. | 282 | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendorrelated changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-003-10 | ST-2024-05-10-0000001 | R1. | RQ-2024-05-10-0000001 | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity did not address one of the nine topics required by Requirement R1. (Part 1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BCS as required by Requirement R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (Part 1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BCS as required by Requirement R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (Part 1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BCS, but did not address one of the seven topics required by Requirement R1. (Part 1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BCS as required by Requirement R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (Part 1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BCS as required by Requirement R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (Part 1.2) | The Responsible Entity did not address two of the nine topics required by Requirement R1. (Part 1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BCS as required by Requirement R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (Part 1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BCS as required by Requirement R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (Part 1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BCS, but did not address two of the seven topics required by Requirement R1. (Part 1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BCS as required by Requirement R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (Part 1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BCS as required by Requirement R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (Part 1.2) | The Responsible Entity did not address three of the nine topics required by Requirement R1. (Part 1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BCS as required by Requirement R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (Part 1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BCS as required by Requirement R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (Requirement R1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BCS, but did not address three of the seven topics required by Requirement R1. (Part 1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BCS as required by Requirement R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (Part 1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BCS as required by Requirement R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (Part 1.2) | The Responsible Entity did not address four or more of the nine topics required by Requirement R1. (Part 1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BCS as required by Requirement R1. (Part 1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies as required by Requirement R1 within 18 calendar months of the previous review. (Requirement R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BCS as required by Requirement R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (Part 1.1) OR The Responsible Entity did not address four or more of the seven topics required by Requirement R1. (Part 1.2) OR The Responsible Entity did not have any documented cyber security policies for its assets identified in CIP-002 containing low impact BCS as required by Requirement R1. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BCS as required by Requirement R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.2) | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-003-10 | ST-2024-05-10-0000001 | R2. | RQ-2024-05-10-0000002 | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BCS shall implement one or more documented cyber security plan(s) for its low impact BCS, and Shared Cyber Infrastructure (SCI) that supports a low impact BCS, that include the sections in Attachment 1. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity failed to document cyber security awareness according to Requirement R2, Attachment 1, Section 1. (Requirement R2) OR The Responsible Entity failed to document its cyber security plan(s) for electronic access controls according to Requirement R2, Attachment 1, Section 3. (Requirement R2) OR The Responsible Entity failed to document one or more Cyber Security Incident response plan(s) according to Requirement R2, Attachment 1, Section 4. (Requirement R2) OR The Responsible Entity failed to update each Cyber Security Incident response plan(s) within 180 days according to Requirement R2, Attachment 1, Section 4. (Requirement R2) OR The Responsible Entity failed to manage its Transient Cyber Asset(s) according to Requirement R2, Attachment 1, Section 5.1. (Requirement R2) OR The Responsible Entity failed to document the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (Requirement R2) OR The Responsible Entity implemented vendor electronic remote access security controls but failed to document its cyber security process for vendor electronic remote access security controls according to Requirement R2, Attachment 1, Section 6. (Requirement R2) | The Responsible Entity failed to reinforce cyber security practices at least once every 15 calendar months according to Requirement R2, Attachment 1, Section 1. (Requirement R2) OR The Responsible Entity failed to document physical security controls according to Requirement R2, Attachment 1, Section 2. (Requirement R2) OR The Responsible Entity failed to document electronic access controls according to Requirement R2, Attachment 1, Section 3. (Requirement R2) OR The Responsible Entity failed to implement authentication for all Dial-up Connectivity according to Requirement R2, Attachment 1, Section 3.2 (Requirement R2) OR The Responsible Entity failed to include the process for identification, classification, and response to Cyber Security Incidents according to Requirement R2, Attachment 1, Section 4. (Requirement R2) OR The Responsible Entity failed to document the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident and subsequent notification to the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (Requirement R2) OR The Responsible Entity failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Sections 5.1 and 5.3. (Requirement R2) OR The Responsible Entity failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (Requirement R2) OR The Responsible Entity failed to implement the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (Requirement R2) OR The Responsible Entity documented its cyber security process for vendor electronic remote access security controls, but failed to implement vendor electronic remote access security controls according to Requirement R2. Attachment 1, Section 6. (Requirement R2) | The Responsible Entity failed to implement the physical security controls according to Requirement R2, Attachment 1, Section 2. (Requirement R2) OR The Responsible Entity failed to permit only necessary inbound and outbound electronic access controls according to Requirement R2, Attachment 1, Section 3.1. (Requirement R2) OR The Responsible Entity documented failed to test each Cyber Security Incident response plan(s) at least once every 36 calendar months according to Requirement R2, Attachment 1, Section 4. (Requirement R2) OR The Responsible Entity failed to notify the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (Requirement R2) OR The Responsible Entity failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Section 5.1. (Requirement R2) OR The Responsible Entity failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (Requirement R2) OR The Responsible Entity failed to implement mitigation for the threat of detected malicious code on the Removable Media prior to connecting Removable Media according to Requirement R2, Attachment 1, Section 5.3. (Requirement R2) OR The Responsible Entity failed to document and implement its cyber security process for vendor electronic remote access security controls according to Requirement R2, Attachment 1, Section 6. (Requirement R2) | The Responsible Entity failed to document and implement one or more cyber security plan(s) according to Requirement R2, Attachment 1. (Requirement R2) | Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-003-10 | ST-2024-05-10-0000001 | R3. | RQ-2024-05-10-0000003 | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar day of the change. (Requirement R3) | The Responsible Entity did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (Requirement R3) | The Responsible Entity did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (Requirement R3) | The Responsible Entity did not identify, by name, a CIP Senior Manager. OR The Responsible Entity did not document changes to the CIP Senior Manager within 60 calendar days of the change. (Requirement R3) | An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-003-10 | ST-2024-05-10-0000001 | R4. | RQ-2024-05-10-0000004 | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (Requirement R4) | The Responsible Entity did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (Requirement R4) | The Responsible Entity did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (Requirement R4) | The Responsible Entity does not have a process to delegate actions from the CIP Senior Manager. (Requirement R4) OR The Responsible Entity did not document changes to the delegate within 60 calendar days of the change. (Requirement R4) | An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-003-1 (British Columbia) | 666700000010032 | R1. | 666700000010522 | Cyber Security Policy - The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-003-1 (British Columbia) | 666700000010032 | R2. | 666700000010523 | Leadership - The Responsible Entity shall assign a senior manager with overall responsibility for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002 through CIP-009 |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 20000000
CIP-003-1 (British Columbia) | 666700000010032 | R3. | 666700000010524 | Exceptions - Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 30000000
CIP-003-1 (British Columbia) | 666700000010032 | R4. | 666700000010525 | Information Protection - The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 40000000
CIP-003-1 (British Columbia) | 666700000010032 | R5. | 666700000010526 | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 50000000
CIP-003-1 (British Columbia) | 666700000010032 | R6. | 666700000010527 | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendorrelated changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 60000000
CIP-003-1 (Ontario) | 79780000024 | R1. | 79780000260 | Cyber Security Policy - The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | The Responsible Entity has documented but not implemented a cyber security policy. | The Responsible Entity has not documented nor implemented a cyber security policy. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-003-1 (Ontario) | 79780000024 | R2. | 79780000264 | Leadership - The Responsible Entity shall assign a senior manager with overall responsibility for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002 through CIP-009 |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity has not assigned a senior manager with overall responsibility for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002 through CIP-009. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-003-1 (Ontario) | 79780000024 | R3. | 79780000268 | Exceptions - Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | In Instances where the Responsible Entity cannot conform to its cyber security policy (pertaining to CIP 002 through CIP 009), exceptions were documented, but were not authorized by the senior manager or delegate(s). | In Instances where the Responsible Entity cannot conform to its cyber security policy (pertaining to CIP 002 through CIP 009), exceptions were not documented, and were not authorized by the senior manager or delegate(s). |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-003-1 (Ontario) | 79780000024 | R4. | 79780000272 | Information Protection - The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity implemented but did not document a program to identify, classify, and protect information associated with Critical Cyber Assets. | The Responsible Entity documented but did not implement a program to identify, classify, and protect information associated with Critical Cyber Assets. | The Responsible Entity did not implement nor document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-003-1 (Ontario) | 79780000024 | R5. | 79780000276 | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | N/A | The Responsible Entity implemented but did not document a program for managing access to protected Critical Cyber Asset information. | The Responsible Entity documented but did not implement a program for managing access to protected Critical Cyber Asset information. | The Responsible Entity did not implement nor document a program for managing access to protected Critical Cyber Asset information. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-003-1 (Ontario) | 79780000024 | R6. | 79780000282 | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendorrelated changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity has established but not documented a change control process&lt;br/&gt;OR&lt;br/&gt;The Responsible Entity has established but not documented a configuration management process. | The Responsible Entity has established but not documented both a change control process and configuration management process. | The Responsible Entity has not established and documented a change control process &lt;br/&gt;OR &lt;br/&gt;The Responsible Entity has not established and documented a configuration management process. | The Responsible Entity has not established and documented a change control process&lt;br/&gt;AND&lt;br/&gt;The Responsible Entity has not established and documented a configuration management process. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-003-2 | 209 | R1. | 2370 | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-003-2 | 209 | R2. | 2374 | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-2 through CIP-009-2. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-003-2 | 209 | R3. | 2379 | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-003-2 | 209 | R4. | 2383 | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-003-2 | 209 | R5. | 2387 | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  | CIP-003-1 R5. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-003-2 | 209 | R6. | 2393 | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-003-2 (Ontario) | 79780000209 | R1. | 79780002370 | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-003-2 (Ontario) | 79780000209 | R2. | 79780002374 | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-2 through CIP-009-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-003-2 (Ontario) | 79780000209 | R3. | 79780002379 | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-003-2 (Ontario) | 79780000209 | R4. | 79780002383 | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-003-2 (Ontario) | 79780000209 | R5. | 79780002387 | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-003-2 (Ontario) | 79780000209 | R6. | 79780002393 | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-003-3 | 223 | R1. | 2729 | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M1. The Responsible Entity shall make available documentation of its cyber security policy as specified in Requirement R1. Additionally, the Responsible Entity shall demonstrate that the cyber security policy is available as specified in Requirement R1.2. (Retirement approved by FERC effective January 21, 2014.) | 2010-10-01 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-003-3 | 223 | R2. | 2733 | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M2. The Responsible Entity shall make available documentation of the assignment of, and changes to, its leadership as specified in Requirement R2. | 2010-10-01 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-003-3 | 223 | R3. | 2738 | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | The Responsible Entity shall make available documentation of the exceptions, as specified in Requirement R3. (Retirement approved by FERC effective January 21, 2014.) | 2010-10-01 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-003-3 | 223 | R4. | 2742 | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M4. The Responsible Entity shall make available documentation of its information protection program as specified in Requirement R4. | 2010-10-01 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-003-3 | 223 | R5. | 2746 | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M5. The Responsible Entity shall make available its access control documentation as specified in Requirement R5. | 2010-10-01 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-003-3 | 223 | R6. | 2752 | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M6. The Responsible Entity shall make available its change control and configuration management documentation as specified in Requirement R6. | 2010-10-01 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-003-3a | 430 | R1. | 5266 | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M1. The Responsible Entity shall make available documentation of its cyber security policy as specified in Requirement R1. Additionally, the Responsible Entity shall demonstrate that the cyber security policy is available as specified in Requirement R1.2. (Retirement approved by FERC effective January 21, 2014.) |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-003-3a | 430 | R2. | 5265 | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M2. The Responsible Entity shall make available documentation of the assignment of, and changes to, its leadership as specified in Requirement R2. |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-003-3a | 430 | R3. | 5268 | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M3. The Responsible Entity shall make available documentation of the exceptions, as specified in Requirement R3. (Retirement approved by FERC effective January 21, 2014.) |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-003-3a | 430 | R4. | 5264 | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M4. The Responsible Entity shall make available documentation of its information protection program as specified in Requirement R4. |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-003-3a | 430 | R5. | 5269 | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M5. The Responsible Entity shall make available its access control documentation as specified in Requirement R5. |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-003-3a | 430 | R6. | 5267 | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M6. The Responsible Entity shall make available its change control and configuration management documentation as specified in Requirement R6. |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-003-3a (Ontario) | 79780000430 | R1. | 79780005266 | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M1. The Responsible Entity shall make available documentation of its cyber security policy as specified in Requirement R1. Additionally, the Responsible Entity shall demonstrate that the cyber security policy is available as specified in Requirement R1.2. (Retirement approved by FERC effective January 21, 2014.) |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | NPCC-ON | [6 empty] | 10000000
CIP-003-3a (Ontario) | 79780000430 | R2. | 79780005265 | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M2. The Responsible Entity shall make available documentation of the assignment of, and changes to, its leadership as specified in Requirement R2. |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | NPCC-ON | [6 empty] | 20000000
CIP-003-3a (Ontario) | 79780000430 | R3. | 79780005268 | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M3. The Responsible Entity shall make available documentation of the exceptions, as specified in Requirement R3. (Retirement approved by FERC effective January 21, 2014.) |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | NPCC-ON | [6 empty] | 30000000
CIP-003-3a (Ontario) | 79780000430 | R4. | 79780005264 | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M4. The Responsible Entity shall make available documentation of its information protection program as specified in Requirement R4. |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | NPCC-ON | [6 empty] | 40000000
CIP-003-3a (Ontario) | 79780000430 | R5. | 79780005269 | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M5. The Responsible Entity shall make available its access control documentation as specified in Requirement R5. |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | NPCC-ON | [6 empty] | 50000000
CIP-003-3a (Ontario) | 79780000430 | R6. | 79780005267 | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M6. The Responsible Entity shall make available its change control and configuration management documentation as specified in Requirement R6. |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | NPCC-ON | [6 empty] | 60000000
CIP-003-3 (British Columbia) | 666700000010033 | R1. | 666700000010528 | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M1. The Responsible Entity shall make available documentation of its cyber security policy as specified in Requirement R1. Additionally, the Responsible Entity shall demonstrate that the cyber security policy is available as specified in Requirement R1.2. (Retirement approved by FERC effective January 21, 2014.) | 2012-07-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-003-3 (British Columbia) | 666700000010033 | R2. | 666700000010529 | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M2. The Responsible Entity shall make available documentation of the assignment of, and changes to, its leadership as specified in Requirement R2. | 2012-07-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 20000000
CIP-003-3 (British Columbia) | 666700000010033 | R3. | 666700000010530 | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | The Responsible Entity shall make available documentation of the exceptions, as specified in Requirement R3. (Retirement approved by FERC effective January 21, 2014.) | 2012-07-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 30000000
CIP-003-3 (British Columbia) | 666700000010033 | R4. | 666700000010531 | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M4. The Responsible Entity shall make available documentation of its information protection program as specified in Requirement R4. | 2012-07-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 40000000
CIP-003-3 (British Columbia) | 666700000010033 | R5. | 666700000010532 | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M5. The Responsible Entity shall make available its access control documentation as specified in Requirement R5. | 2012-07-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 50000000
CIP-003-3 (British Columbia) | 666700000010033 | R6. | 666700000010533 | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M6. The Responsible Entity shall make available its change control and configuration management documentation as specified in Requirement R6. | 2012-07-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 60000000
CIP-003-3 (Manitoba) | 77660000000223 | R1. | 776600000002729 | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M1. The Responsible Entity shall make available documentation of its cyber security policy as specified in Requirement R1. Additionally, the Responsible Entity shall demonstrate that the cyber security policy is available as specified in Requirement R1.2. (Retirement approved by FERC effective January 21, 2014.) | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
CIP-003-3 (Manitoba) | 77660000000223 | R2. | 776600000002733 | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M2. The Responsible Entity shall make available documentation of the assignment of, and changes to, its leadership as specified in Requirement R2. | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
CIP-003-3 (Manitoba) | 77660000000223 | R3. | 776600000002738 | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | The Responsible Entity shall make available documentation of the exceptions, as specified in Requirement R3. (Retirement approved by FERC effective January 21, 2014.) | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
CIP-003-3 (Manitoba) | 77660000000223 | R4. | 776600000002742 | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M4. The Responsible Entity shall make available documentation of its information protection program as specified in Requirement R4. | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 40000000
CIP-003-3 (Manitoba) | 77660000000223 | R5. | 776600000002746 | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M5. The Responsible Entity shall make available its access control documentation as specified in Requirement R5. | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 50000000
CIP-003-3 (Manitoba) | 77660000000223 | R6. | 776600000002752 | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M6. The Responsible Entity shall make available its change control and configuration management documentation as specified in Requirement R6. | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 60000000
CIP-003-3 (Ontario) | 79780000223 | R1. | 79780002729 | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M1. The Responsible Entity shall make available documentation of its cyber security policy as specified in Requirement R1. Additionally, the Responsible Entity shall demonstrate that the cyber security policy is available as specified in Requirement R1.2. (Retirement approved by FERC effective January 21, 2014.) | 2010-10-01 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-003-3 (Ontario) | 79780000223 | R2. | 79780002733 | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M2. The Responsible Entity shall make available documentation of the assignment of, and changes to, its leadership as specified in Requirement R2. | 2010-10-01 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-003-3 (Ontario) | 79780000223 | R3. | 79780002738 | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | &lt;p&gt;The Responsible Entity shall make available documentation of the exceptions, as specified in&lt;br/&gt;Requirement R3. (Retirement approved by FERC effective January 21, 2014.)&lt;/p&gt; | 2010-10-01 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-003-3 (Ontario) | 79780000223 | R4. | 79780002742 | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M4. The Responsible Entity shall make available documentation of its information protection program as specified in Requirement R4. | 2010-10-01 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-003-3 (Ontario) | 79780000223 | R5. | 79780002746 | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M5. The Responsible Entity shall make available its access control documentation as specified in Requirement R5. | 2010-10-01 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-003-3 (Ontario) | 79780000223 | R6. | 79780002752 | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M6. The Responsible Entity shall make available its change control and configuration management documentation as specified in Requirement R6. | 2010-10-01 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-003-4 | 249 | R1. | 3218 | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | The Responsible Entity has documented but not implemented a cyber security policy. | The Responsible Entity has not documented or implemented a cyber security policy. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-003-4 | 249 | R2. | 3222 | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-4 through CIP-009-4. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity has not assigned a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002 through CIP-009-4. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-003-4 | 249 | R3. | 3227 | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | In Instances where the Responsible Entity cannot conform to its cyber security policy, in R1, exceptions were documented, but were not authorized by the senior manager or delegate(s). | In Instances where the Responsible Entity cannot conform to its cyber security policy, in R1, exceptions were not documented, and were not authorized by the senior manager or delegate(s). |  | 2014-10-01 |  | 2014-01-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-003-4 | 249 | R4. | 3231 | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity implemented but did not document a program to identify, classify, and protect information associated with Critical Cyber Assets. | The Responsible Entity documented but did not implement a program to identify, classify, and protect information associated with Critical Cyber Assets. | The Responsible Entity did not implement or did not document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-003-4 | 249 | R5. | 3235 | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | The Responsible Entity implemented but did not document a program for managing access to protected Critical Cyber Asset information. | The Responsible Entity documented but did not implement a program for managing access to protected Critical Cyber Asset information. | The Responsible Entity did not implement or did not document a program for managing access to protected Critical Cyber Asset information. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-003-4 | 249 | R6. | 3241 | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity has established but not documented a change control process OR The Responsible Entity has established but not documented a configuration management process. | The Responsible Entity has established but not documented both a change control process and configuration management process | The Responsible Entity has not established and documented a change control process OR The Responsible Entity has not established and documented a configuration management process. | The Responsible Entity has not established and documented a change control process AND The Responsible Entity has not established and documented a configuration management process. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-003-4a | 431 | R1. | 5290 | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | The Responsible Entity has documented but not implemented a cyber security policy. | The Responsible Entity has not documented or implemented a cyber security policy. |  |  |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-003-4a | 431 | R2. | 5289 | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-4 through CIP-009-4. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity has not assigned a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002 through CIP-009-4. |  |  |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-003-4a | 431 | R3. | 5292 | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | In Instances where the Responsible Entity cannot conform to its cyber security policy, in R1, exceptions were documented, but were not authorized by the senior manager or delegate(s). | In Instances where the Responsible Entity cannot conform to its cyber security policy, in R1, exceptions were not documented, and were not authorized by the senior manager or delegate(s). |  |  |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-003-4a | 431 | R4. | 5288 | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity implemented but did not document a program to identify, classify, and protect information associated with Critical Cyber Assets. | The Responsible Entity documented but did not implement a program to identify, classify, and protect information associated with Critical Cyber Assets. | The Responsible Entity did not implement or did not document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  |  |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-003-4a | 431 | R5. | 5293 | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | The Responsible Entity implemented but did not document a program for managing access to protected Critical Cyber Asset information | The Responsible Entity documented but did not implement a program for managing access to protected Critical Cyber Asset information. | The Responsible Entity did not implement or did not document a program for managing access to protected Critical Cyber Asset information. |  |  |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-003-4a | 431 | R6. | 5291 | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Planning | Low | The Responsible Entity has established but not documented a change control process OR The Responsible Entity has established but not documented a configuration management process. | The Responsible Entity has established but not documented both a change control process and configuration management process. | The Responsible Entity has not established and documented a change control process OR The Responsible Entity has not established and documented a configuration management process. | The Responsible Entity has not established and documented a change control process AND The Responsible Entity has not established and documented a configuration management process. |  |  |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-003-4a (Ontario) | 79780000431 | R1. | 79780005290 | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity has not documented or implemented a cyber security policy. |  |  |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-003-4a (Ontario) | 79780000431 | R2. | 79780005289 | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-4 through CIP-009-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity has not assigned a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002 through CIP-009. |  |  |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-003-4a (Ontario) | 79780000431 | R3. | 79780005292 | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | In Instances where the Responsible Entity cannot conform to its cyber security policy, in R1, exceptions were documented, but were not authorized by the senior manager or delegate(s). | In Instances where the Responsible Entity cannot conform to its cyber security policy, in R1, exceptions were not documented. |  |  |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-003-4a (Ontario) | 79780000431 | R4. | 79780005288 | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not implement or did not document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  |  |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-003-4a (Ontario) | 79780000431 | R5. | 79780005293 | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity did not implement or did not document a program for managing access to protected Critical Cyber Asset information. |  |  |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-003-4a (Ontario) | 79780000431 | R6. | 79780005291 | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Planning | Low | N/A | N/A | N/A | The Responsible Entity has not established or documented a change control process for the activities required in R6, OR The Responsible Entity has not established or documented a configuration management process for the activities required in R6. |  |  |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-003-4 (Ontario) | 79780000249 | R1. | 79780003218 | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity has not documented or implemented a cyber security policy. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-003-4 (Ontario) | 79780000249 | R2. | 79780003222 | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-4 through CIP-009-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity has not assigned a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002 through CIP-009. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-003-4 (Ontario) | 79780000249 | R3. | 79780003227 | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | In Instances where the Responsible Entity cannot conform to its cyber security policy, in R1, exceptions were documented, but were not authorized by the senior manager or delegate(s). | In Instances where the Responsible Entity cannot conform to its cyber security policy, in R1, exceptions were not documented. |  | 2014-10-01 |  | 2014-01-21 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-003-4 (Ontario) | 79780000249 | R4. | 79780003231 | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not implement or did not document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-003-4 (Ontario) | 79780000249 | R5. | 79780003235 | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity did not implement or did not document a program for managing access to protected Critical Cyber Asset information. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-003-4 (Ontario) | 79780000249 | R6. | 79780003241 | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity has not established or documented a change control process for the activities required in R6, OR The Responsible Entity has not established or documented a configuration management process for the activities required in R6. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-003-5 | 347 | R1. | 4482 | Each Responsible Entity, for its high impact and medium impact BES Cyber Systems, shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1) or The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate according to Requirement R1 within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1) or The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate according to Requirement R1 within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1) or The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate according to Requirement R1 within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1) or The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1) or The Responsible Entity did not complete its review of the one or more documented cyber security policies as required by R1 within 18 calendar months of the previous review. (R1) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate according to Requirement R1 within 18 calendar months of the previous approval. (R1) | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-003-5 | 347 | R2. | 4483 | Each Responsible Entity for its assets identified in CIP-002-5, Requirement R1, Part R1.3, shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented cyber security policies that collectively address the following topics, and review and obtain CIP Senior Manager approval for those policies at least once every 15 calendar months: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only three of the topics as required by R2 and has identified deficiencies but did not assess or correct the deficiencies. (R2) or The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only three of the topics as required by R2 but did not identify, assess, or correct the deficiencies. OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by R2 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R2) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by R2 by the CIP Senior Manager according to Requirement R2 within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R2) | The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only two of the topics as required by R2 and has identified deficiencies but did not assess or correct the deficiencies. (R2) or The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only two of the topics as required by R2 but did not identify, assess, or correct the deficiencies. or The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by R2 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R2) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by R2 by the CIP Senior Manager according to Requirement R2 within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R2) | The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only one of the topics as required by R2 and has identified deficiencies but did not assess or correct the deficiencies. (R2) or The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only one of the topics as required by R2 but did not identify, assess, or correct the deficiencies. or The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by R2 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R2) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by R2 by the CIP Senior Manager according to Requirement R2 within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R2) | The Responsible Entity did not document or implement any cyber security policies for assets with a low impact rating that address the topics as required by R2. (R2) or The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by R2 within 18 calendar months of the previous review. (R2) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by R2 by the CIP Senior Manager according to Requirement R2 within 18 calendar months of the previous approval. (R2) | M2. Examples of evidence may include, but are not limited to, one or more documented cyber security policies and evidence of processes, procedures, or plans that demonstrate the implementation of the required topics; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2017-04-01 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-003-5 | 347 | R3. | 4484 | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. or The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-003-5 | 347 | R4. | 4485 | The Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, has a process to delegate actions from the CIP Senior Manager, and has Identified deficiencies but did not assess or correct the deficiencies.(R4) or The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, has a process to delegate actions from the CIP Senior Manager, but did not identify, assess, or correct the deficiencies.(R4) or The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-003-5 (British Columbia) | 666700000010034 | R1. | 666700000010534 | Each Responsible Entity, for its high impact and medium impact BES Cyber Systems, shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1) or The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate according to Requirement R1 within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1) or The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate according to Requirement R1 within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1) or The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate according to Requirement R1 within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1) or The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1) or The Responsible Entity did not complete its review of the one or more documented cyber security policies as required by R1 within 18 calendar months of the previous review. (R1) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate according to Requirement R1 within 18 calendar months of the previous approval. (R1) | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2018-10-01 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-003-5 (British Columbia) | 666700000010034 | R2. | 666700000010535 | Each Responsible Entity for its assets identified in CIP-002-5, Requirement R1, Part R1.3, shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented cyber security policies that collectively address the following topics, and review and obtain CIP Senior Manager approval for those policies at least once every 15 calendar months: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only three of the topics as required by R2 and has identified deficiencies but did not assess or correct the deficiencies. (R2) or The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only three of the topics as required by R2 but did not identify, assess, or correct the deficiencies. OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by R2 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R2) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by R2 by the CIP Senior Manager according to Requirement R2 within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R2) | The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only two of the topics as required by R2 and has identified deficiencies but did not assess or correct the deficiencies. (R2) or The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only two of the topics as required by R2 but did not identify, assess, or correct the deficiencies. or The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by R2 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R2) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by R2 by the CIP Senior Manager according to Requirement R2 within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R2) | The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only one of the topics as required by R2 and has identified deficiencies but did not assess or correct the deficiencies. (R2) or The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only one of the topics as required by R2 but did not identify, assess, or correct the deficiencies. or The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by R2 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R2) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by R2 by the CIP Senior Manager according to Requirement R2 within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R2) | The Responsible Entity did not document or implement any cyber security policies for assets with a low impact rating that address the topics as required by R2. (R2) or The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by R2 within 18 calendar months of the previous review. (R2) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by R2 by the CIP Senior Manager according to Requirement R2 within 18 calendar months of the previous approval. (R2) | M2. Examples of evidence may include, but are not limited to, one or more documented cyber security policies and evidence of processes, procedures, or plans that demonstrate the implementation of the required topics; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2018-10-01 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 20000000
CIP-003-5 (British Columbia) | 666700000010034 | R3. | 666700000010536 | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. or The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | 2018-10-01 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 30000000
CIP-003-5 (British Columbia) | 666700000010034 | R4. | 666700000010537 | The Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, has a process to delegate actions from the CIP Senior Manager, and has Identified deficiencies but did not assess or correct the deficiencies.(R4) or The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, has a process to delegate actions from the CIP Senior Manager, but did not identify, assess, or correct the deficiencies.(R4) or The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | 2018-10-01 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 40000000
CIP-003-5 (Ontario) | 79780000347 | R1. | 79780004482 | Each Responsible Entity, for its high impact and medium impact BES Cyber Systems, shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: [See Standard for sub-req's] |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1) or The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate according to Requirement R1 within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1) or The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate according to Requirement R1 within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1) or The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate according to Requirement R1 within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1) or The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1) or The Responsible Entity did not complete its review of the one or more documented cyber security policies as required by R1 within 18 calendar months of the previous review. (R1) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate according to Requirement R1 within 18 calendar months of the previous approval. (R1) | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. |  |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-003-5 (Ontario) | 79780000347 | R2. | 79780004483 | Each Responsible Entity for its assets identified in CIP-002-5, Requirement R1, Part R1.3, shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented cyber security policies that collectively address the following topics, and review and obtain CIP Senior Manager approval for those policies at least once every 15 calendar months: [See Standard for sub-req's] |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only three of the topics as required by R2 and has identified deficiencies but did not assess or correct the deficiencies. (R2) or The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only three of the topics as required by R2 but did not identify, assess, or correct the deficiencies. OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by R2 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R2) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by R2 by the CIP Senior Manager according to Requirement R2 within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R2) | The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only two of the topics as required by R2 and has identified deficiencies but did not assess or correct the deficiencies. (R2) or The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only two of the topics as required by R2 but did not identify, assess, or correct the deficiencies. or The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by R2 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R2) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by R2 by the CIP Senior Manager according to Requirement R2 within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R2) | The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only one of the topics as required by R2 and has identified deficiencies but did not assess or correct the deficiencies. (R2) or The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only one of the topics as required by R2 but did not identify, assess, or correct the deficiencies. or The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by R2 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R2) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by R2 by the CIP Senior Manager according to Requirement R2 within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R2) | The Responsible Entity did not document or implement any cyber security policies for assets with a low impact rating that address the topics as required by R2. (R2) or The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by R2 within 18 calendar months of the previous review. (R2) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by R2 by the CIP Senior Manager according to Requirement R2 within 18 calendar months of the previous approval. (R2) | M2. Examples of evidence may include, but are not limited to, one or more documented cyber security policies and evidence of processes, procedures, or plans that demonstrate the implementation of the required topics; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2017-04-01 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-003-5 (Ontario) | 79780000347 | R3. | 79780004484 | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. or The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. |  |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-003-5 (Ontario) | 79780000347 | R4. | 79780004485 | The Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, has a process to delegate actions from the CIP Senior Manager, and has Identified deficiencies but did not assess or correct the deficiencies.(R4) or The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, has a process to delegate actions from the CIP Senior Manager, but did not identify, assess, or correct the deficiencies.(R4) or The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. |  |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-003-5 (Saskatchewan) | 83750000000347 | R1. | 837500000004482 | Each Responsible Entity, for its high impact and medium impact BES Cyber Systems, shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1) or The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate according to Requirement R1 within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1) or The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate according to Requirement R1 within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1) or The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate according to Requirement R1 within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1) or The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1) or The Responsible Entity did not complete its review of the one or more documented cyber security policies as required by R1 within 18 calendar months of the previous review. (R1) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate according to Requirement R1 within 18 calendar months of the previous approval. (R1) | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. |  |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 10000000
CIP-003-5 (Saskatchewan) | 83750000000347 | R2. | 837500000004483 | Each Responsible Entity for its assets identified in CIP-002-5, Requirement R1, Part R1.3, shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented cyber security policies that collectively address the following topics, and review and obtain CIP Senior Manager approval for those policies at least once every 15 calendar months: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only three of the topics as required by R2 and has identified deficiencies but did not assess or correct the deficiencies. (R2) or The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only three of the topics as required by R2 but did not identify, assess, or correct the deficiencies. OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by R2 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R2) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by R2 by the CIP Senior Manager according to Requirement R2 within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R2) | The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only two of the topics as required by R2 and has identified deficiencies but did not assess or correct the deficiencies. (R2) or The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only two of the topics as required by R2 but did not identify, assess, or correct the deficiencies. or The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by R2 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R2) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by R2 by the CIP Senior Manager according to Requirement R2 within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R2) | The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only one of the topics as required by R2 and has identified deficiencies but did not assess or correct the deficiencies. (R2) or The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only one of the topics as required by R2 but did not identify, assess, or correct the deficiencies. or The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by R2 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R2) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by R2 by the CIP Senior Manager according to Requirement R2 within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R2) | The Responsible Entity did not document or implement any cyber security policies for assets with a low impact rating that address the topics as required by R2. (R2) or The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by R2 within 18 calendar months of the previous review. (R2) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by R2 by the CIP Senior Manager according to Requirement R2 within 18 calendar months of the previous approval. (R2) | M2. Examples of evidence may include, but are not limited to, one or more documented cyber security policies and evidence of processes, procedures, or plans that demonstrate the implementation of the required topics; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. |  |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 20000000
CIP-003-5 (Saskatchewan) | 83750000000347 | R3. | 837500000004484 | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. or The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. |  |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 30000000
CIP-003-5 (Saskatchewan) | 83750000000347 | R4. | 837500000004485 | The Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, has a process to delegate actions from the CIP Senior Manager, and has Identified deficiencies but did not assess or correct the deficiencies.(R4) or The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, has a process to delegate actions from the CIP Senior Manager, but did not identify, assess, or correct the deficiencies.(R4) or The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. |  |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 40000000
CIP-003-6 | 506 | R1. | 6058 | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1) The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies as required by R1 within 18 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate within 18 calendar months of the previous approval. (R1) | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-003-6 | 506 | R2. | 6059 | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. Note: An inventory, list, or discrete identification of low impact BES Cyber Systems or their BES Cyber Assets is not required. Lists of authorized users are not required. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity had one or more documented cyber security policies for assets with a low impact rating but failed to address one of the topics as required by Requirement R2. (R2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R2) | The Responsible Entity had one or more documented cyber security policies for assets with a low impact rating but failed to address two of the topics as required by Requirement R2. (R2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R2) | The Responsible Entity had one or more documented cyber security policies for assets with a low impact rating but failed to address three of the topics as required by Requirement R2. (R2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R2) | The Responsible Entity did not have any documented cyber security policies for assets with a low impact rating that address the topics as required by Requirement R2. (R2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 within 18 calendar months of the previous review. (R2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 by the CIP Senior Manager within 18 calendar months of the previous approval. (R2) | Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | 2016-07-01 |  | 2019-12-31 | R2, Attachment 1, Sections 1 and 4 are effective on 4/1/2017 ¦ Attachment 1 - Sections 2 and 3 are effective on 9/1/2018* | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-003-6 | 506 | R3. | 6060 | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. OR The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) | An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-003-6 | 506 | R4. | 6061 | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) | An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-003-6 (Manitoba) | 77660000000506 | R1. | 776600000006058 | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1) The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies as required by R1 within 18 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate within 18 calendar months of the previous approval. (R1) | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2017-07-01 |  | 2021-06-30 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-MB | [6 empty] | 10000000
CIP-003-6 (Manitoba) | 77660000000506 | R2. | 776600000006059 | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. Note: An inventory, list, or discrete identification of low impact BES Cyber Systems or their BES Cyber Assets is not required. Lists of authorized users are not required. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity had one or more documented cyber security policies for assets with a low impact rating but failed to address one of the topics as required by Requirement R2. (R2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R2) | The Responsible Entity had one or more documented cyber security policies for assets with a low impact rating but failed to address two of the topics as required by Requirement R2. (R2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R2) | The Responsible Entity had one or more documented cyber security policies for assets with a low impact rating but failed to address three of the topics as required by Requirement R2. (R2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R2) | The Responsible Entity did not have any documented cyber security policies for assets with a low impact rating that address the topics as required by Requirement R2. (R2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 within 18 calendar months of the previous review. (R2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 by the CIP Senior Manager within 18 calendar months of the previous approval. (R2) | Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | 2017-07-01 |  | 2021-06-30 | R2, Attachment 1, Sections 1 and 4 are effective on 4/1/2017 ¦ Attachment 1 - Sections 2 and 3 are effective on 9/1/2018* | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-MB | [6 empty] | 20000000
CIP-003-6 (Manitoba) | 77660000000506 | R3. | 776600000006060 | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. OR The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) | An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | 2017-07-01 |  | 2021-06-30 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-MB | [6 empty] | 30000000
CIP-003-6 (Manitoba) | 77660000000506 | R4. | 776600000006061 | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) | An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | 2017-07-01 |  | 2021-06-30 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-MB | [6 empty] | 40000000
CIP-003-6 (Ontario) | 79780000506 | R1. | 79780006058 | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1) The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies as required by R1 within 18 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate within 18 calendar months of the previous approval. (R1) | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-ON | [6 empty] | 10000000
CIP-003-6 (Ontario) | 79780000506 | R2. | 79780006059 | &lt;p&gt;Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1.&lt;/p&gt; &lt;p&gt;Note: An inventory, list, or discrete identification of low impact BES Cyber Systems or&lt;br/&gt;their BES Cyber Assets is not required. Lists of authorized users are not required.&lt;/p&gt; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity had one or more documented cyber security policies for assets with a low impact rating but failed to address one of the topics as required by Requirement R2. (R2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R2) | The Responsible Entity had one or more documented cyber security policies for assets with a low impact rating but failed to address two of the topics as required by Requirement R2. (R2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R2) | The Responsible Entity had one or more documented cyber security policies for assets with a low impact rating but failed to address three of the topics as required by Requirement R2. (R2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R2) | The Responsible Entity did not have any documented cyber security policies for assets with a low impact rating that address the topics as required by Requirement R2. (R2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 within 18 calendar months of the previous review. (R2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 by the CIP Senior Manager within 18 calendar months of the previous approval. (R2) | &lt;p&gt;Evidence shall include each of the documented cyber security plan(s) that collectively&lt;br/&gt;include each of the sections in Attachment 1 and additional evidence to demonstrate&lt;br/&gt;implementation of the cyber security plan(s). Additional examples of evidence per&lt;br/&gt;section are located in Attachment 2.&lt;/p&gt; | 2016-07-01 |  | 2019-12-31 | R2, Attachment 1, Sections 1 and 4 are effective on 4/1/2017 ¦ Attachment 1 - Sections 2 and 3 are effective on 9/1/2018* | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-ON | [6 empty] | 20000000
CIP-003-6 (Ontario) | 79780000506 | R3. | 79780006060 | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. OR The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) | &lt;p&gt;An example of evidence may include, but is not limited to, a dated and approved&lt;br/&gt;document from a high level official designating the name of the individual identified&lt;br/&gt;as the CIP Senior Manager.&lt;/p&gt; | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-ON | [6 empty] | 30000000
CIP-003-6 (Ontario) | 79780000506 | R4. | 79780006061 | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) | &lt;p&gt;An example of evidence may include, but is not limited to, a dated document,&lt;br/&gt;approved by the CIP Senior Manager, listing individuals (by name or title) who are&lt;br/&gt;delegated the authority to approve or authorize specifically identified items.&lt;/p&gt; | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-ON | [6 empty] | 40000000
CIP-003-6 (Saskatchewan) | 83750000000506 | R1. | 837500000006058 | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1) The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies as required by R1 within 18 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate within 18 calendar months of the previous approval. (R1) | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-SK | [6 empty] | 10000000
CIP-003-6 (Saskatchewan) | 83750000000506 | R2. | 837500000006059 | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. Note: An inventory, list, or discrete identification of low impact BES Cyber Systems or their BES Cyber Assets is not required. Lists of authorized users are not required. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity had one or more documented cyber security policies for assets with a low impact rating but failed to address one of the topics as required by Requirement R2. (R2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R2) | The Responsible Entity had one or more documented cyber security policies for assets with a low impact rating but failed to address two of the topics as required by Requirement R2. (R2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R2) | The Responsible Entity had one or more documented cyber security policies for assets with a low impact rating but failed to address three of the topics as required by Requirement R2. (R2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R2) | The Responsible Entity did not have any documented cyber security policies for assets with a low impact rating that address the topics as required by Requirement R2. (R2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 within 18 calendar months of the previous review. (R2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 by the CIP Senior Manager within 18 calendar months of the previous approval. (R2) | Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | 2016-07-01 |  | 2019-12-31 | R2, Attachment 1, Sections 1 and 4 are effective on 4/1/2017 ¦ Attachment 1 - Sections 2 and 3 are effective on 9/1/2018* | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-SK | [6 empty] | 20000000
CIP-003-6 (Saskatchewan) | 83750000000506 | R3. | 837500000006060 | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. OR The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) | An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-SK | [6 empty] | 30000000
CIP-003-6 (Saskatchewan) | 83750000000506 | R4. | 837500000006061 | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) | An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-SK | [6 empty] | 40000000
CIP-003-7 | 563 | R1. | 7984 | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address one of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address two of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address three of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies as required by R1 within 18 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address four or more of the six topics required by R1. (R1.2) OR The Responsible Entity did not have any documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.2) | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-003-7 | 563 | R2. | 7985 | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document cyber security awareness according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity implemented electronic access controls but failed to document its cyber security plan(s) for electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document one or more Cyber Security Incident response plan(s) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to update each Cyber Security Incident response plan(s) within 180 days according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to manage its Transient Cyber Asset(s) according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets, but failed to document the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to reinforce cyber security practices at least once every 15 calendar months according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls but failed to implement authentication for all Dial-up Connectivity that provides access to low impact BES Cyber System(s), per Cyber Asset capability according to Requirement R2, Attachment 1, Section 3.2 (R2) OR The Responsible Entity documented one or more incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to include the process for identification, classification, and response to Cyber Security Incidents according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident and subsequent notification to the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Sections 5.1 and 5.3. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented the physical access controls for its assets containing low impact BES Cyber Systems, but failed to implement the physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls for its assets containing low impact BES Cyber Systems, but failed to permit only necessary inbound and outbound electronic access controls according to Requirement R2, Attachment 1, Section 3.1. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to test each Cyber Security Incident response plan(s) at least once every 36 calendar months according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident, but failed to notify the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the threat of detected malicious code on the Removable Media prior to connecting Removable Media to a low impact BES Cyber System according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity failed to document and implement one or more cyber security plan(s) for its assets containing low impact BES Cyber Systems according to Requirement R2, Attachment 1. (R2) | M2. Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-003-7 | 563 | R3. | 8004 | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. OR The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-003-7 | 563 | R4. | 8005 | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-003-7 (British Columbia) | 666700000010035 | R1. | 666700000010538 | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address one of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address two of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address three of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies as required by R1 within 18 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address four or more of the six topics required by R1. (R1.2) OR The Responsible Entity did not have any documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.2) | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2019-10-01 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | WECC-BC | [6 empty] | 10000000
CIP-003-7 (British Columbia) | 666700000010035 | R2. | 666700000010539 | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document cyber security awareness according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity implemented electronic access controls but failed to document its cyber security plan(s) for electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document one or more Cyber Security Incident response plan(s) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to update each Cyber Security Incident response plan(s) within 180 days according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to manage its Transient Cyber Asset(s) according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets, but failed to document the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to reinforce cyber security practices at least once every 15 calendar months according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls but failed to implement authentication for all Dial-up Connectivity that provides access to low impact BES Cyber System(s), per Cyber Asset capability according to Requirement R2, Attachment 1, Section 3.2 (R2) OR The Responsible Entity documented one or more incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to include the process for identification, classification, and response to Cyber Security Incidents according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident and subsequent notification to the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Sections 5.1 and 5.3. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented the physical access controls for its assets containing low impact BES Cyber Systems, but failed to implement the physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls for its assets containing low impact BES Cyber Systems, but failed to permit only necessary inbound and outbound electronic access controls according to Requirement R2, Attachment 1, Section 3.1. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to test each Cyber Security Incident response plan(s) at least once every 36 calendar months according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident, but failed to notify the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the threat of detected malicious code on the Removable Media prior to connecting Removable Media to a low impact BES Cyber System according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity failed to document and implement one or more cyber security plan(s) for its assets containing low impact BES Cyber Systems according to Requirement R2, Attachment 1. (R2) | M2. Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | 2019-10-01 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | WECC-BC | [6 empty] | 20000000
CIP-003-7 (British Columbia) | 666700000010035 | R3. | 666700000010540 | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. OR The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | 2019-10-01 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | WECC-BC | [6 empty] | 30000000
CIP-003-7 (British Columbia) | 666700000010035 | R4. | 666700000010541 | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | 2019-10-01 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | WECC-BC | [6 empty] | 40000000
CIP-003-7 (Nova Scotia) | 78830000000563 | R1. | 788300000007984 | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address one of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address two of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address three of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies as required by R1 within 18 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address four or more of the six topics required by R1. (R1.2) OR The Responsible Entity did not have any documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.2) | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2021-01-01 |  | 2021-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-NS | [6 empty] | 10000000
CIP-003-7 (Nova Scotia) | 78830000000563 | R2. | 788300000007985 | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document cyber security awareness according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity implemented electronic access controls but failed to document its cyber security plan(s) for electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document one or more Cyber Security Incident response plan(s) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to update each Cyber Security Incident response plan(s) within 180 days according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to manage its Transient Cyber Asset(s) according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets, but failed to document the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to reinforce cyber security practices at least once every 15 calendar months according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls but failed to implement authentication for all Dial-up Connectivity that provides access to low impact BES Cyber System(s), per Cyber Asset capability according to Requirement R2, Attachment 1, Section 3.2 (R2) OR The Responsible Entity documented one or more incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to include the process for identification, classification, and response to Cyber Security Incidents according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident and subsequent notification to the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Sections 5.1 and 5.3. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented the physical access controls for its assets containing low impact BES Cyber Systems, but failed to implement the physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls for its assets containing low impact BES Cyber Systems, but failed to permit only necessary inbound and outbound electronic access controls according to Requirement R2, Attachment 1, Section 3.1. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to test each Cyber Security Incident response plan(s) at least once every 36 calendar months according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident, but failed to notify the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the threat of detected malicious code on the Removable Media prior to connecting Removable Media to a low impact BES Cyber System according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity failed to document and implement one or more cyber security plan(s) for its assets containing low impact BES Cyber Systems according to Requirement R2, Attachment 1. (R2) | M2. Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | 2021-01-01 |  | 2021-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-NS | [6 empty] | 20000000
CIP-003-7 (Nova Scotia) | 78830000000563 | R3. | 788300000008004 | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. OR The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | 2021-01-01 |  | 2021-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-NS | [6 empty] | 30000000
CIP-003-7 (Nova Scotia) | 78830000000563 | R4. | 788300000008005 | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | 2021-01-01 |  | 2021-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-NS | [6 empty] | 40000000
CIP-003-7 (Ontario) | 79780000563 | R1. | 79780007984 | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address one of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address two of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address three of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies as required by R1 within 18 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address four or more of the six topics required by R1. (R1.2) OR The Responsible Entity did not have any documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.2) | &lt;p&gt;Examples of evidence may include, but are not limited to, policy documents; revision&lt;br/&gt;history, records of review, or workflow evidence from a document management&lt;br/&gt;system that indicate review of each cyber security policy at least once every 15&lt;br/&gt;calendar months; and documented approval by the CIP Senior Manager for each cyber&lt;br/&gt;security policy.&lt;/p&gt; | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-ON | [6 empty] | 10000000
CIP-003-7 (Ontario) | 79780000563 | R2. | 79780007985 | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document cyber security awareness according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity implemented electronic access controls but failed to document its cyber security plan(s) for electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document one or more Cyber Security Incident response plan(s) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to update each Cyber Security Incident response plan(s) within 180 days according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to manage its Transient Cyber Asset(s) according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets, but failed to document the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to reinforce cyber security practices at least once every 15 calendar months according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls but failed to implement authentication for all Dial-up Connectivity that provides access to low impact BES Cyber System(s), per Cyber Asset capability according to Requirement R2, Attachment 1, Section 3.2 (R2) OR The Responsible Entity documented one or more incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to include the process for identification, classification, and response to Cyber Security Incidents according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident and subsequent notification to the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Sections 5.1 and 5.3. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented the physical access controls for its assets containing low impact BES Cyber Systems, but failed to implement the physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls for its assets containing low impact BES Cyber Systems, but failed to permit only necessary inbound and outbound electronic access controls according to Requirement R2, Attachment 1, Section 3.1. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to test each Cyber Security Incident response plan(s) at least once every 36 calendar months according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident, but failed to notify the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the threat of detected malicious code on the Removable Media prior to connecting Removable Media to a low impact BES Cyber System according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity failed to document and implement one or more cyber security plan(s) for its assets containing low impact BES Cyber Systems according to Requirement R2, Attachment 1. (R2) | M2. Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-ON | [6 empty] | 20000000
CIP-003-7 (Ontario) | 79780000563 | R3. | 79780008004 | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. OR The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-ON | [6 empty] | 30000000
CIP-003-7 (Ontario) | 79780000563 | R4. | 79780008005 | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-ON | [6 empty] | 40000000
CIP-003-7 (Saskatchewan) | 83750000000563 | R1. | 837500000007984 | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address one of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address two of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address three of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies as required by R1 within 18 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address four or more of the six topics required by R1. (R1.2) OR The Responsible Entity did not have any documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.2) | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-01-01 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-SK | [6 empty] | 10000000
CIP-003-7 (Saskatchewan) | 83750000000563 | R2. | 837500000007985 | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document cyber security awareness according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity implemented electronic access controls but failed to document its cyber security plan(s) for electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document one or more Cyber Security Incident response plan(s) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to update each Cyber Security Incident response plan(s) within 180 days according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to manage its Transient Cyber Asset(s) according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets, but failed to document the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to reinforce cyber security practices at least once every 15 calendar months according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls but failed to implement authentication for all Dial-up Connectivity that provides access to low impact BES Cyber System(s), per Cyber Asset capability according to Requirement R2, Attachment 1, Section 3.2 (R2) OR The Responsible Entity documented one or more incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to include the process for identification, classification, and response to Cyber Security Incidents according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident and subsequent notification to the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Sections 5.1 and 5.3. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented the physical access controls for its assets containing low impact BES Cyber Systems, but failed to implement the physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls for its assets containing low impact BES Cyber Systems, but failed to permit only necessary inbound and outbound electronic access controls according to Requirement R2, Attachment 1, Section 3.1. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to test each Cyber Security Incident response plan(s) at least once every 36 calendar months according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident, but failed to notify the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the threat of detected malicious code on the Removable Media prior to connecting Removable Media to a low impact BES Cyber System according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity failed to document and implement one or more cyber security plan(s) for its assets containing low impact BES Cyber Systems according to Requirement R2, Attachment 1. (R2) | M2. Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | 2020-01-01 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-SK | [6 empty] | 20000000
CIP-003-7 (Saskatchewan) | 83750000000563 | R3. | 837500000008004 | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. OR The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | 2020-01-01 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-SK | [6 empty] | 30000000
CIP-003-7 (Saskatchewan) | 83750000000563 | R4. | 837500000008005 | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | 2020-01-01 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-SK | [6 empty] | 40000000
CIP-003-8 | 597 | R1. | 8679 | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1.) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address one of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address two of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address three of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address four or more of the six topics required by R1. (R1.2) OR The Responsible Entity did not have any documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.2) | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-04-01 |  | 2026-03-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-003-8 | 597 | R2. | 8697 | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. |  | BA, DP, DP-UFLS, GO, GOP, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document cyber security awareness according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity implemented electronic access controls but failed to document its cyber security plan(s) for electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document one or more Cyber Security Incident response plan(s) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to update each Cyber Security Incident response plan(s) within 180 days according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to manage its Transient Cyber Asset(s) according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets, but failed to document the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to reinforce cyber security practices at least once every 15 calendar months according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls but failed to implement authentication for all Dial-up Connectivity that provides access to low impact BES Cyber System(s), per Cyber Asset capability according to Requirement R2, Attachment 1, Section 3.2 (R2) OR The Responsible Entity documented one or more incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to include the process for identification, classification, and response to Cyber Security Incidents according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident and subsequent notification to the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Sections 5.1 and 5.3. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented the physical access controls for its assets containing low impact BES Cyber Systems, but failed to implement the physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls for its assets containing low impact BES Cyber Systems, but failed to permit only necessary inbound and outbound electronic access controls according to Requirement R2, Attachment 1, Section 3.1. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to test each Cyber Security Incident response plan(s) at least once every 36 calendar months according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident, but failed to notify the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the threat of detected malicious code on the Removable Media prior to connecting Removable Media to a low impact BES Cyber System according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity failed to document and implement one or more cyber security plan(s) for its assets containing low impact BES Cyber Systems according to Requirement R2, Attachment 1. (R2) | M2. Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | 2020-04-01 |  | 2026-03-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-003-8 | 597 | R3. | 8698 | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. OR The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | 2020-04-01 |  | 2026-03-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-003-8 | 597 | R4. | 8699 | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | 2020-04-01 |  | 2026-03-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-003-8 (British Columbia) | 666700000010036 | R1. | 666700000010542 | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1.) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address one of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address two of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address three of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address four or more of the six topics required by R1. (R1.2) OR The Responsible Entity did not have any documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.2) | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | WECC-BC | [6 empty] | 10000000
CIP-003-8 (British Columbia) | 666700000010036 | R2. | 666700000010543 | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. |  | BA, DP, DP-UFLS, GO, GOP, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document cyber security awareness according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity implemented electronic access controls but failed to document its cyber security plan(s) for electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document one or more Cyber Security Incident response plan(s) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to update each Cyber Security Incident response plan(s) within 180 days according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to manage its Transient Cyber Asset(s) according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets, but failed to document the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to reinforce cyber security practices at least once every 15 calendar months according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls but failed to implement authentication for all Dial-up Connectivity that provides access to low impact BES Cyber System(s), per Cyber Asset capability according to Requirement R2, Attachment 1, Section 3.2 (R2) OR The Responsible Entity documented one or more incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to include the process for identification, classification, and response to Cyber Security Incidents according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident and subsequent notification to the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Sections 5.1 and 5.3. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented the physical access controls for its assets containing low impact BES Cyber Systems, but failed to implement the physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls for its assets containing low impact BES Cyber Systems, but failed to permit only necessary inbound and outbound electronic access controls according to Requirement R2, Attachment 1, Section 3.1. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to test each Cyber Security Incident response plan(s) at least once every 36 calendar months according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident, but failed to notify the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the threat of detected malicious code on the Removable Media prior to connecting Removable Media to a low impact BES Cyber System according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity failed to document and implement one or more cyber security plan(s) for its assets containing low impact BES Cyber Systems according to Requirement R2, Attachment 1. (R2) | M2. Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | WECC-BC | [6 empty] | 20000000
CIP-003-8 (British Columbia) | 666700000010036 | R3. | 666700000010544 | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. OR The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | WECC-BC | [6 empty] | 30000000
CIP-003-8 (British Columbia) | 666700000010036 | R4. | 666700000010545 | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | WECC-BC | [6 empty] | 40000000
CIP-003-8 (Manitoba) | 77660000000597 | R1. | 776600000008679 | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1.) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address one of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address two of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address three of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address four or more of the six topics required by R1. (R1.2) OR The Responsible Entity did not have any documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.2) | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2021-07-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-MB | [6 empty] | 10000000
CIP-003-8 (Manitoba) | 77660000000597 | R2. | 776600000008697 | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. |  | BA, DP, DP-UFLS, GO, GOP, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document cyber security awareness according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity implemented electronic access controls but failed to document its cyber security plan(s) for electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document one or more Cyber Security Incident response plan(s) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to update each Cyber Security Incident response plan(s) within 180 days according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to manage its Transient Cyber Asset(s) according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets, but failed to document the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to reinforce cyber security practices at least once every 15 calendar months according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls but failed to implement authentication for all Dial-up Connectivity that provides access to low impact BES Cyber System(s), per Cyber Asset capability according to Requirement R2, Attachment 1, Section 3.2 (R2) OR The Responsible Entity documented one or more incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to include the process for identification, classification, and response to Cyber Security Incidents according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident and subsequent notification to the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Sections 5.1 and 5.3. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented the physical access controls for its assets containing low impact BES Cyber Systems, but failed to implement the physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls for its assets containing low impact BES Cyber Systems, but failed to permit only necessary inbound and outbound electronic access controls according to Requirement R2, Attachment 1, Section 3.1. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to test each Cyber Security Incident response plan(s) at least once every 36 calendar months according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident, but failed to notify the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the threat of detected malicious code on the Removable Media prior to connecting Removable Media to a low impact BES Cyber System according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity failed to document and implement one or more cyber security plan(s) for its assets containing low impact BES Cyber Systems according to Requirement R2, Attachment 1. (R2) | M2. Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | 2021-07-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-MB | [6 empty] | 20000000
CIP-003-8 (Manitoba) | 77660000000597 | R3. | 776600000008698 | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. OR The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | 2021-07-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-MB | [6 empty] | 30000000
CIP-003-8 (Manitoba) | 77660000000597 | R4. | 776600000008699 | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | 2021-07-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-MB | [6 empty] | 40000000
CIP-003-8 (Nova Scotia) | 78830000000597 | R1. | 788300000008679 | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1.) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address one of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address two of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address three of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address four or more of the six topics required by R1. (R1.2) OR The Responsible Entity did not have any documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.2) | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2021-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-NS | [6 empty] | 10000000
CIP-003-8 (Nova Scotia) | 78830000000597 | R2. | 788300000008697 | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. |  | BA, DP, DP-UFLS, GO, GOP, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document cyber security awareness according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity implemented electronic access controls but failed to document its cyber security plan(s) for electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document one or more Cyber Security Incident response plan(s) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to update each Cyber Security Incident response plan(s) within 180 days according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to manage its Transient Cyber Asset(s) according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets, but failed to document the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to reinforce cyber security practices at least once every 15 calendar months according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls but failed to implement authentication for all Dial-up Connectivity that provides access to low impact BES Cyber System(s), per Cyber Asset capability according to Requirement R2, Attachment 1, Section 3.2 (R2) OR The Responsible Entity documented one or more incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to include the process for identification, classification, and response to Cyber Security Incidents according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident and subsequent notification to the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Sections 5.1 and 5.3. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented the physical access controls for its assets containing low impact BES Cyber Systems, but failed to implement the physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls for its assets containing low impact BES Cyber Systems, but failed to permit only necessary inbound and outbound electronic access controls according to Requirement R2, Attachment 1, Section 3.1. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to test each Cyber Security Incident response plan(s) at least once every 36 calendar months according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident, but failed to notify the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the threat of detected malicious code on the Removable Media prior to connecting Removable Media to a low impact BES Cyber System according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity failed to document and implement one or more cyber security plan(s) for its assets containing low impact BES Cyber Systems according to Requirement R2, Attachment 1. (R2) | M2. Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | 2021-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-NS | [6 empty] | 20000000
CIP-003-8 (Nova Scotia) | 78830000000597 | R3. | 788300000008698 | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. OR The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | 2021-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-NS | [6 empty] | 30000000
CIP-003-8 (Nova Scotia) | 78830000000597 | R4. | 788300000008699 | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | 2021-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-NS | [6 empty] | 40000000
CIP-003-8 (Ontario) | 79780000597 | R1. | 79780008679 | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1.) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address one of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address two of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address three of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address four or more of the six topics required by R1. (R1.2) OR The Responsible Entity did not have any documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.2) | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service &lt;br/&gt;&lt;br/&gt;equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-ON | [6 empty] | 10000000
CIP-003-8 (Ontario) | 79780000597 | R2. | 79780008697 | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document cyber security awareness according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity implemented electronic access controls but failed to document its cyber security plan(s) for electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document one or more Cyber Security Incident response plan(s) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to update each Cyber Security Incident response plan(s) within 180 days according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to manage its Transient Cyber Asset(s) according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets, but failed to document the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to reinforce cyber security practices at least once every 15 calendar months according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls but failed to implement authentication for all Dial-up Connectivity that provides access to low impact BES Cyber System(s), per Cyber Asset capability according to Requirement R2, Attachment 1, Section 3.2 (R2) OR The Responsible Entity documented one or more incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to include the process for identification, classification, and response to Cyber Security Incidents according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident and subsequent notification to the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Sections 5.1 and 5.3. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented the physical access controls for its assets containing low impact BES Cyber Systems, but failed to implement the physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls for its assets containing low impact BES Cyber Systems, but failed to permit only necessary inbound and outbound electronic access controls according to Requirement R2, Attachment 1, Section 3.1. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to test each Cyber Security Incident response plan(s) at least once every 36 calendar months according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident, but failed to notify the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the threat of detected malicious code on the Removable Media prior to connecting Removable Media to a low impact BES Cyber System according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity failed to document and implement one or more cyber security plan(s) for its assets containing low impact BES Cyber Systems according to Requirement R2, Attachment 1. (R2) | M2. Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | 2020-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service &lt;br/&gt;&lt;br/&gt;equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-ON | [6 empty] | 20000000
CIP-003-8 (Ontario) | 79780000597 | R3. | 79780008698 | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. OR The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | 2020-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service &lt;br/&gt;&lt;br/&gt;equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-ON | [6 empty] | 30000000
CIP-003-8 (Ontario) | 79780000597 | R4. | 79780008699 | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | 2020-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service &lt;br/&gt;&lt;br/&gt;equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | NPCC-ON | [6 empty] | 40000000
CIP-003-8 (Saskatchewan) | 83750000000597 | R1. | 837500000008679 | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1.) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address one of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address two of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address three of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address four or more of the six topics required by R1. (R1.2) OR The Responsible Entity did not have any documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.2) | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-SK | [6 empty] | 10000000
CIP-003-8 (Saskatchewan) | 83750000000597 | R2. | 837500000008697 | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. |  | BA, DP, DP-UFLS, GO, GOP, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document cyber security awareness according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity implemented electronic access controls but failed to document its cyber security plan(s) for electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document one or more Cyber Security Incident response plan(s) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to update each Cyber Security Incident response plan(s) within 180 days according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to manage its Transient Cyber Asset(s) according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets, but failed to document the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to reinforce cyber security practices at least once every 15 calendar months according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls but failed to implement authentication for all Dial-up Connectivity that provides access to low impact BES Cyber System(s), per Cyber Asset capability according to Requirement R2, Attachment 1, Section 3.2 (R2) OR The Responsible Entity documented one or more incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to include the process for identification, classification, and response to Cyber Security Incidents according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident and subsequent notification to the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Sections 5.1 and 5.3. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented the physical access controls for its assets containing low impact BES Cyber Systems, but failed to implement the physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls for its assets containing low impact BES Cyber Systems, but failed to permit only necessary inbound and outbound electronic access controls according to Requirement R2, Attachment 1, Section 3.1. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to test each Cyber Security Incident response plan(s) at least once every 36 calendar months according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident, but failed to notify the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the threat of detected malicious code on the Removable Media prior to connecting Removable Media to a low impact BES Cyber System according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity failed to document and implement one or more cyber security plan(s) for its assets containing low impact BES Cyber Systems according to Requirement R2, Attachment 1. (R2) | M2. Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-SK | [6 empty] | 20000000
CIP-003-8 (Saskatchewan) | 83750000000597 | R3. | 837500000008698 | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. OR The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-SK | [6 empty] | 30000000
CIP-003-8 (Saskatchewan) | 83750000000597 | R4. | 837500000008699 | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-SK | [6 empty] | 40000000
CIP-003-9 | ST-2022-12-02-0000001 | R1. | RQ-2022-12-02-0000001 | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems, but did not address one of the seven topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems as required by Requirement R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems, but did not address two of the seven topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems as required by Requirement R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems, but did not address three of the seven topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies as required by R1 within 18 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems, but did not address four or more of the seven topics required by R1. (R1.2) OR The Responsible Entity did not have any documented cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems as required by R1. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.2) | M1. Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2026-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-003-9 | ST-2022-12-02-0000001 | R2. | RQ-2022-12-02-0000002 | Each Responsible Entity with at least one asset identified in CIP‐002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. Note: An inventory, list, or discrete identification of low impact BES Cyber Systems or their BES Cyber Assets is not required. Lists of authorized users are not required. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document cyber security awareness according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity implemented electronic access controls but failed to document its cyber security plan(s) for electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document one or more Cyber Security Incident response plan(s) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to update each Cyber Security Incident response plan(s) within 180 days according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to manage its Transient Cyber Asset(s) according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets, but failed to document the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) OR The Responsible Entity implemented vendor electronic remote access security controls but failed to document its cyber security process for vendor electronic remote access security controls according to Requirement R2, Attachment 1, Section 6. (R2) | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to reinforce cyber security practices at least once every 15 calendar months according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls but failed to implement authentication for all Dial‐up Connectivity that provides access to low impact BES Cyber System(s), per Cyber Asset capability according to Requirement R2, Attachment 1, Section 3.2 (R2) OR The Responsible Entity documented one or more incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to include the process for identification, classification, and response to Cyber Security Incidents according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident and subsequent notification to the Electricity Information Sharing and Analysis Center (E‐ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Sections 5.1 and 5.3. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) OR The Responsible Entity documented its cyber security process for vendor electronic remote access security controls, but failed to implement vendor electronic remote access security controls according to Requirement R2, Attachment 1, Section 6. (R2) | The Responsible Entity documented the physical access controls for its assets containing low impact BES Cyber Systems, but failed to implement the physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls for its assets containing low impact BES Cyber Systems, but failed to permit only necessary inbound and outbound electronic access controls according to Requirement R2, Attachment 1, Section 3.1. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to test each Cyber Security Incident response plan(s) at least once every 36 calendar months according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident, but failed to notify the Electricity Information Sharing and Analysis Center (E‐ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the threat of detected malicious code on the Removable Media prior to connecting Removable Media to a low impact BES Cyber System according to Requirement R2, Attachment 1, Section 5.3. (R2) OR The Responsible Entity failed to document and implement its cyber security process for vendor electronic remote access security controls according to Requirement R2, Attachment 1, Section 6. (R2) | The Responsible Entity failed to document and implement one or more cyber security plan(s) for its assets containing low impact BES Cyber Systems according to Requirement R2, Attachment 1. (R2) | M2. Evidence shall include each of the documented cyber security plan(s) that collectively include each of the sections in Attachment 1 and additional evidence to demonstrate implementation of the cyber security plan(s). Additional examples of evidence per section are located in Attachment 2. | 2026-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-003-9 | ST-2022-12-02-0000001 | R3. | RQ-2022-12-02-0000003 | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. OR The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) | M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager.M3. An example of evidence may include, but is not limited to, a dated and approved document from a high level official designating the name of the individual identified as the CIP Senior Manager. | 2026-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-003-9 | ST-2022-12-02-0000001 | R4. | RQ-2022-12-02-0000004 | he Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) | M4. An example of evidence may include, but is not limited to, a dated document, approved by the CIP Senior Manager, listing individuals (by name or title) who are delegated the authority to approve or authorize specifically identified items. | 2026-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-003-AB-5 (Alberta) | 656600000009007 | R1. | 656600000009092 | Each Responsible Entity, for its High Impact and Medium Impact BES cyber systems, shall review and obtain CIP senior manager approval at least once every 15 months for one or more documented cyber security policies that collectively address the following topics: |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 10000000
CIP-003-AB-5 (Alberta) | 656600000009007 | R2. | 656600000009093 | Each Responsible Entity for its assets identified in CIP-002-AB-5.1, requirement R1, part 1.3, shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented cyber security policies that collectively address the following topics, and review and obtain CIP senior manager approval for those policies at least once every 15 months: |  | ISO | [28 empty] | 2018-10-01 | [5 empty] | WECC-AB | [6 empty] | 20000000
CIP-003-AB-5 (Alberta) | 656600000009007 | R3. | 656600000009094 | Each Responsible Entity shall identify a CIP senior manager by name and document any change within 30 days of the change. |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 30000000
CIP-003-AB-5 (Alberta) | 656600000009007 | R4. | 656600000009095 | The Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP reliability standards, the CIP senior manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP senior manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 40000000
CIP-004-1 | 25 | R1. | 283 | Awareness — The Responsible Entity shall establish, maintain, and document a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: Direct communications (e.g., emails, memos, computer based training, etc.); Indirect communications (e.g., posters, intranet, brochures, etc.); Management support and reinforcement (e.g., presentations, meetings, etc.). |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-004-1 | 25 | R2. | 284 | Training — The Responsible Entity shall establish, maintain, and document an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and review the program annually and update as necessary. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-004-1 | 25 | R3. | 292 | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access. A personnel risk assessment shall be conducted pursuant to that program within thirty days of such personnel being granted such access. Such program shall at a minimum include: |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-004-1 | 25 | R4. | 296 | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-004-1 (British Columbia) | 666700000010037 | R1. | 666700000010546 | Awareness — The Responsible Entity shall establish, maintain, and document a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: Direct communications (e.g., emails, memos, computer based training, etc.); Indirect communications (e.g., posters, intranet, brochures, etc.); Management support and reinforcement (e.g., presentations, meetings, etc.). |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-004-1 (British Columbia) | 666700000010037 | R2. | 666700000010547 | Training — The Responsible Entity shall establish, maintain, and document an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and review the program annually and update as necessary. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 20000000
CIP-004-1 (British Columbia) | 666700000010037 | R3. | 666700000010548 | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access. A personnel risk assessment shall be conducted pursuant to that program within thirty days of such personnel being granted such access. Such program shall at a minimum include: |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 30000000
CIP-004-1 (British Columbia) | 666700000010037 | R4. | 666700000010549 | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 40000000
CIP-004-1 (Ontario) | 79780000025 | R1. | 79780000283 | Awareness — The Responsible Entity shall establish, maintain, and document a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: Direct communications (e.g., emails, memos, computer based training, etc.); Indirect communications (e.g., posters, intranet, brochures, etc.); Management support and reinforcement (e.g., presentations, meetings, etc.). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity established and maintained but did not document a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access receive on-going reinforcement in sound security practices. | The Responsible Entity established and maintained but did not document a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access receive on-going reinforcement in sound security practices.&lt;br/&gt;AND&lt;br/&gt;The Re | The Responsible Entity did document but did not establish nor maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access receive on-going reinforcement in sound security practices. | The Responsible Entity did not establish, maintain, nor document a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access receive on-going reinforcement in sound security practices. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-004-1 (Ontario) | 79780000025 | R2. | 79780000284 | Training — The Responsible Entity shall establish, maintain, and document an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and review the program annually and update as necessary. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity established and maintained but did not document an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. | The Responsible Entity established and maintained but did not document an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets&lt;br/&gt;AND &lt;br/&gt;The Responsible Entity did not re | The Responsible Entity did document but did not establish nor maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. | The Responsible Entity did not establish, maintain, nor document an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-004-1 (Ontario) | 79780000025 | R3. | 79780000292 | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access. A personnel risk assessment shall be conducted pursuant to that program within thirty days of such personnel being granted such access. Such program shall at a minimum include: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | N/A | The Responsible Entity has a personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted ph | The Responsible Entity has a personnel risk assessment program as stated in R3, but conducted the personnel risk assessment pursuant to that program in more than thirty (30) days of such personnel being granted such access. | The Responsible Entity does not have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or au |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-004-1 (Ontario) | 79780000025 | R4. | 79780000296 | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-004-2 | 210 | R1. | 2394 | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: Direct communications (e.g. emails, memos, computer based training, etc.); Indirect communications (e.g. posters, intranet, brochures, etc.); Management support and reinforcement (e.g., presentations, meetings, etc.). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-004-2 | 210 | R2. | 2395 | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-004-2 | 210 | R3. | 2403 | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-004-2 | 210 | R4. | 2407 | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  | CIP-004-1 R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-004-2 (Ontario) | 79780000210 | R1. | 79780002394 | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: Direct communications (e.g. emails, memos, computer based training, etc.); Indirect communications (e.g. posters, intranet, brochures, etc.); Management support and reinforcement (e.g., presentations, meetings, etc.). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-004-2 (Ontario) | 79780000210 | R2. | 79780002395 | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-004-2 (Ontario) | 79780000210 | R3. | 79780002403 | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-004-2 (Ontario) | 79780000210 | R4. | 79780002407 | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-004-3 | 224 | R1. | 2753 | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-10-01 |  | 2012-12-11 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-004-3 | 224 | R2. | 2754 | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-10-01 |  | 2012-12-11 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-004-3 | 224 | R3. | 2762 | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-10-01 |  | 2012-12-11 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-004-3 | 224 | R4. | 2766 | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-10-01 |  | 2012-12-11 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-004-3a | 333 | R1. | 4363 | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M1. The Responsible Entity shall make available documentation of its security awareness and reinforcement program as specified in Requirement R1. | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-004-3a | 333 | R2. | 4364 | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M2. The Responsible Entity shall make available documentation of its cyber security training program, review, and records as specified in Requirement R2. | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-004-3a | 333 | R3. | 4366 | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M3. The Responsible Entity shall make available documentation of the personnel risk assessment program and that personnel risk assessments have been applied to all personnel who have authorized cyber or authorized unescorted physical access to Critical Cyber Assets, as specified in Requirement R3. | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-004-3a | 333 | R4. | 4365 | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M4. The Responsible Entity shall make available documentation of the list(s), list review and update, and access revocation as needed as specified in Requirement R4. | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-004-3a (British Columbia) | 666700000010039 | R1. | 666700000010554 | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M1. The Responsible Entity shall make available documentation of its security awareness and reinforcement program as specified in Requirement R1. | 2014-08-01 |  | 2018-09-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | WECC-BC | [6 empty] | 10000000
CIP-004-3a (British Columbia) | 666700000010039 | R2. | 666700000010555 | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M2. The Responsible Entity shall make available documentation of its cyber security training program, review, and records as specified in Requirement R2. | 2014-08-01 |  | 2018-09-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | WECC-BC | [6 empty] | 20000000
CIP-004-3a (British Columbia) | 666700000010039 | R3. | 666700000010556 | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M3. The Responsible Entity shall make available documentation of the personnel risk assessment program and that personnel risk assessments have been applied to all personnel who have authorized cyber or authorized unescorted physical access to Critical Cyber Assets, as specified in Requirement R3. | 2014-08-01 |  | 2018-09-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | WECC-BC | [6 empty] | 30000000
CIP-004-3a (British Columbia) | 666700000010039 | R4. | 666700000010557 | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M4. The Responsible Entity shall make available documentation of the list(s), list review and update, and access revocation as needed as specified in Requirement R4. | 2014-08-01 |  | 2018-09-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | WECC-BC | [6 empty] | 40000000
CIP-004-3a (Manitoba) | 77660000000333 | R1. | 776600000004363 | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M1. The Responsible Entity shall make available documentation of its security awareness and reinforcement program as specified in Requirement R1. | 2014-02-14 |  | 2017-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-MB | [6 empty] | 10000000
CIP-004-3a (Manitoba) | 77660000000333 | R2. | 776600000004364 | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M2. The Responsible Entity shall make available documentation of its cyber security training program, review, and records as specified in Requirement R2. | 2014-02-14 |  | 2017-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-MB | [6 empty] | 20000000
CIP-004-3a (Manitoba) | 77660000000333 | R3. | 776600000004366 | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M3. The Responsible Entity shall make available documentation of the personnel risk assessment program and that personnel risk assessments have been applied to all personnel who have authorized cyber or authorized unescorted physical access to Critical Cyber Assets, as specified in Requirement R3. | 2014-02-14 |  | 2017-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-MB | [6 empty] | 30000000
CIP-004-3a (Manitoba) | 77660000000333 | R4. | 776600000004365 | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M4. The Responsible Entity shall make available documentation of the list(s), list review and update, and access revocation as needed as specified in Requirement R4. | 2014-02-14 |  | 2017-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-MB | [6 empty] | 40000000
CIP-004-3a (Ontario) | 79780000333 | R1. | 79780004363 | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: &lt;br/&gt;• Direct communications (e.g., emails, memos, computer based training, etc.);&lt;br/&gt;• Indirect communications (e.g., posters, intranet, brochures, etc.);&lt;br/&gt;• Management support and reinforcement (e.g., presentations, meetings, etc.). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M1. The Responsible Entity shall make available documentation of its security awareness and reinforcement program as specified in Requirement R1. | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:&lt;br/&gt;&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | NPCC-ON | [6 empty] | 10000000
CIP-004-3a (Ontario) | 79780000333 | R2. | 79780004364 | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M2. The Responsible Entity shall make available documentation of its cyber security training program, review, and records as specified in Requirement R2. | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:&lt;br/&gt;&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | NPCC-ON | [6 empty] | 20000000
CIP-004-3a (Ontario) | 79780000333 | R3. | 79780004366 | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. &lt;br/&gt;The personnel risk assessment program shall at a minimum include: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M3. The Responsible Entity shall make available documentation of the personnel risk assessment program and that personnel risk assessments have been applied to all personnel who have authorized cyber or authorized unescorted physical access to Critical Cyber Assets, as specified in Requirement R3. | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:&lt;br/&gt;&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | NPCC-ON | [6 empty] | 30000000
CIP-004-3a (Ontario) | 79780000333 | R4. | 79780004365 | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M4. The Responsible Entity shall make available documentation of the list(s), list review and update, and access revocation as needed as specified in Requirement R4. | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:&lt;br/&gt;&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | NPCC-ON | [6 empty] | 40000000
CIP-004-3 (British Columbia) | 666700000010038 | R1. | 666700000010550 | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2012-07-01 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-004-3 (British Columbia) | 666700000010038 | R2. | 666700000010551 | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2012-07-01 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 20000000
CIP-004-3 (British Columbia) | 666700000010038 | R3. | 666700000010552 | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2012-07-01 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 30000000
CIP-004-3 (British Columbia) | 666700000010038 | R4. | 666700000010553 | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2012-07-01 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 40000000
CIP-004-3 (Manitoba) | 77660000000224 | R1. | 776600000002753 | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 10000000
CIP-004-3 (Manitoba) | 77660000000224 | R2. | 776600000002754 | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 20000000
CIP-004-3 (Manitoba) | 77660000000224 | R3. | 776600000002762 | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 30000000
CIP-004-3 (Manitoba) | 77660000000224 | R4. | 776600000002766 | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 40000000
CIP-004-3 (Ontario) | 79780000224 | R1. | 79780002753 | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: &lt;br/&gt;• Direct communications (e.g., emails, memos, computer based training, etc.);&lt;br/&gt;• Indirect communications (e.g., posters, intranet, brochures, etc.);&lt;br/&gt;• Management support and reinforcement (e.g., presentations, meetings, etc.). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-10-01 |  | 2012-12-11 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-004-3 (Ontario) | 79780000224 | R2. | 79780002754 | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-10-01 |  | 2012-12-11 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-004-3 (Ontario) | 79780000224 | R3. | 79780002762 | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. &lt;br/&gt;The personnel risk assessment program shall at a minimum include: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-10-01 |  | 2012-12-11 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-004-3 (Ontario) | 79780000224 | R4. | 79780002766 | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-10-01 |  | 2012-12-11 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-004-4 | 250 | R1. | 3242 | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity established, implemented, and maintained but did not document a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive ongoing reinforcement in sound security practices. | The Responsibility Entity did not provide security awareness reinforcement on at least a quarterly basis. | The Responsible Entity did document but did not establish, implement, nor maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. | The Responsible Entity did not establish, implement, maintain, nor document a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. |  |  |  | 2012-12-11 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-004-4 | 250 | R2. | 3243 | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity established, implemented, and maintained but did not document an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. | The Responsibility Entity did not review the training program on an annual basis. | The Responsible Entity did document but did not establish, implement, nor maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. | The Responsible Entity did not establish, implement, maintain, or document an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. |  |  |  | 2012-12-11 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-004-4 | 250 | R3. | 3251 | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity has a personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access, but the program is not documented. | The Responsible Entity has a personnel risk assessment program as stated in R3, but conducted the personnel risk assessment pursuant to that program after such personnel were granted such access except in specified circumstances such as an emergency. | The Responsible Entity does not have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access. OR The Responsible Entity did not conduct the personnel risk assessment pursuant to that program for personnel granted such access except in specified circumstances such as an emergency. |  |  |  | 2012-12-11 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-004-4 | 250 | R4. | 3255 | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing at least one individual but less than 5% of the authorized personnel. | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing 5% or more but less than 10% of the authorized personnel. | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing 10% or more but less than 15%of the authorized personnel. | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing 15% or more of the authorized personnel. |  |  |  | 2012-12-11 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-004-4a | 334 | R1. | 4379 | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity established, implemented, and maintained but did not document a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive ongoing reinforcement in sound security practices. | The Responsibility Entity did not provide security awareness reinforcement on at least a quarterly basis. | The Responsible Entity did document but did not establish, implement, nor maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. | The Responsible Entity did not establish, implement, maintain, nor document a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-004-4a | 334 | R2. | 4380 | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity established, implemented, and maintained but did not document an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. | The Responsibility Entity did not review the training program on an annual basis. | The Responsible Entity did document but did not establish, implement, nor maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. | The Responsible Entity did not establish, implement, maintain, or document an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-004-4a | 334 | R3. | 4382 | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity has a personnel risk assessment program, as stated in R3, for personnel having authorized cyber or authorized unescorted physical access, but the program is not documented. | The Responsible Entity has a personnel risk assessment program as stated in R3, but conducted the personnel risk assessment pursuant to that program after such personnel were granted such access except in specified circumstances such as an emergency. | The Responsible Entity does not have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access. OR The Responsible Entity did not conduct the personnel risk assessment pursuant to that program for personnel granted such access except in specified circumstances such as an emergency |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-004-4a | 334 | R4. | 4381 | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing at least one individual but less than 5% of the authorized personnel. | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing 5% or more but less than 10% of the authorized personnel. | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing 10% or more but less than 15%of the authorized personnel. | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing 15% or more of the authorized personnel. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-004-4a (Ontario) | 79780000334 | R1. | 79780004379 | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | The Responsible Entity did not provide security awareness reinforcement on at least a quarterly basis. | The Responsible Entity did not establish, implement, maintain, or document a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound s |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-004-4a (Ontario) | 79780000334 | R2. | 79780004380 | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | The Responsible Entity did not review the training program on an annual basis. | The Responsible Entity did not establish, implement, maintain, or document an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-004-4a (Ontario) | 79780000334 | R3. | 79780004382 | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity has a personnel risk assessment program, as stated in R3, for personnel having authorized cyber or authorized unescorted physical access, but the program is not documented. | The Responsible Entity has a personnel risk assessment program as stated in R3, but conducted the personnel risk assessment pursuant to that program after such personnel were granted such access except in specified circumstances such as an emergency. | The Responsible Entity does not have a documented personnel risk assessment program, as stated in R3, for personnel having authorized cyber or authorized unescorted physical access. OR The Responsible Entity did not conduct the personnel risk assessmen |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-004-4a (Ontario) | 79780000334 | R4. | 79780004381 | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-004-4 (Ontario) | 79780000250 | R1. | 79780003242 | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | The Responsible Entity did not provide security awareness reinforcement on at least a quarterly basis. | The Responsible Entity did not establish, implement, maintain, or document a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound s |  |  |  | 2012-12-11 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-004-4 (Ontario) | 79780000250 | R2. | 79780003243 | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | The Responsible Entity did not review the training program on an annual basis. | The Responsible Entity did not establish, implement, maintain, or document an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. |  |  |  | 2012-12-11 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-004-4 (Ontario) | 79780000250 | R3. | 79780003251 | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity has a personnel risk assessment program, as stated in R3, for personnel having authorized cyber or authorized unescorted physical access, but the program is not documented. | The Responsible Entity has a personnel risk assessment program as stated in R3, but conducted the personnel risk assessment pursuant to that program after such personnel were granted such access except in specified circumstances such as an emergency. | The Responsible Entity does not have a documented personnel risk assessment program, as stated in R3, for personnel having authorized cyber or authorized unescorted physical access. OR The Responsible Entity did not conduct the personnel risk assessmen |  |  |  | 2012-12-11 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-004-4 (Ontario) | 79780000250 | R4. | 79780003255 | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing |  |  |  | 2012-12-11 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-004-5 | 348 | R1. | 4486 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-5 Table R1 – Security Awareness Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so within the subsequent quarter but beyond 30 calendar days after the start of that calendar quarter. (1.1) | The Responsible Entity did not document or implement any security awareness process(es) to reinforce cyber security practices. (R1) or The Responsible Entity did not reinforce cyber security practices and associated physical security practices for at least two consecutive calendar quarters. (1.1) |  |  |  | 2013-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-004-5 | 348 | R2. | 4487 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-5 Table R2 – Cyber Security Training Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity implemented a cyber security training program but failed to include one of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or Responsible Entity implemented a cyber security training program but failed to train one individual (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train one individual with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include two of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train two individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train two individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include three of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train three individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train three individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity did not implement a cyber security training program appropriate to individual roles, functions, or responsibilities. (R2) or The Responsible Entity implemented a cyber security training program but failed to include four or more of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train four or more individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train four or more individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) |  |  |  | 2013-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-004-5 | 348 | R3. | 4488 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented personnel risk assessment programs to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-5 Table R3 – Personnel Risk Assessment Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for one individual, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for one individual, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for one individual, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for one individual, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for one individual with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for two individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for two individuals, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for two individuals, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for two individuals, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for two individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for three individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for three individuals, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for three individuals, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for three individuals, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for three individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity did not have all of the required elements as described by 3.1 through 3.4 included within documented program(s) for implementing Personnel Risk Assessments (PRAs), for individuals, including contractors and service vendors, for obtaining and retaining authorized cyber or authorized unescorted physical access. (R3) or The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for four or more individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for four or more individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date and has identified deficiencies, and did not identify, assess, and correct the deficiencies. (3.5) |  |  |  | 2013-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-004-5 | 348 | R4. | 4489 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access management programs that collectively include each of the applicable requirement parts in CIP-004-5 Table R4 – Access Management Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Low | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter, and did not identify, assess and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System, privileges were incorrect or unnecessary, and did not identify, assess and correct the deficiencies.(4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System Information storage location, privileges were incorrect or unnecessary, and did not identify, assess and correct the deficiencies. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for two BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for two BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for three BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for three BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) | The Responsible Entity did not implement any documented program(s) for access management. (R4) or The Responsible Entity has implemented one or more documented program(s) for access management that includes a process to authorize electronic access, unescorted physical access, or access to the designated storage locations where BES Cyber System Information is located, and did not identify, assess, and correct the deficiencies. (4.1) or The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records for at least two consecutive calendar quarters, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) |  |  |  | 2013-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-004-5 | 348 | R5. | 4490 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access revocation programs that collectively include each of the applicable requirement parts in CIP-004-5 Table R5 – Access Revocation. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for one individual, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s user accounts upon termination action but did not do so for within 30 calendar days of the date of termination action for one or more individuals, and did not identify, assess, and correct the deficiencies. (5.4) or The Responsible Entity has implemented one or more process(es) to change passwords for shared accounts known to the user upon termination action, reassignment, or transfer, but did not do so for within 30 calendar days of the date of termination action, reassignment, or transfer for one or more individuals, and did not identify, assess, and correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more process(es) to determine and document extenuating operating circumstances following a termination action, reassignment, or transfer, but did not change one or more passwords for shared accounts known to the user within 10 calendar days following the end of the extenuating operating circumstances, and did not identify, assess, and correct the deficiencies. (5.5) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for one individual, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for one individual, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for two individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for two individuals, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for two individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for three or more individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) | The Responsible Entity has not implemented any documented program(s) for access revocation for electronic access, unescorted physical access, or BES Cyber System Information storage locations. (R5) or The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for three or more individuals, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for three or more individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) |  |  |  | 2013-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-004-5.1 | 426 | R1. | 5245 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-5 Table R1 – Security Awareness Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so within the subsequent quarter but beyond 30 calendar days after the start of that calendar quarter. (1.1) | The Responsible Entity did not document or implement any security awareness process(es) to reinforce cyber security practices. (R1) or The Responsible Entity did not reinforce cyber security practices and associated physical security practices for at least two consecutive calendar quarters. (1.1) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R1 – Security Awareness Program and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-004-5.1 | 426 | R2. | 5246 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-5 Table R2 – Cyber Security Training Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity implemented a cyber security training program but failed to include one of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or Responsible Entity implemented a cyber security training program but failed to train one individual (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train one individual with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include two of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train two individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train two individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include three of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train three individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train three individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity did not implement a cyber security training program appropriate to individual roles, functions, or responsibilities. (R2) or The Responsible Entity implemented a cyber security training program but failed to include four or more of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train four or more individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train four or more individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-5.1 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-004-5.1 | 426 | R3. | 5247 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented personnel risk assessment programs to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R3 – Personnel Risk Assessment Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for one individual, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for one individual, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for one individual, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for one individual, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for one individual with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for two individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for two individuals, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for two individuals, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for two individuals, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for two individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for three individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for three individuals, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for three individuals, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for three individuals, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for three individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity did not have all of the required elements as described by 3.1 through 3.4 included within documented program(s) for implementing Personnel Risk Assessments (PRAs), for individuals, including contractors and service vendors, for obtaining and retaining authorized cyber or authorized unescorted physical access. (R3) or The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for four or more individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for four or more individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date and has identified deficiencies, and did not identify, assess, and correct the deficiencies. (3.5) | Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-004-5.1 | 426 | R4. | 5248 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access management programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R4 – Access Management Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter, and did not identify, assess and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System, privileges were incorrect or unnecessary, and did not identify, assess and correct the deficiencies.(4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System Information storage location, privileges were incorrect or unnecessary, and did not identify, assess and correct the deficiencies. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 10 and 20 calendar days after the start of a subsequent calendar quarter, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for two BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for two BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 20 and 30 calendar days after the start of a subsequent calendar quarter, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for three BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for three BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) | The Responsible Entity did not implement any documented program(s) for access management. (R4) or The Responsible Entity has implemented one or more documented program(s) for access management that includes a process to authorize electronic access, unescorted physical access, or access to the designated storage locations where BES Cyber System Information is located, and did not identify, assess, and correct the deficiencies. (4.1) or The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records for at least two consecutive calendar quarters, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-004-5.1 | 426 | R5. | 5249 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access revocation programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R5 – Access Revocation. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for one individual, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s user accounts upon termination action but did not do so for within 30 calendar days of the date of termination action for one or more individuals, and did not identify, assess, and correct the deficiencies. (5.4) or The Responsible Entity has implemented one or more process(es) to change passwords for shared accounts known to the user upon termination action, reassignment, or transfer, but did not do so for within 30 calendar days of the date of termination action, reassignment, or transfer for one or more individuals, and did not identify, assess, and correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more process(es) to determine and document extenuating operating circumstances following a termination action, reassignment, or transfer, but did not change one or more passwords for shared accounts known to the user within 10 calendar days following the end of the extenuating operating circumstances, and did not identify, assess, and correct the deficiencies. (5.5) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for one individual, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for one individual, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for two individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for two individuals, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for two individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for three or more individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) | The Responsible Entity has not implemented any documented program(s) for access revocation for electronic access, unescorted physical access, or BES Cyber System Information storage locations. (R5) or The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for three or more individuals, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for three or more individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) | Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-004-5.1 (British Columbia) | 666700000010040 | R1. | 666700000010558 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-5 Table R1 – Security Awareness Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so within the subsequent quarter but beyond 30 calendar days after the start of that calendar quarter. (1.1) | The Responsible Entity did not document or implement any security awareness process(es) to reinforce cyber security practices. (R1) or The Responsible Entity did not reinforce cyber security practices and associated physical security practices for at least two consecutive calendar quarters. (1.1) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R1 – Security Awareness Program and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-004-5.1 (British Columbia) | 666700000010040 | R2. | 666700000010559 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-5 Table R2 – Cyber Security Training Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity implemented a cyber security training program but failed to include one of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or Responsible Entity implemented a cyber security training program but failed to train one individual (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train one individual with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include two of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train two individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train two individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include three of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train three individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train three individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity did not implement a cyber security training program appropriate to individual roles, functions, or responsibilities. (R2) or The Responsible Entity implemented a cyber security training program but failed to include four or more of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train four or more individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train four or more individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-5.1 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). |  |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 20000000
CIP-004-5.1 (British Columbia) | 666700000010040 | R3. | 666700000010560 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented personnel risk assessment programs to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R3 – Personnel Risk Assessment Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for one individual, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for one individual, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for one individual, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for one individual, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for one individual with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for two individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for two individuals, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for two individuals, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for two individuals, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for two individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for three individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for three individuals, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for three individuals, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for three individuals, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for three individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity did not have all of the required elements as described by 3.1 through 3.4 included within documented program(s) for implementing Personnel Risk Assessments (PRAs), for individuals, including contractors and service vendors, for obtaining and retaining authorized cyber or authorized unescorted physical access. (R3) or The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for four or more individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for four or more individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date and has identified deficiencies, and did not identify, assess, and correct the deficiencies. (3.5) | Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). |  |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 30000000
CIP-004-5.1 (British Columbia) | 666700000010040 | R4. | 666700000010561 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access management programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R4 – Access Management Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter, and did not identify, assess and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System, privileges were incorrect or unnecessary, and did not identify, assess and correct the deficiencies.(4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System Information storage location, privileges were incorrect or unnecessary, and did not identify, assess and correct the deficiencies. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 10 and 20 calendar days after the start of a subsequent calendar quarter, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for two BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for two BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 20 and 30 calendar days after the start of a subsequent calendar quarter, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for three BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for three BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) | The Responsible Entity did not implement any documented program(s) for access management. (R4) or The Responsible Entity has implemented one or more documented program(s) for access management that includes a process to authorize electronic access, unescorted physical access, or access to the designated storage locations where BES Cyber System Information is located, and did not identify, assess, and correct the deficiencies. (4.1) or The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records for at least two consecutive calendar quarters, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. |  |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 40000000
CIP-004-5.1 (British Columbia) | 666700000010040 | R5. | 666700000010562 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access revocation programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R5 – Access Revocation. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for one individual, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s user accounts upon termination action but did not do so for within 30 calendar days of the date of termination action for one or more individuals, and did not identify, assess, and correct the deficiencies. (5.4) or The Responsible Entity has implemented one or more process(es) to change passwords for shared accounts known to the user upon termination action, reassignment, or transfer, but did not do so for within 30 calendar days of the date of termination action, reassignment, or transfer for one or more individuals, and did not identify, assess, and correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more process(es) to determine and document extenuating operating circumstances following a termination action, reassignment, or transfer, but did not change one or more passwords for shared accounts known to the user within 10 calendar days following the end of the extenuating operating circumstances, and did not identify, assess, and correct the deficiencies. (5.5) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for one individual, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for one individual, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for two individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for two individuals, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for two individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for three or more individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) | The Responsible Entity has not implemented any documented program(s) for access revocation for electronic access, unescorted physical access, or BES Cyber System Information storage locations. (R5) or The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for three or more individuals, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for three or more individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) | Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 50000000
CIP-004-5.1 (Ontario) | 79780000426 | R1. | 79780005245 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-5 Table R1 – Security Awareness Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so within the subsequent quarter but beyond 30 calendar days after the start of that calendar quarter. (1.1) | The Responsible Entity did not document or implement any security awareness process(es) to reinforce cyber security practices. (R1) or The Responsible Entity did not reinforce cyber security practices and associated physical security practices for at least two consecutive calendar quarters. (1.1) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R1 – Security Awareness Program and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-004-5.1 (Ontario) | 79780000426 | R2. | 79780005246 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-5 Table R2 – Cyber Security Training Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity implemented a cyber security training program but failed to include one of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or Responsible Entity implemented a cyber security training program but failed to train one individual (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train one individual with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include two of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train two individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train two individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include three of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train three individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train three individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity did not implement a cyber security training program appropriate to individual roles, functions, or responsibilities. (R2) or The Responsible Entity implemented a cyber security training program but failed to include four or more of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train four or more individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train four or more individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-5.1 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). |  |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-004-5.1 (Ontario) | 79780000426 | R3. | 79780005247 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented personnel risk assessment programs to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-5 Table R3 – Personnel Risk Assessment Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for one individual, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for one individual, and did not identify, assess, and correct the deficiencies. (3.1 &amp;amp; 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for one individual, and did not identify, assess, and correct the deficiencies. (3.2 &amp;amp; 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for one individual, and did not identify, assess, and correct the deficiencies. (3.3 &amp;amp; 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for one individual with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for two individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for two individuals, and did not identify, assess, and correct the deficiencies. (3.1 &amp;amp; 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for two individuals, and did not identify, assess, and correct the deficiencies. (3.2 &amp;amp; 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for two individuals, and did not identify, assess, and correct the deficiencies. (3.3 &amp;amp; 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for two individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for three individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for three individuals, and did not identify, assess, and correct the deficiencies. (3.1 &amp;amp; 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for three individuals, and did not identify, assess, and correct the deficiencies. (3.2 &amp;amp; 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for three individuals, and did not identify, assess, and correct the deficiencies. (3.3 &amp;amp; 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for three individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity did not have all of the required elements as described by 3.1 through 3.4 included within documented program(s) for implementing Personnel Risk Assessments (PRAs), for individuals, including contractors and service vendors, for obtaining and retaining authorized cyber or authorized unescorted physical access. (R3) or The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for four or more individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.1 &amp;amp; 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.2 &amp;amp; 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.3 &amp;amp; 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for four or more individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date and has identified deficiencies, and did not identify, assess, and correct the deficiencies. (3.5) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R1 – Security Awareness Program and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-004-5.1 (Ontario) | 79780000426 | R4. | 79780005248 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access management programs that collectively include each of the applicable requirement parts in CIP-004-5 Table R4 – Access Management Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Low | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter, and did not identify, assess and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System, privileges were incorrect or unnecessary, and did not identify, assess and correct the deficiencies.(4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System Information storage location, privileges were incorrect or unnecessary, and did not identify, assess and correct the deficiencies. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 10 and 20 calendar days after the start of a subsequent calendar quarter, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for two BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for two BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 20 and 30 calendar days after the start of a subsequent calendar quarter, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for three BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for three BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) | The Responsible Entity did not implement any documented program(s) for access management. (R4) or The Responsible Entity has implemented one or more documented program(s) for access management that includes a process to authorize electronic access, unescorted physical access, or access to the designated storage locations where BES Cyber System Information is located, and did not identify, assess, and correct the deficiencies. (4.1) or The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records for at least two consecutive calendar quarters, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. |  |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-004-5.1 (Ontario) | 79780000426 | R5. | 79780005249 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access revocation programs that collectively include each of the applicable requirement parts in CIP-004-5 Table R5 – Access Revocation. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for one individual, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s user accounts upon termination action but did not do so for within 30 calendar days of the date of termination action for one or more individuals, and did not identify, assess, and correct the deficiencies. (5.4) or The Responsible Entity has implemented one or more process(es) to change passwords for shared accounts known to the user upon termination action, reassignment, or transfer, but did not do so for within 30 calendar days of the date of termination action, reassignment, or transfer for one or more individuals, and did not identify, assess, and correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more process(es) to determine and document extenuating operating circumstances following a termination action, reassignment, or transfer, but did not change one or more passwords for shared accounts known to the user within 10 calendar days following the end of the extenuating operating circumstances, and did not identify, assess, and correct the deficiencies. (5.5) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for one individual, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for one individual, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for two individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for two individuals, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for two individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for three or more individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) | The Responsible Entity has not implemented any documented program(s) for access revocation for electronic access, unescorted physical access, or BES Cyber System Information storage locations. (R5) or The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for three or more individuals, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for three or more individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) | M3.1. An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to confirm identity. |  |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-004-5.1 (Saskatchewan) | 83750000000426 | R1. | 837500000005245 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-5 Table R1 – Security Awareness Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so within the subsequent quarter but beyond 30 calendar days after the start of that calendar quarter. (1.1) | The Responsible Entity did not document or implement any security awareness process(es) to reinforce cyber security practices. (R1) or The Responsible Entity did not reinforce cyber security practices and associated physical security practices for at least two consecutive calendar quarters. (1.1) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R1 – Security Awareness Program and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 10000000
CIP-004-5.1 (Saskatchewan) | 83750000000426 | R2. | 837500000005246 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-5 Table R2 – Cyber Security Training Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity implemented a cyber security training program but failed to include one of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or Responsible Entity implemented a cyber security training program but failed to train one individual (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train one individual with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include two of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train two individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train two individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include three of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train three individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train three individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity did not implement a cyber security training program appropriate to individual roles, functions, or responsibilities. (R2) or The Responsible Entity implemented a cyber security training program but failed to include four or more of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train four or more individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train four or more individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-5.1 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). |  |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 20000000
CIP-004-5.1 (Saskatchewan) | 83750000000426 | R3. | 837500000005247 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented personnel risk assessment programs to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R3 – Personnel Risk Assessment Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for one individual, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for one individual, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for one individual, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for one individual, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for one individual with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for two individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for two individuals, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for two individuals, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for two individuals, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for two individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for three individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for three individuals, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for three individuals, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for three individuals, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for three individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity did not have all of the required elements as described by 3.1 through 3.4 included within documented program(s) for implementing Personnel Risk Assessments (PRAs), for individuals, including contractors and service vendors, for obtaining and retaining authorized cyber or authorized unescorted physical access. (R3) or The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for four or more individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for four or more individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date and has identified deficiencies, and did not identify, assess, and correct the deficiencies. (3.5) | Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). |  |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 30000000
CIP-004-5.1 (Saskatchewan) | 83750000000426 | R4. | 837500000005248 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access management programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R4 – Access Management Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter, and did not identify, assess and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System, privileges were incorrect or unnecessary, and did not identify, assess and correct the deficiencies.(4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System Information storage location, privileges were incorrect or unnecessary, and did not identify, assess and correct the deficiencies. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 10 and 20 calendar days after the start of a subsequent calendar quarter, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for two BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for two BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 20 and 30 calendar days after the start of a subsequent calendar quarter, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for three BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for three BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) | The Responsible Entity did not implement any documented program(s) for access management. (R4) or The Responsible Entity has implemented one or more documented program(s) for access management that includes a process to authorize electronic access, unescorted physical access, or access to the designated storage locations where BES Cyber System Information is located, and did not identify, assess, and correct the deficiencies. (4.1) or The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records for at least two consecutive calendar quarters, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. |  |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 40000000
CIP-004-5.1 (Saskatchewan) | 83750000000426 | R5. | 837500000005249 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access revocation programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R5 – Access Revocation. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for one individual, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s user accounts upon termination action but did not do so for within 30 calendar days of the date of termination action for one or more individuals, and did not identify, assess, and correct the deficiencies. (5.4) or The Responsible Entity has implemented one or more process(es) to change passwords for shared accounts known to the user upon termination action, reassignment, or transfer, but did not do so for within 30 calendar days of the date of termination action, reassignment, or transfer for one or more individuals, and did not identify, assess, and correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more process(es) to determine and document extenuating operating circumstances following a termination action, reassignment, or transfer, but did not change one or more passwords for shared accounts known to the user within 10 calendar days following the end of the extenuating operating circumstances, and did not identify, assess, and correct the deficiencies. (5.5) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for one individual, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for one individual, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for two individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for two individuals, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for two individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for three or more individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) | The Responsible Entity has not implemented any documented program(s) for access revocation for electronic access, unescorted physical access, or BES Cyber System Information storage locations. (R5) or The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for three or more individuals, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for three or more individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) | Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 50000000
CIP-004-5 (Ontario) | 79780000348 | R1. | 79780004486 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-5 Table R1 – Security Awareness Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Low | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so within the subsequent quarter but beyond 30 calendar days after the start of that calendar quarter. (1.1) | The Responsible Entity did not document or implement any security awareness process(es) to reinforce cyber security practices. (R1) or The Responsible Entity did not reinforce cyber security practices and associated physical security practices for at least two consecutive calendar quarters. (1.1) |  |  |  | 2013-09-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-004-5 (Ontario) | 79780000348 | R2. | 79780004487 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-5 Table R2 – Cyber Security Training Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Low | The Responsible Entity implemented a cyber security training program but failed to include one of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or Responsible Entity implemented a cyber security training program but failed to train one individual (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train one individual with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include two of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train two individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train two individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include three of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train three individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train three individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity did not implement a cyber security training program appropriate to individual roles, functions, or responsibilities. (R2) or The Responsible Entity implemented a cyber security training program but failed to include four or more of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train four or more individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train four or more individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) |  |  |  | 2013-09-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-004-5 (Ontario) | 79780000348 | R3. | 79780004488 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented personnel risk assessment programs to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-5 Table R3 – Personnel Risk Assessment Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Medium | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for one individual, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for one individual, and did not identify, assess, and correct the deficiencies. (3.1 &amp;amp; 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for one individual, and did not identify, assess, and correct the deficiencies. (3.2 &amp;amp; 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for one individual, and did not identify, assess, and correct the deficiencies. (3.3 &amp;amp; 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for one individual with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for two individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for two individuals, and did not identify, assess, and correct the deficiencies. (3.1 &amp;amp; 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for two individuals, and did not identify, assess, and correct the deficiencies. (3.2 &amp;amp; 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for two individuals, and did not identify, assess, and correct the deficiencies. (3.3 &amp;amp; 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for two individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for three individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for three individuals, and did not identify, assess, and correct the deficiencies. (3.1 &amp;amp; 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for three individuals, and did not identify, assess, and correct the deficiencies. (3.2 &amp;amp; 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for three individuals, and did not identify, assess, and correct the deficiencies. (3.3 &amp;amp; 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for three individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity did not have all of the required elements as described by 3.1 through 3.4 included within documented program(s) for implementing Personnel Risk Assessments (PRAs), for individuals, including contractors and service vendors, for obtaining and retaining authorized cyber or authorized unescorted physical access. (R3) or The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for four or more individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.1 &amp;amp; 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.2 &amp;amp; 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.3 &amp;amp; 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for four or more individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date and has identified deficiencies, and did not identify, assess, and correct the deficiencies. (3.5) |  |  |  | 2013-09-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-004-5 (Ontario) | 79780000348 | R4. | 79780004489 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access management programs that collectively include each of the applicable requirement parts in CIP-004-5 Table R4 – Access Management Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Low | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter, and did not identify, assess and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System, privileges were incorrect or unnecessary, and did not identify, assess and correct the deficiencies.(4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System Information storage location, privileges were incorrect or unnecessary, and did not identify, assess and correct the deficiencies. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for two BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for two BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for three BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for three BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) | The Responsible Entity did not implement any documented program(s) for access management. (R4) or The Responsible Entity has implemented one or more documented program(s) for access management that includes a process to authorize electronic access, unescorted physical access, or access to the designated storage locations where BES Cyber System Information is located, and did not identify, assess, and correct the deficiencies. (4.1) or The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records for at least two consecutive calendar quarters, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) |  |  |  | 2013-09-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-004-5 (Ontario) | 79780000348 | R5. | 79780004490 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access revocation programs that collectively include each of the applicable requirement parts in CIP-004-5 Table R5 – Access Revocation. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Medium | The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for one individual, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s user accounts upon termination action but did not do so for within 30 calendar days of the date of termination action for one or more individuals, and did not identify, assess, and correct the deficiencies. (5.4) or The Responsible Entity has implemented one or more process(es) to change passwords for shared accounts known to the user upon termination action, reassignment, or transfer, but did not do so for within 30 calendar days of the date of termination action, reassignment, or transfer for one or more individuals, and did not identify, assess, and correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more process(es) to determine and document extenuating operating circumstances following a termination action, reassignment, or transfer, but did not change one or more passwords for shared accounts known to the user within 10 calendar days following the end of the extenuating operating circumstances, and did not identify, assess, and correct the deficiencies. (5.5) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for one individual, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for one individual, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for two individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for two individuals, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for two individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for three or more individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) | The Responsible Entity has not implemented any documented program(s) for access revocation for electronic access, unescorted physical access, or BES Cyber System Information storage locations. (R5) or The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for three or more individuals, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for three or more individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) |  |  |  | 2013-09-30 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-004-6 | 507 | R1. | 6062 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R1 – Security Awareness Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so within the subsequent quarter but beyond 30 calendar days after the start of that calendar quarter. (1.1) | The Responsible Entity did not document or implement any security awareness process(es) to reinforce cyber security practices. (R1) OR The Responsible Entity did not reinforce cyber security practices and associated physical security practices for at least two consecutive calendar quarters. (1.1) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R1 – Security Awareness Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-004-6 | 507 | R2. | 6063 | Each Responsible Entity shall implement one or more cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity implemented a cyber security training program but failed to include one of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train one individual (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train one individual with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include two of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train two individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train two individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include three of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train three individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train three individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity did not implement a cyber security training program appropriate to individual roles, functions, or responsibilities. (R2) OR The Responsible Entity implemented a cyber security training program but failed to include four or more of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train four or more individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train four or more individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-004-6 | 507 | R3. | 6064 | Each Responsible Entity shall implement one or more documented personnel risk assessment program(s) to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for one individual. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for one individual. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for one individual. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for one individual. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for one individual with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for two individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for two individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for two individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for two individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for two individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5 | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for three individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for three individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for three individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for three individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for three individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity did not have all of the required elements as described by 3.1 through 3.4 included within documented program(s) for implementing Personnel Risk Assessments (PRAs), for individuals, including contractors and service vendors, for obtaining and retaining authorized cyber or authorized unescorted physical access. (R3) OR The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for four or more individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for four or more individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for four or more individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for four or more individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for four or more individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-004-6 | 507 | R4. | 6065 | Each Responsible Entity shall implement one or more documented access management program(s) that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System Information storage location, privileges were incorrect or unnecessary. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 10 and 20 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for two BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for more than 5% but less than (or equal to) 10% of its BES Cyber System Information storage locations, privileges were incorrect or unnecessary. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 20 and 30 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for three BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for three BES Cyber System Information storage locations, privileges were incorrect or unnecessary. (4.4) | The Responsible Entity did not implement any documented program(s) for access management. (R4) OR The Responsible Entity has implemented one or more documented program(s) for access management that includes a process to authorize electronic access, unescorted physical access, or access to the designated storage locations where BES Cyber System Information is located. (4.1) OR The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records for at least two consecutive calendar quarters. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber System Information storage locations, privileges were incorrect or unnecessary. (4.4) | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-004-6 | 507 | R5. | 6066 | Each Responsible Entity shall implement one or more documented access revocation program(s) that collectively include each of the applicable requirement parts in CIP-004-6 Table R5 – Access Revocation. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information OR The Responsible Entity has implemented one or more process(es) to revoke the individual’s user accounts upon termination action but did not do so for within 30 calendar days of the date of termination action for one or more individuals. (5.4) OR The Responsible Entity has implemented one or more process(es) to change passwords for shared accounts known to the user upon termination action, reassignment, or transfer, but did not do so for within 30 calendar days of the date of termination action, reassignment, or transfer for one or more individuals. (5.5) OR The Responsible Entity has implemented one or more process(es) to determine and document extenuating operating circumstances following a termination action, reassignment, or transfer, but did not change one or more passwords for shared accounts known to the user within 10 calendar days following the end of the extenuating operating circumstances. (5.5) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for one individual. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for one individual, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) OR The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for two individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action. (5.3) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for two individuals. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for two individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) OR The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for three or more individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action. (5.3) | The Responsible Entity has not implemented any documented program(s) for access revocation for electronic access, unescorted physical access, or BES Cyber System Information storage locations. (R5) OR The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for three or more individuals. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for three or more individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) | M5. Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-004-6 (British Columbia) | 666700000010041 | R1. | 666700000010563 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R1 – Security Awareness Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so within the subsequent quarter but beyond 30 calendar days after the start of that calendar quarter. (1.1) | The Responsible Entity did not document or implement any security awareness process(es) to reinforce cyber security practices. (R1) OR The Responsible Entity did not reinforce cyber security practices and associated physical security practices for at least two consecutive calendar quarters. (1.1) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R1 – Security Awareness Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2018-10-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | WECC-BC | [6 empty] | 10000000
CIP-004-6 (British Columbia) | 666700000010041 | R2. | 666700000010564 | Each Responsible Entity shall implement one or more cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity implemented a cyber security training program but failed to include one of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train one individual (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train one individual with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include two of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train two individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train two individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include three of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train three individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train three individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity did not implement a cyber security training program appropriate to individual roles, functions, or responsibilities. (R2) OR The Responsible Entity implemented a cyber security training program but failed to include four or more of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train four or more individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train four or more individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | 2018-10-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | WECC-BC | [6 empty] | 20000000
CIP-004-6 (British Columbia) | 666700000010041 | R3. | 666700000010565 | Each Responsible Entity shall implement one or more documented personnel risk assessment program(s) to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for one individual. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for one individual. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for one individual. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for one individual. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for one individual with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for two individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for two individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for two individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for two individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for two individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5 | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for three individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for three individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for three individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for three individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for three individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity did not have all of the required elements as described by 3.1 through 3.4 included within documented program(s) for implementing Personnel Risk Assessments (PRAs), for individuals, including contractors and service vendors, for obtaining and retaining authorized cyber or authorized unescorted physical access. (R3) OR The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for four or more individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for four or more individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for four or more individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for four or more individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for four or more individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | 2018-10-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | WECC-BC | [6 empty] | 30000000
CIP-004-6 (British Columbia) | 666700000010041 | R4. | 666700000010566 | Each Responsible Entity shall implement one or more documented access management program(s) that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System Information storage location, privileges were incorrect or unnecessary. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 10 and 20 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for two BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for more than 5% but less than (or equal to) 10% of its BES Cyber System Information storage locations, privileges were incorrect or unnecessary. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 20 and 30 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for three BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for three BES Cyber System Information storage locations, privileges were incorrect or unnecessary. (4.4) | The Responsible Entity did not implement any documented program(s) for access management. (R4) OR The Responsible Entity has implemented one or more documented program(s) for access management that includes a process to authorize electronic access, unescorted physical access, or access to the designated storage locations where BES Cyber System Information is located. (4.1) OR The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records for at least two consecutive calendar quarters. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber System Information storage locations, privileges were incorrect or unnecessary. (4.4) | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | 2018-10-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | WECC-BC | [6 empty] | 40000000
CIP-004-6 (British Columbia) | 666700000010041 | R5. | 666700000010567 | Each Responsible Entity shall implement one or more documented access revocation program(s) that collectively include each of the applicable requirement parts in CIP-004-6 Table R5 – Access Revocation. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information OR The Responsible Entity has implemented one or more process(es) to revoke the individual’s user accounts upon termination action but did not do so for within 30 calendar days of the date of termination action for one or more individuals. (5.4) OR The Responsible Entity has implemented one or more process(es) to change passwords for shared accounts known to the user upon termination action, reassignment, or transfer, but did not do so for within 30 calendar days of the date of termination action, reassignment, or transfer for one or more individuals. (5.5) OR The Responsible Entity has implemented one or more process(es) to determine and document extenuating operating circumstances following a termination action, reassignment, or transfer, but did not change one or more passwords for shared accounts known to the user within 10 calendar days following the end of the extenuating operating circumstances. (5.5) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for one individual. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for one individual, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) OR The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for two individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action. (5.3) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for two individuals. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for two individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) OR The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for three or more individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action. (5.3) | The Responsible Entity has not implemented any documented program(s) for access revocation for electronic access, unescorted physical access, or BES Cyber System Information storage locations. (R5) OR The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for three or more individuals. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for three or more individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) | M5. Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2018-10-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | WECC-BC | [6 empty] | 50000000
CIP-004-6 (Manitoba) | 77660000000507 | R1. | 776600000006062 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R1 – Security Awareness Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so within the subsequent quarter but beyond 30 calendar days after the start of that calendar quarter. (1.1) | The Responsible Entity did not document or implement any security awareness process(es) to reinforce cyber security practices. (R1) OR The Responsible Entity did not reinforce cyber security practices and associated physical security practices for at least two consecutive calendar quarters. (1.1) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R1 – Security Awareness Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2017-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-MB | [6 empty] | 10000000
CIP-004-6 (Manitoba) | 77660000000507 | R2. | 776600000006063 | Each Responsible Entity shall implement one or more cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity implemented a cyber security training program but failed to include one of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train one individual (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train one individual with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include two of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train two individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train two individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include three of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train three individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train three individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity did not implement a cyber security training program appropriate to individual roles, functions, or responsibilities. (R2) OR The Responsible Entity implemented a cyber security training program but failed to include four or more of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train four or more individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train four or more individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | 2017-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-MB | [6 empty] | 20000000
CIP-004-6 (Manitoba) | 77660000000507 | R3. | 776600000006064 | Each Responsible Entity shall implement one or more documented personnel risk assessment program(s) to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for one individual. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for one individual. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for one individual. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for one individual. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for one individual with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for two individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for two individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for two individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for two individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for two individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5 | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for three individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for three individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for three individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for three individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for three individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity did not have all of the required elements as described by 3.1 through 3.4 included within documented program(s) for implementing Personnel Risk Assessments (PRAs), for individuals, including contractors and service vendors, for obtaining and retaining authorized cyber or authorized unescorted physical access. (R3) OR The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for four or more individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for four or more individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for four or more individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for four or more individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for four or more individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | 2017-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-MB | [6 empty] | 30000000
CIP-004-6 (Manitoba) | 77660000000507 | R4. | 776600000006065 | Each Responsible Entity shall implement one or more documented access management program(s) that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System Information storage location, privileges were incorrect or unnecessary. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 10 and 20 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for two BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for more than 5% but less than (or equal to) 10% of its BES Cyber System Information storage locations, privileges were incorrect or unnecessary. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 20 and 30 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for three BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for three BES Cyber System Information storage locations, privileges were incorrect or unnecessary. (4.4) | The Responsible Entity did not implement any documented program(s) for access management. (R4) OR The Responsible Entity has implemented one or more documented program(s) for access management that includes a process to authorize electronic access, unescorted physical access, or access to the designated storage locations where BES Cyber System Information is located. (4.1) OR The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records for at least two consecutive calendar quarters. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber System Information storage locations, privileges were incorrect or unnecessary. (4.4) | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | 2017-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-MB | [6 empty] | 40000000
CIP-004-6 (Manitoba) | 77660000000507 | R5. | 776600000006066 | Each Responsible Entity shall implement one or more documented access revocation program(s) that collectively include each of the applicable requirement parts in CIP-004-6 Table R5 – Access Revocation. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information OR The Responsible Entity has implemented one or more process(es) to revoke the individual’s user accounts upon termination action but did not do so for within 30 calendar days of the date of termination action for one or more individuals. (5.4) OR The Responsible Entity has implemented one or more process(es) to change passwords for shared accounts known to the user upon termination action, reassignment, or transfer, but did not do so for within 30 calendar days of the date of termination action, reassignment, or transfer for one or more individuals. (5.5) OR The Responsible Entity has implemented one or more process(es) to determine and document extenuating operating circumstances following a termination action, reassignment, or transfer, but did not change one or more passwords for shared accounts known to the user within 10 calendar days following the end of the extenuating operating circumstances. (5.5) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for one individual. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for one individual, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) OR The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for two individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action. (5.3) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for two individuals. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for two individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) OR The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for three or more individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action. (5.3) | The Responsible Entity has not implemented any documented program(s) for access revocation for electronic access, unescorted physical access, or BES Cyber System Information storage locations. (R5) OR The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for three or more individuals. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for three or more individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) | M5. Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2017-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-MB | [6 empty] | 50000000
CIP-004-6 (Nova Scotia) | 78830000000507 | R1. | 788300000006062 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R1 – Security Awareness Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so within the subsequent quarter but beyond 30 calendar days after the start of that calendar quarter. (1.1) | The Responsible Entity did not document or implement any security awareness process(es) to reinforce cyber security practices. (R1) OR The Responsible Entity did not reinforce cyber security practices and associated physical security practices for at least two consecutive calendar quarters. (1.1) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R1 – Security Awareness Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2017-01-01 |  | 2024-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | NPCC-NS | [6 empty] | 10000000
CIP-004-6 (Nova Scotia) | 78830000000507 | R2. | 788300000006063 | Each Responsible Entity shall implement one or more cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity implemented a cyber security training program but failed to include one of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train one individual (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train one individual with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include two of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train two individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train two individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include three of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train three individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train three individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity did not implement a cyber security training program appropriate to individual roles, functions, or responsibilities. (R2) OR The Responsible Entity implemented a cyber security training program but failed to include four or more of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train four or more individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train four or more individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | 2017-01-01 |  | 2024-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | NPCC-NS | [6 empty] | 20000000
CIP-004-6 (Nova Scotia) | 78830000000507 | R3. | 788300000006064 | Each Responsible Entity shall implement one or more documented personnel risk assessment program(s) to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for one individual. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for one individual. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for one individual. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for one individual. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for one individual with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for two individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for two individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for two individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for two individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for two individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5 | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for three individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for three individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for three individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for three individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for three individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity did not have all of the required elements as described by 3.1 through 3.4 included within documented program(s) for implementing Personnel Risk Assessments (PRAs), for individuals, including contractors and service vendors, for obtaining and retaining authorized cyber or authorized unescorted physical access. (R3) OR The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for four or more individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for four or more individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for four or more individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for four or more individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for four or more individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | 2017-01-01 |  | 2024-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | NPCC-NS | [6 empty] | 30000000
CIP-004-6 (Nova Scotia) | 78830000000507 | R4. | 788300000006065 | Each Responsible Entity shall implement one or more documented access management program(s) that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System Information storage location, privileges were incorrect or unnecessary. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 10 and 20 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for two BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for more than 5% but less than (or equal to) 10% of its BES Cyber System Information storage locations, privileges were incorrect or unnecessary. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 20 and 30 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for three BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for three BES Cyber System Information storage locations, privileges were incorrect or unnecessary. (4.4) | The Responsible Entity did not implement any documented program(s) for access management. (R4) OR The Responsible Entity has implemented one or more documented program(s) for access management that includes a process to authorize electronic access, unescorted physical access, or access to the designated storage locations where BES Cyber System Information is located. (4.1) OR The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records for at least two consecutive calendar quarters. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber System Information storage locations, privileges were incorrect or unnecessary. (4.4) | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | 2017-01-01 |  | 2024-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | NPCC-NS | [6 empty] | 40000000
CIP-004-6 (Nova Scotia) | 78830000000507 | R5. | 788300000006066 | Each Responsible Entity shall implement one or more documented access revocation program(s) that collectively include each of the applicable requirement parts in CIP-004-6 Table R5 – Access Revocation. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information OR The Responsible Entity has implemented one or more process(es) to revoke the individual’s user accounts upon termination action but did not do so for within 30 calendar days of the date of termination action for one or more individuals. (5.4) OR The Responsible Entity has implemented one or more process(es) to change passwords for shared accounts known to the user upon termination action, reassignment, or transfer, but did not do so for within 30 calendar days of the date of termination action, reassignment, or transfer for one or more individuals. (5.5) OR The Responsible Entity has implemented one or more process(es) to determine and document extenuating operating circumstances following a termination action, reassignment, or transfer, but did not change one or more passwords for shared accounts known to the user within 10 calendar days following the end of the extenuating operating circumstances. (5.5) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for one individual. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for one individual, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) OR The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for two individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action. (5.3) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for two individuals. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for two individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) OR The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for three or more individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action. (5.3) | The Responsible Entity has not implemented any documented program(s) for access revocation for electronic access, unescorted physical access, or BES Cyber System Information storage locations. (R5) OR The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for three or more individuals. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for three or more individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) | M5. Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2017-01-01 |  | 2024-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | NPCC-NS | [6 empty] | 50000000
CIP-004-6 (Ontario) | 79780000507 | R1. | 79780006062 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R1 – Security Awareness Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so within the subsequent quarter but beyond 30 calendar days after the start of that calendar quarter. (1.1) | The Responsible Entity did not document or implement any security awareness process(es) to reinforce cyber security practices. (R1) OR The Responsible Entity did not reinforce cyber security practices and associated physical security practices for at least two consecutive calendar quarters. (1.1) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R1 – Security Awareness Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | NPCC-ON | [6 empty] | 10000000
CIP-004-6 (Ontario) | 79780000507 | R2. | 79780006063 | Each Responsible Entity shall implement one or more cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity implemented a cyber security training program but failed to include one of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train one individual (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train one individual with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include two of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train two individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train two individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include three of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train three individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train three individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity did not implement a cyber security training program appropriate to individual roles, functions, or responsibilities. (R2) OR The Responsible Entity implemented a cyber security training program but failed to include four or more of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train four or more individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train four or more individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | NPCC-ON | [6 empty] | 20000000
CIP-004-6 (Ontario) | 79780000507 | R3. | 79780006064 | Each Responsible Entity shall implement one or more documented personnel risk assessment program(s) to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for one individual. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for one individual. (3.1 &amp;amp; 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for one individual. (3.2 &amp;amp; 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for one individual. (3.3 &amp;amp; 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for one individual with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for two individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for two individuals. (3.1 &amp;amp; 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for two individuals. (3.2 &amp;amp; 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for two individuals. (3.3 &amp;amp; 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for two individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5 | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for three individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for three individuals. (3.1 &amp;amp; 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for three individuals. (3.2 &amp;amp; 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for three individuals. (3.3 &amp;amp; 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for three individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity did not have all of the required elements as described by 3.1 through 3.4 included within documented program(s) for implementing Personnel Risk Assessments (PRAs), for individuals, including contractors and service vendors, for obtaining and retaining authorized cyber or authorized unescorted physical access. (R3) OR The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for four or more individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for four or more individuals. (3.1 &amp;amp; 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for four or more individuals. (3.2 &amp;amp; 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for four or more individuals. (3.3 &amp;amp; 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for four or more individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | NPCC-ON | [6 empty] | 30000000
CIP-004-6 (Ontario) | 79780000507 | R4. | 79780006065 | Each Responsible Entity shall implement one or more documented access management program(s) that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System Information storage location, privileges were incorrect or unnecessary. (4.4) | &lt;p&gt;The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 10 and 20 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for two BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) OR&lt;/p&gt; &lt;p&gt;The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber &lt;br/&gt;System Information is correct and necessary within 15 calendar months of the previous verification &lt;br/&gt;but for more than 5% but less than (or equal to) 10% of its BES Cyber System Information storage &lt;br/&gt;locations, privileges were incorrect or unnecessary. (4.4)&lt;/p&gt; &lt;p/&gt; | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 20 and 30 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for three BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for three BES Cyber System Information storage locations, privileges were incorrect or unnecessary. (4.4) | The Responsible Entity did not implement any documented program(s) for access management. (R4) OR The Responsible Entity has implemented one or more documented program(s) for access management that includes a process to authorize electronic access, unescorted physical access, or access to the designated storage locations where BES Cyber System Information is located. (4.1) OR The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records for at least two consecutive calendar quarters. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber System Information storage locations, privileges were incorrect or unnecessary. (4.4) | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | NPCC-ON | [6 empty] | 40000000
CIP-004-6 (Ontario) | 79780000507 | R5. | 79780006066 | Each Responsible Entity shall implement one or more documented access revocation program(s) that collectively include each of the applicable requirement parts in CIP-004-6 Table R5 – Access Revocation. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information OR The Responsible Entity has implemented one or more process(es) to revoke the individual’s user accounts upon termination action but did not do so for within 30 calendar days of the date of termination action for one or more individuals. (5.4) OR The Responsible Entity has implemented one or more process(es) to change passwords for shared accounts known to the user upon termination action, reassignment, or transfer, but did not do so for within 30 calendar days of the date of termination action, reassignment, or transfer for one or more individuals. (5.5) OR The Responsible Entity has implemented one or more process(es) to determine and document extenuating operating circumstances following a termination action, reassignment, or transfer, but did not change one or more passwords for shared accounts known to the user within 10 calendar days following the end of the extenuating operating circumstances. (5.5) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for one individual. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for one individual, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) OR The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for two individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action. (5.3) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for two individuals. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for two individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) OR The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for three or more individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action. (5.3) | The Responsible Entity has not implemented any documented program(s) for access revocation for electronic access, unescorted physical access, or BES Cyber System Information storage locations. (R5) OR The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for three or more individuals. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for three or more individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) | M5. Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | NPCC-ON | [6 empty] | 50000000
CIP-004-6 (Saskatchewan) | 83750000000507 | R1. | 837500000006062 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R1 – Security Awareness Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so within the subsequent quarter but beyond 30 calendar days after the start of that calendar quarter. (1.1) | The Responsible Entity did not document or implement any security awareness process(es) to reinforce cyber security practices. (R1) OR The Responsible Entity did not reinforce cyber security practices and associated physical security practices for at least two consecutive calendar quarters. (1.1) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R1 – Security Awareness Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  | 2024-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-SK | [6 empty] | 10000000
CIP-004-6 (Saskatchewan) | 83750000000507 | R2. | 837500000006063 | Each Responsible Entity shall implement one or more cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity implemented a cyber security training program but failed to include one of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train one individual (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train one individual with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include two of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train two individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train two individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include three of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train three individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train three individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity did not implement a cyber security training program appropriate to individual roles, functions, or responsibilities. (R2) OR The Responsible Entity implemented a cyber security training program but failed to include four or more of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train four or more individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train four or more individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | M2. Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | 2016-07-01 |  | 2024-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-SK | [6 empty] | 20000000
CIP-004-6 (Saskatchewan) | 83750000000507 | R3. | 837500000006064 | Each Responsible Entity shall implement one or more documented personnel risk assessment program(s) to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for one individual. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for one individual. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for one individual. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for one individual. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for one individual with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for two individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for two individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for two individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for two individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for two individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5 | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for three individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for three individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for three individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for three individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for three individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity did not have all of the required elements as described by 3.1 through 3.4 included within documented program(s) for implementing Personnel Risk Assessments (PRAs), for individuals, including contractors and service vendors, for obtaining and retaining authorized cyber or authorized unescorted physical access. (R3) OR The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for four or more individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for four or more individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for four or more individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for four or more individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for four or more individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | M3. Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | 2016-07-01 |  | 2024-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-SK | [6 empty] | 30000000
CIP-004-6 (Saskatchewan) | 83750000000507 | R4. | 837500000006065 | Each Responsible Entity shall implement one or more documented access management program(s) that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System Information storage location, privileges were incorrect or unnecessary. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 10 and 20 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for two BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for more than 5% but less than (or equal to) 10% of its BES Cyber System Information storage locations, privileges were incorrect or unnecessary. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 20 and 30 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for three BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for three BES Cyber System Information storage locations, privileges were incorrect or unnecessary. (4.4) | The Responsible Entity did not implement any documented program(s) for access management. (R4) OR The Responsible Entity has implemented one or more documented program(s) for access management that includes a process to authorize electronic access, unescorted physical access, or access to the designated storage locations where BES Cyber System Information is located. (4.1) OR The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records for at least two consecutive calendar quarters. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber System Information storage locations, privileges were incorrect or unnecessary. (4.4) | M4. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | 2016-07-01 |  | 2024-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-SK | [6 empty] | 40000000
CIP-004-6 (Saskatchewan) | 83750000000507 | R5. | 837500000006066 | Each Responsible Entity shall implement one or more documented access revocation program(s) that collectively include each of the applicable requirement parts in CIP-004-6 Table R5 – Access Revocation. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information OR The Responsible Entity has implemented one or more process(es) to revoke the individual’s user accounts upon termination action but did not do so for within 30 calendar days of the date of termination action for one or more individuals. (5.4) OR The Responsible Entity has implemented one or more process(es) to change passwords for shared accounts known to the user upon termination action, reassignment, or transfer, but did not do so for within 30 calendar days of the date of termination action, reassignment, or transfer for one or more individuals. (5.5) OR The Responsible Entity has implemented one or more process(es) to determine and document extenuating operating circumstances following a termination action, reassignment, or transfer, but did not change one or more passwords for shared accounts known to the user within 10 calendar days following the end of the extenuating operating circumstances. (5.5) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for one individual. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for one individual, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) OR The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for two individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action. (5.3) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for two individuals. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for two individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) OR The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for three or more individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action. (5.3) | The Responsible Entity has not implemented any documented program(s) for access revocation for electronic access, unescorted physical access, or BES Cyber System Information storage locations. (R5) OR The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for three or more individuals. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for three or more individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) | M5. Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-6 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  | 2024-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-SK | [6 empty] | 50000000
CIP-004-7 | ST-2021-08-17-0000001 | R1. | RQ-2021-08-17-0000001 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-7 Table R1 – Security Awareness Program. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so within the subsequent quarter but beyond 30 calendar days after the start of that calendar quarter. (1.1) | The Responsible Entity did not document or implement any security awareness process(es) to reinforce cyber security practices. (R1) OR The Responsible Entity did not reinforce cyber security practices and associated physical security practices for at least two consecutive calendar quarters. (1.1) | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-004-7 Table R1 – Security Awareness Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2024-01-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-004-7 | ST-2021-08-17-0000001 | R2. | RQ-2021-08-17-0000002 | Each Responsible Entity shall implement one or more cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-7 Table R2 – Cyber Security Training Program. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity implemented a cyber security training program but failed to include one of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train one individual (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train one individual with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include two of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train two individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train two individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include three of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train three individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train three individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity did not implement a cyber security training program appropriate to individual roles, functions, or responsibilities. (R2) OR The Responsible Entity implemented a cyber security training program but failed to include four or more of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train four or more individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train four or more individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-7 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | 2024-01-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-004-7 | ST-2021-08-17-0000001 | R3. | RQ-2021-08-17-0000003 | Each Responsible Entity shall implement one or more documented personnel risk assessment program(s) to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-7 Table R3 – Personnel Risk Assessment Program. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for one individual. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for one individual. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for one individual. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for one individual. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for one individual with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for two individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for two individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for two individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for two individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for two individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for three individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for three individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for three individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for three individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for three individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity did not have all of the required elements as described by 3.1 through 3.4 included within documented program(s) for implementing Personnel Risk Assessments (PRAs), for individuals, including contractors and service vendors, for obtaining and retaining authorized cyber or authorized unescorted physical access. (R3) OR The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for four or more individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for four or more individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for four or more individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for four or more individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for four or more individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-7 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | 2024-01-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-004-7 | ST-2021-08-17-0000001 | R4. | RQ-2021-08-17-0000004 | Each Responsible Entity shall implement one or more documented access management program(s) that collectively include each of the applicable requirement parts in CIP-004-7 Table R4 – Access Management Program. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for 5% or less of its BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 10 and 20 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for more than 5% but less than (or equal to) 10% of its BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 20 and 30 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for more than 10% but less than (or equal to) 15% of its BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) | The Responsible Entity did not implement any documented program(s) for access management. (R4) OR The Responsible Entity did not implement one or more documented program(s) for access management that includes a process to authorize electronic access or unescorted physical access. (4.1) OR The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records for at least two consecutive calendar quarters. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for more than 15% of its BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) | Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-7 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | 2024-01-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-004-7 | ST-2021-08-17-0000001 | R5. | RQ-2021-08-17-0000005 | Each Responsible Entity shall implement one or more documented access revocation program(s) that collectively include each of the applicable requirement parts in CIP-004-7 Table R5 – Access Revocation. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity has implemented one or more process(es) to revoke the individual’s user accounts upon termination action but did not do so for within 30 calendar days of the date of termination action for one or more individuals. (5.3) OR The Responsible Entity has implemented one or more process(es) to change passwords for shared accounts known to the user upon termination action, reassignment, or transfer, but did not do so for within 30 calendar days of the date of termination action, reassignment, or transfer for one or more individuals. (5.4) OR The Responsible Entity has implemented one or more process(es) to determine and document extenuating operating circumstances following a termination action, reassignment, or transfer, but did not change one or more passwords for shared accounts known to the user within 10 calendar days following the end of the extenuating operating circumstances. (5.4) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for one individual. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for one individual, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for two individuals. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for two individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) | The Responsible Entity has not implemented any documented program(s) for access revocation for electronic access or unescorted physical access. (R5) OR The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for three or more individuals. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for three or more individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) | Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-7 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2024-01-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-004-7 | ST-2021-08-17-0000001 | R6. | RQ-2021-08-17-0000006 | Each Responsible Entity shall implement one or more documented access management program(s) to authorize, verify, and revoke provisioned access to BCSI pertaining to the “Applicable Systems” identified in CIP-004-7 Table R6 – Access Management for BES Cyber System Information that collectively include each of the applicable requirement parts in CIP‐004‐X Table R6 – Access Management for BES Cyber System Information. To be considered access to BCSI in the context of this requirement, an individual has both the ability to obtain and use BCSI. Provisioned access is to be considered the result of the specific actions taken to provide an individual(s) the means to access BCSI (e.g., may include physical keys or access cards, user accounts and associated rights and privileges, encryption keys). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity has implemented one or more program(s) as required by Requirement R6 Part 6.1 but, for one individual, did not authorize provisioned electronic access to electronic BCSI or provisioned physical access to physical BCSI. (6.1) OR The Responsible Entity performed the verification required by Requirement R6 Part 6.2 more than 15 calendar months but less than or equal to 16 calendar months of the previous verification. (6.2) OR The Responsible Entity has implemented one or more program(s) to remove the individual’s ability to use provisioned access to BCSI but, for one individual, did not do so by the timeframe required in Requirement R6, Part 6.3. | The Responsible Entity has implemented one or more program(s) as required by Requirement R6 Part 6.1 but, for two individuals, did not authorize provisioned electronic access to electronic BCSI or provisioned physical access to physical BCSI. (6.1) OR The Responsible Entity performed the verification required by Requirement R6 Part 6.2 more than 16 calendar months but less than or equal to 17 calendar months of the previous verification. (6.2) OR The Responsible Entity has implemented one or more program(s) to remove the individual’s ability to use provisioned access to BCSI but, for two individuals, did not do so by the timeframe required in Requirement R6, Part 6.3. | The Responsible Entity has implemented one or more program(s) as required by Requirement R6 Part 6.1 but, for three individuals, did not authorize provisioned electronic access to electronic BCSI or provisioned physical access to physical BCSI. (6.1) OR The Responsible Entity performed the verification required by Requirement R6 Part 6.2 more than 17 calendar months but less than or equal to 18 calendar months of the previous verification. (6.2) OR The Responsible Entity has implemented one or more program(s) to remove the individual’s ability to use provisioned access to BCSI but, for three individuals, did not do so by the timeframe required in Requirement R6, Part 6.3. | The Responsible Entity did not implement one or more documented access management program(s) for BCSI. (R6) OR The Responsible Entity has implemented one or more program(s) as required by Requirement R6 Part 6.1 but, for four or more individuals, did not authorize provisioned electronic access to electronic BCSI or provisioned physical access to physical BCSI. (6.1) OR The Responsible Entity performed the verification required by Requirement R6 Part 6.2 more than 18 calendar months of the previous verification. (6.2) OR The Responsible Entity has implemented one or more program(s) to remove the individual’s ability to use provisioned access to BCSI but, for four or more individuals, did not do so by the timeframe required in Requirement R6, Part 6.3. | Evidence must include each of the applicable documented programs that collectively include the applicable requirement parts in CIP-004-7Table R6 – Access Management for BES Cyber System Information and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2024-01-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-004-7 (Nova Scotia) | ST-2021-08-17-0000001-NS | R1. | RQ-2021-08-17-0000001-NS | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-7 Table R1 – Security Awareness Program. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so within the subsequent quarter but beyond 30 calendar days after the start of that calendar quarter. (1.1) | The Responsible Entity did not document or implement any security awareness process(es) to reinforce cyber security practices. (R1) OR The Responsible Entity did not reinforce cyber security practices and associated physical security practices for at least two consecutive calendar quarters. (1.1) | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-004-7 Table R1 – Security Awareness Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2024-04-01 | [5 empty] | NPCC-NS | [6 empty] | 10000000
CIP-004-7 (Nova Scotia) | ST-2021-08-17-0000001-NS | R2. | RQ-2021-08-17-0000002-NS | Each Responsible Entity shall implement one or more cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-7 Table R2 – Cyber Security Training Program. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity implemented a cyber security training program but failed to include one of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train one individual (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train one individual with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include two of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train two individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train two individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include three of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train three individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train three individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity did not implement a cyber security training program appropriate to individual roles, functions, or responsibilities. (R2) OR The Responsible Entity implemented a cyber security training program but failed to include four or more of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train four or more individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train four or more individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-7 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | 2024-04-01 | [5 empty] | NPCC-NS | [6 empty] | 20000000
CIP-004-7 (Nova Scotia) | ST-2021-08-17-0000001-NS | R3. | RQ-2021-08-17-0000003-NS | Each Responsible Entity shall implement one or more documented personnel risk assessment program(s) to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-7 Table R3 – Personnel Risk Assessment Program. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for one individual. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for one individual. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for one individual. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for one individual. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for one individual with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for two individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for two individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for two individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for two individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for two individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for three individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for three individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for three individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for three individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for three individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity did not have all of the required elements as described by 3.1 through 3.4 included within documented program(s) for implementing Personnel Risk Assessments (PRAs), for individuals, including contractors and service vendors, for obtaining and retaining authorized cyber or authorized unescorted physical access. (R3) OR The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for four or more individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for four or more individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for four or more individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for four or more individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for four or more individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-7 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | 2024-04-01 | [5 empty] | NPCC-NS | [6 empty] | 30000000
CIP-004-7 (Nova Scotia) | ST-2021-08-17-0000001-NS | R4. | RQ-2021-08-17-0000004-NS | Each Responsible Entity shall implement one or more documented access management program(s) that collectively include each of the applicable requirement parts in CIP-004-7 Table R4 – Access Management Program. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for 5% or less of its BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 10 and 20 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for more than 5% but less than (or equal to) 10% of its BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 20 and 30 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for more than 10% but less than (or equal to) 15% of its BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) | The Responsible Entity did not implement any documented program(s) for access management. (R4) OR The Responsible Entity did not implement one or more documented program(s) for access management that includes a process to authorize electronic access or unescorted physical access. (4.1) OR The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records for at least two consecutive calendar quarters. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for more than 15% of its BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) | Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-7 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | 2024-04-01 | [5 empty] | NPCC-NS | [6 empty] | 40000000
CIP-004-7 (Nova Scotia) | ST-2021-08-17-0000001-NS | R5. | RQ-2021-08-17-0000005-NS | Each Responsible Entity shall implement one or more documented access revocation program(s) that collectively include each of the applicable requirement parts in CIP-004-7 Table R5 – Access Revocation. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity has implemented one or more process(es) to revoke the individual’s user accounts upon termination action but did not do so for within 30 calendar days of the date of termination action for one or more individuals. (5.3) OR The Responsible Entity has implemented one or more process(es) to change passwords for shared accounts known to the user upon termination action, reassignment, or transfer, but did not do so for within 30 calendar days of the date of termination action, reassignment, or transfer for one or more individuals. (5.4) OR The Responsible Entity has implemented one or more process(es) to determine and document extenuating operating circumstances following a termination action, reassignment, or transfer, but did not change one or more passwords for shared accounts known to the user within 10 calendar days following the end of the extenuating operating circumstances. (5.4) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for one individual. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for one individual, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for two individuals. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for two individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) | The Responsible Entity has not implemented any documented program(s) for access revocation for electronic access or unescorted physical access. (R5) OR The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for three or more individuals. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for three or more individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) | Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-7 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2024-04-01 | [5 empty] | NPCC-NS | [6 empty] | 50000000
CIP-004-7 (Nova Scotia) | ST-2021-08-17-0000001-NS | R6. | RQ-2021-08-17-0000006-NS | Each Responsible Entity shall implement one or more documented access management program(s) to authorize, verify, and revoke provisioned access to BCSI pertaining to the “Applicable Systems” identified in CIP-004-7 Table R6 – Access Management for BES Cyber System Information that collectively include each of the applicable requirement parts in CIP‐004‐X Table R6 – Access Management for BES Cyber System Information. To be considered access to BCSI in the context of this requirement, an individual has both the ability to obtain and use BCSI. Provisioned access is to be considered the result of the specific actions taken to provide an individual(s) the means to access BCSI (e.g., may include physical keys or access cards, user accounts and associated rights and privileges, encryption keys). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity has implemented one or more program(s) as required by Requirement R6 Part 6.1 but, for one individual, did not authorize provisioned electronic access to electronic BCSI or provisioned physical access to physical BCSI. (6.1) OR The Responsible Entity performed the verification required by Requirement R6 Part 6.2 more than 15 calendar months but less than or equal to 16 calendar months of the previous verification. (6.2) OR The Responsible Entity has implemented one or more program(s) to remove the individual’s ability to use provisioned access to BCSI but, for one individual, did not do so by the timeframe required in Requirement R6, Part 6.3. | The Responsible Entity has implemented one or more program(s) as required by Requirement R6 Part 6.1 but, for two individuals, did not authorize provisioned electronic access to electronic BCSI or provisioned physical access to physical BCSI. (6.1) OR The Responsible Entity performed the verification required by Requirement R6 Part 6.2 more than 16 calendar months but less than or equal to 17 calendar months of the previous verification. (6.2) OR The Responsible Entity has implemented one or more program(s) to remove the individual’s ability to use provisioned access to BCSI but, for two individuals, did not do so by the timeframe required in Requirement R6, Part 6.3. | The Responsible Entity has implemented one or more program(s) as required by Requirement R6 Part 6.1 but, for three individuals, did not authorize provisioned electronic access to electronic BCSI or provisioned physical access to physical BCSI. (6.1) OR The Responsible Entity performed the verification required by Requirement R6 Part 6.2 more than 17 calendar months but less than or equal to 18 calendar months of the previous verification. (6.2) OR The Responsible Entity has implemented one or more program(s) to remove the individual’s ability to use provisioned access to BCSI but, for three individuals, did not do so by the timeframe required in Requirement R6, Part 6.3. | The Responsible Entity did not implement one or more documented access management program(s) for BCSI. (R6) OR The Responsible Entity has implemented one or more program(s) as required by Requirement R6 Part 6.1 but, for four or more individuals, did not authorize provisioned electronic access to electronic BCSI or provisioned physical access to physical BCSI. (6.1) OR The Responsible Entity performed the verification required by Requirement R6 Part 6.2 more than 18 calendar months of the previous verification. (6.2) OR The Responsible Entity has implemented one or more program(s) to remove the individual’s ability to use provisioned access to BCSI but, for four or more individuals, did not do so by the timeframe required in Requirement R6, Part 6.3. | Evidence must include each of the applicable documented programs that collectively include the applicable requirement parts in CIP-004-7Table R6 – Access Management for BES Cyber System Information and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2024-04-01 | [5 empty] | NPCC-NS | [6 empty] | 60000000
CIP-004-8 | ST-2024-05-10-0000004 | R1. | RQ-2024-05-10-0000010 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-8 Table R1 – Security Awareness Program. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (Part 1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter. (Part 1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so within the subsequent quarter but beyond 30 calendar days after the start of that calendar quarter. (Part 1.1) | The Responsible Entity did not document or implement any security awareness process(es) to reinforce cyber security practices. (Requirement R1) OR The Responsible Entity did not reinforce cyber security practices and associated physical security practices for at least two consecutive calendar quarters. (Part 1.1) | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-004-8 Table R1 – Security Awareness Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-004-8 | ST-2024-05-10-0000004 | R2. | RQ-2024-05-10-0000011 | Each Responsible Entity shall implement one or more cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-8 Table R2 – Cyber Security Training Program. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Low | The Responsible Entity did not include one of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (Part 2.1) OR The Responsible Entity did not train one individual (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (Part 2.2) OR The Responsible Entity did not train one individual with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (Part 2.3) | The Responsible Entity did not include two of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (Part 2.1) OR The Responsible Entity did not train two individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (Part 2.2) OR The Responsible Entity did not train two individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (Part 2.3) | The Responsible Entity did not include three of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (Part 2.1) OR The Responsible Entity did not train three individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (Part 2.2) OR The Responsible Entity did not train three individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (Part 2.3) | The Responsible Entity did not implement a cyber security training program appropriate to individual roles, functions, or responsibilities. (Requirement R2) OR The Responsible Entity did not include four or more of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (Part 2.1) OR The Responsible Entity did not train four or more individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (Part 2.2) OR The Responsible Entity did not train four or more individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (Part 2.3) | Evidence must include the training program that includes each of the applicable requirement parts in CIP-004-8 Table R2 – Cyber Security Training Program and additional evidence to demonstrate implementation of the program(s). | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-004-8 | ST-2024-05-10-0000004 | R3. | RQ-2024-05-10-0000012 | Each Responsible Entity shall implement one or more documented personnel risk assessment program(s) to attain and retain authorized electronic or authorized unescorted physical access to Applicable Systems that collectively include each of the applicable requirement parts in CIP-004-8 Table R3 – Personnel Risk Assessment Program |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity did not conduct the personnel risk assessments as a condition of granting authorized electronic or authorized unescorted physical access for one individual. (Requirement R3) OR The Responsible Entity did not confirm identity for one individual. (Parts 3.1 & 3.4) OR The Responsible Entity did not include the required checks described in 3.2.1 through 3.2.2 for one individual. (Parts 3.2 & 3.4) OR The Responsible Entity did not evaluate criminal history records check for access authorization for one individual. (Parts 3.3 & 3.4) OR The Responsible Entity did not conduct personnel risk assessments for one individual with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous personnel risk assessments completion date. (Part 3.5) | The Responsible Entity did not conduct the personnel risk assessments as a condition of granting authorized electronic or authorized unescorted physical access for two individuals. (Requirement R3) OR The Responsible Entity did not confirm identity for two individuals. (Parts 3.1 & 3.4) OR The Responsible Entity did not include the required checks described in 3.2.1 through 3.2.2 for two individuals. (Parts 3.2 & 3.4) OR The Responsible Entity did not evaluate criminal history records check for access authorization for two individuals. (Parts 3.3 & 3.4) OR The Responsible Entity did not conduct personnel risk assessments for two individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous personnel risk assessments completion date. (Part 3.5) | The Responsible Entity did not conduct the personnel risk assessments as a condition of granting authorized electronic or authorized unescorted physical access for three individuals. (Requirement R3) OR The Responsible Entity did not confirm identity for three individuals. (Parts 3.1 & 3.4) OR The Responsible Entity did not include the required checks described in 3.2.1 through 3.2.2 for three individuals. (Parts 3.2 & 3.4) OR The Responsible Entity did not evaluate criminal history records check for access authorization for three individuals. (Parts 3.3 through 3.4) OR The Responsible Entity did not conduct personnel risk assessments for three individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous personnel risk assessments completion date. (Part 3.5) | The Responsible Entity did not have all of the required elements as described by 3.1 through 3.4 included within documented program(s) for implementing personnel risk assessments, for individuals, including contractors and service vendors, for obtaining and retaining authorized cyber or authorized unescorted physical access. (Requirement R3) OR The Responsible Entity did not conduct the personnel risk assessments as a condition of granting authorized electronic or authorized unescorted physical access for four or more individuals. (Requirement R3) OR The Responsible Entity did not confirm identity for four or more individuals. (Parts 3.1 & 3.4) OR The Responsible Entity did not include the required checks described in 3.2.1 through 3.2.2 for four or more individuals. (Parts 3.2 & 3.4) OR The Responsible Entity did not evaluate criminal history records check for access authorization for four or more individuals. (Parts 3.3 through 3.4) OR The Responsible Entity did not conduct personnel risk assessments for four or more individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous personnel risk assessments completion date. (Part 3.5) | Evidence must include the documented personnel risk assessment programs that collectively include each of the applicable requirement parts in CIP-004-8 Table R3 – Personnel Risk Assessment Program and additional evidence to demonstrate implementation of the program(s). | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-004-8 | ST-2024-05-10-0000004 | R4. | RQ-2024-05-10-0000013 | Each Responsible Entity shall implement one or more documented access management program(s) that collectively include each of the applicable requirement parts in CIP-004-8 Table R4 – Access Management Program. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (Part 4.2) OR The Responsible Entity did not verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification for 5% or less of its BCS or SCI, privileges were incorrect or unnecessary. (Part 4.3) | The Responsible Entity did not authorize electronic access or unescorted physical access based on need for one individual. (Part 4.1) OR The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 10 and 20 calendar days after the start of a subsequent calendar quarter. (Part 4.2) OR The Responsible Entity did not verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification for more than 5% but less than (or equal to) 10% of its BCS or SCI, privileges were incorrect or unnecessary. (Part 4.3) | The Responsible Entity did not authorize electronic access or unescorted physical access based on need for two individuals. (Part 4.1) OR The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 20 and 30 calendar days after the start of a subsequent calendar quarter. (Part 4.2) OR The Responsible Entity did not verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification for more than 10% but less than (or equal to) 15% of its BCS or SCI, privileges were incorrect or unnecessary. (Part 4.3) | The Responsible Entity did not implement any documented program(s) for access management. (Requirement R4) OR The Responsible Entity did not authorize electronic access or unescorted physical access based on need for three or more individuals. (Part 4.1) OR The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records for at least two consecutive calendar quarters. (Part 4.2) OR The Responsible Entity did not verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification for more than 15% of its BCS or SCI, privileges were incorrect or unnecessary. (Part 4.3) | Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-004-8 Table R4 – Access Management Program and additional evidence to demonstrate that the access management program was implemented as described in the Measures column of the table. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-004-8 | ST-2024-05-10-0000004 | R5. | RQ-2024-05-10-0000014 | Each Responsible Entity shall implement one or more documented access revocation program(s) that collectively include each of the applicable requirement parts in CIP-004-8 Table R5 – Access Revocation. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity did not revoke individual’s user accounts upon termination action within 30 calendar days of the date of termination action for one or more individuals. (Part 5.3) OR The Responsible Entity did not change passwords for shared accounts known to the user upon termination action, reassignment, or transfer within 30 calendar days of the date of termination action, reassignment, or transfer for one or more individuals. (Part 5.4) OR The Responsible Entity did not change one or more passwords for shared accounts known to the user within 10 calendar days following the end of the extenuating operating circumstances. (Part 5.4) | The Responsible Entity did not initiate removal of the ability for unescorted physical access and IRA upon a termination action or complete the removal within 24 hours of the termination action for one individual. (Part 5.1) OR The Responsible Entity for one individual, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (Part 5.2) | The Responsible Entity did not initiate removal of the ability for unescorted physical access and IRA upon a termination action or complete the removal within 24 hours of the termination action for two individuals. (Part 5.1) OR The Responsible Entity for two individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (Part 5.2) | The Responsible Entity has not implemented any documented program(s) for access revocation for electronic access or unescorted physical access. (Requirement R5) OR The Responsible Entity did not initiate removal of the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action for three or more individuals. (Part 5.1) OR The Responsible Entity for three or more individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (Part 5.2) | Evidence must include each of the applicable documented programs that collectively include each of the applicable requirement parts in CIP-004-8 Table R5 – Access Revocation and additional evidence to demonstrate implementation as described in the Measures column of the table. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-004-8 | ST-2024-05-10-0000004 | R6. | RQ-2024-05-10-0000015 | Each Responsible Entity shall implement one or more documented access management program(s) to authorize, verify, and revoke provisioned access to BCSI pertaining to the Applicable Systems identified in CIP-004-8 Table R6 – Access Management for BES Cyber System Information that collectively include each of the applicable requirement parts in CIP‐004‐8 Table R6 – Access Management for BES Cyber System Information. To be considered access to BCSI in the context of this requirement, an individual has both the ability to obtain and use BCSI. Provisioned access is to be considered the result of the specific actions taken to provide an individual(s) the means to access BCSI (e.g., may include physical keys or access cards, user accounts and associated rights and privileges, encryption keys). |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity, for one individual, did not authorize provisioned electronic access to electronic BCSI or provisioned physical access to physical BCSI. (Part 6.1) OR The Responsible Entity did not perform the verification required by Part 6.2 within 15 calendar months but did in less than or equal to 16 calendar months of the previous verification. (Part 6.2) OR The Responsible Entity, for one individual, did not remove the individual’s ability to use provisioned access to BCSI by the timeframe required in Part 6.3. | The Responsible Entity, for two individuals, did not authorize provisioned electronic access to electronic BCSI or provisioned physical access to physical BCSI. (Part 6.1) OR The Responsible Entity did not perform the verification required by Part 6.2 within 16 calendar months but did in less than or equal to 17 calendar months of the previous verification. (Part 6.2) OR The Responsible Entity, for two individuals, did remove each individual’s ability to use provisioned access to BCSI by the timeframe required in Part 6.3. | The Responsible Entity, for three individuals, did not authorize provisioned electronic access to electronic BCSI or provisioned physical access to physical BCSI. (Part 6.1) OR The Responsible Entity did not perform the verification required by Part 6.2 within 17 calendar months but less than or equal to 18 calendar months of the previous verification. (Part 6.2) OR The Responsible Entity, for three individuals, did not remove each individual’s ability to use provisioned access to BCSI by the timeframe required in Part 6.3. | The Responsible Entity did not implement one or more documented access management program(s) for BCSI. (Requirement R6) OR The Responsible Entity, for four or more individuals, did not authorize provisioned electronic access to electronic BCSI or provisioned physical access to physical BCSI. (Part 6.1) OR The Responsible Entity did not perform the verification required by Part 6.2 more than 18 calendar months of the previous verification. (Part 6.2) OR The Responsible Entity, for four or more individuals, did not remove each individual’s ability to use provisioned access to BCSI by the timeframe required in Part 6.3. | Evidence must include each of the applicable documented programs that collectively include the applicable requirement parts in CIP-004-8 Table R6 – Access Management for BES Cyber System Information and additional evidence to demonstrate implementation as described in the Measures column of the table. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-004-AB-5.1 (Alberta) | 656600000009008 | R1. | 656600000009096 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP]004-AB]5.1 Table R1 - Security Awareness Program. |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 10000000
CIP-004-AB-5.1 (Alberta) | 656600000009008 | R2. | 656600000009097 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP]004-AB]5.1 Table R2 - Cyber Security Training Program. |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 20000000
CIP-004-AB-5.1 (Alberta) | 656600000009008 | R3. | 656600000009098 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented personnel risk assessment programs to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP]004-AB]5.1 Table R3 - Personnel Risk Assessment Program. |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 30000000
CIP-004-AB-5.1 (Alberta) | 656600000009008 | R4. | 656600000009099 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access management programs that collectively include each of the applicable requirement parts in CIP]004-AB-5.1 Table R4 - Access Management Program. |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 40000000
CIP-004-AB-5.1 (Alberta) | 656600000009008 | R5. | 656600000009100 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access revocation programs that collectively include each of the applicable requirement parts in CIP]004-AB]5.1 Table R5 - Access Revocation. |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 50000000
CIP-005-1 | 26 | R1. | 299 | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-005-1 | 26 | R2. | 306 | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-005-1 | 26 | R3. | 317 | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-005-1 | 26 | R4. | 320 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-005-1 | 26 | R5. | 326 | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-005-1a | 277 | R1. | 3617 | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2011-02-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-005-1a | 277 | R2. | 3619 | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2011-02-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-005-1a | 277 | R3. | 3616 | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2011-02-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-005-1a | 277 | R4. | 3618 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2011-02-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-005-1a | 277 | R5. | 3620 | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2011-02-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-005-1a (Ontario) | 79780000277 | R1. | 79780003617 | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | The Responsible Entity did not document one or more access points to the electronic security perimeter(s). | The Responsible Entity identified but did not document one or more Electronic Security Perimeter(s). | The Responsible Entity did not ensure that one or more of the Critical Cyber Assets resides within an Electronic Security Perimeter. &lt;br/&gt;OR&lt;br/&gt;The Responsible Entity did not identify nor document one or more Electronic Security Perimeter(s). | The Responsible Entity did not ensure that one or more Critical Cyber Assets resides within an Electronic Security Perimeter, and the Responsible Entity did not identify and document the Electronic Security Perimeter(s) and all access points to the perime |  |  |  | 2011-02-01 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-005-1a (Ontario) | 79780000277 | R2. | 79780003619 | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity implemented but did not document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | The Responsible Entity documented but did not implement the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | The Responsible Entity did not implement nor document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  |  |  | 2011-02-01 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-005-1a (Ontario) | 79780000277 | R3. | 79780003616 | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | The Responsible Entity did not document the electronic or manual processes for monitoring and logging access to access points. &lt;br/&gt;OR&lt;br/&gt;The Responsible Entity did not implement electronic or manual processes monitoring and logging at less than 5% of the access | The Responsible Entity did not implement electronic or manual processes monitoring and logging at 5% or more but less than 10% of the access points. | The Responsible Entity did not implement electronic or manual processes monitoring and logging at 10% or more but less than 15 % of the access points. | The Responsible Entity did not implement electronic or manual processes monitoring and logging at 15% or more of the access points. |  |  |  | 2011-02-01 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-005-1a (Ontario) | 79780000277 | R4. | 79780003618 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | The Responsible Entity did not perform a Vulnerability Assessment at least annually for less than 5% of access points to the Electronic Security Perimeter(s). | The Responsible Entity did not perform a Vulnerability Assessment at least annually for 5% or more but less than 10% of access points to the Electronic Security Perimeter(s). | The Responsible Entity did not perform a Vulnerability Assessment at least annually for 10% or more but less than 15% of access points to the Electronic Security Perimeter(s). | The Responsible Entity did not perform a Vulnerability Assessment at least annually for 15% or more of access points to the Electronic Security Perimeter(s). &lt;br/&gt;OR&lt;br/&gt;The vulnerability assessment did not include one (1) or more of the subrequirements R 4.1, R4 |  |  |  | 2011-02-01 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-005-1a (Ontario) | 79780000277 | R5. | 79780003620 | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity did not review, update, and maintain at least one but less than or equal to 5% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 5% but less than or equal to 10% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 10% but less than or equal to 15% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 15% of the documentation to support compliance with the requirements of Standard CIP-005. |  |  |  | 2011-02-01 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-005-1 (British Columbia) | 666700000010042 | R1. | 666700000010568 | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-005-1 (British Columbia) | 666700000010042 | R2. | 666700000010569 | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 20000000
CIP-005-1 (British Columbia) | 666700000010042 | R3. | 666700000010570 | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 30000000
CIP-005-1 (British Columbia) | 666700000010042 | R4. | 666700000010571 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 40000000
CIP-005-1 (British Columbia) | 666700000010042 | R5. | 666700000010572 | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 50000000
CIP-005-1 (Ontario) | 79780000026 | R1. | 79780000299 | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | The Responsible Entity did not document one or more access points to the electronic security perimeter(s). | The Responsible Entity identified but did not document one or more Electronic Security Perimeter(s). | The Responsible Entity did not ensure that one or more of the Critical Cyber Assets resides within an Electronic Security Perimeter. &lt;br/&gt;OR&lt;br/&gt;The Responsible Entity did not identify nor document one or more Electronic Security Perimeter(s). | The Responsible Entity did not ensure that one or more Critical Cyber Assets resides within an Electronic Security Perimeter, and the Responsible Entity did not identify and document the Electronic Security Perimeter(s) and all access points to the perime |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-005-1 (Ontario) | 79780000026 | R2. | 79780000306 | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity implemented but did not document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | The Responsible Entity documented but did not implement the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | The Responsible Entity did not implement nor document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-005-1 (Ontario) | 79780000026 | R3. | 79780000317 | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | The Responsible Entity did not document the electronic or manual processes for monitoring and logging access to access points. &lt;br/&gt;OR&lt;br/&gt;The Responsible Entity did not implement electronic or manual processes monitoring and logging at less than 5% of the access | The Responsible Entity did not implement electronic or manual processes monitoring and logging at 5% or more but less than 10% of the access points. | The Responsible Entity did not implement electronic or manual processes monitoring and logging at 10% or more but less than 15 % of the access points. | The Responsible Entity did not implement electronic or manual processes monitoring and logging at 15% or more of the access points. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-005-1 (Ontario) | 79780000026 | R4. | 79780000320 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | The Responsible Entity did not perform a Vulnerability Assessment at least annually for less than 5% of access points to the Electronic Security Perimeter(s). | The Responsible Entity did not perform a Vulnerability Assessment at least annually for 5% or more but less than 10% of access points to the Electronic Security Perimeter(s). | The Responsible Entity did not perform a Vulnerability Assessment at least annually for 10% or more but less than 15% of access points to the Electronic Security Perimeter(s). | The Responsible Entity did not perform a Vulnerability Assessment at least annually for 15% or more of access points to the Electronic Security Perimeter(s). &lt;br/&gt;OR&lt;br/&gt;The vulnerability assessment did not include one (1) or more of the subrequirements R 4.1, R4 |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-005-1 (Ontario) | 79780000026 | R5. | 79780000326 | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity did not review, update, and maintain at least one but less than or equal to 5% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 5% but less than or equal to 10% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 10% but less than or equal to 15% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 15% of the documentation to support compliance with the requirements of Standard CIP-005. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-005-2 | 211 | R1. | 2410 | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  | CIP-005-1 R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-005-2 | 211 | R2. | 2417 | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  | CIP-005-1 R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-005-2 | 211 | R3. | 2428 | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  | CIP-005-1 R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-005-2 | 211 | R4. | 2431 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-005-2 | 211 | R5. | 2437 | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-005-2a | 278 | R1. | 3648 | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2011-02-01 |  |  | CIP-005-1 R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-005-2a | 278 | R2. | 3650 | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2011-02-01 |  |  | CIP-005-1 R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-005-2a | 278 | R3. | 3647 | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2011-02-01 |  |  | CIP-005-1 R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-005-2a | 278 | R4. | 3649 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2011-02-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-005-2a | 278 | R5. | 3651 | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2011-02-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-005-2a (Ontario) | 79780000278 | R1. | 79780003648 | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2011-02-01 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-005-2a (Ontario) | 79780000278 | R2. | 79780003650 | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2011-02-01 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-005-2a (Ontario) | 79780000278 | R3. | 79780003647 | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2011-02-01 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-005-2a (Ontario) | 79780000278 | R4. | 79780003649 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2011-02-01 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-005-2a (Ontario) | 79780000278 | R5. | 79780003651 | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2011-02-01 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-005-2 (Ontario) | 79780000211 | R1. | 79780002410 | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-005-2 (Ontario) | 79780000211 | R2. | 79780002417 | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-005-2 (Ontario) | 79780000211 | R3. | 79780002428 | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-005-2 (Ontario) | 79780000211 | R4. | 79780002431 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-005-2 (Ontario) | 79780000211 | R5. | 79780002437 | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-005-3 | 225 | R1. | 2769 | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-10-01 |  | 2011-02-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-005-3 | 225 | R2. | 2776 | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-10-01 |  | 2011-02-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-005-3 | 225 | R3. | 2787 | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-10-01 |  | 2011-02-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-005-3 | 225 | R4. | 2790 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-10-01 |  | 2011-02-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-005-3 | 225 | R5. | 2796 | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-10-01 |  | 2011-02-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-005-3a | 244 | R1. | 3153 | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. OR The Responsible Entity did not identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). | M1. The Responsible Entity shall make available documentation about the Electronic Security Perimeter as specified in Requirement R1. | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-005-3a | 244 | R2. | 3155 | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not implement or did not document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | M2. The Responsible Entity shall make available documentation of the electronic access controls to the Electronic Security Perimeter(s), as specified in Requirement R2. | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-005-3a | 244 | R3. | 3152 | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not implement or did not document electronic or manual processes monitoring and logging access points. | M3. The Responsible Entity shall make available documentation of controls implemented to log and monitor access to the Electronic Security Perimeter(s) as specified in Requirement R3. | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-005-3a | 244 | R4. | 3154 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not perform a Vulnerability Assessment at least annually for one or more of the access points to the Electronic Security Perimeter(s). ORThe vulnerability assessment did not include one (1) or more of the subrequirements R4.1, R4.2, R4.3, R4.4, R4.5. | M4. The Responsible Entity shall make available documentation of its annual vulnerability assessment as specified in Requirement R4. | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-005-3a | 244 | R5. | 3156 | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity did not review, update, and maintain greater than 5% but less than or equal to 10% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 5% but less than or equal to 10% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 10% but less than or equal to 15% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 15% of the documentation to support compliance with the requirements of Standard CIP-005. | M5. The Responsible Entity shall make available access logs and documentation of review, changes, and log retention as specified in Requirement R5. | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-005-3a (British Columbia) | 666700000010044 | R1. | 666700000010578 | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. OR The Responsible Entity did not identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). | M1. The Responsible Entity shall make available documentation about the Electronic Security Perimeter as specified in Requirement R1. | 2013-07-15 |  | 2018-09-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | WECC-BC | [6 empty] | 10000000
CIP-005-3a (British Columbia) | 666700000010044 | R2. | 666700000010579 | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not implement or did not document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | M2. The Responsible Entity shall make available documentation of the electronic access controls to the Electronic Security Perimeter(s), as specified in Requirement R2. | 2013-07-15 |  | 2018-09-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | WECC-BC | [6 empty] | 20000000
CIP-005-3a (British Columbia) | 666700000010044 | R3. | 666700000010580 | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not implement or did not document electronic or manual processes monitoring and logging access points. | M3. The Responsible Entity shall make available documentation of controls implemented to log and monitor access to the Electronic Security Perimeter(s) as specified in Requirement R3. | 2013-07-15 |  | 2018-09-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | WECC-BC | [6 empty] | 30000000
CIP-005-3a (British Columbia) | 666700000010044 | R4. | 666700000010581 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not perform a Vulnerability Assessment at least annually for one or more of the access points to the Electronic Security Perimeter(s). ORThe vulnerability assessment did not include one (1) or more of the subrequirements R4.1, R4.2, R4.3, R4.4, R4.5. | M4. The Responsible Entity shall make available documentation of its annual vulnerability assessment as specified in Requirement R4. | 2013-07-15 |  | 2018-09-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | WECC-BC | [6 empty] | 40000000
CIP-005-3a (British Columbia) | 666700000010044 | R5. | 666700000010582 | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity did not review, update, and maintain greater than 5% but less than or equal to 10% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 5% but less than or equal to 10% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 10% but less than or equal to 15% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 15% of the documentation to support compliance with the requirements of Standard CIP-005. | M5. The Responsible Entity shall make available access logs and documentation of review, changes, and log retention as specified in Requirement R5. | 2013-07-15 |  | 2018-09-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | WECC-BC | [6 empty] | 50000000
CIP-005-3a (Manitoba) | 77660000000244 | R1. | 776600000003153 | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. OR The Responsible Entity did not identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). | M1. The Responsible Entity shall make available documentation about the Electronic Security Perimeter as specified in Requirement R1. | 2014-02-14 |  | 2017-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-MB | [6 empty] | 10000000
CIP-005-3a (Manitoba) | 77660000000244 | R2. | 776600000003155 | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not implement or did not document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | M2. The Responsible Entity shall make available documentation of the electronic access controls to the Electronic Security Perimeter(s), as specified in Requirement R2. | 2014-02-14 |  | 2017-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-MB | [6 empty] | 20000000
CIP-005-3a (Manitoba) | 77660000000244 | R3. | 776600000003152 | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not implement or did not document electronic or manual processes monitoring and logging access points. | M3. The Responsible Entity shall make available documentation of controls implemented to log and monitor access to the Electronic Security Perimeter(s) as specified in Requirement R3. | 2014-02-14 |  | 2017-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-MB | [6 empty] | 30000000
CIP-005-3a (Manitoba) | 77660000000244 | R4. | 776600000003154 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not perform a Vulnerability Assessment at least annually for one or more of the access points to the Electronic Security Perimeter(s). ORThe vulnerability assessment did not include one (1) or more of the subrequirements R4.1, R4.2, R4.3, R4.4, R4.5. | M4. The Responsible Entity shall make available documentation of its annual vulnerability assessment as specified in Requirement R4. | 2014-02-14 |  | 2017-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-MB | [6 empty] | 40000000
CIP-005-3a (Manitoba) | 77660000000244 | R5. | 776600000003156 | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity did not review, update, and maintain greater than 5% but less than or equal to 10% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 5% but less than or equal to 10% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 10% but less than or equal to 15% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 15% of the documentation to support compliance with the requirements of Standard CIP-005. | M5. The Responsible Entity shall make available access logs and documentation of review, changes, and log retention as specified in Requirement R5. | 2014-02-14 |  | 2017-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-MB | [6 empty] | 50000000
CIP-005-3a (Ontario) | 79780000244 | R1. | 79780003153 | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. OR The Responsible Entity did not identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). | M1. The Responsible Entity shall make available documentation about the Electronic Security&lt;br/&gt;Perimeter as specified in Requirement R1. | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | NPCC-ON | [6 empty] | 10000000
CIP-005-3a (Ontario) | 79780000244 | R2. | 79780003155 | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not implement or did not document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | M2. The Responsible Entity shall make available documentation of the electronic access controls to&lt;br/&gt;the Electronic Security Perimeter(s), as specified in Requirement R2. | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | NPCC-ON | [6 empty] | 20000000
CIP-005-3a (Ontario) | 79780000244 | R3. | 79780003152 | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not implement or did not document electronic or manual processes monitoring and logging access points. | M3. The Responsible Entity shall make available documentation of controls implemented to log and monitor access to the Electronic Security Perimeter(s) as specified in Requirement R3. | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | NPCC-ON | [6 empty] | 30000000
CIP-005-3a (Ontario) | 79780000244 | R4. | 79780003154 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not perform a Vulnerability Assessment at least annually for one or more of the access points to the Electronic Security Perimeter(s). ORThe vulnerability assessment did not include one (1) or more of the subrequirements R4.1, R4.2, R4.3, R4.4, R4.5. | M4. The Responsible Entity shall make available documentation of its annual vulnerability assessment as specified in Requirement R4. | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | NPCC-ON | [6 empty] | 40000000
CIP-005-3a (Ontario) | 79780000244 | R5. | 79780003156 | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity did not review, update, and maintain greater than 5% but less than or equal to 10% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 5% but less than or equal to 10% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 10% but less than or equal to 15% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 15% of the documentation to support compliance with the requirements of Standard CIP-005. | M5. The Responsible Entity shall make available access logs and documentation of review, changes, and log retention as specified in Requirement R5. | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | NPCC-ON | [6 empty] | 50000000
CIP-005-3 (British Columbia) | 666700000010043 | R1. | 666700000010573 | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2012-07-01 |  | 2013-07-14 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-005-3 (British Columbia) | 666700000010043 | R2. | 666700000010574 | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2012-07-01 |  | 2013-07-14 |  |  |  | WECC-BC | [6 empty] | 20000000
CIP-005-3 (British Columbia) | 666700000010043 | R3. | 666700000010575 | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2012-07-01 |  | 2013-07-14 |  |  |  | WECC-BC | [6 empty] | 30000000
CIP-005-3 (British Columbia) | 666700000010043 | R4. | 666700000010576 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2012-07-01 |  | 2013-07-14 |  |  |  | WECC-BC | [6 empty] | 40000000
CIP-005-3 (British Columbia) | 666700000010043 | R5. | 666700000010577 | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2012-07-01 |  | 2013-07-14 |  |  |  | WECC-BC | [6 empty] | 50000000
CIP-005-3 (Manitoba) | 77660000000225 | R1. | 776600000002769 | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 10000000
CIP-005-3 (Manitoba) | 77660000000225 | R2. | 776600000002776 | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 20000000
CIP-005-3 (Manitoba) | 77660000000225 | R3. | 776600000002787 | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 30000000
CIP-005-3 (Manitoba) | 77660000000225 | R4. | 776600000002790 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 40000000
CIP-005-3 (Manitoba) | 77660000000225 | R5. | 776600000002796 | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 50000000
CIP-005-3 (Ontario) | 79780000225 | R1. | 79780002769 | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-10-01 |  | 2011-02-01 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-005-3 (Ontario) | 79780000225 | R2. | 79780002776 | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-10-01 |  | 2011-02-01 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-005-3 (Ontario) | 79780000225 | R3. | 79780002787 | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-10-01 |  | 2011-02-01 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-005-3 (Ontario) | 79780000225 | R4. | 79780002790 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-10-01 |  | 2011-02-01 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-005-3 (Ontario) | 79780000225 | R5. | 79780002796 | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-10-01 |  | 2011-02-01 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-005-4a | 251 | R1. | 3258 | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | The Responsible Entity did not document one or more access points to the Electronic Security Perimeter(s). | The Responsible Entity identified but did not document one or more Electronic Security Perimeter(s). | The Responsible Entity did not ensure that one or more of the Critical Cyber Assets resides within an Electronic Security Perimeter. OR The Responsible Entity did not identify nor document one or more Electronic Security Perimeter(s). | The Responsible Entity did not ensure that one or more Critical Cyber Assets resides within an Electronic Security Perimeter, and the Responsible Entity did not identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s) for all Critical Cyber Assets. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-005-4a | 251 | R2. | 3265 | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity implemented but did not document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | The Responsible Entity documented but did not implement the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | The Responsible Entity did not implement nor document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-005-4a | 251 | R3. | 3276 | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Planning, Same-Day Operations | Medium | The Responsible Entity did not document the electronic or manual processes for monitoring and logging access to access points. OR The Responsible Entity did not implement electronic or manual processes monitoring and logging at less than 5% of the access points. | The Responsible Entity did not implement electronic or manual processes monitoring and logging at 5% or more but less than 10% of the access points. | The Responsible Entity did not implement electronic or manual processes monitoring and logging at 10% or more but less than 15 % of the access points. | The Responsible Entity did not implement electronic or manual processes monitoring and logging at 15% or more of the access points. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-005-4a | 251 | R4. | 3279 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Planning | Medium | The Responsible Entity did not perform a Vulnerability Assessment at least annually for less than 5% of access points to the Electronic Security Perimeter(s). | The Responsible Entity did not perform a Vulnerability Assessment at least annually for 5% or more but less than 10% of access points to the Electronic Security Perimeter(s). | The Responsible Entity did not perform a Vulnerability Assessment at least annually for 10% or more but less than 15% of access points to the Electronic Security Perimeter(s). | The Responsible Entity did not perform a Vulnerability Assessment at least annually for 15% or more of access points to the Electronic Security Perimeter(s). OR The vulnerability assessment did not include one (1) or more of the subrequirements R 4.1, R4.2, R4.3, R4.4, R4.5. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-005-4a | 251 | R5. | 3285 | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Planning, Same-Day Operations | Low | The Responsible Entity did not review, update, and maintain at least one but less than or equal to 5% of the documentation to support compliance with the requirements of Standard CIP-005-4. | The Responsible Entity did not review, update, and maintain greater than 5% but less than or equal to 10% of the documentation to support compliance with the requirements of Standard CIP-005-4. | The Responsible Entity did not review, update, and maintain greater than 10% but less than or equal to 15% of the documentation to support compliance with the requirements of Standard CIP-005-4. | The Responsible Entity did not review, update, and maintain greater than 15% of the documentation to support compliance with the requirements of Standard CIP-005-4. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-005-4a (Ontario) | 79780000251 | R1. | 79780003258 | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. OR The Responsible Entity did not identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s) |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-005-4a (Ontario) | 79780000251 | R2. | 79780003265 | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not implement or did not document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-005-4a (Ontario) | 79780000251 | R3. | 79780003276 | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Planning, Same-Day Operations | Medium | N/A | N/A | N/A | The Responsible Entity did not implement or did not document electronic or manual processes monitoring and logging access points. | M2.3. An example of evidence may include, but is not limited to, architecture documents detailing the authentication factors used. &lt;br/&gt;Examples of authenticators may include, but are not limited to, &lt;br/&gt;• Something the individual knows such as passwords or PINs. This does not include User ID;&lt;br/&gt;• Something the individual has such as tokens, digital certificates, or smart cards; or &lt;br/&gt;• Something the individual is such as fingerprints, iris scans, or other biometric characteristics. | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-005-4a (Ontario) | 79780000251 | R4. | 79780003279 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Planning | Medium | N/A | N/A | N/A | The Responsible Entity did not perform a Vulnerability Assessment at least annually for one or more of the access points to the Electronic Security Perimeter(s). OR The vulnerability assessment did not include one (1) or more of the subrequirements R4.1 |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-005-4a (Ontario) | 79780000251 | R5. | 79780003285 | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Planning, Same-Day Operations | Low | The Responsible Entity did not review, update, and maintain at least one but less than or equal to 5% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 5% but less than or equal to 10% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 10% but less than or equal to 15% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 15% of the documentation to support compliance with the requirements of Standard CIP-005. | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-005-5 | 349 | R1. | 4491 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-5 Table R1 – Electronic Security Perimeter. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | N/A | N/A | The Responsible Entity did not have a method for detecting malicious communications for both inbound and outbound communications. (1.5) | The Responsible Entity did not document one or more processes for CIP-005-5 Table R1 – Electronic Security Perimeter. (R1) OR The Responsible Entity did not have all applicable Cyber Assets connected to a network via a routable protocol within a defined Electronic Security Perimeter (ESP). (1.1) OR External Routable Connectivity through the ESP was not through an identified EAP. (1.2) OR The Responsible Entity did not require inbound and outbound access permissions and deny all other access by default. (1.3) OR The Responsible Entity did not perform authentication when establishing dial-up connectivity with the applicable Cyber Assets, where technically feasible. (1.4) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-5 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-005-5 | 349 | R2. | 4492 | Each Responsible Entity allowing Interactive Remote Access to BES Cyber Systems shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-5 Table R2 – Interactive Remote Access Management. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity does not have documented processes for one or more of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for one of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for two of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for three of the applicable items for Requirement Parts 2.1 through 2.3. | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-5 Table R2 – Interactive Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-005-5 (British Columbia) | 666700000010045 | R1. | 666700000010583 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-5 Table R1 – Electronic Security Perimeter. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | N/A | N/A | The Responsible Entity did not have a method for detecting malicious communications for both inbound and outbound communications. (1.5) | The Responsible Entity did not document one or more processes for CIP-005-5 Table R1 – Electronic Security Perimeter. (R1) OR The Responsible Entity did not have all applicable Cyber Assets connected to a network via a routable protocol within a defined Electronic Security Perimeter (ESP). (1.1) OR External Routable Connectivity through the ESP was not through an identified EAP. (1.2) OR The Responsible Entity did not require inbound and outbound access permissions and deny all other access by default. (1.3) OR The Responsible Entity did not perform authentication when establishing dial-up connectivity with the applicable Cyber Assets, where technically feasible. (1.4) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-5 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2018-10-01 |  | 2023-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | WECC-BC | [6 empty] | 10000000
CIP-005-5 (British Columbia) | 666700000010045 | R2. | 666700000010584 | Each Responsible Entity allowing Interactive Remote Access to BES Cyber Systems shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-5 Table R2 – Interactive Remote Access Management. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity does not have documented processes for one or more of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for one of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for two of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for three of the applicable items for Requirement Parts 2.1 through 2.3. | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-5 Table R2 – Interactive Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2018-10-01 |  | 2023-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | WECC-BC | [6 empty] | 20000000
CIP-005-5 (Manitoba) | 77660000000349 | R1. | 776600000004491 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-5 Table R1 – Electronic Security Perimeter. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | N/A | N/A | The Responsible Entity did not have a method for detecting malicious communications for both inbound and outbound communications. (1.5) | The Responsible Entity did not document one or more processes for CIP-005-5 Table R1 – Electronic Security Perimeter. (R1) OR The Responsible Entity did not have all applicable Cyber Assets connected to a network via a routable protocol within a defined Electronic Security Perimeter (ESP). (1.1) OR External Routable Connectivity through the ESP was not through an identified EAP. (1.2) OR The Responsible Entity did not require inbound and outbound access permissions and deny all other access by default. (1.3) OR The Responsible Entity did not perform authentication when establishing dial-up connectivity with the applicable Cyber Assets, where technically feasible. (1.4) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-5 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2017-07-01 |  | 2021-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | MRO-MB | [6 empty] | 10000000
CIP-005-5 (Manitoba) | 77660000000349 | R2. | 776600000004492 | Each Responsible Entity allowing Interactive Remote Access to BES Cyber Systems shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-5 Table R2 – Interactive Remote Access Management. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity does not have documented processes for one or more of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for one of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for two of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for three of the applicable items for Requirement Parts 2.1 through 2.3. | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-5 Table R2 – Interactive Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2017-07-01 |  | 2021-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | MRO-MB | [6 empty] | 20000000
CIP-005-5 (Nova Scotia) | 78830000000349 | R1. | 788300000004491 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-5 Table R1 – Electronic Security Perimeter. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | N/A | N/A | The Responsible Entity did not have a method for detecting malicious communications for both inbound and outbound communications. (1.5) | The Responsible Entity did not document one or more processes for CIP-005-5 Table R1 – Electronic Security Perimeter. (R1) OR The Responsible Entity did not have all applicable Cyber Assets connected to a network via a routable protocol within a defined Electronic Security Perimeter (ESP). (1.1) OR External Routable Connectivity through the ESP was not through an identified EAP. (1.2) OR The Responsible Entity did not require inbound and outbound access permissions and deny all other access by default. (1.3) OR The Responsible Entity did not perform authentication when establishing dial-up connectivity with the applicable Cyber Assets, where technically feasible. (1.4) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-5 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  | 2021-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | NPCC-NS | [6 empty] | 10000000
CIP-005-5 (Nova Scotia) | 78830000000349 | R2. | 788300000004492 | Each Responsible Entity allowing Interactive Remote Access to BES Cyber Systems shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-5 Table R2 – Interactive Remote Access Management. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity does not have documented processes for one or more of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for one of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for two of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for three of the applicable items for Requirement Parts 2.1 through 2.3. | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-5 Table R2 – Interactive Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  | 2021-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | NPCC-NS | [6 empty] | 20000000
CIP-005-5 (Ontario) | 79780000349 | R1. | 79780004491 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-5 Table R1 – Electronic Security Perimeter. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | N/A | N/A | The Responsible Entity did not have a method for detecting malicious communications for both inbound and outbound communications. (1.5) | The Responsible Entity did not document one or more processes for CIP-005-5 Table R1 – Electronic Security Perimeter. (R1) OR The Responsible Entity did not have all applicable Cyber Assets connected to a network via a routable protocol within a defined Electronic Security Perimeter (ESP). (1.1) OR External Routable Connectivity through the ESP was not through an identified EAP. (1.2) OR The Responsible Entity did not require inbound and outbound access permissions and deny all other access by default. (1.3) OR The Responsible Entity did not perform authentication when establishing dial-up connectivity with the applicable Cyber Assets, where technically feasible. (1.4) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-5 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | NPCC-ON | [6 empty] | 10000000
CIP-005-5 (Ontario) | 79780000349 | R2. | 79780004492 | Each Responsible Entity allowing Interactive Remote Access to BES Cyber Systems shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-5 Table R2 – Interactive Remote Access Management. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity does not have documented processes for one or more of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for one of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for two of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for three of the applicable items for Requirement Parts 2.1 through 2.3. | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-5 Table R2 – Interactive Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | NPCC-ON | [6 empty] | 20000000
CIP-005-5 (Saskatchewan) | 83750000000349 | R1. | 837500000004491 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-5 Table R1 – Electronic Security Perimeter. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | N/A | N/A | The Responsible Entity did not have a method for detecting malicious communications for both inbound and outbound communications. (1.5) | The Responsible Entity did not document one or more processes for CIP-005-5 Table R1 – Electronic Security Perimeter. (R1) OR The Responsible Entity did not have all applicable Cyber Assets connected to a network via a routable protocol within a defined Electronic Security Perimeter (ESP). (1.1) OR External Routable Connectivity through the ESP was not through an identified EAP. (1.2) OR The Responsible Entity did not require inbound and outbound access permissions and deny all other access by default. (1.3) OR The Responsible Entity did not perform authentication when establishing dial-up connectivity with the applicable Cyber Assets, where technically feasible. (1.4) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-5 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | MRO-SK | [6 empty] | 10000000
CIP-005-5 (Saskatchewan) | 83750000000349 | R2. | 837500000004492 | Each Responsible Entity allowing Interactive Remote Access to BES Cyber Systems shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-5 Table R2 – Interactive Remote Access Management. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity does not have documented processes for one or more of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for one of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for two of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for three of the applicable items for Requirement Parts 2.1 through 2.3. | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-5 Table R2 – Interactive Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | MRO-SK | [6 empty] | 20000000
CIP-005-6 | 570 | R1. | 8096 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium |  |  | The Responsible Entity did not have a method for detecting malicious communications for both inbound and outbound communications. (1.5) | The Responsible Entity did not document one or more processes for CIP-005-6 Table R1 – Electronic Security Perimeter. (R1) OR The Responsible Entity did not have all applicable Cyber Assets connected to a network via a routable protocol within a defined Electronic Security Perimeter (ESP). (1.1) OR External Routable Connectivity through the ESP was not through an identified EAP. (1.2) OR The Responsible Entity did not require inbound and outbound access permissions and deny all other access by default. (1.3) OR The Responsible Entity did not perform authentication when establishing dial-up connectivity with the applicable Cyber Assets, where technically feasible. (1.4) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-005-6 | 570 | R2. | 8102 | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-6 Table R2 –Remote Access Management. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity does not have documented processes for one or more of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for one of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for two of the applicable items for Requirement Parts 2.1 through 2.3; OR The Responsible Entity did not have either: one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4); or one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). | The Responsible Entity did not implement processes for three of the applicable items for Requirement Parts 2.1 through 2.3; OR The Responsible Entity did not have one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4) and one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-6 Table R2 –Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-005-6 (British Columbia) | 666700000010046 | R1. | 666700000010585 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium |  |  | The Responsible Entity did not have a method for detecting malicious communications for both inbound and outbound communications. (1.5) | The Responsible Entity did not document one or more processes for CIP-005-6 Table R1 – Electronic Security Perimeter. (R1) OR The Responsible Entity did not have all applicable Cyber Assets connected to a network via a routable protocol within a defined Electronic Security Perimeter (ESP). (1.1) OR External Routable Connectivity through the ESP was not through an identified EAP. (1.2) OR The Responsible Entity did not require inbound and outbound access permissions and deny all other access by default. (1.3) OR The Responsible Entity did not perform authentication when establishing dial-up connectivity with the applicable Cyber Assets, where technically feasible. (1.4) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2023-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | WECC-BC | [6 empty] | 10000000
CIP-005-6 (British Columbia) | 666700000010046 | R2. | 666700000010586 | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-6 Table R2 –Remote Access Management. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity does not have documented processes for one or more of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for one of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for two of the applicable items for Requirement Parts 2.1 through 2.3; OR The Responsible Entity did not have either: one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4); or one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). | The Responsible Entity did not implement processes for three of the applicable items for Requirement Parts 2.1 through 2.3; OR The Responsible Entity did not have one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4) and one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-6 Table R2 –Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2023-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | WECC-BC | [6 empty] | 20000000
CIP-005-6 (Manitoba) | 77660000000570 | R1. | 776600000008096 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium |  |  | The Responsible Entity did not have a method for detecting malicious communications for both inbound and outbound communications. (1.5) | The Responsible Entity did not document one or more processes for CIP-005-6 Table R1 – Electronic Security Perimeter. (R1) OR The Responsible Entity did not have all applicable Cyber Assets connected to a network via a routable protocol within a defined Electronic Security Perimeter (ESP). (1.1) OR External Routable Connectivity through the ESP was not through an identified EAP. (1.2) OR The Responsible Entity did not require inbound and outbound access permissions and deny all other access by default. (1.3) OR The Responsible Entity did not perform authentication when establishing dial-up connectivity with the applicable Cyber Assets, where technically feasible. (1.4) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2021-07-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | MRO-MB | [6 empty] | 10000000
CIP-005-6 (Manitoba) | 77660000000570 | R2. | 776600000008102 | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-6 Table R2 –Remote Access Management. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity does not have documented processes for one or more of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for one of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for two of the applicable items for Requirement Parts 2.1 through 2.3; OR The Responsible Entity did not have either: one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4); or one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). | The Responsible Entity did not implement processes for three of the applicable items for Requirement Parts 2.1 through 2.3; OR The Responsible Entity did not have one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4) and one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-6 Table R2 –Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2021-07-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | MRO-MB | [6 empty] | 20000000
CIP-005-6 (Nova Scotia) | 78830000000570 | R1. | 788300000008096 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium |  |  | The Responsible Entity did not have a method for detecting malicious communications for both inbound and outbound communications. (1.5) | The Responsible Entity did not document one or more processes for CIP-005-6 Table R1 – Electronic Security Perimeter. (R1) OR The Responsible Entity did not have all applicable Cyber Assets connected to a network via a routable protocol within a defined Electronic Security Perimeter (ESP). (1.1) OR External Routable Connectivity through the ESP was not through an identified EAP. (1.2) OR The Responsible Entity did not require inbound and outbound access permissions and deny all other access by default. (1.3) OR The Responsible Entity did not perform authentication when establishing dial-up connectivity with the applicable Cyber Assets, where technically feasible. (1.4) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2021-04-01 |  | 2022-12-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | NPCC-NS | [6 empty] | 10000000
CIP-005-6 (Nova Scotia) | 78830000000570 | R2. | 788300000008102 | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-6 Table R2 –Remote Access Management. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity does not have documented processes for one or more of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for one of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for two of the applicable items for Requirement Parts 2.1 through 2.3; OR The Responsible Entity did not have either: one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4); or one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). | The Responsible Entity did not implement processes for three of the applicable items for Requirement Parts 2.1 through 2.3; OR The Responsible Entity did not have one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4) and one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-6 Table R2 –Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2021-04-01 |  | 2022-12-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | NPCC-NS | [6 empty] | 20000000
CIP-005-6 (Ontario) | 79780000570 | R1. | 79780008096 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium |  |  | The Responsible Entity did not have a method for detecting malicious communications for both inbound and outbound communications. (1.5) | The Responsible Entity did not document one or more processes for CIP-005-6 Table R1 – Electronic Security Perimeter. (R1) OR The Responsible Entity did not have all applicable Cyber Assets connected to a network via a routable protocol within a defined Electronic Security Perimeter (ESP). (1.1) OR External Routable Connectivity through the ESP was not through an identified EAP. (1.2) OR The Responsible Entity did not require inbound and outbound access permissions and deny all other access by default. (1.3) OR The Responsible Entity did not perform authentication when establishing dial-up connectivity with the applicable Cyber Assets, where technically feasible. (1.4) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | NPCC-ON | [6 empty] | 10000000
CIP-005-6 (Ontario) | 79780000570 | R2. | 79780008102 | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-6 Table R2 –Remote Access Management. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity does not have documented processes for one or more of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for one of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for two of the applicable items for Requirement Parts 2.1 through 2.3; OR The Responsible Entity did not have either: one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4); or one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). | The Responsible Entity did not implement processes for three of the applicable items for Requirement Parts 2.1 through 2.3; OR The Responsible Entity did not have one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4) and one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-6 Table R2 –Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | NPCC-ON | [6 empty] | 20000000
CIP-005-6 (Saskatchewan) | 83750000000570 | R1. | 837500000008096 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium |  |  | The Responsible Entity did not have a method for detecting malicious communications for both inbound and outbound communications. (1.5) | The Responsible Entity did not document one or more processes for CIP-005-6 Table R1 – Electronic Security Perimeter. (R1) OR The Responsible Entity did not have all applicable Cyber Assets connected to a network via a routable protocol within a defined Electronic Security Perimeter (ESP). (1.1) OR External Routable Connectivity through the ESP was not through an identified EAP. (1.2) OR The Responsible Entity did not require inbound and outbound access permissions and deny all other access by default. (1.3) OR The Responsible Entity did not perform authentication when establishing dial-up connectivity with the applicable Cyber Assets, where technically feasible. (1.4) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2020-10-01 |  | 2022-12-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | MRO-SK | [6 empty] | 10000000
CIP-005-6 (Saskatchewan) | 83750000000570 | R2. | 837500000008102 | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-6 Table R2 –Remote Access Management. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity does not have documented processes for one or more of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for one of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for two of the applicable items for Requirement Parts 2.1 through 2.3; OR The Responsible Entity did not have either: one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4); or one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). | The Responsible Entity did not implement processes for three of the applicable items for Requirement Parts 2.1 through 2.3; OR The Responsible Entity did not have one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4) and one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-6 Table R2 –Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2020-10-01 |  | 2022-12-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | MRO-SK | [6 empty] | 20000000
CIP-005-7 | 635 | R1. | 9448 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-7 Table R1 – Electronic Security Perimeter. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | NULL | NULL | The Responsible Entity did not have a method for detecting malicious communications for both inbound and outbound communications. (1.5) | The Responsible Entity did not document one or more processes for CIP-005-6 Table R1 – Electronic Security Perimeter. (R1) ORThe Responsible Entity did not have all applicable Cyber Assets connected to a network via a routable protocol within a defined Electronic Security Perimeter (ESP). (1.1)ORExternal Routable Connectivity through the ESP was not through an identified EAP. (1.2)OR The Responsible Entity did not require inbound and outbound access permissions and deny all other access by default. (1.3) The Responsible Entity did not perform authentication when establishing dial-up connectivity with the applicable Cyber Assets, where technically feasible. (1.4) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-7 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2022-10-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-005-7 | 635 | R2. | 9449 | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-7 Table R2 –Remote Access Management. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity does not have documented processes for one or more of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for one of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for two of the applicable items for Requirement Parts 2.1 through 2.3;OR The Responsible Entity did not have either: one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4); or one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). | The Responsible Entity did not implement processes for three of the applicable items for Requirement Parts 2.1 through 2.3; OR The Responsible Entity did not have one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4) and one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP 005-7 Table R2 –Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2022-10-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-005-7 | 635 | R3. | 9450 | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts in CIP-005-7 Table R3 –Vendor Remote Access Management for EACMS and PACS. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity did not document one or more processes for CIP-005-7 Table R3 – Vendor Remote Access Management for EACMS and PACS. (R3) | The Responsible Entity had method(s) as required by Part 3.1 for EACMS but did not have a method to determine authenticated vendor-initiated remote connections for PACS (3.1).OR The Responsible Entity had method(s) as required by Part 3.2 for EACMS but did not have a method to terminate authenticated vendor-initiated remote connections for PACS (3.2). | The Responsible Entity did not implement processes for either Part 3.1 or Part 3.2. (R3) OR The Responsible Entity had method(s) as required by Part 3.1 for PACS but did not have a method to determine authenticated vendor-initiated remote connections for EACMS (3.1). OR The Responsible Entity had method(s) as required by Part 3.2 for PACS but did not have a method to terminate authenticated vendor-initiated remote connections or control the ability to reconnect for EACMS (3.2). | The Responsible Entity did not implement any processes for CIP-005-7 Table R3 – Vendor Remote Access Management for EACMS and PACS. (R3) OR The Responsible Entity did not have any methods as required by Parts 3.1 and 3.2 (R3). | M3. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP 005-7 Table R3 – Vendor Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2022-10-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-005-7 (Manitoba) | ST-2023-10-03-0000001 | R1. | RQ-2023-10-03-0000001 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-7 Table R1 – Electronic Security Perimeter |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium |  |  | The Responsible Entity did not have a method for detecting malicious communications for both inbound and outbound communications. (1.5) | The Responsible Entity did not document one or more processes for CIP-005-6 Table R1 – Electronic Security Perimeter. (R1) OR The Responsible Entity did not have all applicable Cyber Assets connected to a network via a routable protocol within a defined Electronic Security Perimeter (ESP). (1.1) OR External Routable Connectivity through the ESP was not through an identified EAP. (1.2) OR The Responsible Entity did not require inbound and outbound access permissions and deny all other access by default. (1.3) OR The Responsible Entity did not perform authentication when establishing dial-up connectivity with the applicable Cyber Assets, where technically feasible. (1.4) | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-7 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2023-07-01 |  |  |  | : For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator 4.1.4. Generator Owner CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 2 of 20 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 3 of 20 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | MRO-MB | [6 empty] | 10000000
CIP-005-7 (Manitoba) | ST-2023-10-03-0000001 | R2. | RQ-2023-10-03-0000002 | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-7 Table R2 –Remote Access Management. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity does not have documented processes for one or more of the applicable items for Requirement Parts 2.1 through 2.3 | The Responsible Entity did not implement processes for one of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for two of the applicable items for Requirement Parts 2.1 through 2.3; OR The Responsible Entity did not have either: one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and systemto-system remote access) (2.4); or one or more methods to disable active vendor remote access (including Interactive Remote Access and systemto-system remote access) (2.5). | The Responsible Entity did not implement processes for three of the applicable items for Requirement Parts 2.1 through 2.3; OR The Responsible Entity did not have one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4) and one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). | Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP005-7 Table R2 –Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2023-07-01 |  |  |  | : For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator 4.1.4. Generator Owner CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 2 of 20 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 3 of 20 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | MRO-MB | [6 empty] | 20000000
CIP-005-7 (Manitoba) | ST-2023-10-03-0000001 | R3. | RQ-2023-10-03-0000003 | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts in CIP-005-7 Table R3 –Vendor Remote Access Management for EACMS and PACS |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity did not document one or more processes for CIP-005-7 Table R3 – Vendor Remote Access Management for EACMS and PACS. (R3) | The Responsible Entity had method(s) as required by Part 3.1 for EACMS but did not have a method to determine authenticated vendor-initiated remote connections for PACS (3.1). OR The Responsible Entity had method(s) as required by Part 3.2 for EACMS but did not have a method to terminate authenticated vendor-initiated remote connections for PACS (3.2). | The Responsible Entity did not implement processes for either Part 3.1 or Part 3.2. (R3) OR The Responsible Entity had method(s) as required by Part 3.1 for PACS but did not have a method to determine authenticated vendor-initiated remote connections for EACMS (3.1). OR The Responsible Entity had method(s) as required by Part 3.2 for PACS but did not have a method to terminate authenticated vendor-initiated remote connections or control the ability to reconnect for EACMS (3.2). | The Responsible Entity did not implement any processes for CIP-005-7 Table R3 – Vendor Remote Access Management for EACMS and PACS. (R3) OR The Responsible Entity did not have any methods as required by Parts 3.1 and 3.2 (R3). | Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP005-7 Table R3 – Vendor Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table | 2023-07-01 |  |  |  | : For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator 4.1.4. Generator Owner CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 2 of 20 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 3 of 20 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | MRO-MB | [6 empty] | 30000000
CIP-005-7 (Nova Scotia) | 78830000000635 | R1. | 788300000009448 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-7 Table R1 – Electronic Security Perimeter. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | NULL | NULL | The Responsible Entity did not have a method for detecting malicious communications for both inbound and outbound communications. (1.5) | The Responsible Entity did not document one or more processes for CIP-005-6 Table R1 – Electronic Security Perimeter. (R1) ORThe Responsible Entity did not have all applicable Cyber Assets connected to a network via a routable protocol within a defined Electronic Security Perimeter (ESP). (1.1)ORExternal Routable Connectivity through the ESP was not through an identified EAP. (1.2)OR The Responsible Entity did not require inbound and outbound access permissions and deny all other access by default. (1.3) The Responsible Entity did not perform authentication when establishing dial-up connectivity with the applicable Cyber Assets, where technically feasible. (1.4) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-7 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2023-01-01 | [5 empty] | NPCC-NS | [6 empty] | 10000000
CIP-005-7 (Nova Scotia) | 78830000000635 | R2. | 788300000009449 | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-7 Table R2 –Remote Access Management. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity does not have documented processes for one or more of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for one of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for two of the applicable items for Requirement Parts 2.1 through 2.3;OR The Responsible Entity did not have either: one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4); or one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). | The Responsible Entity did not implement processes for three of the applicable items for Requirement Parts 2.1 through 2.3; OR The Responsible Entity did not have one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4) and one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP 005-7 Table R2 –Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2023-01-01 | [5 empty] | NPCC-NS | [6 empty] | 20000000
CIP-005-7 (Nova Scotia) | 78830000000635 | R3. | 788300000009450 | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts in CIP-005-7 Table R3 –Vendor Remote Access Management for EACMS and PACS. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity did not document one or more processes for CIP-005-7 Table R3 – Vendor Remote Access Management for EACMS and PACS. (R3) | The Responsible Entity had method(s) as required by Part 3.1 for EACMS but did not have a method to determine authenticated vendor-initiated remote connections for PACS (3.1).OR The Responsible Entity had method(s) as required by Part 3.2 for EACMS but did not have a method to terminate authenticated vendor-initiated remote connections for PACS (3.2). | The Responsible Entity did not implement processes for either Part 3.1 or Part 3.2. (R3) OR The Responsible Entity had method(s) as required by Part 3.1 for PACS but did not have a method to determine authenticated vendor-initiated remote connections for EACMS (3.1). OR The Responsible Entity had method(s) as required by Part 3.2 for PACS but did not have a method to terminate authenticated vendor-initiated remote connections or control the ability to reconnect for EACMS (3.2). | The Responsible Entity did not implement any processes for CIP-005-7 Table R3 – Vendor Remote Access Management for EACMS and PACS. (R3) OR The Responsible Entity did not have any methods as required by Parts 3.1 and 3.2 (R3). | M3. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP 005-7 Table R3 – Vendor Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2023-01-01 | [5 empty] | NPCC-NS | [6 empty] | 30000000
CIP-005-7 (Ontario) | 79780000635 | R1. | 79780009448 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-7 Table R1 – Electronic Security Perimeter. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | Medium | NULL | NULL | The Responsible Entity did not have a method for detecting malicious communications for both inbound and outbound communications. (1.5) | The Responsible Entity did not document one or more processes for CIP-005-6 Table R1 – Electronic Security Perimeter. (R1) ORThe Responsible Entity did not have all applicable Cyber Assets connected to a network via a routable protocol within a defined Electronic Security Perimeter (ESP). (1.1)ORExternal Routable Connectivity through the ESP was not through an identified EAP. (1.2)OR The Responsible Entity did not require inbound and outbound access permissions and deny all other access by default. (1.3) The Responsible Entity did not perform authentication when establishing dial-up connectivity with the applicable Cyber Assets, where technically feasible. (1.4) | [7 empty] | NPCC-ON | [6 empty] | 10000000
CIP-005-7 (Ontario) | 79780000635 | R2. | 79780009449 | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-7 Table R2 –Remote Access Management. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | Medium | The Responsible Entity does not have documented processes for one or more of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for one of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for two of the applicable items for Requirement Parts 2.1 through 2.3;OR The Responsible Entity did | The Responsible Entity did not implement processes for three of the applicable items for Requirement Parts 2.1 through 2.3; OR The Responsible Entity did | [7 empty] | NPCC-ON | [6 empty] | 20000000
CIP-005-7 (Ontario) | 79780000635 | R3. | 79780009450 | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts in CIP-005-7 Table R3 –Vendor Remote Access Management for EACMS and PACS. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | Medium | The Responsible Entity did not document one or more processes for CIP-005-7 Table R3 – Vendor Remote Access Management for EACMS and PACS. (R3) | The Responsible Entity had method(s) as required by Part 3.1 for EACMS but did not have a method to determine authenticated vendor-initiated remote connections for PACS (3.1).OR The Responsible Entity had method(s) as required by Part 3.2 for EACMS but did not have a method to terminate authenticated vendor-initiated remote connections for PACS (3.2). | The Responsible Entity did not implement processes for either Part 3.1 or Part 3.2. (R3) OR The Responsible Entity had method(s) as required by Part 3.1 for PACS but did not have a method to determine authenticated vendor-initiated remote connections for EACMS (3.1). OR The Responsible Entity had method(s) as required by Part 3.2 for PACS but did not have a method to terminate authenticated vendor-initiated remote connections or control the ability to reconnect for EACMS (3.2). | The Responsible Entity did not implement any processes for CIP-005-7 Table R3 – Vendor Remote Access Management for EACMS and PACS. (R3) OR The Responsible Entity did not have any methods as required by Parts 3.1 and 3.2 (R3). | [7 empty] | NPCC-ON | [6 empty] | 30000000
CIP-005-7 (Saskatchewan) | 83750000000635 | R1. | 837500000009448 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-7 Table R1 – Electronic Security Perimeter. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | NULL | NULL | The Responsible Entity did not have a method for detecting malicious communications for both inbound and outbound communications. (1.5) | The Responsible Entity did not document one or more processes for CIP-005-6 Table R1 – Electronic Security Perimeter. (R1) ORThe Responsible Entity did not have all applicable Cyber Assets connected to a network via a routable protocol within a defined Electronic Security Perimeter (ESP). (1.1)ORExternal Routable Connectivity through the ESP was not through an identified EAP. (1.2)OR The Responsible Entity did not require inbound and outbound access permissions and deny all other access by default. (1.3) The Responsible Entity did not perform authentication when establishing dial-up connectivity with the applicable Cyber Assets, where technically feasible. (1.4) | M1. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-7 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2023-01-01 | [5 empty] | MRO-SK | [6 empty] | 10000000
CIP-005-7 (Saskatchewan) | 83750000000635 | R2. | 837500000009449 | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-7 Table R2 –Remote Access Management. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity does not have documented processes for one or more of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for one of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for two of the applicable items for Requirement Parts 2.1 through 2.3;OR The Responsible Entity did not have either: one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4); or one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). | The Responsible Entity did not implement processes for three of the applicable items for Requirement Parts 2.1 through 2.3; OR The Responsible Entity did not have one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4) and one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). | M2. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP 005-7 Table R2 –Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2023-01-01 | [5 empty] | MRO-SK | [6 empty] | 20000000
CIP-005-7 (Saskatchewan) | 83750000000635 | R3. | 837500000009450 | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts in CIP-005-7 Table R3 –Vendor Remote Access Management for EACMS and PACS. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity did not document one or more processes for CIP-005-7 Table R3 – Vendor Remote Access Management for EACMS and PACS. (R3) | The Responsible Entity had method(s) as required by Part 3.1 for EACMS but did not have a method to determine authenticated vendor-initiated remote connections for PACS (3.1).OR The Responsible Entity had method(s) as required by Part 3.2 for EACMS but did not have a method to terminate authenticated vendor-initiated remote connections for PACS (3.2). | The Responsible Entity did not implement processes for either Part 3.1 or Part 3.2. (R3) OR The Responsible Entity had method(s) as required by Part 3.1 for PACS but did not have a method to determine authenticated vendor-initiated remote connections for EACMS (3.1). OR The Responsible Entity had method(s) as required by Part 3.2 for PACS but did not have a method to terminate authenticated vendor-initiated remote connections or control the ability to reconnect for EACMS (3.2). | The Responsible Entity did not implement any processes for CIP-005-7 Table R3 – Vendor Remote Access Management for EACMS and PACS. (R3) OR The Responsible Entity did not have any methods as required by Parts 3.1 and 3.2 (R3). | M3. Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP 005-7 Table R3 – Vendor Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2023-01-01 | [5 empty] | MRO-SK | [6 empty] | 30000000
CIP-005-8 | ST-2024-05-10-0000005 | R1. | RQ-2024-05-10-0000016 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-8 Table R1 – Electronic Security Perimeter. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium |  |  | The Responsible Entity did not have a method for detecting known or suspected malicious routable protocol communications entering or leaving the ESP required by Part 1.5. OR The Responsible Entity did not document the reason for permitting communications. (Part 1.2) | The Responsible Entity did not document one or more processes for CIP-005-8 Table R1 – Electronic Security Perimeter. (R1) OR The Responsible Entity did not protect the Applicable Systems connected to the network with routable protocol with an ESP. (Part 1.1) OR The Responsible Entity did not permit only needed communications and deny all other communications, through the ESP; excluding time sensitive communications of Protection Systems. (Part 1.2) OR The Responsible Entity did not protect ESP and SCI configurations by implementing methods to permit only needed network accessibility to Management Interfaces for Applicable Systems per system capability. (Part 1.3) OR The Responsible Entity did not perform authentication when establishing Dial-up Connectivity with the Applicable Systems. (Part 1.4) OR The Responsible Entity did not implement a method to protect the data traversing communication links, used to span a single ESP between PSPs, as required by Part 1.6. | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-005-8 Table R1 – Electronic Security Perimeter and additional evidence to demonstrate implementation as described in the Measures column of the table. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-005-8 | ST-2024-05-10-0000005 | R2. | RQ-2024-05-10-0000017 | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts, per system capability, in CIP-005-8 Table R2 – Remote Access Management. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity does not have documented processes for one or more of the applicable Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for one of the applicable Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for two of the applicable Requirement Parts 2.1 through 2.3. OR The Responsible Entity did not have either: one or more method(s) for determining active vendor remote access sessions (including IRA and system-to-system remote access) (Part 2.4); or one or more methods to disable active vendor remote access (including IRA and system-to-system remote access) (Part 2.5). | The Responsible Entity did not implement processes for three of the applicable Requirement Parts 2.1 through 2.3. OR The Responsible Entity did not have one or more method(s) for determining active vendor remote access sessions (including IRA and system-to-system remote access) (Part 2.4) and one or more methods to disable active vendor remote access (including IRA and system-to-system remote access) (Part 2.5). OR The Responsible Entity did not prevent Intermediate System(s) from sharing CPU resources or memory resources with any part of a high or medium impact BCS or associated PCAs. (Part 2.6). OR The Responsible Entity did not ensure routable protocol communications from an Intermediate System to high or medium impact BCS or associated PCAs went through an ESP (Part 2.7). | Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-8 Table R2 – Remote Access Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-005-8 | ST-2024-05-10-0000005 | R3. | RQ-2024-05-10-0000018 | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts in CIP-005-8 Table R3 –Vendor Remote Access Management for EACMS, PACS, and SCI. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Responsible Entity did not document one or more processes for CIP-005-8 Table R3 – Vendor Remote Access Management for EACMS, PACS, and SCI. (Requirement R3) | The Responsible Entity did not have a method to determine authenticated vendor-initiated remote connections for PACS or SCI supporting PACS (Part 3.1). OR The Responsible Entity did not have a method to terminate authenticated vendor-initiated remote connections for PACS or SCI supporting PACS (Part 3.2). | The Responsible Entity did not implement processes for either Part 3.1 or Part 3.2. (Requirement R3) OR The Responsible Entity did not have a method to determine authenticated vendor-initiated remote connections for EACMS or SCI supporting EACMS (Part 3.1). OR The Responsible Entity did not have a method to terminate authenticated vendor-initiated remote connections or control the ability to reconnect for EACMS or SCI supporting EACMS (Part 3.2). | The Responsible Entity did not implement any processes for CIP-005-8 Table R3 – Vendor Remote Access Management for EACMS, PACS, and SCI. (Requirement R3) OR The Responsible Entity did not have any methods as required by Parts 3.1 and 3.2 (Requirement R3). | Evidence must include the documented processes that collectively address each of the applicable requirement parts in CIP-005-8 Table R3 – Vendor Remote Access Management for EACMS, PACS, and SCI and additional evidence to demonstrate implementation as described in the Measures column of the table. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-005-AB-5 (Alberta) | 656600000009009 | R1. | 656600000009101 | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP]005-AB]5 Table R1 - Electronic Security Perimeter. |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 10000000
CIP-005-AB-5 (Alberta) | 656600000009009 | R2. | 656600000009102 | Each Responsible Entity allowing Interactive Remote Access to BES cyber systems shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP]005-AB ]5 Table R2 - Interactive Remote Access Management. |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 20000000
CIP-006-1 | 27 | R1. | 330 | Physical Security Plan — The Responsible Entity shall create and maintain a physical security plan, approved by a senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-006-1 | 27 | R2. | 340 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-006-1 | 27 | R3. | 345 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008. One or more of the following monitoring methods shall be used: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-006-1 | 27 | R4. | 348 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-006-1 | 27 | R5. | 352 | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-006-1 | 27 | R6. | 353 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-006-1a | 28 | R1. | 357 | Physical Security Plan — The Responsible Entity shall create and maintain a physical security plan, approved by a senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | The Responsible Entity created a physical security plan but did not gain approval by a senior manager or delegate(s). OR The Responsible Entity created but did not maintain a physical security plan. | The Responsible Entity did not create and maintain a physical security plan. |  |  |  | 2009-12-22 |  |  | CIP-006-1 R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-006-1a | 28 | R2. | 367 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2009-12-22 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-006-1a | 28 | R3. | 372 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008. One or more of the following monitoring methods shall be used: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2009-12-22 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-006-1a | 28 | R4. | 375 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2009-12-22 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-006-1a | 28 | R5. | 379 | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2009-12-22 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-006-1a | 28 | R6. | 380 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2009-12-22 |  |  | CIP-006-1 R6. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-006-1a (Ontario) | 79780000028 | R1. | 79780000357 | Physical Security Plan — The Responsible Entity shall create and maintain a physical security plan, approved by a senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | The Responsible Entity created a physical security plan but did not gain approval by a senior manager or delegate(s).&lt;br/&gt;OR&lt;br/&gt;The Responsible Entity created but did not maintain a physical security plan. | The Responsible Entity did not create and maintain a physical security plan. |  |  |  | 2009-12-22 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-006-1a (Ontario) | 79780000028 | R2. | 79780000367 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity has implemented but not documented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the acc | The Responsible Entity has documented but not implemented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the acc | The Responsible Entity has not documented nor implemented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the acc |  |  |  | 2009-12-22 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-006-1a (Ontario) | 79780000028 | R3. | 79780000372 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008. One or more of the following monitoring methods shall be used: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity has implemented but not documented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the | The Responsible Entity has documented but not implemented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the | The Responsible Entity has not documented nor implemented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the |  |  |  | 2009-12-22 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-006-1a (Ontario) | 79780000028 | R4. | 79780000375 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity has implemented but not documented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the logging methods identified in Requirements R4. | The Responsible Entity has implemented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the logging methods identified in Requirements R4.1, R4.2, or R4.3, b | The Responsible Entity has documented but not implemented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the logging methods identified in Requirements R4. | The Responsible Entity has not implemented nor documented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the logging methods identified in Requirements R4. |  |  |  | 2009-12-22 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-006-1a (Ontario) | 79780000028 | R5. | 79780000379 | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity retained physical access logs for 75 or more calendar days, but for less than 90 calendar days. | The Responsible Entity retained physical access logs for 60 or more calendar days, but for less than 75 calendar days. | The Responsible Entity retained physical access logs for 45 or more calendar days , but for less than 60 calendar days. | The Responsible Entity retained physical access logs for less than 45 calendar days. |  |  |  | 2009-12-22 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-006-1a (Ontario) | 79780000028 | R6. | 79780000380 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | The Responsible Entity has implemented a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly but the program does not include one of the requirements R6.1, R6.2, and R6.3. | The Responsible Entity has implemented a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly but the program does not include two of the requirements R6.1, R6.2, and R6.3. | The Responsible Entity has implemented a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly but the program does not include any of the requirements R6.1, R6.2, and R6.3. | The Responsible Entity has not implemented a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly. |  |  |  | 2009-12-22 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-006-1b | 232 | R1. | 2925 | Physical Security Plan — The Responsible Entity shall create and maintain a physical security plan, approved by a senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2009-12-22 |  |  | CIP-006-1 R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-006-1b | 232 | R2. | 2926 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2009-12-22 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-006-1b | 232 | R3. | 2927 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008. One or more of the following monitoring methods shall be used: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2009-12-22 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-006-1b | 232 | R4. | 2923 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2009-12-22 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-006-1b | 232 | R5. | 2924 | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low |  | . | [5 empty] | 2009-12-22 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-006-1b | 232 | R6. | 2928 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2009-12-22 |  |  | CIP-006-1 R6. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-006-1b (Ontario) | 79780000232 | R1. | 79780002925 | Physical Security Plan — The Responsible Entity shall create and maintain a physical security plan, approved by a senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | The Responsible Entity created a physical security plan but did not gain approval by a senior manager or delegate(s).&lt;br/&gt;OR&lt;br/&gt;The Responsible Entity created but did not maintain a physical security plan. | The Responsible Entity did not create and maintain a physical security plan. |  |  |  | 2009-12-22 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-006-1b (Ontario) | 79780000232 | R2. | 79780002926 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity has implemented but not documented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the acc | The Responsible Entity has documented but not implemented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the acc | The Responsible Entity has not documented nor implemented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the acc |  |  |  | 2009-12-22 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-006-1b (Ontario) | 79780000232 | R3. | 79780002927 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008. One or more of the following monitoring methods shall be used: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity has implemented but not documented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the | The Responsible Entity has documented but not implemented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the | The Responsible Entity has not documented nor implemented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the |  |  |  | 2009-12-22 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-006-1b (Ontario) | 79780000232 | R4. | 79780002923 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity has implemented but not documented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the logging methods identified in Requirements R4. | The Responsible Entity has implemented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the logging methods identified in Requirements R4.1, R4.2, or R4.3, b | The Responsible Entity has documented but not implemented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the logging methods identified in Requirements R4. | The Responsible Entity has not implemented nor documented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the logging methods identified in Requirements R4. |  |  |  | 2009-12-22 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-006-1b (Ontario) | 79780000232 | R5. | 79780002924 | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity retained physical access logs for 75 or more calendar days, but for less than 90 calendar days. | The Responsible Entity retained physical access logs for 60 or more calendar days, but for less than 75 calendar days. | The Responsible Entity retained physical access logs for 45 or more calendar days , but for less than 60 calendar days. | The Responsible Entity retained physical access logs for less than 45 calendar days. |  |  |  | 2009-12-22 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-006-1b (Ontario) | 79780000232 | R6. | 79780002928 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | The Responsible Entity has implemented a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly but the program does not include one of the requirements R6.1, R6.2, and R6.3. | The Responsible Entity has implemented a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly but the program does not include two of the requirements R6.1, R6.2, and R6.3. | The Responsible Entity has implemented a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly but the program does not include any of the requirements R6.1, R6.2, and R6.3. | The Responsible Entity has not implemented a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly. |  |  |  | 2009-12-22 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-006-1 (British Columbia) | 666700000010047 | R1. | 666700000010587 | Physical Security Plan — The Responsible Entity shall create and maintain a physical security plan, approved by a senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-006-1 (British Columbia) | 666700000010047 | R2. | 666700000010588 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 20000000
CIP-006-1 (British Columbia) | 666700000010047 | R3. | 666700000010589 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008. One or more of the following monitoring methods shall be used: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 30000000
CIP-006-1 (British Columbia) | 666700000010047 | R4. | 666700000010590 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 40000000
CIP-006-1 (British Columbia) | 666700000010047 | R5. | 666700000010591 | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 50000000
CIP-006-1 (British Columbia) | 666700000010047 | R6. | 666700000010592 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 60000000
CIP-006-1c | 233 | R1. | 2955 | Physical Security Plan — The Responsible Entity shall create and maintain a physical security plan, approved by a senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-04-20 |  |  | CIP-006-1 R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-006-1c | 233 | R2. | 2950 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-04-20 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-006-1c | 233 | R3. | 2953 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008. One or more of the following monitoring methods shall be used: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-04-20 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-006-1c | 233 | R4. | 2951 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2010-04-20 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-006-1c | 233 | R5. | 2954 | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2010-04-20 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-006-1c | 233 | R6. | 2952 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-04-20 |  |  | CIP-006-1 R6. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-006-1c (Ontario) | 79780000233 | R1. | 79780002955 | Physical Security Plan — The Responsible Entity shall create and maintain a physical security plan, approved by a senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | The Responsible Entity created a physical security plan but did not gain approval by a senior manager or delegate(s).&lt;br/&gt;OR&lt;br/&gt;The Responsible Entity created but did not maintain a physical security plan. | The Responsible Entity did not create and maintain a physical security plan. |  |  |  | 2010-04-20 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-006-1c (Ontario) | 79780000233 | R2. | 79780002950 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity has implemented but not documented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the acc | The Responsible Entity has documented but not implemented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the acc | The Responsible Entity has not documented nor implemented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the acc |  |  |  | 2010-04-20 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-006-1c (Ontario) | 79780000233 | R3. | 79780002953 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008. One or more of the following monitoring methods shall be used: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity has implemented but not documented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the | The Responsible Entity has documented but not implemented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the | The Responsible Entity has not documented nor implemented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the |  |  |  | 2010-04-20 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-006-1c (Ontario) | 79780000233 | R4. | 79780002951 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity has implemented but not documented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the logging methods identified in Requirements R4. | The Responsible Entity has implemented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the logging methods identified in Requirements R4.1, R4.2, or R4.3, b | The Responsible Entity has documented but not implemented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the logging methods identified in Requirements R4. | The Responsible Entity has not implemented nor documented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the logging methods identified in Requirements R4. |  |  |  | 2010-04-20 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-006-1c (Ontario) | 79780000233 | R5. | 79780002954 | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity retained physical access logs for 75 or more calendar days, but for less than 90 calendar days. | The Responsible Entity retained physical access logs for 60 or more calendar days, but for less than 75 calendar days. | The Responsible Entity retained physical access logs for 45 or more calendar days , but for less than 60 calendar days. | The Responsible Entity retained physical access logs for less than 45 calendar days. |  |  |  | 2010-04-20 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-006-1c (Ontario) | 79780000233 | R6. | 79780002952 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | The Responsible Entity has implemented a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly but the program does not include one of the requirements R6.1, R6.2, and R6.3. | The Responsible Entity has implemented a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly but the program does not include two of the requirements R6.1, R6.2, and R6.3. | The Responsible Entity has implemented a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly but the program does not include any of the requirements R6.1, R6.2, and R6.3. | The Responsible Entity has not implemented a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly. |  |  |  | 2010-04-20 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-006-1 (Ontario) | 79780000027 | R1. | 79780000330 | Physical Security Plan — The Responsible Entity shall create and maintain a physical security plan, approved by a senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | The Responsible Entity created a physical security plan but did not gain approval by a senior manager or delegate(s).&lt;br/&gt;OR&lt;br/&gt;The Responsible Entity created but did not maintain a physical security plan. | The Responsible Entity did not create and maintain a physical security plan. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-006-1 (Ontario) | 79780000027 | R2. | 79780000340 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity has implemented but not documented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the acc | The Responsible Entity has documented but not implemented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the acc | The Responsible Entity has not documented nor implemented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the acc |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-006-1 (Ontario) | 79780000027 | R3. | 79780000345 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008. One or more of the following monitoring methods shall be used: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity has implemented but not documented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the | The Responsible Entity has documented but not implemented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the | The Responsible Entity has not documented nor implemented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using at least one of the |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-006-1 (Ontario) | 79780000027 | R4. | 79780000348 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity has implemented but not documented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the logging methods identified in Requirements R4. | The Responsible Entity has implemented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the logging methods identified in Requirements R4.1, R4.2, or R4.3, b | The Responsible Entity has documented but not implemented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the logging methods identified in Requirements R4. | The Responsible Entity has not implemented nor documented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the logging methods identified in Requirements R4. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-006-1 (Ontario) | 79780000027 | R5. | 79780000352 | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity retained physical access logs for 75 or more calendar days, but for less than 90 calendar days. | The Responsible Entity retained physical access logs for 60 or more calendar days, but for less than 75 calendar days. | The Responsible Entity retained physical access logs for 45 or more calendar days , but for less than 60 calendar days. | The Responsible Entity retained physical access logs for less than 45 calendar days. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-006-1 (Ontario) | 79780000027 | R6. | 79780000353 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | The Responsible Entity has implemented a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly but the program does not include one of the requirements R6.1, R6.2, and R6.3. | The Responsible Entity has implemented a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly but the program does not include two of the requirements R6.1, R6.2, and R6.3. | The Responsible Entity has implemented a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly but the program does not include any of the requirements R6.1, R6.2, and R6.3. | The Responsible Entity has not implemented a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-006-2 | 212 | R1. | 2441 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-07-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-006-2 | 212 | R2. | 2450 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-07-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-006-2 | 212 | R3. | 2453 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-07-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-006-2 | 212 | R4. | 2454 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: --Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. --Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. --Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. --Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-07-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-006-2 | 212 | R5. | 2455 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-2. One or more of the following monitoring methods shall be used: --Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. --Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-07-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-006-2 | 212 | R6. | 2456 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: --Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. --Video Recording: Electronic capture of video images of sufficient quality to determine identity. --Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-07-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-006-2 | 212 | R7. | 2457 | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-07-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
CIP-006-2 | 212 | R8. | 2458 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-07-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
CIP-006-2a | 299 | R1. | 3892 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-07-15 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-006-2a | 299 | R2. | 3894 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-07-15 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-006-2a | 299 | R3. | 3893 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-07-15 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-006-2a | 299 | R4. | 3890 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: --Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. --Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. --Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. --Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-07-15 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-006-2a | 299 | R5. | 3891 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-2. One or more of the following monitoring methods shall be used: --Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. --Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-07-15 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-006-2a | 299 | R6. | 3897 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: --Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. --Video Recording: Electronic capture of video images of sufficient quality to determine identity. --Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-07-15 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-006-2a | 299 | R7. | 3896 | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-07-15 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
CIP-006-2a | 299 | R8. | 3895 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-07-15 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
CIP-006-2a (Ontario) | 79780000299 | R1. | 79780003892 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-07-15 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-006-2a (Ontario) | 79780000299 | R2. | 79780003894 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-07-15 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-006-2a (Ontario) | 79780000299 | R3. | 79780003893 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-07-15 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-006-2a (Ontario) | 79780000299 | R4. | 79780003890 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: --Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. --Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. --Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. --Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-07-15 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-006-2a (Ontario) | 79780000299 | R5. | 79780003891 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-2. One or more of the following monitoring methods shall be used: --Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. --Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-07-15 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-006-2a (Ontario) | 79780000299 | R6. | 79780003897 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: --Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. --Video Recording: Electronic capture of video images of sufficient quality to determine identity. --Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-07-15 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-006-2a (Ontario) | 79780000299 | R7. | 79780003896 | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-07-15 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 70000000
CIP-006-2a (Ontario) | 79780000299 | R8. | 79780003895 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-07-15 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 80000000
CIP-006-2b | 230 | R1. | 2883 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-07-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-006-2b | 230 | R2. | 2885 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-07-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-006-2b | 230 | R3. | 2884 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-07-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-006-2b | 230 | R4. | 2881 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: --Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. --Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. --Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. --Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-07-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-006-2b | 230 | R5. | 2882 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-2. One or more of the following monitoring methods shall be used: --Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. --Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-07-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-006-2b | 230 | R6. | 2888 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: --Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. --Video Recording: Electronic capture of video images of sufficient quality to determine identity. --Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2010-07-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-006-2b | 230 | R7. | 2887 | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2010-07-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
CIP-006-2b | 230 | R8. | 2886 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-07-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
CIP-006-2b (Ontario) | 79780000230 | R1. | 79780002883 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-07-14 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-006-2b (Ontario) | 79780000230 | R2. | 79780002885 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-07-14 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-006-2b (Ontario) | 79780000230 | R3. | 79780002884 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-07-14 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-006-2b (Ontario) | 79780000230 | R4. | 79780002881 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: --Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. --Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. --Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. --Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-07-14 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-006-2b (Ontario) | 79780000230 | R5. | 79780002882 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-2. One or more of the following monitoring methods shall be used: --Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. --Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-07-14 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-006-2b (Ontario) | 79780000230 | R6. | 79780002888 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: --Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. --Video Recording: Electronic capture of video images of sufficient quality to determine identity. --Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2010-07-14 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-006-2b (Ontario) | 79780000230 | R7. | 79780002887 | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2010-07-14 |  |  |  | NPCC-ON | [6 empty] | 70000000
CIP-006-2b (Ontario) | 79780000230 | R8. | 79780002886 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-07-14 |  |  |  | NPCC-ON | [6 empty] | 80000000
CIP-006-2c | 231 | R1. | 2904 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-006-2c | 231 | R2. | 2906 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-006-2c | 231 | R3. | 2905 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-006-2c | 231 | R4. | 2902 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: --Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. --Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. --Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. --Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-006-2c | 231 | R5. | 2903 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-2. One or more of the following monitoring methods shall be used: --Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. --Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-006-2c | 231 | R6. | 2909 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: --Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. --Video Recording: Electronic capture of video images of sufficient quality to determine identity. --Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-006-2c | 231 | R7. | 2908 | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
CIP-006-2c | 231 | R8. | 2907 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
CIP-006-2c (Ontario) | 79780000231 | R1. | 79780002904 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-006-2c (Ontario) | 79780000231 | R2. | 79780002906 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-006-2c (Ontario) | 79780000231 | R3. | 79780002905 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-006-2c (Ontario) | 79780000231 | R4. | 79780002902 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: --Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. --Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. --Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. --Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-006-2c (Ontario) | 79780000231 | R5. | 79780002903 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-2. One or more of the following monitoring methods shall be used: --Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. --Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-006-2c (Ontario) | 79780000231 | R6. | 79780002909 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: --Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. --Video Recording: Electronic capture of video images of sufficient quality to determine identity. --Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-006-2c (Ontario) | 79780000231 | R7. | 79780002908 | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 70000000
CIP-006-2c (Ontario) | 79780000231 | R8. | 79780002907 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 80000000
CIP-006-2 (Ontario) | 79780000212 | R1. | 79780002441 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-07-14 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-006-2 (Ontario) | 79780000212 | R2. | 79780002450 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-07-14 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-006-2 (Ontario) | 79780000212 | R3. | 79780002453 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-07-14 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-006-2 (Ontario) | 79780000212 | R4. | 79780002454 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: --Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. --Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. --Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. --Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-07-14 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-006-2 (Ontario) | 79780000212 | R5. | 79780002455 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-2. One or more of the following monitoring methods shall be used: --Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. --Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-07-14 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-006-2 (Ontario) | 79780000212 | R6. | 79780002456 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: --Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. --Video Recording: Electronic capture of video images of sufficient quality to determine identity. --Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-07-14 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-006-2 (Ontario) | 79780000212 | R7. | 79780002457 | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-07-14 |  |  |  | NPCC-ON | [6 empty] | 70000000
CIP-006-2 (Ontario) | 79780000212 | R8. | 79780002458 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-07-14 |  |  |  | NPCC-ON | [6 empty] | 80000000
CIP-006-3 | 226 | R1. | 2800 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [9 empty] | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-006-3 | 226 | R2. | 2811 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [9 empty] | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-006-3 | 226 | R3. | 2814 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [9 empty] | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-006-3 | 226 | R4. | 2815 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [9 empty] | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-006-3 | 226 | R5. | 2816 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [9 empty] | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-006-3 | 226 | R6. | 2817 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [9 empty] | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-006-3 | 226 | R7. | 2818 | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [9 empty] | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
CIP-006-3 | 226 | R8. | 2819 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [9 empty] | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
CIP-006-3a | 300 | R1. | 3913 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-10-01 |  | 2011-05-18 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-006-3a | 300 | R2. | 3918 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-10-01 |  | 2011-05-18 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-006-3a | 300 | R3. | 3915 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-10-01 |  | 2011-05-18 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-006-3a | 300 | R4. | 3916 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-10-01 |  | 2011-05-18 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-006-3a | 300 | R5. | 3917 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-10-01 |  | 2011-05-18 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-006-3a | 300 | R6. | 3914 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-10-01 |  | 2011-05-18 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-006-3a | 300 | R7. | 3911 | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-10-01 |  | 2011-05-18 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
CIP-006-3a | 300 | R8. | 3912 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-10-01 |  | 2011-05-18 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
CIP-006-3a (Ontario) | 79780000300 | R1. | 79780003913 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-10-01 |  | 2011-05-18 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-006-3a (Ontario) | 79780000300 | R2. | 79780003918 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-10-01 |  | 2011-05-18 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-006-3a (Ontario) | 79780000300 | R3. | 79780003915 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-10-01 |  | 2011-05-18 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-006-3a (Ontario) | 79780000300 | R4. | 79780003916 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods:&lt;br/&gt;• Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another.&lt;br/&gt;• Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems.&lt;br/&gt;• Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station.&lt;br/&gt;• Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-10-01 |  | 2011-05-18 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-006-3a (Ontario) | 79780000300 | R5. | 79780003917 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used:&lt;br/&gt;• Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response.&lt;br/&gt;• Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-10-01 |  | 2011-05-18 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-006-3a (Ontario) | 79780000300 | R6. | 79780003914 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent:&lt;br/&gt;• Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method.&lt;br/&gt;• Video Recording: Electronic capture of video images of sufficient quality to determine identity.&lt;br/&gt;• Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-10-01 |  | 2011-05-18 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-006-3a (Ontario) | 79780000300 | R7. | 79780003911 | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-10-01 |  | 2011-05-18 |  |  |  | NPCC-ON | [6 empty] | 70000000
CIP-006-3a (Ontario) | 79780000300 | R8. | 79780003912 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-10-01 |  | 2011-05-18 |  |  |  | NPCC-ON | [6 empty] | 80000000
CIP-006-3c | 234 | R1. | 2979 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | The Responsible Entity created a physical security plan but did not gain approval by a senior manager or delegate(s). OR The Responsible Entity created and implemented but did not maintain a physical security plan. | The Responsible Entity did not document, implement, and maintain a physical security plan. | M1. The Responsible Entity shall make available the physical security plan as specified in Requirement R1 and documentation of the implementation, review and updating of the plan. | 2011-05-19 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-006-3c | 234 | R2. | 2984 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | A Cyber Asset that authorizes and/or logs access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, was not protected from unauthorized physical access. Perimeter access point such as electronic lock control mechanisms and badge readers was not afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3a Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. | M2. The Responsible Entity shall make available documentation that the physical access control systems are protected as specified in Requirement R2. | 2011-05-19 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-006-3c | 234 | R3. | 2981 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | A Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) does not reside within an identified Physical Security Perimeter. | M3. The Responsible Entity shall make available documentation that the electronic access control systems are located within an identified Physical Security Perimeter as specified in Requirement R3. | 2011-05-19 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-006-3c | 234 | R4. | 2982 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity has not documented or has not implemented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. | M4. The Responsible Entity shall make available documentation identifying the methods for controlling physical access to each access point of a Physical Security Perimeter as specified in Requirement R4. | 2011-05-19 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-006-3c | 234 | R5. | 2983 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity has not documented or has not implemented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more of the following monitoring methods: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. OR An unauthorized access attempt was not reviewed immediately and handled in accordance with CIP-008-3. | M5. The Responsible Entity shall make available documentation identifying the methods for monitoring physical access as specified in Requirement R5. | 2011-05-19 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-006-3c | 234 | R6. | 2980 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity has not implemented or has not documented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method, • Video Recording: Electronic capture of video images of sufficient quality to determine identity, or • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. OR The Responsible Entity has not recorded sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. | M6. The Responsible Entity shall make available documentation identifying the methods for logging physical access as specified in Requirement R6. | 2011-05-19 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-006-3c | 234 | R7. | 2977 | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A |  | N/A | M7. The Responsible Entity shall make available documentation to show retention of access logs as specified in Requirement R7. | 2011-05-19 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
CIP-006-3c | 234 | R8. | 2978 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity has not implemented a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. OR The implemented program does not include one or more of the requirements; R8.1, R8.2, and R8.3. | M8. The Responsible Entity shall make available documentation to show its implementation of a physical security system maintenance and testing program as specified in Requirement R8. | 2011-05-19 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
CIP-006-3c (British Columbia) | 666700000010048 | R1. | 666700000010593 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | The Responsible Entity created a physical security plan but did not gain approval by a senior manager or delegate(s). OR The Responsible Entity created and implemented but did not maintain a physical security plan. | The Responsible Entity did not document, implement, and maintain a physical security plan. | M1. The Responsible Entity shall make available the physical security plan as specified in Requirement R1 and documentation of the implementation, review and updating of the plan. | 2012-07-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-006-3c (British Columbia) | 666700000010048 | R2. | 666700000010594 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | A Cyber Asset that authorizes and/or logs access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, was not protected from unauthorized physical access. Perimeter access point such as electronic lock control mechanisms and badge readers was not afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3a Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. | M2. The Responsible Entity shall make available documentation that the physical access control systems are protected as specified in Requirement R2. | 2012-07-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 20000000
CIP-006-3c (British Columbia) | 666700000010048 | R3. | 666700000010595 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | A Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) does not reside within an identified Physical Security Perimeter. | M3. The Responsible Entity shall make available documentation that the electronic access control systems are located within an identified Physical Security Perimeter as specified in Requirement R3. | 2012-07-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 30000000
CIP-006-3c (British Columbia) | 666700000010048 | R4. | 666700000010596 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity has not documented or has not implemented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. | M4. The Responsible Entity shall make available documentation identifying the methods for controlling physical access to each access point of a Physical Security Perimeter as specified in Requirement R4. | 2012-07-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 40000000
CIP-006-3c (British Columbia) | 666700000010048 | R5. | 666700000010597 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity has not documented or has not implemented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more of the following monitoring methods: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. OR An unauthorized access attempt was not reviewed immediately and handled in accordance with CIP-008-3. | M5. The Responsible Entity shall make available documentation identifying the methods for monitoring physical access as specified in Requirement R5. | 2012-07-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 50000000
CIP-006-3c (British Columbia) | 666700000010048 | R6. | 666700000010598 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity has not implemented or has not documented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method, • Video Recording: Electronic capture of video images of sufficient quality to determine identity, or • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. OR The Responsible Entity has not recorded sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. | M6. The Responsible Entity shall make available documentation identifying the methods for logging physical access as specified in Requirement R6. | 2012-07-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 60000000
CIP-006-3c (British Columbia) | 666700000010048 | R7. | 666700000010599 | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A |  | N/A | M7. The Responsible Entity shall make available documentation to show retention of access logs as specified in Requirement R7. | 2012-07-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 70000000
CIP-006-3c (British Columbia) | 666700000010048 | R8. | 666700000010600 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity has not implemented a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. OR The implemented program does not include one or more of the requirements; R8.1, R8.2, and R8.3. | M8. The Responsible Entity shall make available documentation to show its implementation of a physical security system maintenance and testing program as specified in Requirement R8. | 2012-07-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 80000000
CIP-006-3c (Manitoba) | 77660000000234 | R1. | 776600000002979 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | The Responsible Entity created a physical security plan but did not gain approval by a senior manager or delegate(s). OR The Responsible Entity created and implemented but did not maintain a physical security plan. | The Responsible Entity did not document, implement, and maintain a physical security plan. | M1. The Responsible Entity shall make available the physical security plan as specified in Requirement R1 and documentation of the implementation, review and updating of the plan. | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
CIP-006-3c (Manitoba) | 77660000000234 | R2. | 776600000002984 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | A Cyber Asset that authorizes and/or logs access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, was not protected from unauthorized physical access. Perimeter access point such as electronic lock control mechanisms and badge readers was not afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3a Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. | M2. The Responsible Entity shall make available documentation that the physical access control systems are protected as specified in Requirement R2. | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
CIP-006-3c (Manitoba) | 77660000000234 | R3. | 776600000002981 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | A Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) does not reside within an identified Physical Security Perimeter. | M3. The Responsible Entity shall make available documentation that the electronic access control systems are located within an identified Physical Security Perimeter as specified in Requirement R3. | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
CIP-006-3c (Manitoba) | 77660000000234 | R4. | 776600000002982 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity has not documented or has not implemented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. | M4. The Responsible Entity shall make available documentation identifying the methods for controlling physical access to each access point of a Physical Security Perimeter as specified in Requirement R4. | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 40000000
CIP-006-3c (Manitoba) | 77660000000234 | R5. | 776600000002983 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity has not documented or has not implemented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more of the following monitoring methods: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. OR An unauthorized access attempt was not reviewed immediately and handled in accordance with CIP-008-3. | M5. The Responsible Entity shall make available documentation identifying the methods for monitoring physical access as specified in Requirement R5. | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 50000000
CIP-006-3c (Manitoba) | 77660000000234 | R6. | 776600000002980 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity has not implemented or has not documented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method, • Video Recording: Electronic capture of video images of sufficient quality to determine identity, or • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. OR The Responsible Entity has not recorded sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. | M6. The Responsible Entity shall make available documentation identifying the methods for logging physical access as specified in Requirement R6. | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 60000000
CIP-006-3c (Manitoba) | 77660000000234 | R7. | 776600000002977 | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A |  | N/A | M7. The Responsible Entity shall make available documentation to show retention of access logs as specified in Requirement R7. | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 70000000
CIP-006-3c (Manitoba) | 77660000000234 | R8. | 776600000002978 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity has not implemented a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. OR The implemented program does not include one or more of the requirements; R8.1, R8.2, and R8.3. | M8. The Responsible Entity shall make available documentation to show its implementation of a physical security system maintenance and testing program as specified in Requirement R8. | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 80000000
CIP-006-3c (Ontario) | 79780000234 | R1. | 79780002979 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | The Responsible Entity created a physical security plan but did not gain approval by a senior manager or delegate(s). OR The Responsible Entity created and implemented but did not maintain a physical security plan. | The Responsible Entity did not document, implement, and maintain a physical security plan. | M1. The Responsible Entity shall make available the physical security plan as specified in Requirement R1 and documentation of the implementation, review and updating of the plan. | 2011-05-19 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-006-3c (Ontario) | 79780000234 | R2. | 79780002984 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | A Cyber Asset that authorizes and/or logs access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, was not protected from unauthorized physical access. Perimeter access point such as electronic lock control mechanisms and badge readers was not afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3a Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. | M2. The Responsible Entity shall make available documentation that the physical access control systems are protected as specified in Requirement R2. | 2011-05-19 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-006-3c (Ontario) | 79780000234 | R3. | 79780002981 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | A Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) does not reside within an identified Physical Security Perimeter. | M3. The Responsible Entity shall make available documentation that the electronic access control systems are located within an identified Physical Security Perimeter as specified in Requirement R3. | 2011-05-19 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-006-3c (Ontario) | 79780000234 | R4. | 79780002982 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods:&lt;br/&gt;• Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another.&lt;br/&gt;• Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems.&lt;br/&gt;• Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station.&lt;br/&gt;• Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity has not documented or has not implemented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. | M4. The Responsible Entity shall make available documentation identifying the methods for controlling physical access to each access point of a Physical Security Perimeter as specified in Requirement R4. | 2011-05-19 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-006-3c (Ontario) | 79780000234 | R5. | 79780002983 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used:&lt;br/&gt;• Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response.&lt;br/&gt;• Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity has not documented or has not implemented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more of the following monitoring methods: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. OR An unauthorized access attempt was not reviewed immediately and handled in accordance with CIP-008-3. | M5. The Responsible Entity shall make available documentation identifying the methods for monitoring physical access as specified in Requirement R5. | 2011-05-19 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-006-3c (Ontario) | 79780000234 | R6. | 79780002980 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent:&lt;br/&gt;• Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method.&lt;br/&gt;• Video Recording: Electronic capture of video images of sufficient quality to determine identity.&lt;br/&gt;• Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity has not implemented or has not documented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method, • Video Recording: Electronic capture of video images of sufficient quality to determine identity, or • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. OR The Responsible Entity has not recorded sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. | M6. The Responsible Entity shall make available documentation identifying the methods for logging physical access as specified in Requirement R6. | 2011-05-19 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-006-3c (Ontario) | 79780000234 | R7. | 79780002977 | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A |  | N/A | M7. The Responsible Entity shall make available documentation to show retention of access logs as specified in Requirement R7. | 2011-05-19 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 70000000
CIP-006-3c (Ontario) | 79780000234 | R8. | 79780002978 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity has not implemented a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. OR The implemented program does not include one or more of the requirements; R8.1, R8.2, and R8.3. | M8. The Responsible Entity shall make available documentation to show its implementation of a physical security system maintenance and testing program as specified in Requirement R8. | 2011-05-19 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 80000000
CIP-006-3d | 310 | R1. | 4029 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-006-3d | 310 | R2. | 4034 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-006-3d | 310 | R3. | 4031 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-006-3d | 310 | R4. | 4032 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-006-3d | 310 | R5. | 4033 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-006-3d | 310 | R6. | 4030 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-006-3d | 310 | R7. | 4027 | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
CIP-006-3d | 310 | R8. | 4028 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
CIP-006-3d (Ontario) | 79780000310 | R1. | 79780004029 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-006-3d (Ontario) | 79780000310 | R2. | 79780004034 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-006-3d (Ontario) | 79780000310 | R3. | 79780004031 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-006-3d (Ontario) | 79780000310 | R4. | 79780004032 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods:&lt;br/&gt;• Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another.&lt;br/&gt;• Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems.&lt;br/&gt;• Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station.&lt;br/&gt;• Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-006-3d (Ontario) | 79780000310 | R5. | 79780004033 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used:&lt;br/&gt;• Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response.&lt;br/&gt;• Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-006-3d (Ontario) | 79780000310 | R6. | 79780004030 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent:&lt;br/&gt;• Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method.&lt;br/&gt;• Video Recording: Electronic capture of video images of sufficient quality to determine identity.&lt;br/&gt;• Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-006-3d (Ontario) | 79780000310 | R7. | 79780004027 | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 70000000
CIP-006-3d (Ontario) | 79780000310 | R8. | 79780004028 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 80000000
CIP-006-3 (Manitoba) | 77660000000226 | R1. | 776600000002800 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 10000000
CIP-006-3 (Manitoba) | 77660000000226 | R2. | 776600000002811 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 20000000
CIP-006-3 (Manitoba) | 77660000000226 | R3. | 776600000002814 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 30000000
CIP-006-3 (Manitoba) | 77660000000226 | R4. | 776600000002815 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 40000000
CIP-006-3 (Manitoba) | 77660000000226 | R5. | 776600000002816 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 50000000
CIP-006-3 (Manitoba) | 77660000000226 | R6. | 776600000002817 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 60000000
CIP-006-3 (Manitoba) | 77660000000226 | R7. | 776600000002818 | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 70000000
CIP-006-3 (Manitoba) | 77660000000226 | R8. | 776600000002819 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 80000000
CIP-006-3 (Ontario) | 79780000226 | R1. | 79780002800 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [9 empty] | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-006-3 (Ontario) | 79780000226 | R2. | 79780002811 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [9 empty] | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-006-3 (Ontario) | 79780000226 | R3. | 79780002814 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [9 empty] | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-006-3 (Ontario) | 79780000226 | R4. | 79780002815 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods:&lt;br/&gt;• Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another.&lt;br/&gt;• Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems.&lt;br/&gt;• Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station.&lt;br/&gt;• Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [9 empty] | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-006-3 (Ontario) | 79780000226 | R5. | 79780002816 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used:&lt;br/&gt;• Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response.&lt;br/&gt;• Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [9 empty] | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-006-3 (Ontario) | 79780000226 | R6. | 79780002817 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent:&lt;br/&gt;• Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method.&lt;br/&gt;• Video Recording: Electronic capture of video images of sufficient quality to determine identity.&lt;br/&gt;• Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [9 empty] | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-006-3 (Ontario) | 79780000226 | R7. | 79780002818 | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [9 empty] | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 70000000
CIP-006-3 (Ontario) | 79780000226 | R8. | 79780002819 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [9 empty] | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 80000000
CIP-006-4c | 252 | R1. | 3289 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | The Responsible Entity created a physical security plan but did not gain approval by a senior manager or delegate(s). OR The Responsible Entity created and implemented but did not maintain a physical security plan. | The Responsible Entity did not document, implement, and maintain a physical security plan. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-006-4c | 252 | R2. | 3300 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | A Cyber Asset that authorizes and/or logs access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers was provided with all but one (1) of the protective measures specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4 Requirements R2 and R3; Standard CIP-006-4 Requirements R4 and R5; Standard CIP-007-4; Standard CIP-008-4; and Standard CIP- 009-4. | A Cyber Asset that authorizes and/or logs access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers was provided with all but two (2) of the protective measures specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP005-4 Requirements R2 and R3; Standard CIP-006-4 Requirements R4 and R5; Standard CIP-007-4; Standard CIP-008-4; and Standard CIP009-4. | A Cyber Asset that authorizes and/or logs access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers was provided with all but three (3) of the protective measures specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4 Requirements R2 and R3; Standard CIP-006-4 Requirements R4 and R5; Standard CIP-007-4; Standard CIP-008-4; and Standard CIP-009-4. | A Cyber Asset that authorizes and/or logs access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, was not protected from unauthorized physical access. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-006-4c | 252 | R3. | 3303 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | A Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) does not reside within an identified Physical Security Perimeter. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-006-4c | 252 | R4. | 3304 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity has implemented but not documented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “mantrap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. | The Responsible Entity has documented but not implemented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. | The Responsible Entity has not documented or has not implemented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets.. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-006-4c | 252 | R5. | 3305 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-4. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity has implemented but not documented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twentyfour hours a day, seven days a week using one or more of the following monitoring methods: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. | The Responsible Entity has documented but not implemented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more of the following monitoring methods: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. | The Responsible Entity has not documented or has not implemented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more of the following monitoring methods: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. OR An unauthorized access attempt was not reviewed immediately and handled in accordance with CIP-008-4. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-006-4c | 252 | R6. | 3306 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity has implemented but not documented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method, • Video Recording: Electronic capture of video images of sufficient quality to determine identity, or • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4, and has provided logging that records sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. | The Responsible Entity has implemented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method, • Video Recording: Electronic capture of video images of sufficient quality to determine identity, or • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4, but has not provided logging that records sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week.. | The Responsible Entity has documented but not implemented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method, • Video Recording: Electronic capture of video images of sufficient quality to determine identity, or • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. | The Responsible Entity has not implemented or has not documented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method, • Video Recording: Electronic capture of video images of sufficient quality to determine identity, or • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-006-4c | 252 | R7. | 3307 | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity retained physical access logs for 75 or more calendar days, but for less than 90 calendar days. | The Responsible Entity retained physical access logs for 60 or more calendar days, but for less than 75 calendar days | The Responsible Entity retained physical access logs for 45 or more calendar days, but for less than 60 calendar days. | The Responsible Entity retained physical access logs for less than 45 calendar days. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
CIP-006-4c | 252 | R8. | 3308 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | The Responsible Entity has implemented a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly but the program does not include one of the Requirements R8.1, R8.2, and R8.3. | The Responsible Entity has implemented a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly but the program does not include two of the Requirements R8.1, R8.2, and R8.3. | The Responsible Entity has implemented a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly but the program does not include any of the Requirements R8.1, R8.2, and R8.3. | The Responsible Entity has not implemented a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
CIP-006-4c (Ontario) | 79780000252 | R1. | 79780003289 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | The Responsible Entity created a physical security plan but did not gain approval by a senior manager or delegate(s). OR The Responsible Entity created and implemented but did not maintain a physical security plan. | The Responsible Entity did not document, implement, and maintain a physical security plan. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-006-4c (Ontario) | 79780000252 | R2. | 79780003300 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | A Cyber Asset that authorizes and/or logs access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, was not protected from unauthorize |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-006-4c (Ontario) | 79780000252 | R3. | 79780003303 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | A Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) does not reside within an identified Physical Security Perimeter. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-006-4c (Ontario) | 79780000252 | R4. | 79780003304 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity has not documented or has not implemented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more of t |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-006-4c (Ontario) | 79780000252 | R5. | 79780003305 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-4. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity has not documented or has not implemented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more o |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-006-4c (Ontario) | 79780000252 | R6. | 79780003306 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity has not implemented or has not documented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equi |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-006-4c (Ontario) | 79780000252 | R7. | 79780003307 | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The responsible entity did not retain physical access logs for at least ninety calendar days. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 70000000
CIP-006-4c (Ontario) | 79780000252 | R8. | 79780003308 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity has not implemented a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. OR The implemented program does not include one or more of the requirements; R |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 80000000
CIP-006-4d | 311 | R1. | 4052 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-006-4d | 311 | R2. | 4057 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-006-4d | 311 | R3. | 4054 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-006-4d | 311 | R4. | 4055 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-006-4d | 311 | R5. | 4056 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-4. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-006-4d | 311 | R6. | 4053 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Long-Term Planning, Same-Day Operations | Low | [7 empty] | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-006-4d | 311 | R7. | 4050 | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Long-Term Planning, Same-Day Operations | Low | [7 empty] | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
CIP-006-4d | 311 | R8. | 4051 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Long-Term Planning, Same-Day Operations | Medium | [7 empty] | 2013-03-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
CIP-006-4d (Ontario) | 79780000311 | R1. | 79780004052 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | The Responsible Entity created a physical security plan but did not gain approval by a senior manager or delegate(s). OR The Responsible Entity created and implemented but did not maintain a physical security plan. | The Responsible Entity did not document, implement, and maintain a physical security plan. |  |  |  | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-006-4d (Ontario) | 79780000311 | R2. | 79780004057 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | A Cyber Asset that authorizes and/or logs access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, was not protected from unauthorize |  |  |  | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-006-4d (Ontario) | 79780000311 | R3. | 79780004054 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | A Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) does not reside within an identified Physical Security Perimeter. |  |  |  | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-006-4d (Ontario) | 79780000311 | R4. | 79780004055 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity has not documented or has not implemented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more of t |  |  |  | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-006-4d (Ontario) | 79780000311 | R5. | 79780004056 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-4. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity has not documented or has not implemented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more o |  |  |  | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-006-4d (Ontario) | 79780000311 | R6. | 79780004053 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Long-Term Planning, Same-Day Operations | Low | N/A | N/A | N/A | The Responsible Entity has not implemented or has not documented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equi | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. |  |  | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-006-4d (Ontario) | 79780000311 | R7. | 79780004050 | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Long-Term Planning, Same-Day Operations | Low | N/A | N/A | N/A | The responsible entity did not retain physical access logs for at least ninety calendar days. | M1.1. An example of evidence may include, but is not limited to, documentation that operational or procedural controls exist. |  |  | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 70000000
CIP-006-4d (Ontario) | 79780000311 | R8. | 79780004051 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Long-Term Planning, Same-Day Operations | Medium | N/A | N/A | N/A | The Responsible Entity has not implemented a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. OR The implemented program does not include one or more of the requirements; R | M1.2. An example of evidence may include, but is not limited to, language in the physical security plan that describes each Physical Security Perimeter and how unescorted physical access is controlled by one or more different methods and proof that unescorted physical access is restricted to only authorized individuals, such as a list of authorized individuals accompanied by access logs. |  |  | 2013-03-21 |  |  |  | NPCC-ON | [6 empty] | 80000000
CIP-006-4d (Saskatchewan) | 83750000000311 | R1. | 837500000004052 | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2012-02-09 |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 10000000
CIP-006-4d (Saskatchewan) | 83750000000311 | R2. | 837500000004057 | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2012-02-09 |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 20000000
CIP-006-4d (Saskatchewan) | 83750000000311 | R3. | 837500000004054 | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2012-02-09 |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 30000000
CIP-006-4d (Saskatchewan) | 83750000000311 | R4. | 837500000004055 | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2012-02-09 |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 40000000
CIP-006-4d (Saskatchewan) | 83750000000311 | R5. | 837500000004056 | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-4. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2012-02-09 |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 50000000
CIP-006-4d (Saskatchewan) | 83750000000311 | R6. | 837500000004053 | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Long-Term Planning, Same-Day Operations | Low | [5 empty] | 2012-02-09 |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 60000000
CIP-006-4d (Saskatchewan) | 83750000000311 | R7. | 837500000004050 | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Long-Term Planning, Same-Day Operations | Low | [5 empty] | 2012-02-09 |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 70000000
CIP-006-4d (Saskatchewan) | 83750000000311 | R8. | 837500000004051 | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Long-Term Planning, Same-Day Operations | Medium | [5 empty] | 2012-02-09 |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 80000000
CIP-006-5 | 350 | R1. | 4493 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-5 Table R1 – Physical Security Plan. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning, Same-Day Operations | Medium | The Responsible Entity has a process to log authorized physical entry into any Physical Security Perimeter with sufficient information to identify the individual and date and time of entry and identified deficiencies but did not assess or correct the deficiencies. (1.8) OR The Responsible Entity has a process to log authorized physical entry into any Physical Security Perimeter with sufficient information to identify the individual and date and time of entry but did not identify, assess, or correct the deficiencies. (1.8) OR The Responsible Entity has a process to retain physical access logs for 90 calendar days and identified deficiencies but did not assess or correct the deficiencies. (1.9) OR The Responsible Entity has a process to retain physical access logs for 90 calendar days but did not identify, assess, or correct the deficiencies. (1.9) | The Responsible Entity has a process to alert for unauthorized physical access to Physical Access Control Systems and identified deficiencies but did not assess or correct the deficiencies. (1.7) OR The Responsible Entity has a process to alert for unauthorized physical access to Physical Access Control Systems but did not identify, assess, or correct the deficiencies. (1.7) OR The Responsible Entity has a process communicate alerts within 15 minutes to identified personnel and identified deficiencies but did not assess or correct the deficiencies. (1.7) OR The Responsible Entity has a process communicate alerts within 15 minutes to identified personnel but did not identify, assess, or correct the deficiencies. (1.7) | The Responsible Entity has a process to alert for detected unauthorized access through a physical access point into a Physical security Perimeter and identified deficiencies but did not assess or correct the deficiencies. (1.5) OR The Responsible Entity has a process to alert for detected unauthorized access through a physical access point into a Physical security Perimeter but did not identify, assess, or correct deficiencies. (1.5) OR The Responsible Entity has a process to communicate alerts within 15 minutes to identified personnel and identified deficiencies but did not assess or correct the deficiencies. (1.5) OR The Responsible Entity has a process to communicate alerts within 15 minutes to identified personnel but did not identify, assess, or correct the deficiencies. (1.5) OR The Responsible Entity has a process to monitor for unauthorized physical access to a Physical Access Control Systems and identified deficiencies but did not assess or correct the deficiencies. (1.6) OR The Responsible Entity has a process to monitor for unauthorized physical access to a Physical Access Control Systems but did not identify, assess, or correct the deficiencies. (1.6) | The Responsible Entity did not document or implement operational or procedural controls to restrict physical access. (1.1) OR The Responsible Entity documented and implemented operational or procedural controls to restrict physical access and identified deficiencies but did not assess or correct the deficiencies. (1.1) OR The Responsible Entity documented and implemented operational or procedural controls to restrict physical access but did not identify, assess, or correct the deficiencies. (1.1) OR The Responsible Entity has documented and implemented physical access controls, but at least one control does not exist to restrict access to Applicable Systems. (1.2) OR The Responsible Entity has documented and implemented physical access controls, restricts access to Applicable Systems using at least one control, and identified deficiencies, but did not assess or correct the deficiencies. (1.2) OR The Responsible Entity has documented and implemented physical access controls, restricts access to Applicable Systems using at least one control, but did not identify, assess, or correct the deficiencies. (1.2) OR The Responsible Entity has documented and implemented physical access controls, but at least two different controls do not exist to restrict access to Applicable Systems. (1.3) OR The Responsible Entity documented and implemented operational or procedural controls, restricts access to Applicable Systems using at least two different controls, and identified deficiencies, but did not assess or correct the deficiencies. (1.3) OR The Responsible Entity documented and implemented operational or procedural controls, restricts access to Applicable Systems using at least two different controls, but did not identify, assess, or correct the deficiencies. (1.3) OR The Responsible Entity does not have a process to monitor for unauthorized access through a physical access point into a Physical Security Perimeter. (1.4) OR The Responsible Entity has a process to monitor for unauthorized access through a physical access point into a Physical Security Perimeter and identified deficiencies, but did not assess or correct the deficiencies. (1.4) OR The Responsible Entity has a process to monitor for unauthorized access through a physical access point into a Physical Security Perimeter, but did not identify, assess, or correct the deficiencies. (1.4) OR The Responsible Entity does not have a process to alert for detected unauthorized access through a physical access point into a Physical security Perimeter or to communicate such alerts within 15 minutes to identified personnel. (1.5) OR The Responsible Entity does not have a process to monitor each Physical Access Control System for unauthorized physical access to a Physical Access Control Systems. (1.6) OR The Responsible Entity does not have a process to alert for unauthorized physical access to Physical Access Control Systems or to communicate such alerts within 15 minutes to identified personnel (1.7) OR The Responsible Entity does not have a process to log authorized physical entry into each Physical Security Perimeter with sufficient information to identify the individual and date and time of entry. (1.8) OR The Responsible Entity does not have a process to retain physical access logs for 90 calendar days. (1.9) | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-5 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. |  |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-006-5 | 350 | R2. | 4494 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented visitor control programs that include each of the applicable requirement parts in CIP-006-5 Table R2 – Visitor Control Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | The Responsible Entity included a visitor control program that requires logging of each of the initial entry and last exit dates and times of the visitor, the visitor’s name, and the point of contact and identified deficiencies but did not assess or correct the deficiencies. (2.2) OR The Responsible Entity included a visitor control program that requires logging of the initial entry and last exit dates and times of the visitor, the visitor’s name, and the point of contact and but did not identify, assess, or correct the deficiencies. (2.2) OR The Responsible Entity included a visitor control program to retain visitor logs for at least ninety days and identified deficiencies but did not assess or correct the deficiencies. (2.3) OR The Responsible Entity included a visitor control program to retain visitor logs for at least ninety days but did not identify, assess, or correct the deficiencies. (2.3) | The Responsible Entity included a visitor control program that requires continuous escorted access of visitors within any Physical Security Perimeter, and identified deficiencies but did not assess or correct deficiencies. (2.1) OR The Responsible Entity included a visitor control program that requires continuous escorted access of visitors within any Physical Security Perimeter but did not identify, assess, or correct deficiencies. (2.1) | The Responsible Entity has failed to include or implement a visitor control program that requires continuous escorted access of visitors within any Physical Security Perimeter. (2.1) OR The Responsible Entity has failed to include or implement a visitor control program that requires logging of the initial entry and last exit dates and times of the visitor, the visitor’s name, and the point of contact. (2.2) OR The Responsible Entity failed to include or implement a visitor control program to retain visitor logs for at least ninety days. (2.3) | Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-5 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-006-5 | 350 | R3. | 4495 | Each Responsible Entity shall implement one or more documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-5 Table R3 – Maintenance and Testing Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Medium | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 24 calendar months but did complete required testing within 25 calendar months. (3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 25 calendar months but did complete required testing within 26 calendar months. (3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 26 calendar months but did complete required testing within 27 calendar months. (3.1) | The Responsible Entity has not documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter. (3.1) OR The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 27 calendar months. (3.1) | M3. Evidence must include each of the documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-5 Table R3 – Maintenance and Testing Program and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-006-5 (British Columbia) | 666700000010049 | R1. | 666700000010601 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-5 Table R1 – Physical Security Plan. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning, Same-Day Operations | Medium | The Responsible Entity has a process to log authorized physical entry into any Physical Security Perimeter with sufficient information to identify the individual and date and time of entry and identified deficiencies but did not assess or correct the deficiencies. (1.8) OR The Responsible Entity has a process to log authorized physical entry into any Physical Security Perimeter with sufficient information to identify the individual and date and time of entry but did not identify, assess, or correct the deficiencies. (1.8) OR The Responsible Entity has a process to retain physical access logs for 90 calendar days and identified deficiencies but did not assess or correct the deficiencies. (1.9) OR The Responsible Entity has a process to retain physical access logs for 90 calendar days but did not identify, assess, or correct the deficiencies. (1.9) | The Responsible Entity has a process to alert for unauthorized physical access to Physical Access Control Systems and identified deficiencies but did not assess or correct the deficiencies. (1.7) OR The Responsible Entity has a process to alert for unauthorized physical access to Physical Access Control Systems but did not identify, assess, or correct the deficiencies. (1.7) OR The Responsible Entity has a process communicate alerts within 15 minutes to identified personnel and identified deficiencies but did not assess or correct the deficiencies. (1.7) OR The Responsible Entity has a process communicate alerts within 15 minutes to identified personnel but did not identify, assess, or correct the deficiencies. (1.7) | The Responsible Entity has a process to alert for detected unauthorized access through a physical access point into a Physical security Perimeter and identified deficiencies but did not assess or correct the deficiencies. (1.5) OR The Responsible Entity has a process to alert for detected unauthorized access through a physical access point into a Physical security Perimeter but did not identify, assess, or correct deficiencies. (1.5) OR The Responsible Entity has a process to communicate alerts within 15 minutes to identified personnel and identified deficiencies but did not assess or correct the deficiencies. (1.5) OR The Responsible Entity has a process to communicate alerts within 15 minutes to identified personnel but did not identify, assess, or correct the deficiencies. (1.5) OR The Responsible Entity has a process to monitor for unauthorized physical access to a Physical Access Control Systems and identified deficiencies but did not assess or correct the deficiencies. (1.6) OR The Responsible Entity has a process to monitor for unauthorized physical access to a Physical Access Control Systems but did not identify, assess, or correct the deficiencies. (1.6) | The Responsible Entity did not document or implement operational or procedural controls to restrict physical access. (1.1) OR The Responsible Entity documented and implemented operational or procedural controls to restrict physical access and identified deficiencies but did not assess or correct the deficiencies. (1.1) OR The Responsible Entity documented and implemented operational or procedural controls to restrict physical access but did not identify, assess, or correct the deficiencies. (1.1) OR The Responsible Entity has documented and implemented physical access controls, but at least one control does not exist to restrict access to Applicable Systems. (1.2) OR The Responsible Entity has documented and implemented physical access controls, restricts access to Applicable Systems using at least one control, and identified deficiencies, but did not assess or correct the deficiencies. (1.2) OR The Responsible Entity has documented and implemented physical access controls, restricts access to Applicable Systems using at least one control, but did not identify, assess, or correct the deficiencies. (1.2) OR The Responsible Entity has documented and implemented physical access controls, but at least two different controls do not exist to restrict access to Applicable Systems. (1.3) OR The Responsible Entity documented and implemented operational or procedural controls, restricts access to Applicable Systems using at least two different controls, and identified deficiencies, but did not assess or correct the deficiencies. (1.3) OR The Responsible Entity documented and implemented operational or procedural controls, restricts access to Applicable Systems using at least two different controls, but did not identify, assess, or correct the deficiencies. (1.3) OR The Responsible Entity does not have a process to monitor for unauthorized access through a physical access point into a Physical Security Perimeter. (1.4) OR The Responsible Entity has a process to monitor for unauthorized access through a physical access point into a Physical Security Perimeter and identified deficiencies, but did not assess or correct the deficiencies. (1.4) OR The Responsible Entity has a process to monitor for unauthorized access through a physical access point into a Physical Security Perimeter, but did not identify, assess, or correct the deficiencies. (1.4) OR The Responsible Entity does not have a process to alert for detected unauthorized access through a physical access point into a Physical security Perimeter or to communicate such alerts within 15 minutes to identified personnel. (1.5) OR The Responsible Entity does not have a process to monitor each Physical Access Control System for unauthorized physical access to a Physical Access Control Systems. (1.6) OR The Responsible Entity does not have a process to alert for unauthorized physical access to Physical Access Control Systems or to communicate such alerts within 15 minutes to identified personnel (1.7) OR The Responsible Entity does not have a process to log authorized physical entry into each Physical Security Perimeter with sufficient information to identify the individual and date and time of entry. (1.8) OR The Responsible Entity does not have a process to retain physical access logs for 90 calendar days. (1.9) | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-5 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. |  |  | 2018-09-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | WECC-BC | [6 empty] | 10000000
CIP-006-5 (British Columbia) | 666700000010049 | R2. | 666700000010602 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented visitor control programs that include each of the applicable requirement parts in CIP-006-5 Table R2 – Visitor Control Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | The Responsible Entity included a visitor control program that requires logging of each of the initial entry and last exit dates and times of the visitor, the visitor’s name, and the point of contact and identified deficiencies but did not assess or correct the deficiencies. (2.2) OR The Responsible Entity included a visitor control program that requires logging of the initial entry and last exit dates and times of the visitor, the visitor’s name, and the point of contact and but did not identify, assess, or correct the deficiencies. (2.2) OR The Responsible Entity included a visitor control program to retain visitor logs for at least ninety days and identified deficiencies but did not assess or correct the deficiencies. (2.3) OR The Responsible Entity included a visitor control program to retain visitor logs for at least ninety days but did not identify, assess, or correct the deficiencies. (2.3) | The Responsible Entity included a visitor control program that requires continuous escorted access of visitors within any Physical Security Perimeter, and identified deficiencies but did not assess or correct deficiencies. (2.1) OR The Responsible Entity included a visitor control program that requires continuous escorted access of visitors within any Physical Security Perimeter but did not identify, assess, or correct deficiencies. (2.1) | The Responsible Entity has failed to include or implement a visitor control program that requires continuous escorted access of visitors within any Physical Security Perimeter. (2.1) OR The Responsible Entity has failed to include or implement a visitor control program that requires logging of the initial entry and last exit dates and times of the visitor, the visitor’s name, and the point of contact. (2.2) OR The Responsible Entity failed to include or implement a visitor control program to retain visitor logs for at least ninety days. (2.3) | Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-5 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2018-09-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | WECC-BC | [6 empty] | 20000000
CIP-006-5 (British Columbia) | 666700000010049 | R3. | 666700000010603 | Each Responsible Entity shall implement one or more documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-5 Table R3 – Maintenance and Testing Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Medium | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 24 calendar months but did complete required testing within 25 calendar months. (3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 25 calendar months but did complete required testing within 26 calendar months. (3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 26 calendar months but did complete required testing within 27 calendar months. (3.1) | The Responsible Entity has not documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter. (3.1) OR The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 27 calendar months. (3.1) | M3. Evidence must include each of the documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-5 Table R3 – Maintenance and Testing Program and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2018-09-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | WECC-BC | [6 empty] | 30000000
CIP-006-5 (Ontario) | 79780000350 | R1. | 79780004493 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-5 Table R1 – Physical Security Plan. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning, Same-Day Operations | Medium | The Responsible Entity has a process to log authorized physical entry into any Physical Security Perimeter with sufficient information to identify the individual and date and time of entry and identified deficiencies but did not assess or correct the deficiencies. (1.8) OR The Responsible Entity has a process to log authorized physical entry into any Physical Security Perimeter with sufficient information to identify the individual and date and time of entry but did not identify, assess, or correct the deficiencies. (1.8) OR The Responsible Entity has a process to retain physical access logs for 90 calendar days and identified deficiencies but did not assess or correct the deficiencies. (1.9) OR The Responsible Entity has a process to retain physical access logs for 90 calendar days but did not identify, assess, or correct the deficiencies. (1.9) | The Responsible Entity has a process to alert for unauthorized physical access to Physical Access Control Systems and identified deficiencies but did not assess or correct the deficiencies. (1.7) OR The Responsible Entity has a process to alert for unauthorized physical access to Physical Access Control Systems but did not identify, assess, or correct the deficiencies. (1.7) OR The Responsible Entity has a process communicate alerts within 15 minutes to identified personnel and identified deficiencies but did not assess or correct the deficiencies. (1.7) OR The Responsible Entity has a process communicate alerts within 15 minutes to identified personnel but did not identify, assess, or correct the deficiencies. (1.7) | The Responsible Entity has a process to alert for detected unauthorized access through a physical access point into a Physical security Perimeter and identified deficiencies but did not assess or correct the deficiencies. (1.5) OR The Responsible Entity has a process to alert for detected unauthorized access through a physical access point into a Physical security Perimeter but did not identify, assess, or correct deficiencies. (1.5) OR The Responsible Entity has a process to communicate alerts within 15 minutes to identified personnel and identified deficiencies but did not assess or correct the deficiencies. (1.5) OR The Responsible Entity has a process to communicate alerts within 15 minutes to identified personnel but did not identify, assess, or correct the deficiencies. (1.5) OR The Responsible Entity has a process to monitor for unauthorized physical access to a Physical Access Control Systems and identified deficiencies but did not assess or correct the deficiencies. (1.6) OR The Responsible Entity has a process to monitor for unauthorized physical access to a Physical Access Control Systems but did not identify, assess, or correct the deficiencies. (1.6) | The Responsible Entity did not document or implement operational or procedural controls to restrict physical access. (1.1) OR The Responsible Entity documented and implemented operational or procedural controls to restrict physical access and identified deficiencies but did not assess or correct the deficiencies. (1.1) OR The Responsible Entity documented and implemented operational or procedural controls to restrict physical access but did not identify, assess, or correct the deficiencies. (1.1) OR The Responsible Entity has documented and implemented physical access controls, but at least one control does not exist to restrict access to Applicable Systems. (1.2) OR The Responsible Entity has documented and implemented physical access controls, restricts access to Applicable Systems using at least one control, and identified deficiencies, but did not assess or correct the deficiencies. (1.2) OR The Responsible Entity has documented and implemented physical access controls, restricts access to Applicable Systems using at least one control, but did not identify, assess, or correct the deficiencies. (1.2) OR The Responsible Entity has documented and implemented physical access controls, but at least two different controls do not exist to restrict access to Applicable Systems. (1.3) OR The Responsible Entity documented and implemented operational or procedural controls, restricts access to Applicable Systems using at least two different controls, and identified deficiencies, but did not assess or correct the deficiencies. (1.3) OR The Responsible Entity documented and implemented operational or procedural controls, restricts access to Applicable Systems using at least two different controls, but did not identify, assess, or correct the deficiencies. (1.3) OR The Responsible Entity does not have a process to monitor for unauthorized access through a physical access point into a Physical Security Perimeter. (1.4) OR The Responsible Entity has a process to monitor for unauthorized access through a physical access point into a Physical Security Perimeter and identified deficiencies, but did not assess or correct the deficiencies. (1.4) OR The Responsible Entity has a process to monitor for unauthorized access through a physical access point into a Physical Security Perimeter, but did not identify, assess, or correct the deficiencies. (1.4) OR The Responsible Entity does not have a process to alert for detected unauthorized access through a physical access point into a Physical security Perimeter or to communicate such alerts within 15 minutes to identified personnel. (1.5) OR The Responsible Entity does not have a process to monitor each Physical Access Control System for unauthorized physical access to a Physical Access Control Systems. (1.6) OR The Responsible Entity does not have a process to alert for unauthorized physical access to Physical Access Control Systems or to communicate such alerts within 15 minutes to identified personnel (1.7) OR The Responsible Entity does not have a process to log authorized physical entry into each Physical Security Perimeter with sufficient information to identify the individual and date and time of entry. (1.8) OR The Responsible Entity does not have a process to retain physical access logs for 90 calendar days. (1.9) | M1.6. An example of evidence may include, but is not limited to, documentation of controls that monitor for unauthorized physical access to a PACS. |  |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | NPCC-ON | [6 empty] | 10000000
CIP-006-5 (Ontario) | 79780000350 | R2. | 79780004494 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented visitor control programs that include each of the applicable requirement parts in CIP-006-5 Table R2 – Visitor Control Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Medium | N/A | The Responsible Entity included a visitor control program that requires logging of each of the initial entry and last exit dates and times of the visitor, the visitor’s name, and the point of contact and identified deficiencies but did not assess or correct the deficiencies. (2.2) OR The Responsible Entity included a visitor control program that requires logging of the initial entry and last exit dates and times of the visitor, the visitor’s name, and the point of contact and but did not identify, assess, or correct the deficiencies. (2.2) OR The Responsible Entity included a visitor control program to retain visitor logs for at least ninety days and identified deficiencies but did not assess or correct the deficiencies. (2.3) OR The Responsible Entity included a visitor control program to retain visitor logs for at least ninety days but did not identify, assess, or correct the deficiencies. (2.3) | The Responsible Entity included a visitor control program that requires continuous escorted access of visitors within any Physical Security Perimeter, and identified deficiencies but did not assess or correct deficiencies. (2.1) OR The Responsible Entity included a visitor control program that requires continuous escorted access of visitors within any Physical Security Perimeter but did not identify, assess, or correct deficiencies. (2.1) | The Responsible Entity has failed to include or implement a visitor control program that requires continuous escorted access of visitors within any Physical Security Perimeter. (2.1) OR The Responsible Entity has failed to include or implement a visitor control program that requires logging of the initial entry and last exit dates and times of the visitor, the visitor’s name, and the point of contact. (2.2) OR The Responsible Entity failed to include or implement a visitor control program to retain visitor logs for at least ninety days. (2.3) | M.3.1. An example of evidence may include, but is not limited to, a maintenance and testing program that provides for testing each Physical Access Control System and locally mounted hardware or devices associated with each applicable Physical Security Perimeter at least once every 24 calendar months and additional evidence to demonstrate that this testing was done, such as dated maintenance records, or other documentation showing testing and maintenance has been performed on each applicable device or system at least once every 24 calendar months. |  |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | NPCC-ON | [6 empty] | 20000000
CIP-006-5 (Ontario) | 79780000350 | R3. | 79780004495 | Each Responsible Entity shall implement one or more documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-5 Table R3 – Maintenance and Testing Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Low | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 24 calendar months but did complete required testing within 25 calendar months. (3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 25 calendar months but did complete required testing within 26 calendar months. (3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 26 calendar months but did complete required testing within 27 calendar months. (3.1) | The Responsible Entity has not documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter. (3.1) OR The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 27 calendar months. (3.1) | M3. Evidence must include each of the documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-5 Table R3 – Maintenance and Testing Program and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | NPCC-ON | [6 empty] | 30000000
CIP-006-5 (Saskatchewan) | 83750000000350 | R1. | 837500000004493 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-5 Table R1 – Physical Security Plan. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning, Same-Day Operations | Medium | The Responsible Entity has a process to log authorized physical entry into any Physical Security Perimeter with sufficient information to identify the individual and date and time of entry and identified deficiencies but did not assess or correct the deficiencies. (1.8) OR The Responsible Entity has a process to log authorized physical entry into any Physical Security Perimeter with sufficient information to identify the individual and date and time of entry but did not identify, assess, or correct the deficiencies. (1.8) OR The Responsible Entity has a process to retain physical access logs for 90 calendar days and identified deficiencies but did not assess or correct the deficiencies. (1.9) OR The Responsible Entity has a process to retain physical access logs for 90 calendar days but did not identify, assess, or correct the deficiencies. (1.9) | The Responsible Entity has a process to alert for unauthorized physical access to Physical Access Control Systems and identified deficiencies but did not assess or correct the deficiencies. (1.7) OR The Responsible Entity has a process to alert for unauthorized physical access to Physical Access Control Systems but did not identify, assess, or correct the deficiencies. (1.7) OR The Responsible Entity has a process communicate alerts within 15 minutes to identified personnel and identified deficiencies but did not assess or correct the deficiencies. (1.7) OR The Responsible Entity has a process communicate alerts within 15 minutes to identified personnel but did not identify, assess, or correct the deficiencies. (1.7) | The Responsible Entity has a process to alert for detected unauthorized access through a physical access point into a Physical security Perimeter and identified deficiencies but did not assess or correct the deficiencies. (1.5) OR The Responsible Entity has a process to alert for detected unauthorized access through a physical access point into a Physical security Perimeter but did not identify, assess, or correct deficiencies. (1.5) OR The Responsible Entity has a process to communicate alerts within 15 minutes to identified personnel and identified deficiencies but did not assess or correct the deficiencies. (1.5) OR The Responsible Entity has a process to communicate alerts within 15 minutes to identified personnel but did not identify, assess, or correct the deficiencies. (1.5) OR The Responsible Entity has a process to monitor for unauthorized physical access to a Physical Access Control Systems and identified deficiencies but did not assess or correct the deficiencies. (1.6) OR The Responsible Entity has a process to monitor for unauthorized physical access to a Physical Access Control Systems but did not identify, assess, or correct the deficiencies. (1.6) | The Responsible Entity did not document or implement operational or procedural controls to restrict physical access. (1.1) OR The Responsible Entity documented and implemented operational or procedural controls to restrict physical access and identified deficiencies but did not assess or correct the deficiencies. (1.1) OR The Responsible Entity documented and implemented operational or procedural controls to restrict physical access but did not identify, assess, or correct the deficiencies. (1.1) OR The Responsible Entity has documented and implemented physical access controls, but at least one control does not exist to restrict access to Applicable Systems. (1.2) OR The Responsible Entity has documented and implemented physical access controls, restricts access to Applicable Systems using at least one control, and identified deficiencies, but did not assess or correct the deficiencies. (1.2) OR The Responsible Entity has documented and implemented physical access controls, restricts access to Applicable Systems using at least one control, but did not identify, assess, or correct the deficiencies. (1.2) OR The Responsible Entity has documented and implemented physical access controls, but at least two different controls do not exist to restrict access to Applicable Systems. (1.3) OR The Responsible Entity documented and implemented operational or procedural controls, restricts access to Applicable Systems using at least two different controls, and identified deficiencies, but did not assess or correct the deficiencies. (1.3) OR The Responsible Entity documented and implemented operational or procedural controls, restricts access to Applicable Systems using at least two different controls, but did not identify, assess, or correct the deficiencies. (1.3) OR The Responsible Entity does not have a process to monitor for unauthorized access through a physical access point into a Physical Security Perimeter. (1.4) OR The Responsible Entity has a process to monitor for unauthorized access through a physical access point into a Physical Security Perimeter and identified deficiencies, but did not assess or correct the deficiencies. (1.4) OR The Responsible Entity has a process to monitor for unauthorized access through a physical access point into a Physical Security Perimeter, but did not identify, assess, or correct the deficiencies. (1.4) OR The Responsible Entity does not have a process to alert for detected unauthorized access through a physical access point into a Physical security Perimeter or to communicate such alerts within 15 minutes to identified personnel. (1.5) OR The Responsible Entity does not have a process to monitor each Physical Access Control System for unauthorized physical access to a Physical Access Control Systems. (1.6) OR The Responsible Entity does not have a process to alert for unauthorized physical access to Physical Access Control Systems or to communicate such alerts within 15 minutes to identified personnel (1.7) OR The Responsible Entity does not have a process to log authorized physical entry into each Physical Security Perimeter with sufficient information to identify the individual and date and time of entry. (1.8) OR The Responsible Entity does not have a process to retain physical access logs for 90 calendar days. (1.9) | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-5 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. |  |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | MRO-SK | [6 empty] | 10000000
CIP-006-5 (Saskatchewan) | 83750000000350 | R2. | 837500000004494 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented visitor control programs that include each of the applicable requirement parts in CIP-006-5 Table R2 – Visitor Control Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | The Responsible Entity included a visitor control program that requires logging of each of the initial entry and last exit dates and times of the visitor, the visitor’s name, and the point of contact and identified deficiencies but did not assess or correct the deficiencies. (2.2) OR The Responsible Entity included a visitor control program that requires logging of the initial entry and last exit dates and times of the visitor, the visitor’s name, and the point of contact and but did not identify, assess, or correct the deficiencies. (2.2) OR The Responsible Entity included a visitor control program to retain visitor logs for at least ninety days and identified deficiencies but did not assess or correct the deficiencies. (2.3) OR The Responsible Entity included a visitor control program to retain visitor logs for at least ninety days but did not identify, assess, or correct the deficiencies. (2.3) | The Responsible Entity included a visitor control program that requires continuous escorted access of visitors within any Physical Security Perimeter, and identified deficiencies but did not assess or correct deficiencies. (2.1) OR The Responsible Entity included a visitor control program that requires continuous escorted access of visitors within any Physical Security Perimeter but did not identify, assess, or correct deficiencies. (2.1) | The Responsible Entity has failed to include or implement a visitor control program that requires continuous escorted access of visitors within any Physical Security Perimeter. (2.1) OR The Responsible Entity has failed to include or implement a visitor control program that requires logging of the initial entry and last exit dates and times of the visitor, the visitor’s name, and the point of contact. (2.2) OR The Responsible Entity failed to include or implement a visitor control program to retain visitor logs for at least ninety days. (2.3) | Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-5 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | MRO-SK | [6 empty] | 20000000
CIP-006-5 (Saskatchewan) | 83750000000350 | R3. | 837500000004495 | Each Responsible Entity shall implement one or more documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-5 Table R3 – Maintenance and Testing Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Medium | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 24 calendar months but did complete required testing within 25 calendar months. (3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 25 calendar months but did complete required testing within 26 calendar months. (3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 26 calendar months but did complete required testing within 27 calendar months. (3.1) | The Responsible Entity has not documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter. (3.1) OR The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 27 calendar months. (3.1) | M3. Evidence must include each of the documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-5 Table R3 – Maintenance and Testing Program and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | MRO-SK | [6 empty] | 30000000
CIP-006-6 | 516 | R1. | 6104 | Each Responsible Entity shall implement one or more documented physical security plan(s) that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning, Same-Day Operations | Medium | N/A | N/A | N/A | The Responsible Entity did not document or implement physical security plans. (R1) OR The Responsible Entity did not document or implement operational or procedural controls to restrict physical access. (1.1) OR The Responsible Entity has documented and implemented physical access controls, but at least one control does not exist to restrict access to Applicable Systems. (1.2) OR The Responsible Entity has documented and implemented physical access controls, but at least two different controls do not exist to restrict access to Applicable Systems. (1.3) OR The Responsible Entity does not have a process to monitor for unauthorized access through a physical access point into a Physical Security Perimeter. (1.4) OR The Responsible Entity does not have a process to alert for detected unauthorized access through a physical access point into a Physical Security Perimeter or to communicate such alerts within 15 minutes to identified personnel. (1.5) OR The Responsible Entity does not have a process to monitor each Physical Access Control System for unauthorized physical access to a Physical Access Control Systems. (1.6) OR The Responsible Entity does not have a process to alert for unauthorized physical access to Physical Access Control Systems or to communicate such alerts within 15 minutes to identified personnel. (1.7) OR The Responsible Entity does not have a process to log authorized physical entry into each Physical Security Perimeter with sufficient information to identify the individual and date and time of entry. (1.8) OR The Responsible Entity does not have a process to retain physical access logs for 90 calendar days. (1.9) OR The Responsible Entity did not document or implement physical access restrictions, encryption, monitoring or equally effective logical protections for cabling and other nonprogrammable communication components used for connection between applicable Cyber Assets within the same Electronic Security Perimeter in those instances when such cabling and components are located outside of a Physical Security Perimeter. (1.10) | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | 2016-07-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-006-6 | 516 | R2. | 6105 | Each Responsible Entity shall implement one or more documented visitor control program(s) that include each of the applicable requirement parts in CIP-006-6 Table R2 – Visitor Control Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | N/A | N/A | The Responsible Entity has failed to include or implement a visitor control program that requires continuous escorted access of visitors within any Physical Security Perimeter. (2.1) OR The Responsible Entity has failed to include or implement a visitor control program that requires logging of the initial entry and last exit dates and times of the visitor, the visitor’s name, and the point of contact. (2.2) OR The Responsible Entity failed to include or implement a visitor control program to retain visitor logs for at least ninety days. (2.3) | M2. Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-6 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-006-6 | 516 | R3. | 6106 | Each Responsible Entity shall implement one or more documented Physical Access Control System maintenance and testing program(s) that collectively include each of the applicable requirement parts in CIP-006-6 Table R3 – Maintenance and Testing Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Medium | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 24 calendar months but did complete required testing within 25 calendar months. (3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 25 calendar months but did complete required testing within 26 calendar months. (3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 26 calendar months but did complete required testing within 27 calendar months. (3.1) | The Responsible Entity did not document or implement a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter. (3.1) OR The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 27 calendar months. (3.1) | M3. Evidence must include each of the documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-6 Table R3 – Maintenance and Testing Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-006-6 (British Columbia) | 666700000010050 | R1. | 666700000010604 | Each Responsible Entity shall implement one or more documented physical security plan(s) that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning, Same-Day Operations | Medium | N/A | N/A | N/A | The Responsible Entity did not document or implement physical security plans. (R1) OR The Responsible Entity did not document or implement operational or procedural controls to restrict physical access. (1.1) OR The Responsible Entity has documented and implemented physical access controls, but at least one control does not exist to restrict access to Applicable Systems. (1.2) OR The Responsible Entity has documented and implemented physical access controls, but at least two different controls do not exist to restrict access to Applicable Systems. (1.3) OR The Responsible Entity does not have a process to monitor for unauthorized access through a physical access point into a Physical Security Perimeter. (1.4) OR The Responsible Entity does not have a process to alert for detected unauthorized access through a physical access point into a Physical Security Perimeter or to communicate such alerts within 15 minutes to identified personnel. (1.5) OR The Responsible Entity does not have a process to monitor each Physical Access Control System for unauthorized physical access to a Physical Access Control Systems. (1.6) OR The Responsible Entity does not have a process to alert for unauthorized physical access to Physical Access Control Systems or to communicate such alerts within 15 minutes to identified personnel. (1.7) OR The Responsible Entity does not have a process to log authorized physical entry into each Physical Security Perimeter with sufficient information to identify the individual and date and time of entry. (1.8) OR The Responsible Entity does not have a process to retain physical access logs for 90 calendar days. (1.9) OR The Responsible Entity did not document or implement physical access restrictions, encryption, monitoring or equally effective logical protections for cabling and other nonprogrammable communication components used for connection between applicable Cyber Assets within the same Electronic Security Perimeter in those instances when such cabling and components are located outside of a Physical Security Perimeter. (1.10) | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | 2018-10-01 | [5 empty] | WECC-BC | [6 empty] | 10000000
CIP-006-6 (British Columbia) | 666700000010050 | R2. | 666700000010605 | Each Responsible Entity shall implement one or more documented visitor control program(s) that include each of the applicable requirement parts in CIP-006-6 Table R2 – Visitor Control Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | N/A | N/A | The Responsible Entity has failed to include or implement a visitor control program that requires continuous escorted access of visitors within any Physical Security Perimeter. (2.1) OR The Responsible Entity has failed to include or implement a visitor control program that requires logging of the initial entry and last exit dates and times of the visitor, the visitor’s name, and the point of contact. (2.2) OR The Responsible Entity failed to include or implement a visitor control program to retain visitor logs for at least ninety days. (2.3) | M2. Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-6 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2018-10-01 | [5 empty] | WECC-BC | [6 empty] | 20000000
CIP-006-6 (British Columbia) | 666700000010050 | R3. | 666700000010606 | Each Responsible Entity shall implement one or more documented Physical Access Control System maintenance and testing program(s) that collectively include each of the applicable requirement parts in CIP-006-6 Table R3 – Maintenance and Testing Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Medium | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 24 calendar months but did complete required testing within 25 calendar months. (3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 25 calendar months but did complete required testing within 26 calendar months. (3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 26 calendar months but did complete required testing within 27 calendar months. (3.1) | The Responsible Entity did not document or implement a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter. (3.1) OR The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 27 calendar months. (3.1) | M3. Evidence must include each of the documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-6 Table R3 – Maintenance and Testing Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2018-10-01 | [5 empty] | WECC-BC | [6 empty] | 30000000
CIP-006-6 (Manitoba) | 77660000000516 | R1. | 776600000006104 | Each Responsible Entity shall implement one or more documented physical security plan(s) that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning, Same-Day Operations | Medium | N/A | N/A | N/A | The Responsible Entity did not document or implement physical security plans. (R1) OR The Responsible Entity did not document or implement operational or procedural controls to restrict physical access. (1.1) OR The Responsible Entity has documented and implemented physical access controls, but at least one control does not exist to restrict access to Applicable Systems. (1.2) OR The Responsible Entity has documented and implemented physical access controls, but at least two different controls do not exist to restrict access to Applicable Systems. (1.3) OR The Responsible Entity does not have a process to monitor for unauthorized access through a physical access point into a Physical Security Perimeter. (1.4) OR The Responsible Entity does not have a process to alert for detected unauthorized access through a physical access point into a Physical Security Perimeter or to communicate such alerts within 15 minutes to identified personnel. (1.5) OR The Responsible Entity does not have a process to monitor each Physical Access Control System for unauthorized physical access to a Physical Access Control Systems. (1.6) OR The Responsible Entity does not have a process to alert for unauthorized physical access to Physical Access Control Systems or to communicate such alerts within 15 minutes to identified personnel. (1.7) OR The Responsible Entity does not have a process to log authorized physical entry into each Physical Security Perimeter with sufficient information to identify the individual and date and time of entry. (1.8) OR The Responsible Entity does not have a process to retain physical access logs for 90 calendar days. (1.9) OR The Responsible Entity did not document or implement physical access restrictions, encryption, monitoring or equally effective logical protections for cabling and other nonprogrammable communication components used for connection between applicable Cyber Assets within the same Electronic Security Perimeter in those instances when such cabling and components are located outside of a Physical Security Perimeter. (1.10) | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | 2017-07-01 | [5 empty] | MRO-MB | [6 empty] | 10000000
CIP-006-6 (Manitoba) | 77660000000516 | R2. | 776600000006105 | Each Responsible Entity shall implement one or more documented visitor control program(s) that include each of the applicable requirement parts in CIP-006-6 Table R2 – Visitor Control Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | N/A | N/A | The Responsible Entity has failed to include or implement a visitor control program that requires continuous escorted access of visitors within any Physical Security Perimeter. (2.1) OR The Responsible Entity has failed to include or implement a visitor control program that requires logging of the initial entry and last exit dates and times of the visitor, the visitor’s name, and the point of contact. (2.2) OR The Responsible Entity failed to include or implement a visitor control program to retain visitor logs for at least ninety days. (2.3) | M2. Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-6 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2017-07-01 | [5 empty] | MRO-MB | [6 empty] | 20000000
CIP-006-6 (Manitoba) | 77660000000516 | R3. | 776600000006106 | Each Responsible Entity shall implement one or more documented Physical Access Control System maintenance and testing program(s) that collectively include each of the applicable requirement parts in CIP-006-6 Table R3 – Maintenance and Testing Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Medium | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 24 calendar months but did complete required testing within 25 calendar months. (3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 25 calendar months but did complete required testing within 26 calendar months. (3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 26 calendar months but did complete required testing within 27 calendar months. (3.1) | The Responsible Entity did not document or implement a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter. (3.1) OR The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 27 calendar months. (3.1) | M3. Evidence must include each of the documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-6 Table R3 – Maintenance and Testing Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2017-07-01 | [5 empty] | MRO-MB | [6 empty] | 30000000
CIP-006-6 (Nova Scotia) | 78830000000516 | R1. | 788300000006104 | Each Responsible Entity shall implement one or more documented physical security plan(s) that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning, Same-Day Operations | Medium | N/A | N/A | N/A | The Responsible Entity did not document or implement physical security plans. (R1) OR The Responsible Entity did not document or implement operational or procedural controls to restrict physical access. (1.1) OR The Responsible Entity has documented and implemented physical access controls, but at least one control does not exist to restrict access to Applicable Systems. (1.2) OR The Responsible Entity has documented and implemented physical access controls, but at least two different controls do not exist to restrict access to Applicable Systems. (1.3) OR The Responsible Entity does not have a process to monitor for unauthorized access through a physical access point into a Physical Security Perimeter. (1.4) OR The Responsible Entity does not have a process to alert for detected unauthorized access through a physical access point into a Physical Security Perimeter or to communicate such alerts within 15 minutes to identified personnel. (1.5) OR The Responsible Entity does not have a process to monitor each Physical Access Control System for unauthorized physical access to a Physical Access Control Systems. (1.6) OR The Responsible Entity does not have a process to alert for unauthorized physical access to Physical Access Control Systems or to communicate such alerts within 15 minutes to identified personnel. (1.7) OR The Responsible Entity does not have a process to log authorized physical entry into each Physical Security Perimeter with sufficient information to identify the individual and date and time of entry. (1.8) OR The Responsible Entity does not have a process to retain physical access logs for 90 calendar days. (1.9) OR The Responsible Entity did not document or implement physical access restrictions, encryption, monitoring or equally effective logical protections for cabling and other nonprogrammable communication components used for connection between applicable Cyber Assets within the same Electronic Security Perimeter in those instances when such cabling and components are located outside of a Physical Security Perimeter. (1.10) | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | 2017-01-01 | [5 empty] | NPCC-NS | [6 empty] | 10000000
CIP-006-6 (Ontario) | 79780000516 | R1. | 79780006104 | Each Responsible Entity shall implement one or more documented physical security plan(s) that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning, Same-Day Operations | Medium | N/A | N/A | N/A | The Responsible Entity did not document or implement physical security plans. (R1) OR The Responsible Entity did not document or implement operational or procedural controls to restrict physical access. (1.1) OR The Responsible Entity has documented and implemented physical access controls, but at least one control does not exist to restrict access to Applicable Systems. (1.2) OR The Responsible Entity has documented and implemented physical access controls, but at least two different controls do not exist to restrict access to Applicable Systems. (1.3) OR The Responsible Entity does not have a process to monitor for unauthorized access through a physical access point into a Physical Security Perimeter. (1.4) OR The Responsible Entity does not have a process to alert for detected unauthorized access through a physical access point into a Physical Security Perimeter or to communicate such alerts within 15 minutes to identified personnel. (1.5) OR The Responsible Entity does not have a process to monitor each Physical Access Control System for unauthorized physical access to a Physical Access Control Systems. (1.6) OR The Responsible Entity does not have a process to alert for unauthorized physical access to Physical Access Control Systems or to communicate such alerts within 15 minutes to identified personnel. (1.7) OR The Responsible Entity does not have a process to log authorized physical entry into each Physical Security Perimeter with sufficient information to identify the individual and date and time of entry. (1.8) OR The Responsible Entity does not have a process to retain physical access logs for 90 calendar days. (1.9) OR The Responsible Entity did not document or implement physical access restrictions, encryption, monitoring or equally effective logical protections for cabling and other nonprogrammable communication components used for connection between applicable Cyber Assets within the same Electronic Security Perimeter in those instances when such cabling and components are located outside of a Physical Security Perimeter. (1.10) | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | 2016-07-01 | [5 empty] | NPCC-ON | [6 empty] | 10000000
CIP-006-6 (Ontario) | 79780000516 | R2. | 79780006105 | Each Responsible Entity shall implement one or more documented visitor control program(s) that include each of the applicable requirement parts in CIP-006-6 Table R2 – Visitor Control Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | N/A | N/A | The Responsible Entity has failed to include or implement a visitor control program that requires continuous escorted access of visitors within any Physical Security Perimeter. (2.1) OR The Responsible Entity has failed to include or implement a visitor control program that requires logging of the initial entry and last exit dates and times of the visitor, the visitor’s name, and the point of contact. (2.2) OR The Responsible Entity failed to include or implement a visitor control program to retain visitor logs for at least ninety days. (2.3) | M2. Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-6 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 | [5 empty] | NPCC-ON | [6 empty] | 20000000
CIP-006-6 (Ontario) | 79780000516 | R3. | 79780006106 | Each Responsible Entity shall implement one or more documented Physical Access Control System maintenance and testing program(s) that collectively include each of the applicable requirement parts in CIP-006-6 Table R3 – Maintenance and Testing Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Medium | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 24 calendar months but did complete required testing within 25 calendar months. (3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 25 calendar months but did complete required testing within 26 calendar months. (3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 26 calendar months but did complete required testing within 27 calendar months. (3.1) | The Responsible Entity did not document or implement a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter. (3.1) OR The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 27 calendar months. (3.1) | M3. Evidence must include each of the documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-6 Table R3 – Maintenance and Testing Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 | [5 empty] | NPCC-ON | [6 empty] | 30000000
CIP-006-6 (Saskatchewan) | 83750000000516 | R1. | 837500000006104 | Each Responsible Entity shall implement one or more documented physical security plan(s) that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning, Same-Day Operations | Medium | N/A | N/A | N/A | The Responsible Entity did not document or implement physical security plans. (R1) OR The Responsible Entity did not document or implement operational or procedural controls to restrict physical access. (1.1) OR The Responsible Entity has documented and implemented physical access controls, but at least one control does not exist to restrict access to Applicable Systems. (1.2) OR The Responsible Entity has documented and implemented physical access controls, but at least two different controls do not exist to restrict access to Applicable Systems. (1.3) OR The Responsible Entity does not have a process to monitor for unauthorized access through a physical access point into a Physical Security Perimeter. (1.4) OR The Responsible Entity does not have a process to alert for detected unauthorized access through a physical access point into a Physical Security Perimeter or to communicate such alerts within 15 minutes to identified personnel. (1.5) OR The Responsible Entity does not have a process to monitor each Physical Access Control System for unauthorized physical access to a Physical Access Control Systems. (1.6) OR The Responsible Entity does not have a process to alert for unauthorized physical access to Physical Access Control Systems or to communicate such alerts within 15 minutes to identified personnel. (1.7) OR The Responsible Entity does not have a process to log authorized physical entry into each Physical Security Perimeter with sufficient information to identify the individual and date and time of entry. (1.8) OR The Responsible Entity does not have a process to retain physical access logs for 90 calendar days. (1.9) OR The Responsible Entity did not document or implement physical access restrictions, encryption, monitoring or equally effective logical protections for cabling and other nonprogrammable communication components used for connection between applicable Cyber Assets within the same Electronic Security Perimeter in those instances when such cabling and components are located outside of a Physical Security Perimeter. (1.10) | M1. Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | 2016-07-01 | [5 empty] | MRO-SK | [6 empty] | 10000000
CIP-006-6 (Saskatchewan) | 83750000000516 | R2. | 837500000006105 | Each Responsible Entity shall implement one or more documented visitor control program(s) that include each of the applicable requirement parts in CIP-006-6 Table R2 – Visitor Control Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | N/A | N/A | The Responsible Entity has failed to include or implement a visitor control program that requires continuous escorted access of visitors within any Physical Security Perimeter. (2.1) OR The Responsible Entity has failed to include or implement a visitor control program that requires logging of the initial entry and last exit dates and times of the visitor, the visitor’s name, and the point of contact. (2.2) OR The Responsible Entity failed to include or implement a visitor control program to retain visitor logs for at least ninety days. (2.3) | M2. Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-6 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 | [5 empty] | MRO-SK | [6 empty] | 20000000
CIP-006-6 (Saskatchewan) | 83750000000516 | R3. | 837500000006106 | Each Responsible Entity shall implement one or more documented Physical Access Control System maintenance and testing program(s) that collectively include each of the applicable requirement parts in CIP-006-6 Table R3 – Maintenance and Testing Program. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Medium | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 24 calendar months but did complete required testing within 25 calendar months. (3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 25 calendar months but did complete required testing within 26 calendar months. (3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 26 calendar months but did complete required testing within 27 calendar months. (3.1) | The Responsible Entity did not document or implement a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter. (3.1) OR The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 27 calendar months. (3.1) | M3. Evidence must include each of the documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-6 Table R3 – Maintenance and Testing Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 | [5 empty] | MRO-SK | [6 empty] | 30000000
CIP-006-7 | ST-2024-05-10-0000006 | R1. | RQ-2024-05-10-0000019 | Each Responsible Entity shall implement one or more documented physical security plan(s) that collectively include all of the applicable requirement parts in CIP-006-7 Table R1 – Physical Security Plan. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Same-Day Operations | Medium | N/A | N/A | N/A | The Responsible Entity did not document or implement physical security plans. (Requirement R1) OR The Responsible Entity did not document or implement operational or procedural controls to restrict physical access. (Part 1.1) OR The Responsible Entity has documented and implemented physical access controls, but at least one control does not exist to restrict access to Applicable Systems. (Part 1.2) OR The Responsible Entity has documented and implemented physical access controls, but at least two different controls do not exist to restrict access to Applicable Systems. (Part 1.3) OR The Responsible Entity does not have a process to monitor for unauthorized access through a physical access point into a PSP. (Part 1.4) OR The Responsible Entity does not have a process to alert for detected unauthorized access through a physical access point into a PSP or to communicate such alerts within 15 minutes to identified personnel. (Part 1.5) OR The Responsible Entity does not have a process to monitor each PACS for unauthorized physical access to a PACS. (Part 1.6) OR The Responsible Entity does not have a process to alert for unauthorized physical access to PACS or to communicate such alerts within 15 minutes to identified personnel. (Part 1.7) OR The Responsible Entity does not have a process to log authorized physical entry into each PSP with sufficient information to identify the individual and date and time of entry. (Part 1.8) OR The Responsible Entity does not have a process to retain physical access logs for 90 calendar days. (Part 1.9) | Evidence must include each of the documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-7 Table R1 – Physical Security Plan and additional evidence to demonstrate implementation of the plan or plans as described in the Measures column of the table. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-006-7 | ST-2024-05-10-0000006 | R2. | RQ-2024-05-10-0000020 | Each Responsible Entity shall implement, except during CIP Exceptional Circumstances, one or more documented visitor control program(s) that include each of the applicable requirement parts in CIP-006-7 Table R2 – Visitor Control Program. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | N/A | N/A | The Responsible Entity has failed to include or implement a visitor control program that requires continuous escorted access of visitors within any Physical Security Perimeter. (Part 2.1) OR The Responsible Entity has failed to include or implement a visitor control program that requires logging of the initial entry and last exit dates and times of the visitor, the visitor’s name, and the point of contact. (Part 2.2) OR The Responsible Entity failed to include or implement a visitor control program to retain visitor logs for at least 90 days. (Part 2.3) | Evidence must include one or more documented visitor control programs that collectively include each of the applicable requirement parts in CIP-006-7 Table R2 – Visitor Control Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-006-7 | ST-2024-05-10-0000006 | R3. | RQ-2024-05-10-0000021 | Each Responsible Entity shall implement one or more documented Physical Access Control System maintenance and testing program(s) that collectively include each of the applicable requirement parts in CIP-006-7 Table R3 – Maintenance and Testing Program. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Medium | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 24 calendar months but did complete required testing within 25 calendar months. (Part 3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the PSP, but did not complete required testing within 25 calendar months but did complete required testing within 26 calendar months. (Part 3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for PACS and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 26 calendar months but did complete required testing within 27 calendar months. (Part 3.1) | The Responsible Entity did not document or implement a maintenance and testing program for PACS and locally mounted hardware or devices at the PSP. (Part 3.1) OR The Responsible Entity has documented and implemented a maintenance and testing program for PACS and locally mounted hardware or devices at the PSP, but did not complete required testing within 27 calendar months. (Part 3.1) | Evidence must include each of the documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-7 Table R3 – Maintenance and Testing Program and additional evidence to demonstrate implementation as described in the Measures column of the table. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-006-AB-5 (Alberta) | 656600000009010 | R1. | 656600000009103 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented physical security plans that collectively include all of the applicable requirement parts in CIP]006-AB]5 Table R1 - Physical Security Plan. |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 10000000
CIP-006-AB-5 (Alberta) | 656600000009010 | R2. | 656600000009104 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented visitor control programs that include each of the applicable requirement parts in CIP]006-AB]5 Table R2 - Visitor Control Program. |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 20000000
CIP-006-AB-5 (Alberta) | 656600000009010 | R3. | 656600000009105 | Each Responsible Entity shall implement one or more documented physical access control system maintenance and testing programs that collectively include each of the applicable requirement parts in CIP]006-AB]5 Table R3 - Maintenance and Testing Program. |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 30000000
CIP-007-1 | 29 | R1. | 384 | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-007-1 | 29 | R2. | 388 | Ports and Services — The Responsible Entity shall establish and document a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-007-1 | 29 | R3. | 392 | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003 Requirement R6, shall establish and document a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-007-1 | 29 | R4. | 395 | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-007-1 | 29 | R5. | 398 | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-007-1 | 29 | R6. | 411 | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-007-1 | 29 | R7. | 417 | Disposal or Redeployment — The Responsible Entity shall establish formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
CIP-007-1 | 29 | R8. | 421 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
CIP-007-1 | 29 | R9. | 426 | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007 at least annually. Changes resulting from modifications to the systems or controls shall be documented within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
CIP-007-1 (British Columbia) | 666700000010051 | R1. | 666700000010607 | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-007-1 (British Columbia) | 666700000010051 | R2. | 666700000010608 | Ports and Services — The Responsible Entity shall establish and document a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 20000000
CIP-007-1 (British Columbia) | 666700000010051 | R3. | 666700000010609 | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003 Requirement R6, shall establish and document a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 30000000
CIP-007-1 (British Columbia) | 666700000010051 | R4. | 666700000010610 | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 40000000
CIP-007-1 (British Columbia) | 666700000010051 | R5. | 666700000010611 | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 50000000
CIP-007-1 (British Columbia) | 666700000010051 | R6. | 666700000010612 | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 60000000
CIP-007-1 (British Columbia) | 666700000010051 | R7. | 666700000010613 | Disposal or Redeployment — The Responsible Entity shall establish formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 70000000
CIP-007-1 (British Columbia) | 666700000010051 | R8. | 666700000010614 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 80000000
CIP-007-1 (British Columbia) | 666700000010051 | R9. | 666700000010615 | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007 at least annually. Changes resulting from modifications to the systems or controls shall be documented within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 90000000
CIP-007-1 (Ontario) | 79780000029 | R1. | 79780000384 | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity did create, implement and maintain the test procedures as required in R1.1, but did not document that testing is performed as required in R1.2. &lt;br/&gt;OR&lt;br/&gt;The Responsible Entity did not document the test results as required in R1.3. | The Responsible Entity did not create, implement and maintain the test procedures as required in R1.1. | The Responsible Entity did not create, implement and maintain the test procedures as required in R1.1, &lt;br/&gt;AND&lt;br/&gt;The Responsible Entity did not document that testing was performed as required in R1.2&lt;br/&gt;AND&lt;br/&gt;The Responsible Entity did not document the test results |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-007-1 (Ontario) | 79780000029 | R2. | 79780000388 | Ports and Services — The Responsible Entity shall establish and document a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity established but did not document a process to ensure that only those ports and services required for normal and emergency operations are enabled. | The Responsible Entity documented but did not establish a process to ensure that only those ports and services required for normal and emergency operations are enabled. | The Responsible Entity did not establish nor document a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-007-1 (Ontario) | 79780000029 | R3. | 79780000392 | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003 Requirement R6, shall establish and document a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity established and documented, either separately or as a component of the documented configuration management process specified in CIP-003 Requirement R6, a security patch management program but did not include one or more of the follo | The Responsible Entity established but did not document, either separately or as a component of the documented configuration management process specified in CIP-003 Requirement R6, a security patch management program for tracking, evaluating, testing, and | The Responsible Entity documented but did not establish, either separately or as a component of the documented configuration management process specified in CIP-003 Requirement R6, a security patch management program for tracking, evaluating, testing, and | The Responsible Entity did not establish nor document, either separately or as a component of the documented configuration management process specified in CIP-003 Requirement R6, a security patch management program for tracking, evaluating, testing, and i |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-007-1 (Ontario) | 79780000029 | R4. | 79780000395 | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | The Responsible Entity, as technically feasible, did not use anti-virus software and other malicious software (“malware”) prevention tools, nor implemented compensating measures, on at least one but less than 5% of Cyber Assets within the Electronic Secur | The Responsible Entity, as technically feasible, did not use anti-virus software and other malicious software (“malware”) prevention tools, nor implemented compensating measures, on at least 5% but less than 10% of Cyber Assets within the Electronic Secur | The Responsible Entity, as technically feasible, did not use anti-virus software and other malicious software (“malware”) prevention tools, nor implemented compensating measures, on at least 10% but less than 15% of Cyber Assets within the Electronic Secu | The Responsible Entity, as technically feasible, did not use anti-virus software and other malicious software (“malware”) prevention tools, nor implemented compensating measures, on 15% or more Cyber Assets within the Electronic Security Perimeter(s). |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-007-1 (Ontario) | 79780000029 | R5. | 79780000398 | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | N/A | The Responsible Entity implemented but did not document technical and procedural controls that enforce access authentication of, and accountability for, all user activity. | The Responsible Entity documented but did not implement technical and procedural controls that enforce access authentication of, and accountability for, all user activity. | The Responsible Entity did not document nor implement technical and procedural controls that enforce access authentication of, and accountability for, all user activity. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-007-1 (Ontario) | 79780000029 | R6. | 79780000411 | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity, as technically feasible, did not implement automated tools or organizational process controls to monitor system events that are related to cyber security for at least one but less than 5% of Cyber Assets inside the Electronic Secur | The Responsible Entity, as technically feasible, did not implement automated tools or organizational process controls to monitor system events that are related to cyber security for 5% or more but less than 10% of Cyber Assets inside the Electronic Securi | The Responsible Entity did not implement automated tools or organizational process controls, as technically feasible, to monitor system events that are related to cyber security for 10% or more but less than 15% of Cyber Assets inside the Electronic Secur | The Responsible Entity did not implement automated tools or organizational process controls, as technically feasible, to monitor system events that are related to cyber security for 15% or more of Cyber Assets inside the Electronic Security Perimeter(s). |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-007-1 (Ontario) | 79780000029 | R7. | 79780000417 | Disposal or Redeployment — The Responsible Entity shall establish formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity established formal methods, processes, and procedures for disposal and redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005 but did not maintain records as specifi | The Responsible Entity established formal methods, processes, and procedures for disposal of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005 but did not address redeployment as specified in R7.2. | The Responsible Entity established formal methods, processes, and procedures for redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005 but did not address disposal as specified in R7.1. | The Responsible Entity did not establish formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 70000000
CIP-007-1 (Ontario) | 79780000029 | R8. | 79780000421 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity performed at least annually a Vulnerability Assessment that included 95% or more but less than 100% of Cyber Assets within the Electronic Security Perimeter. | The Responsible Entity performed at least annually a Vulnerability Assessment that included 90% or more but less than 95% of Cyber Assets within the Electronic Security Perimeter. | The Responsible Entity performed at least annually a Vulnerability Assessment that included more than 85% but less than 90% of Cyber Assets within the Electronic Security Perimeter. | The Responsible Entity performed at least annually a Vulnerability Assessment for 85% or less of Cyber Assets within the Electronic Security Perimeter. &lt;br/&gt;OR&lt;br/&gt;The vulnerability assessment did not include one (1) or more of the subrequirements 8.1, 8.2, 8.3, |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 80000000
CIP-007-1 (Ontario) | 79780000029 | R9. | 79780000426 | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007 at least annually. Changes resulting from modifications to the systems or controls shall be documented within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | The Responsible Entity did not review and update the documentation specified in Standard CIP-007 at least annually or the Responsible Entity did not document Changes resulting from modifications to the systems or controls within ninety calendar days of th | The Responsible Entity did not review and update the documentation specified in Standard CIP-007 at least annually nor were Changes resulting from modifications to the systems or controls documented within ninety calendar days of the change. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 90000000
CIP-007-2 | 213 | R1. | 2462 | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-2, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-007-2 | 213 | R2. | 2466 | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-007-2 | 213 | R3. | 2470 | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-2 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-007-2 | 213 | R4. | 2473 | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-03-31 |  |  | CIP-007-1 R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-007-2 | 213 | R5. | 2476 | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2010-03-31 |  |  | CIP-007-1 R5. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-007-2 | 213 | R6. | 2489 | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2010-03-31 |  |  | CIP-007-1 R6. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-007-2 | 213 | R7. | 2495 | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [9 empty] | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
CIP-007-2 | 213 | R8. | 2499 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
CIP-007-2 | 213 | R9. | 2504 | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-2 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
CIP-007-2a | 220 | R1. | 2644 | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-2, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-007-2a | 220 | R2. | 2643 | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-007-2a | 220 | R3. | 2649 | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-2 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-007-2a | 220 | R4. | 2646 | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  | CIP-007-1 R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-007-2a | 220 | R5. | 2647 | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  | CIP-007-1 R5. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-007-2a | 220 | R6. | 2641 | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Planning, Same-Day Operations | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  | 2.4 High Impact BES Cyber Systems and their associated: • PCA Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: • PCA | CIP-007-1 R6. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-007-2a | 220 | R7. | 2642 | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
CIP-007-2a | 220 | R8. | 2645 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
CIP-007-2a | 220 | R9. | 2648 | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-2 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
CIP-007-2a (Ontario) | 79780000220 | R1. | 79780002644 | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-2, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-007-2a (Ontario) | 79780000220 | R2. | 79780002643 | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-007-2a (Ontario) | 79780000220 | R3. | 79780002649 | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-2 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-007-2a (Ontario) | 79780000220 | R4. | 79780002646 | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-007-2a (Ontario) | 79780000220 | R5. | 79780002647 | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-007-2a (Ontario) | 79780000220 | R6. | 79780002641 | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Planning, Same-Day Operations | Low |  |  |  |  | Examples of evidence may include, but are not limited to, documentation of the methods used to determine active vendor remote access (including Interactive Remote Access and system-to-system remote access), such as: &lt;br/&gt;• Methods for accessing logged or monitoring information to determine active vendor remote access sessions;&lt;br/&gt;• Methods for monitoring activity (e.g. connection tables or rule hit counters in a firewall, or user activity monitoring) or open ports (e.g. netstat or related commands to display currently active ports) to determine active system to system remote access sessions; or&lt;br/&gt;• Methods that control vendor initiation of remote access such as vendors calling and requesting a second factor in order to initiate remote access. | 2010-04-01 |  | 2010-09-30 |  | 2.4 High Impact BES Cyber Systems and their associated:&lt;br/&gt;• PCA&lt;br/&gt;Medium Impact BES Cyber Systems with External Routable Connectivity and their associated:&lt;br/&gt;• PCA |  | NPCC-ON | [6 empty] | 60000000
CIP-007-2a (Ontario) | 79780000220 | R7. | 79780002642 | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 70000000
CIP-007-2a (Ontario) | 79780000220 | R8. | 79780002645 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 80000000
CIP-007-2a (Ontario) | 79780000220 | R9. | 79780002648 | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-2 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 90000000
CIP-007-2 (Ontario) | 79780000213 | R1. | 79780002462 | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-2, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-007-2 (Ontario) | 79780000213 | R2. | 79780002466 | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-007-2 (Ontario) | 79780000213 | R3. | 79780002470 | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-2 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-007-2 (Ontario) | 79780000213 | R4. | 79780002473 | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-007-2 (Ontario) | 79780000213 | R5. | 79780002476 | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-007-2 (Ontario) | 79780000213 | R6. | 79780002489 | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-007-2 (Ontario) | 79780000213 | R7. | 79780002495 | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [9 empty] | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 70000000
CIP-007-2 (Ontario) | 79780000213 | R8. | 79780002499 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 80000000
CIP-007-2 (Ontario) | 79780000213 | R9. | 79780002504 | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-2 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 90000000
CIP-007-3 | 449 | R1. | 8605 | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-3, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-007-3 | 449 | R2. | 8609 | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation as specified in Requirement R2. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-007-3 | 449 | R3. | 8613 | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-3 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation and records of its security patch management program, as specified in Requirement R3. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-007-3 | 449 | R4. | 8616 | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation and records of its malicious software prevention program as specified in Requirement R4. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-007-3 | 449 | R5. | 8619 | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-007-3 | 449 | R6. | 8632 | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-007-3 | 449 | R7. | 8638 | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
CIP-007-3 | 449 | R8. | 8642 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
CIP-007-3 | 449 | R9. | 8647 | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-3 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation and records demonstrating the review and update as specified in Requirement R9. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
CIP-007-3a | 227 | R1. | 2823 | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-3, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M1. The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-007-3a | 227 | R2. | 2827 | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M2. The Responsible Entity shall make available documentation as specified in Requirement R2. | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-007-3a | 227 | R3. | 2831 | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-3 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M3. The Responsible Entity shall make available documentation and records of its security patch management program, as specified in Requirement R3. | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-007-3a | 227 | R4. | 2834 | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M4. The Responsible Entity shall make available documentation and records of its malicious software prevention program as specified in Requirement R4. | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-007-3a | 227 | R5. | 2837 | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M5. The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-007-3a | 227 | R6. | 2850 | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M6. The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-007-3a | 227 | R7. | 2856 | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M7. The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
CIP-007-3a | 227 | R8. | 2860 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M8. The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
CIP-007-3a | 227 | R9. | 2865 | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-3 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M9. The Responsible Entity shall make available documentation and records demonstrating the review and update as specified in Requirement R9. | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
CIP-007-3a (British Columbia) | 666700000010053 | R1. | 666700000010625 | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-3, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M1. The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. | 2014-08-01 |  | 2018-09-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | WECC-BC | [6 empty] | 10000000
CIP-007-3a (British Columbia) | 666700000010053 | R2. | 666700000010626 | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M2. The Responsible Entity shall make available documentation as specified in Requirement R2. | 2014-08-01 |  | 2018-09-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | WECC-BC | [6 empty] | 20000000
CIP-007-3a (British Columbia) | 666700000010053 | R3. | 666700000010627 | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-3 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M3. The Responsible Entity shall make available documentation and records of its security patch management program, as specified in Requirement R3. | 2014-08-01 |  | 2018-09-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | WECC-BC | [6 empty] | 30000000
CIP-007-3a (British Columbia) | 666700000010053 | R4. | 666700000010628 | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M4. The Responsible Entity shall make available documentation and records of its malicious software prevention program as specified in Requirement R4. | 2014-08-01 |  | 2018-09-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | WECC-BC | [6 empty] | 40000000
CIP-007-3a (British Columbia) | 666700000010053 | R5. | 666700000010629 | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M5. The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. | 2014-08-01 |  | 2018-09-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | WECC-BC | [6 empty] | 50000000
CIP-007-3a (British Columbia) | 666700000010053 | R6. | 666700000010630 | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M6. The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. | 2014-08-01 |  | 2018-09-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | WECC-BC | [6 empty] | 60000000
CIP-007-3a (British Columbia) | 666700000010053 | R7. | 666700000010631 | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M7. The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. | 2014-08-01 |  | 2018-09-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | WECC-BC | [6 empty] | 70000000
CIP-007-3a (British Columbia) | 666700000010053 | R8. | 666700000010632 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M8. The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. | 2014-08-01 |  | 2018-09-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | WECC-BC | [6 empty] | 80000000
CIP-007-3a (British Columbia) | 666700000010053 | R9. | 666700000010633 | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-3 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M9. The Responsible Entity shall make available documentation and records demonstrating the review and update as specified in Requirement R9. | 2014-08-01 |  | 2018-09-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | WECC-BC | [6 empty] | 90000000
CIP-007-3a (Manitoba) | 77660000000227 | R1. | 776600000002823 | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-3, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M1. The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. | 2016-07-01 |  | 2017-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-MB | [6 empty] | 10000000
CIP-007-3a (Manitoba) | 77660000000227 | R2. | 776600000002827 | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M2. The Responsible Entity shall make available documentation as specified in Requirement R2. | 2016-07-01 |  | 2017-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-MB | [6 empty] | 20000000
CIP-007-3a (Manitoba) | 77660000000227 | R3. | 776600000002831 | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-3 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M3. The Responsible Entity shall make available documentation and records of its security patch management program, as specified in Requirement R3. | 2016-07-01 |  | 2017-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-MB | [6 empty] | 30000000
CIP-007-3a (Manitoba) | 77660000000227 | R4. | 776600000002834 | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | M4. The Responsible Entity shall make available documentation and records of its malicious software prevention program as specified in Requirement R4. | 2016-07-01 |  | 2017-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-MB | [6 empty] | 40000000
CIP-007-3a (Manitoba) | 77660000000227 | R5. | 776600000002837 | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M5. The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. | 2016-07-01 |  | 2017-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-MB | [6 empty] | 50000000
CIP-007-3a (Manitoba) | 77660000000227 | R6. | 776600000002850 | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M6. The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. | 2016-07-01 |  | 2017-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-MB | [6 empty] | 60000000
CIP-007-3a (Manitoba) | 77660000000227 | R7. | 776600000002856 | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M7. The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. | 2016-07-01 |  | 2017-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-MB | [6 empty] | 70000000
CIP-007-3a (Manitoba) | 77660000000227 | R8. | 776600000002860 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M8. The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. | 2016-07-01 |  | 2017-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-MB | [6 empty] | 80000000
CIP-007-3a (Manitoba) | 77660000000227 | R9. | 776600000002865 | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-3 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | M9. The Responsible Entity shall make available documentation and records demonstrating the review and update as specified in Requirement R9. | 2016-07-01 |  | 2017-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | MRO-MB | [6 empty] | 90000000
CIP-007-3a (Ontario) | 79780000227 | R1. | 79780002823 | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-3, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not ensure the prevention of adverse affects described in R1, by not including the required minimum significant changes OR The Responsible Entity did not address one or more of the following: R1.1, R1.2, R1.3. | M1. The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | NPCC-ON | [6 empty] | 10000000
CIP-007-3a (Ontario) | 79780000227 | R2. | 79780002827 | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not establish (implement) or did not document a process to ensure that only those ports and services required for normal and emergency operations are enabled. | M2. The Responsible Entity shall make available documentation as specified in Requirement R2. | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | NPCC-ON | [6 empty] | 20000000
CIP-007-3a (Ontario) | 79780000227 | R3. | 79780002831 | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-3 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity did not establish (implement) or did not document, either separately or as a component of the documented configuration management process specified in CIP-003-3 Requirement R6, a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | M3. The Responsible Entity shall make available documentation and records of its security patch management program, as specified in Requirement R3. | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | NPCC-ON | [6 empty] | 30000000
CIP-007-3a (Ontario) | 79780000227 | R4. | 79780002834 | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity, where technically feasible, did not use anti-virus software or other malicious software (“malware”) prevention tools, on one or more Cyber Assets within the Electronic Security Perimeter(s). | M4. The Responsible Entity shall make available documentation and records of its malicious software prevention program as specified in Requirement R4. | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | NPCC-ON | [6 empty] | 40000000
CIP-007-3a (Ontario) | 79780000227 | R5. | 79780002837 | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity did not document or did not implement technical and procedural controls that enforce access authentication of, and accountability for, all user activity. | M5. The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | NPCC-ON | [6 empty] | 50000000
CIP-007-3a (Ontario) | 79780000227 | R6. | 79780002850 | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity as technically feasible, did not implement automated tools or organizational process controls, to monitor system events that are related to cyber security on one or more of Cyber Assets inside the Electronic Security Perimeter(s). | M6. The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | NPCC-ON | [6 empty] | 60000000
CIP-007-3a (Ontario) | 79780000227 | R7. | 79780002856 | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity did not establish or implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-3. OR The Responsible Entity established formal methods, processes, and procedures for redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-2 but did not address disposal as specified in R7.1. OR The Responsible Entity did not maintain records pertaining to disposal or[ ] redeployment as specified in R7.3. | M7. The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | NPCC-ON | [6 empty] | 70000000
CIP-007-3a (Ontario) | 79780000227 | R8. | 79780002860 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity did not perform a Vulnerability Assessment on one or more Cyber Assets within the Electronic Security Perimeter at least annually. OR The vulnerability assessment did not include one (1) or more of the subrequirements 8.1, 8.2, 8.3, 8.4. | M8. The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | NPCC-ON | [6 empty] | 80000000
CIP-007-3a (Ontario) | 79780000227 | R9. | 79780002865 | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-3 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | The Responsible Entity did not review and update the documentation specified in Standard CIP-007-3 at least annually. OR The Responsible Entity did not document changes resulting from modifications to the systems or controls within thirty calendar days of the change being completed | The Responsible Entity did not review and update the documentation specified in Standard CIP-007-3 at least annually and changes resulting from modifications to the systems or controls were not documented within thirty calendar days of the change being completed. | M9. The Responsible Entity shall make available documentation and records demonstrating the review and update as specified in Requirement R9. | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | NPCC-ON | [6 empty] | 90000000
CIP-007-3b | 432 | R1. | 5315 | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-3, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-007-3b | 432 | R2. | 5314 | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | The Responsible Entity shall make available documentation as specified in Requirement R2. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-007-3b | 432 | R3. | 5320 | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-3 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | The Responsible Entity shall make available documentation and records of its security patch management program, as specified in Requirement R3. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-007-3b | 432 | R4. | 5317 | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | The Responsible Entity shall make available documentation and records of its malicious software prevention program as specified in Requirement R4. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-007-3b | 432 | R5. | 5318 | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-007-3b | 432 | R6. | 5312 | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-007-3b | 432 | R7. | 5313 | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
CIP-007-3b | 432 | R8. | 5316 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
CIP-007-3b | 432 | R9. | 5319 | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-3 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | The Responsible Entity shall make available documentation and records demonstrating the review and update as specified in Requirement R9. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
CIP-007-3b (Ontario) | 79780000432 | R1. | 79780005315 | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-3, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-007-3b (Ontario) | 79780000432 | R2. | 79780005314 | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-007-3b (Ontario) | 79780000432 | R3. | 79780005320 | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-3 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-007-3b (Ontario) | 79780000432 | R4. | 79780005317 | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [7 empty] | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-007-3b (Ontario) | 79780000432 | R5. | 79780005318 | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-007-3b (Ontario) | 79780000432 | R6. | 79780005312 | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-007-3b (Ontario) | 79780000432 | R7. | 79780005313 | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 70000000
CIP-007-3b (Ontario) | 79780000432 | R8. | 79780005316 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 80000000
CIP-007-3b (Ontario) | 79780000432 | R9. | 79780005319 | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-3 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [7 empty] | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 90000000
CIP-007-3 (British Columbia) | 666700000010052 | R1. | 666700000010616 | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-3, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. | 2012-07-01 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-007-3 (British Columbia) | 666700000010052 | R2. | 666700000010617 | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation as specified in Requirement R2. | 2012-07-01 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 20000000
CIP-007-3 (British Columbia) | 666700000010052 | R3. | 666700000010618 | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-3 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation and records of its security patch management program, as specified in Requirement R3. | 2012-07-01 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 30000000
CIP-007-3 (British Columbia) | 666700000010052 | R4. | 666700000010619 | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation and records of its malicious software prevention program as specified in Requirement R4. | 2012-07-01 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 40000000
CIP-007-3 (British Columbia) | 666700000010052 | R5. | 666700000010620 | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. | 2012-07-01 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 50000000
CIP-007-3 (British Columbia) | 666700000010052 | R6. | 666700000010621 | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. | 2012-07-01 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 60000000
CIP-007-3 (British Columbia) | 666700000010052 | R7. | 666700000010622 | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. | 2012-07-01 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 70000000
CIP-007-3 (British Columbia) | 666700000010052 | R8. | 666700000010623 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. | 2012-07-01 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 80000000
CIP-007-3 (British Columbia) | 666700000010052 | R9. | 666700000010624 | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-3 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation and records demonstrating the review and update as specified in Requirement R9. | 2012-07-01 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 90000000
CIP-007-3 (Manitoba) | 77660000000449 | R1. | 776600000008605 | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-3, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
CIP-007-3 (Manitoba) | 77660000000449 | R2. | 776600000008609 | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation as specified in Requirement R2. | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
CIP-007-3 (Manitoba) | 77660000000449 | R3. | 776600000008613 | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-3 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation and records of its security patch management program, as specified in Requirement R3. | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
CIP-007-3 (Manitoba) | 77660000000449 | R4. | 776600000008616 | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation and records of its malicious software prevention program as specified in Requirement R4. | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 40000000
CIP-007-3 (Manitoba) | 77660000000449 | R5. | 776600000008619 | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 50000000
CIP-007-3 (Manitoba) | 77660000000449 | R6. | 776600000008632 | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 60000000
CIP-007-3 (Manitoba) | 77660000000449 | R7. | 776600000008638 | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 70000000
CIP-007-3 (Manitoba) | 77660000000449 | R8. | 776600000008642 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 80000000
CIP-007-3 (Manitoba) | 77660000000449 | R9. | 776600000008647 | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-3 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | The Responsible Entity shall make available documentation and records demonstrating the review and update as specified in Requirement R9. | 2012-04-01 |  | 2016-06-30 |  |  |  | MRO-MB | [6 empty] | 90000000
CIP-007-3 (Ontario) | 79780000449
CIP-007-4a | 253 | R1. | 3312 | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-4, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity did create, implement and maintain the test procedures as required in R1.1, but did not document that testing is performed as required in R1.2. OR The Responsible Entity did not document the test results as required in R1.3. | The Responsible Entity did not create, implement and maintain the test procedures as required in R1.1. | The Responsible Entity did not create, implement and maintain the test procedures as required in R1.1, AND The Responsible Entity did not document that testing was performed as required in R1.2 AND The Responsible Entity did not document the test results as required in R1.3. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-007-4a | 253 | R2. | 3316 | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity established (implemented) but did not document a process to ensure that only those ports and services required for normal and emergency operations are enabled. | The Responsible Entity documented but did not establish (implement) a process to ensure that only those ports and services required for normal and emergency operations are enabled. | The Responsible Entity did not establish (implement) or did not document a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-007-4a | 253 | R3. | 3320 | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity established (implemented) and documented, either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, a security patch management program but did not include one or more of the following: tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity established (implemented) but did not document, either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity documented but did not establish (implement), either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity did not establish (implement) nor document, either separately or as a component of the documented configuration management process specified in CIP003-4 Requirement R6, a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-007-4a | 253 | R4. | 3323 | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | The Responsible Entity, as technically feasible, did not use anti-virus software and other malicious software (“malware”) prevention tools, nor implemented compensating measures, on at least one but less than 5% of Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity, as technically feasible, did not use anti-virus software and other malicious software (“malware”) prevention tools, nor implemented compensating measures, on at least 5% but less than 10% of Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity, as technically feasible, did not use anti-virus software and other malicious software (“malware”) prevention tools, nor implemented compensating measures, on at least 10% but less than 15% of Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity, where technically feasible, did not use anti-virus software or other malicious software (“malware”) prevention tools, on one or more Cyber Assets within the Electronic Security Perimeter(s). |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-007-4a | 253 | R5. | 3326 | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | The Responsible Entity implemented but did not document technical and procedural controls that enforce access authentication of, and accountability for, all user activity. | The Responsible Entity documented but did not implement technical and procedural controls that enforce access authentication of, and accountability for, all user activity. | The Responsible Entity did not document or did not implement technical and procedural controls that enforce access authentication of, and accountability for, all user activity. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-007-4a | 253 | R6. | 3339 | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity, as technically feasible, did not implement automated tools or organizational process controls to monitor system events that are related to cyber security for at least one but less than 5% of Cyber Assets inside the Electronic Security Perimeter(s). | The Responsible Entity, as technically feasible, did not implement automated tools or organizational process controls to monitor system events that are related to cyber security for 5% or more but less than 10% of Cyber Assets inside the Electronic Security Perimeter(s). | The Responsible Entity did not implement automated tools or organizational process controls, as technically feasible, to monitor system events that are related to cyber security for 10% or more but less than 15% of Cyber Assets inside the Electronic Security Perimeter(s). | The Responsible Entity as technically feasible, did not implement automated tools or organizational process controls, to monitor system events that are related to cyber security on one or more of Cyber Assets inside the Electronic Security Perimeter(s). |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-007-4a | 253 | R7. | 3345 | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity established and implemented formal methods, processes, and procedures for disposal and redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP- 005-4 but did not maintain records as specified in R7.3. | The Responsible Entity established and implemented formal methods, processes, and procedures for disposal of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4 but did not address redeployment as specified in R7.2. | The Responsible Entity established and implemented formal methods, processes, and procedures for redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4 but did not address disposal as specified in R7.1. | The Responsible Entity did not establish or implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
CIP-007-4a | 253 | R8. | 3349 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity performed at least annually a Vulnerability Assessment that included 95% or more but less than 100% of Cyber Assets within the Electronic Security Perimeter. | The Responsible Entity performed at least annually a Vulnerability Assessment that included 90% or more but less than 95% of Cyber Assets within the Electronic Security Perimeter. | The Responsible Entity performed at least annually a Vulnerability Assessment that included more than 85% but less than 90% of Cyber Assets within the Electronic Security Perimeter. | The Responsible Entity did not perform a Vulnerability Assessment on one or more Cyber Assets within the Electronic Security Perimeter at least annually. OR The vulnerability assessment did not include one (1) or more of the subrequirements 8.1, 8.2, 8.3, 8.4. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
CIP-007-4a | 253 | R9. | 3354 | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-4 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | The Responsible Entity did not review and update the documentation specified in Standard CIP-007-4 at least annually. OR The Responsible Entity did not document changes resulting from modifications to the systems or controls within thirty calendar days of the change being completed. | The Responsible Entity did not review and update the documentation specified in Standard CIP-007-4 at least annually and changes resulting from modifications to the systems or controls were not documented within thirty calendar days of the change being completed. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
CIP-007-4a (Ontario) | 79780000253 | R1. | 79780003312 | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-4, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not ensure the prevention of adverse affects described in R1, by not including the required minimum significant changes. OR The Responsible Entity did not address one or more of the following: R1.1, R1.2, R1.3. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-007-4a (Ontario) | 79780000253 | R2. | 79780003316 | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not establish (implement) or did not document a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-007-4a (Ontario) | 79780000253 | R3. | 79780003320 | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity did not establish (implement) or did not document, either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, a security patch management program for tracking, evalu |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-007-4a (Ontario) | 79780000253 | R4. | 79780003323 | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity, where technically feasible, did not use anti-virus software or other malicious software (“malware”) prevention tools, on one or more Cyber Assets within the Electronic Security Perimeter(s). |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-007-4a (Ontario) | 79780000253 | R5. | 79780003326 | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity did not document or did not implement technical and procedural controls that enforce access authentication of, and accountability for, all user activity. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-007-4a (Ontario) | 79780000253 | R6. | 79780003339 | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity as technically feasible, did not implement automated tools or organizational process controls, to monitor system events that are related to cyber security on one or more of Cyber Assets inside the Electronic Security Perimeter(s). |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-007-4a (Ontario) | 79780000253 | R7. | 79780003345 | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | The Responsible Entity established and implemented formal methods, processes, and procedures for redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4 but did not address redeployment a | The Responsible Entity did not establish or implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4. OR The Responsib |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 70000000
CIP-007-4a (Ontario) | 79780000253 | R8. | 79780003349 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity did not perform a Vulnerability Assessment on one or more Cyber Assets within the Electronic Security Perimeter at least annually. OR The vulnerability assessment did not include one (1) or more of the subrequirements 8.1, 8.2, 8. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 80000000
CIP-007-4a (Ontario) | 79780000253 | R9. | 79780003354 | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-4 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | The Responsible Entity did not review and update the documentation specified in Standard CIP-007-4 at least annually. OR The Responsible Entity did not document changes resulting from modifications to the systems or controls within thirty calendar days | The Responsible Entity did not review and update the documentation specified in Standard CIP-007-4 at least annually and changes resulting from modifications to the systems or controls were not documented within thirty calendar days of the change being co |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 90000000
CIP-007-4b | 433 | R1. | 5358 | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-4, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity did create, implement and maintain the test procedures as required in R1.1, but did not document that testing is performed as required in R1.2. OR The Responsible Entity did not document the test results as required in R1.3. | The Responsible Entity did not create, implement and maintain the test procedures as required in R1.1 | The Responsible Entity did not create, implement and maintain the test procedures as required in R1.1, AND The Responsible Entity did not document that testing was performed as required in R1.2 AND The Responsible Entity did not document the test results as required in R1.3. |  |  |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-007-4b | 433 | R2. | 5357 | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity established (implemented) but did not document a process to ensure that only those ports and services required for normal and emergency operations are enabled. | The Responsible Entity documented but did not establish (implement) a process to ensure that only those ports and services required for normal and emergency operations are enabled. | The Responsible Entity did not establish (implement) or did not document a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  |  |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-007-4b | 433 | R3. | 5363 | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity established (implemented) and documented, either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, a security patch management program but did not include one or more of the following: tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity established (implemented) but did not document, either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity documented but did not establish (implement), either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity did not establish (implement) nor document, either separately or as a component of the documented configuration management process specified in CIP003-4 Requirement R6, a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  |  |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-007-4b | 433 | R4. | 5360 | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | The Responsible Entity, as technically feasible, did not use anti-virus software and other malicious software (“malware”) prevention tools, nor implemented compensating measures, on at least one but less than 5% of Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity, as technically feasible, did not use anti-virus software and other malicious software (“malware”) prevention tools, nor implemented compensating measures, on at least 5% but less than 10% of Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity, as technically feasible, did not use anti-virus software and other malicious software (“malware”) prevention tools, nor implemented compensating measures, on at least 10% but less than 15% of Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity, as technically feasible, did not use antivirus software and other malicious software (“malware”) prevention tools, nor implemented compensating measures, on 15% or more Cyber Assets within the Electronic Security Perimeter(s). |  |  |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-007-4b | 433 | R5. | 5361 | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | The Responsible Entity implemented but did not document technical and procedural controls that enforce access authentication of, and accountability for, all user activity. | The Responsible Entity documented but did not implement technical and procedural controls that enforce access authentication of, and accountability for, all user activity. | The Responsible Entity did not document nor implement technical and procedural controls that enforce access authentication of, and accountability for, all user activity. |  |  |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-007-4b | 433 | R6. | 5355 | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity, as technically feasible, did not implement automated tools or organizational process controls to monitor system events that are related to cyber security for at least one but less than 5% of Cyber Assets inside the Electronic Security Perimeter(s). | The Responsible Entity, as technically feasible, did not implement automated tools or organizational process controls to monitor system events that are related to cyber security for 5% or more but less than 10% of Cyber Assets inside the Electronic Security Perimeter(s). | The Responsible Entity did not implement automated tools or organizational process controls, as technically feasible, to monitor system events that are related to cyber security for 10% or more but less than 15% of Cyber Assets inside the Electronic Security Perimeter(s). | The Responsible Entity did not implement automated tools or organizational process controls, as technically feasible, to monitor system events that are related to cyber security for 15% or more of Cyber Assets inside the Electronic Security Perimeter(s). |  |  |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
CIP-007-4b | 433 | R7. | 5356 | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity established and implemented formal methods, processes, and procedures for disposal and redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP- 005-4 but did not maintain records as specified in R7.3. | The Responsible Entity established and implemented formal methods, processes, and procedures for disposal of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4 but did not address redeployment as specified in R7.2. | The Responsible Entity established and implemented formal methods, processes, and procedures for redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4 but did not address disposal as specified in R7.1. | The Responsible Entity did not establish or implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4. |  |  |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
CIP-007-4b | 433 | R8. | 5359 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity performed at least annually a Vulnerability Assessment that included 95% or more but less than 100% of Cyber Assets within the Electronic Security Perimeter. | The Responsible Entity performed at least annually a Vulnerability Assessment that included 90% or more but less than 95% of Cyber Assets within the Electronic Security Perimeter. | The Responsible Entity performed at least annually a Vulnerability Assessment that included more than 85% but less than 90% of Cyber Assets within the Electronic Security Perimeter. | The Responsible Entity performed at least annually a Vulnerability Assessment for 85% or less of Cyber Assets within the Electronic Security Perimeter. OR The vulnerability assessment did not include one (1) or more of the subrequirements 8.1, 8.2, 8.3, 8.4. |  |  |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
CIP-007-4b | 433 | R9. | 5362 | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-4 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | The Responsible Entity did not review and update the documentation specified in Standard CIP-007-4 at least annually. OR The Responsible Entity did not document changes resulting from modifications to the systems or controls within thirty calendar days of the change being completed. | The Responsible Entity did not review and update the documentation specified in Standard CIP-007-4 at least annually and changes resulting from modifications to the systems or controls were not documented within thirty calendar days of the change being completed. |  |  |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
CIP-007-4b (Ontario) | 79780000433 | R1. | 79780005358 | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-4, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not ensure the prevention of adverse affects described in R1, by not including the required minimum significant changes. OR The Responsible Entity did not address one or more of the following: R1.1, R1.2, R1.3. |  |  |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-007-4b (Ontario) | 79780000433 | R2. | 79780005357 | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity did not establish (implement) or did not document a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  |  |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-007-4b (Ontario) | 79780000433 | R3. | 79780005363 | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity did not establish (implement) or did not document, either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, a security patch management program for tracking, evalu |  |  |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-007-4b (Ontario) | 79780000433 | R4. | 79780005360 | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity, where technically feasible, did not use anti-virus software or other malicious software (“malware”) prevention tools, on one or more Cyber Assets within the Electronic Security Perimeter(s). |  |  |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-007-4b (Ontario) | 79780000433 | R5. | 79780005361 | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity did not document or did not implement technical and procedural controls that enforce access authentication of, and accountability for, all user activity. |  |  |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-007-4b (Ontario) | 79780000433 | R6. | 79780005355 | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity as technically feasible, did not implement automated tools or organizational process controls, to monitor system events that are related to cyber security on one or more of Cyber Assets inside the Electronic Security Perimeter(s). |  |  |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 60000000
CIP-007-4b (Ontario) | 79780000433 | R7. | 79780005356 | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | The Responsible Entity established and implemented formal methods, processes, and procedures for redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4 but did not address redeployment a | The Responsible Entity did not establish or implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4. OR The Responsib |  |  |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 70000000
CIP-007-4b (Ontario) | 79780000433 | R8. | 79780005359 | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity did not perform a Vulnerability Assessment on one or more Cyber Assets within the Electronic Security Perimeter at least annually. OR The vulnerability assessment did not include one (1) or more of the subrequirements 8.1, 8.2, 8. |  |  |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 80000000
CIP-007-4b (Ontario) | 79780000433 | R9. | 79780005362 | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-4 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | The Responsible Entity did not review and update the documentation specified in Standard CIP-007-4 at least annually. OR The Responsible Entity did not document changes resulting from modifications to the systems or controls within thirty calendar days | The Responsible Entity did not review and update the documentation specified in Standard CIP-007-4 at least annually and changes resulting from modifications to the systems or controls were not documented within thirty calendar days of the change being co |  |  |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 90000000
CIP-007-5 | 351 | R1. | 4496 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R1 – Ports and Services. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | The Responsible Entity has implemented and documented processes for Ports and Services but had no methods to protect against unnecessary physical input/output ports used for network connectivity, console commands, or removable media and has identified deficiencies but did not assess or correct the deficiencies. (1.2) OR The Responsible Entity has implemented and documented processes for Ports and Services but had no methods to protect against unnecessary physical input/output ports used for network connectivity, console commands, or removable media but did not identify, assess, or correct the deficiencies. (1.2) | The Responsible Entity has implemented and documented processes for determining necessary Ports and Services but, where technically feasible, had one or more unneeded logical network accessible ports enabled and has identified deficiencies but did not assess or correct the deficiencies. (1.1) OR The Responsible Entity has implemented and documented processes for determining necessary Ports and Services but, where technically feasible, had one or more unneeded logical network accessible ports enabled but did not identify, assess, or correct the deficiencies. (1.1) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R1 and has identified deficiencies but did not assess or correct the deficiencies. (R1) OR The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R1 but did not identify, assess, or correct the deficiencies. (R1) | Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP007-5 Table R1 – Ports and Services and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-007-5 | 351 | R2. | 4497 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R2 – Security Patch Management. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 35 calendar days but less than 50 calendar days of the last evaluation for the source or sources identified and has identified deficiencies but did not assess or correct the deficiencies. (2.2) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 35 calendar days but less than 50 calendar days of the last evaluation for the source or sources identified but did not identify, assess, or correct the deficiencies. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 35 calendar days but less than 50 calendar days of the evaluation completion and has identified deficiencies but did not assess or correct the deficiencies. (2.3) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 35 calendar days but less than 50 calendar days of the evaluation completion but did not identify, assess, or correct the deficiencies. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes, including the identification of sources, for tracking or evaluating cyber security patches for applicable Cyber Assets and has identified deficiencies but did not assess or correct the deficiencies. (2.1) OR The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes, including the identification of sources, for tracking, or evaluating cyber security patches for applicable Cyber Assets but did not identify, assess, or correct the deficiencies. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 50 calendar days but less than 65 calendar days of the last evaluation for the source or sources identified and has identified deficiencies but did not assess or correct the deficiencies. (2.2) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 50 calendar days but less than 65 calendar days of the last evaluation for the source or sources identified but did not identify, assess, or correct the deficiencies. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 50 calendar days but less than 65 calendar days of the evaluation completion and has identified deficiencies but did not assess or correct the deficiencies. (2.3) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 50 calendar days but less than 65 calendar days of the evaluation completion but did not identify, assess, or correct the deficiencies. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for installing cyber security patches for applicable Cyber Assets and has identified deficiencies but did not assess or correct the deficiencies. (2.1) OR The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for installing cyber security patches for applicable Cyber Assets but did not identify, assess, or correct the deficiencies. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 65 calendar days of the last evaluation for the source or sources identified and has identified deficiencies but did not assess or correct the deficiencies. (2.2) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 65 calendar days of the last evaluation for the days source or sources identified but did not identify, assess, or correct the deficiencies. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 65 calendar days of the evaluation completion and has identified deficiencies but did not assess or correct the deficiencies. (2.3) OR Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 65 calendar days of the evaluation completion but did not identify, assess, or correct the deficiencies. (2.3) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R2 and has identified deficiencies but did not assess or correct the deficiencies. (R2) OR The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R2 but did not identify, assess, or correct the deficiencies. (R2) OR The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for tracking, evaluating, or installing cyber security patches for applicable Cyber Assets and has identified deficiencies but did not assess or correct the deficiencies. (2.1) OR The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for tracking, evaluating, or installing cyber security patches for applicable Cyber Assets but did not identify, assess, or correct the deficiencies. (2.1) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch and documented a revision or extension to the timeframe but did not obtain approval by the CIP Senior Manager or delegate and has identified deficiencies but did not assess or correct the deficiencies. (2.4) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch and documented a revision or extension to the timeframe but did not obtain approval by the CIP Senior Manager or delegate but did not identify, assess, or correct the deficiencies. (2.4) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch but did not implement the plan as created or revised within the timeframe specified in the plan and has identified deficiencies but did not assess or correct the deficiencies. (2.4) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch but did not implement the plan as created or revised within the timeframe specified in the plan but did not identify, assess, or correct the deficiencies. (2.4) | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R2 – Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-007-5 | 351 | R3. | 4498 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R3 – Malicious Code Prevention. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | The Responsible Entity has implemented one or more documented process(es), but, where signatures or patterns are used, the Responsible Entity did not address testing the signatures or patterns and has identified deficiencies but did not assess or correct the deficiencies. (3.3) OR The Responsible Entity has implemented one or more documented process(es), but, where signatures or patterns are used, the Responsible Entity did not address testing the signatures or patterns and did not identify, assess, or correct the deficiencies. (3.3) | The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not mitigate the threat of detected malicious code and has identified deficiencies but did not assess or correct the deficiencies. (3.2) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not mitigate the threat of detected malicious code and did not identify, assess, or correct the deficiencies. (3.2) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention, but where signatures or patterns are used, the Responsible Entity did not update malicious code protections and has identified deficiencies but did not assess or correct the deficiencies. (3.3) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention, but where signatures or patterns are used, the Responsible Entity did not update malicious code protections and did not identify, assess, or correct the deficiencies. (3.3) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R3 and has identified deficiencies but did not assess or correct the deficiencies. (R3) OR The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R3 and did not identify, assess, or correct the deficiencies. (R3) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not deploy method(s) to deter, detect, or prevent malicious code and has identified deficiencies but did not assess or correct the deficiencies. (3.1) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not deploy method(s) to deter, detect, or prevent malicious code and did not identify, assess, or correct the deficiencies. (3.1) | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-007-5 | 351 | R4. | 4499 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R4 – Security Event Monitoring. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Assessment, Same-Day Operations | Medium | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 22 calendar days of the prior review and has identified deficiencies but did not assess or correct the deficiencies. (4.4) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 22 calendar days of the prior review but did not identify, assess, or correct the deficiencies. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 30 calendar days of the prior review and has identified deficiencies but did not assess or correct the deficiencies. (4.4) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 30 calendar days of the prior review but did not identify, assess, or correct the deficiencies. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to generate alerts for necessary security events (as determined by the responsible entity) for the Applicable Systems (per device or system capability) but did not generate alerts for all of the required types of events described in 4.2.1 through 4.2.2 and has identified deficiencies but did not assess or correct the deficiencies. (4.2) OR The Responsible Entity has documented and implemented one or more process(es) to generate alerts for necessary security events (as determined by the responsible entity) for the Applicable Systems (per device or system capability) but did not generate alerts for all of the required types of events described in 4.2.1 through 4.2.2 and did not identify, assess, or correct the deficiencies. (4.2) OR The Responsible Entity has documented and implemented one or more process(es) to log applicable events identified in 4.1 (where technically feasible and except during CIP Exceptional Circumstances) but did not retain applicable event logs for at least the last 90 consecutive days and has identified deficiencies but did not assess or correct the deficiencies. (4.3) OR The Responsible Entity has documented and implemented one or more process(es) to log applicable events identified in 4.1 (where technically feasible and except during CIP Exceptional Circumstances) but did not retain applicable event logs for at least the last 90 consecutive days and did not identify, assess, or correct the deficiencies. (4.3) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed two or more intervals and has identified deficiencies but did not assess or correct the deficiencies. (4.4) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed two or more intervals and did not identify, assess, or correct the deficiencies. (4.4) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R4 and has identified deficiencies but did not assess or correct the deficiencies. (R4) OR The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R4 and did not identify, assess, or correct the deficiencies. (R4) OR The Responsible Entity has documented and implemented one or more process(es) to log events for the Applicable Systems (per device or system capability) but did not detect and log all of the required types of events described in 4.1.1 through 4.1.3 and has identified deficiencies but did not assess or correct the deficiencies. (4.1) or The Responsible Entity has documented and implemented one or more process(es) to log events for the Applicable Systems (per device or system capability) but did not detect and log all of the required types of events described in 4.1.1 through 4.1.3 and did not identify, assess, or correct the deficiencies. (4.1) | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-007-5 | 351 | R5. | 4500 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R5 – System Access Controls. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 15 calendar months but less than or equal to 16 calendar months of the last password change and has identified deficiencies but did not assess or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 15 calendar months but less than or equal to 16 calendar months of the last password change and did not identify, assess, or correct the deficiencies. (5.6) | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 16 calendar months but less than or equal to 17 calendar months of the last password change and has identified deficiencies but did not assess or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 16 calendar months but less than or equal to 17 calendar months of the last password change and did not identify, assess, or correct the deficiencies. (5.6) | The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification or inventory of all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s) and has identified deficiencies but did not assess or correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification or inventory of all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s) and did not identify, assess, or correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification of the individuals with authorized access to shared accounts and has identified deficiencies but did not assess or correct the deficiencies. (5.3) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification of the individuals with authorized access to shared accounts and did not identify, assess, or correct the deficiencies. (5.3) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access that did not technically or procedurally enforce one of the two password parameters as described in 5.5.1 and 5.5.2 and has identified deficiencies but did not assess or correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access that did not technically or procedurally enforce one of the two password parameters as described in 5.5.1 and 5.5.2 and did not identify, assess, or correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 17 calendar months but less than or equal to 18 calendar months of the last password change and has identified deficiencies but did not assess or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 17 calendar months but less than or equal to 18 calendar months of the last password change and did not identify, assess, or correct the deficiencies. (5.6) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R5 and has identified deficiencies but did not assess or correct the deficiencies. (R5) or The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R5 and did not identify, assess, or correct the deficiencies. (R5) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access and has identified deficiencies but did not assess or correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access and did not identify, assess, or correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but did not, per device capability, change known default passwords and has identified deficiencies but did not assess or correct the deficiencies. (5.4) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but did not, per device capability, change known default passwords but did not identify, assess, or correct the deficiencies. (5.4) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but the Responsible Entity did not technically or procedurally enforce all of the password parameters described in 5.5.1 and 5.5.2 and has identified deficiencies but did not assess or correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but the Responsible Entity did not technically or procedurally enforce all of the password parameters described in 5.5.1 and 5.5.2 and did not identify, assess, or correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 18 calendar months of the last password change and has identified deficiencies but did not assess or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 18 calendar months of the last password change and did not identify, assess, or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for System Access Control but, where technically feasible, did not either limit the number of unsuccessful authentication attempts or generate alerts after a threshold of unsuccessful authentication attempts and has identified deficiencies but did not assess or correct the deficiencies. (5.7) or The Responsible Entity has implemented one or more documented process(es) for System Access Control but, where technically feasible, did not either limit the number of unsuccessful authentication attempts or generate alerts after a threshold of unsuccessful authentication attempts and did not identify, assess, or correct the deficiencies. (5.7) | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-007-5 (British Columbia) | 666700000010054 | R1. | 666700000010634 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R1 – Ports and Services. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | The Responsible Entity has implemented and documented processes for Ports and Services but had no methods to protect against unnecessary physical input/output ports used for network connectivity, console commands, or removable media and has identified deficiencies but did not assess or correct the deficiencies. (1.2) OR The Responsible Entity has implemented and documented processes for Ports and Services but had no methods to protect against unnecessary physical input/output ports used for network connectivity, console commands, or removable media but did not identify, assess, or correct the deficiencies. (1.2) | The Responsible Entity has implemented and documented processes for determining necessary Ports and Services but, where technically feasible, had one or more unneeded logical network accessible ports enabled and has identified deficiencies but did not assess or correct the deficiencies. (1.1) OR The Responsible Entity has implemented and documented processes for determining necessary Ports and Services but, where technically feasible, had one or more unneeded logical network accessible ports enabled but did not identify, assess, or correct the deficiencies. (1.1) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R1 and has identified deficiencies but did not assess or correct the deficiencies. (R1) OR The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R1 but did not identify, assess, or correct the deficiencies. (R1) | Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP007-5 Table R1 – Ports and Services and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-007-5 (British Columbia) | 666700000010054 | R2. | 666700000010635 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R2 – Security Patch Management. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 35 calendar days but less than 50 calendar days of the last evaluation for the source or sources identified and has identified deficiencies but did not assess or correct the deficiencies. (2.2) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 35 calendar days but less than 50 calendar days of the last evaluation for the source or sources identified but did not identify, assess, or correct the deficiencies. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 35 calendar days but less than 50 calendar days of the evaluation completion and has identified deficiencies but did not assess or correct the deficiencies. (2.3) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 35 calendar days but less than 50 calendar days of the evaluation completion but did not identify, assess, or correct the deficiencies. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes, including the identification of sources, for tracking or evaluating cyber security patches for applicable Cyber Assets and has identified deficiencies but did not assess or correct the deficiencies. (2.1) OR The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes, including the identification of sources, for tracking, or evaluating cyber security patches for applicable Cyber Assets but did not identify, assess, or correct the deficiencies. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 50 calendar days but less than 65 calendar days of the last evaluation for the source or sources identified and has identified deficiencies but did not assess or correct the deficiencies. (2.2) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 50 calendar days but less than 65 calendar days of the last evaluation for the source or sources identified but did not identify, assess, or correct the deficiencies. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 50 calendar days but less than 65 calendar days of the evaluation completion and has identified deficiencies but did not assess or correct the deficiencies. (2.3) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 50 calendar days but less than 65 calendar days of the evaluation completion but did not identify, assess, or correct the deficiencies. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for installing cyber security patches for applicable Cyber Assets and has identified deficiencies but did not assess or correct the deficiencies. (2.1) OR The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for installing cyber security patches for applicable Cyber Assets but did not identify, assess, or correct the deficiencies. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 65 calendar days of the last evaluation for the source or sources identified and has identified deficiencies but did not assess or correct the deficiencies. (2.2) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 65 calendar days of the last evaluation for the days source or sources identified but did not identify, assess, or correct the deficiencies. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 65 calendar days of the evaluation completion and has identified deficiencies but did not assess or correct the deficiencies. (2.3) OR Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 65 calendar days of the evaluation completion but did not identify, assess, or correct the deficiencies. (2.3) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R2 and has identified deficiencies but did not assess or correct the deficiencies. (R2) OR The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R2 but did not identify, assess, or correct the deficiencies. (R2) OR The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for tracking, evaluating, or installing cyber security patches for applicable Cyber Assets and has identified deficiencies but did not assess or correct the deficiencies. (2.1) OR The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for tracking, evaluating, or installing cyber security patches for applicable Cyber Assets but did not identify, assess, or correct the deficiencies. (2.1) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch and documented a revision or extension to the timeframe but did not obtain approval by the CIP Senior Manager or delegate and has identified deficiencies but did not assess or correct the deficiencies. (2.4) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch and documented a revision or extension to the timeframe but did not obtain approval by the CIP Senior Manager or delegate but did not identify, assess, or correct the deficiencies. (2.4) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch but did not implement the plan as created or revised within the timeframe specified in the plan and has identified deficiencies but did not assess or correct the deficiencies. (2.4) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch but did not implement the plan as created or revised within the timeframe specified in the plan but did not identify, assess, or correct the deficiencies. (2.4) | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R2 – Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 20000000
CIP-007-5 (British Columbia) | 666700000010054 | R3. | 666700000010636 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R3 – Malicious Code Prevention. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | The Responsible Entity has implemented one or more documented process(es), but, where signatures or patterns are used, the Responsible Entity did not address testing the signatures or patterns and has identified deficiencies but did not assess or correct the deficiencies. (3.3) OR The Responsible Entity has implemented one or more documented process(es), but, where signatures or patterns are used, the Responsible Entity did not address testing the signatures or patterns and did not identify, assess, or correct the deficiencies. (3.3) | The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not mitigate the threat of detected malicious code and has identified deficiencies but did not assess or correct the deficiencies. (3.2) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not mitigate the threat of detected malicious code and did not identify, assess, or correct the deficiencies. (3.2) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention, but where signatures or patterns are used, the Responsible Entity did not update malicious code protections and has identified deficiencies but did not assess or correct the deficiencies. (3.3) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention, but where signatures or patterns are used, the Responsible Entity did not update malicious code protections and did not identify, assess, or correct the deficiencies. (3.3) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R3 and has identified deficiencies but did not assess or correct the deficiencies. (R3) OR The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R3 and did not identify, assess, or correct the deficiencies. (R3) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not deploy method(s) to deter, detect, or prevent malicious code and has identified deficiencies but did not assess or correct the deficiencies. (3.1) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not deploy method(s) to deter, detect, or prevent malicious code and did not identify, assess, or correct the deficiencies. (3.1) | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 30000000
CIP-007-5 (British Columbia) | 666700000010054 | R4. | 666700000010637 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R4 – Security Event Monitoring. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Assessment, Same-Day Operations | Medium | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 22 calendar days of the prior review and has identified deficiencies but did not assess or correct the deficiencies. (4.4) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 22 calendar days of the prior review but did not identify, assess, or correct the deficiencies. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 30 calendar days of the prior review and has identified deficiencies but did not assess or correct the deficiencies. (4.4) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 30 calendar days of the prior review but did not identify, assess, or correct the deficiencies. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to generate alerts for necessary security events (as determined by the responsible entity) for the Applicable Systems (per device or system capability) but did not generate alerts for all of the required types of events described in 4.2.1 through 4.2.2 and has identified deficiencies but did not assess or correct the deficiencies. (4.2) OR The Responsible Entity has documented and implemented one or more process(es) to generate alerts for necessary security events (as determined by the responsible entity) for the Applicable Systems (per device or system capability) but did not generate alerts for all of the required types of events described in 4.2.1 through 4.2.2 and did not identify, assess, or correct the deficiencies. (4.2) OR The Responsible Entity has documented and implemented one or more process(es) to log applicable events identified in 4.1 (where technically feasible and except during CIP Exceptional Circumstances) but did not retain applicable event logs for at least the last 90 consecutive days and has identified deficiencies but did not assess or correct the deficiencies. (4.3) OR The Responsible Entity has documented and implemented one or more process(es) to log applicable events identified in 4.1 (where technically feasible and except during CIP Exceptional Circumstances) but did not retain applicable event logs for at least the last 90 consecutive days and did not identify, assess, or correct the deficiencies. (4.3) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed two or more intervals and has identified deficiencies but did not assess or correct the deficiencies. (4.4) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed two or more intervals and did not identify, assess, or correct the deficiencies. (4.4) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R4 and has identified deficiencies but did not assess or correct the deficiencies. (R4) OR The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R4 and did not identify, assess, or correct the deficiencies. (R4) OR The Responsible Entity has documented and implemented one or more process(es) to log events for the Applicable Systems (per device or system capability) but did not detect and log all of the required types of events described in 4.1.1 through 4.1.3 and has identified deficiencies but did not assess or correct the deficiencies. (4.1) or The Responsible Entity has documented and implemented one or more process(es) to log events for the Applicable Systems (per device or system capability) but did not detect and log all of the required types of events described in 4.1.1 through 4.1.3 and did not identify, assess, or correct the deficiencies. (4.1) | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 40000000
CIP-007-5 (British Columbia) | 666700000010054 | R5. | 666700000010638 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R5 – System Access Controls. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 15 calendar months but less than or equal to 16 calendar months of the last password change and has identified deficiencies but did not assess or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 15 calendar months but less than or equal to 16 calendar months of the last password change and did not identify, assess, or correct the deficiencies. (5.6) | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 16 calendar months but less than or equal to 17 calendar months of the last password change and has identified deficiencies but did not assess or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 16 calendar months but less than or equal to 17 calendar months of the last password change and did not identify, assess, or correct the deficiencies. (5.6) | The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification or inventory of all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s) and has identified deficiencies but did not assess or correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification or inventory of all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s) and did not identify, assess, or correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification of the individuals with authorized access to shared accounts and has identified deficiencies but did not assess or correct the deficiencies. (5.3) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification of the individuals with authorized access to shared accounts and did not identify, assess, or correct the deficiencies. (5.3) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access that did not technically or procedurally enforce one of the two password parameters as described in 5.5.1 and 5.5.2 and has identified deficiencies but did not assess or correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access that did not technically or procedurally enforce one of the two password parameters as described in 5.5.1 and 5.5.2 and did not identify, assess, or correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 17 calendar months but less than or equal to 18 calendar months of the last password change and has identified deficiencies but did not assess or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 17 calendar months but less than or equal to 18 calendar months of the last password change and did not identify, assess, or correct the deficiencies. (5.6) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R5 and has identified deficiencies but did not assess or correct the deficiencies. (R5) or The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R5 and did not identify, assess, or correct the deficiencies. (R5) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access and has identified deficiencies but did not assess or correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access and did not identify, assess, or correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but did not, per device capability, change known default passwords and has identified deficiencies but did not assess or correct the deficiencies. (5.4) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but did not, per device capability, change known default passwords but did not identify, assess, or correct the deficiencies. (5.4) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but the Responsible Entity did not technically or procedurally enforce all of the password parameters described in 5.5.1 and 5.5.2 and has identified deficiencies but did not assess or correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but the Responsible Entity did not technically or procedurally enforce all of the password parameters described in 5.5.1 and 5.5.2 and did not identify, assess, or correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 18 calendar months of the last password change and has identified deficiencies but did not assess or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 18 calendar months of the last password change and did not identify, assess, or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for System Access Control but, where technically feasible, did not either limit the number of unsuccessful authentication attempts or generate alerts after a threshold of unsuccessful authentication attempts and has identified deficiencies but did not assess or correct the deficiencies. (5.7) or The Responsible Entity has implemented one or more documented process(es) for System Access Control but, where technically feasible, did not either limit the number of unsuccessful authentication attempts or generate alerts after a threshold of unsuccessful authentication attempts and did not identify, assess, or correct the deficiencies. (5.7) | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 50000000
CIP-007-5 (Ontario) | 79780000351 | R1. | 79780004496 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R1 – Ports and Services. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Medium | N/A | The Responsible Entity has implemented and documented processes for Ports and Services but had no methods to protect against unnecessary physical input/output ports used for network connectivity, console commands, or removable media and has identified deficiencies but did not assess or correct the deficiencies. (1.2) OR The Responsible Entity has implemented and documented processes for Ports and Services but had no methods to protect against unnecessary physical input/output ports used for network connectivity, console commands, or removable media but did not identify, assess, or correct the deficiencies. (1.2) | The Responsible Entity has implemented and documented processes for determining necessary Ports and Services but, where technically feasible, had one or more unneeded logical network accessible ports enabled and has identified deficiencies but did not assess or correct the deficiencies. (1.1) OR The Responsible Entity has implemented and documented processes for determining necessary Ports and Services but, where technically feasible, had one or more unneeded logical network accessible ports enabled but did not identify, assess, or correct the deficiencies. (1.1) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R1 and has identified deficiencies but did not assess or correct the deficiencies. (R1) OR The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R1 but did not identify, assess, or correct the deficiencies. (R1) |  |  |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-007-5 (Ontario) | 79780000351 | R2. | 79780004497 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R2 – Security Patch Management. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Medium | The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 35 calendar days but less than 50 calendar days of the last evaluation for the source or sources identified and has identified deficiencies but did not assess or correct the deficiencies. (2.2) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 35 calendar days but less than 50 calendar days of the last evaluation for the source or sources identified but did not identify, assess, or correct the deficiencies. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 35 calendar days but less than 50 calendar days of the evaluation completion and has identified deficiencies but did not assess or correct the deficiencies. (2.3) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 35 calendar days but less than 50 calendar days of the evaluation completion but did not identify, assess, or correct the deficiencies. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes, including the identification of sources, for tracking or evaluating cyber security patches for applicable Cyber Assets and has identified deficiencies but did not assess or correct the deficiencies. (2.1) OR The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes, including the identification of sources, for tracking, or evaluating cyber security patches for applicable Cyber Assets but did not identify, assess, or correct the deficiencies. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 50 calendar days but less than 65 calendar days of the last evaluation for the source or sources identified and has identified deficiencies but did not assess or correct the deficiencies. (2.2) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 50 calendar days but less than 65 calendar days of the last evaluation for the source or sources identified but did not identify, assess, or correct the deficiencies. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 50 calendar days but less than 65 calendar days of the evaluation completion and has identified deficiencies but did not assess or correct the deficiencies. (2.3) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 50 calendar days but less than 65 calendar days of the evaluation completion but did not identify, assess, or correct the deficiencies. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for installing cyber security patches for applicable Cyber Assets and has identified deficiencies but did not assess or correct the deficiencies. (2.1) OR The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for installing cyber security patches for applicable Cyber Assets but did not identify, assess, or correct the deficiencies. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 65 calendar days of the last evaluation for the source or sources identified and has identified deficiencies but did not assess or correct the deficiencies. (2.2) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 65 calendar days of the last evaluation for the days source or sources identified but did not identify, assess, or correct the deficiencies. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 65 calendar days of the evaluation completion and has identified deficiencies but did not assess or correct the deficiencies. (2.3) OR Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 65 calendar days of the evaluation completion but did not identify, assess, or correct the deficiencies. (2.3) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R2 and has identified deficiencies but did not assess or correct the deficiencies. (R2) OR The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R2 but did not identify, assess, or correct the deficiencies. (R2) OR The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for tracking, evaluating, or installing cyber security patches for applicable Cyber Assets and has identified deficiencies but did not assess or correct the deficiencies. (2.1) OR The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for tracking, evaluating, or installing cyber security patches for applicable Cyber Assets but did not identify, assess, or correct the deficiencies. (2.1) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch and documented a revision or extension to the timeframe but did not obtain approval by the CIP Senior Manager or delegate and has identified deficiencies but did not assess or correct the deficiencies. (2.4) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch and documented a revision or extension to the timeframe but did not obtain approval by the CIP Senior Manager or delegate but did not identify, assess, or correct the deficiencies. (2.4) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch but did not implement the plan as created or revised within the timeframe specified in the plan and has identified deficiencies but did not assess or correct the deficiencies. (2.4) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch but did not implement the plan as created or revised within the timeframe specified in the plan but did not identify, assess, or correct the deficiencies. (2.4) |  |  |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-007-5 (Ontario) | 79780000351 | R3. | 79780004498 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R3 – Malicious Code Prevention. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | Medium | N/A | The Responsible Entity has implemented one or more documented process(es), but, where signatures or patterns are used, the Responsible Entity did not address testing the signatures or patterns and has identified deficiencies but did not assess or correct the deficiencies. (3.3) OR The Responsible Entity has implemented one or more documented process(es), but, where signatures or patterns are used, the Responsible Entity did not address testing the signatures or patterns and did not identify, assess, or correct the deficiencies. (3.3) | The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not mitigate the threat of detected malicious code and has identified deficiencies but did not assess or correct the deficiencies. (3.2) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not mitigate the threat of detected malicious code and did not identify, assess, or correct the deficiencies. (3.2) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention, but where signatures or patterns are used, the Responsible Entity did not update malicious code protections and has identified deficiencies but did not assess or correct the deficiencies. (3.3) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention, but where signatures or patterns are used, the Responsible Entity did not update malicious code protections and did not identify, assess, or correct the deficiencies. (3.3) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R3 and has identified deficiencies but did not assess or correct the deficiencies. (R3) OR The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R3 and did not identify, assess, or correct the deficiencies. (R3) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not deploy method(s) to deter, detect, or prevent malicious code and has identified deficiencies but did not assess or correct the deficiencies. (3.1) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not deploy method(s) to deter, detect, or prevent malicious code and did not identify, assess, or correct the deficiencies. (3.1) |  |  |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-007-5 (Ontario) | 79780000351 | R4. | 79780004499 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R4 – Security Event Monitoring. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 22 calendar days of the prior review and has identified deficiencies but did not assess or correct the deficiencies. (4.4) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 22 calendar days of the prior review but did not identify, assess, or correct the deficiencies. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 30 calendar days of the prior review and has identified deficiencies but did not assess or correct the deficiencies. (4.4) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 30 calendar days of the prior review but did not identify, assess, or correct the deficiencies. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to generate alerts for necessary security events (as determined by the responsible entity) for the Applicable Systems (per device or system capability) but did not generate alerts for all of the required types of events described in 4.2.1 through 4.2.2 and has identified deficiencies but did not assess or correct the deficiencies. (4.2) OR The Responsible Entity has documented and implemented one or more process(es) to generate alerts for necessary security events (as determined by the responsible entity) for the Applicable Systems (per device or system capability) but did not generate alerts for all of the required types of events described in 4.2.1 through 4.2.2 and did not identify, assess, or correct the deficiencies. (4.2) OR The Responsible Entity has documented and implemented one or more process(es) to log applicable events identified in 4.1 (where technically feasible and except during CIP Exceptional Circumstances) but did not retain applicable event logs for at least the last 90 consecutive days and has identified deficiencies but did not assess or correct the deficiencies. (4.3) OR The Responsible Entity has documented and implemented one or more process(es) to log applicable events identified in 4.1 (where technically feasible and except during CIP Exceptional Circumstances) but did not retain applicable event logs for at least the last 90 consecutive days and did not identify, assess, or correct the deficiencies. (4.3) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed two or more intervals and has identified deficiencies but did not assess or correct the deficiencies. (4.4) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed two or more intervals and did not identify, assess, or correct the deficiencies. (4.4) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R4 and has identified deficiencies but did not assess or correct the deficiencies. (R4) OR The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R4 and did not identify, assess, or correct the deficiencies. (R4) OR The Responsible Entity has documented and implemented one or more process(es) to log events for the Applicable Systems (per device or system capability) but did not detect and log all of the required types of events described in 4.1.1 through 4.1.3 and has identified deficiencies but did not assess or correct the deficiencies. (4.1) or The Responsible Entity has documented and implemented one or more process(es) to log events for the Applicable Systems (per device or system capability) but did not detect and log all of the required types of events described in 4.1.1 through 4.1.3 and did not identify, assess, or correct the deficiencies. (4.1) | M1.2. An example of evidence may include, but is not limited to, documentation showing types of protection of physical input/output ports, either logically through system configuration or physically using a port lock or signage. |  |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-007-5 (Ontario) | 79780000351 | R5. | 79780004500 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R5 – System Access Controls. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Assessment, Same-Day Operations | Medium | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 15 calendar months but less than or equal to 16 calendar months of the last password change and has identified deficiencies but did not assess or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 15 calendar months but less than or equal to 16 calendar months of the last password change and did not identify, assess, or correct the deficiencies. (5.6) | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 16 calendar months but less than or equal to 17 calendar months of the last password change and has identified deficiencies but did not assess or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 16 calendar months but less than or equal to 17 calendar months of the last password change and did not identify, assess, or correct the deficiencies. (5.6) | The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification or inventory of all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s) and has identified deficiencies but did not assess or correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification or inventory of all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s) and did not identify, assess, or correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification of the individuals with authorized access to shared accounts and has identified deficiencies but did not assess or correct the deficiencies. (5.3) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification of the individuals with authorized access to shared accounts and did not identify, assess, or correct the deficiencies. (5.3) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access that did not technically or procedurally enforce one of the two password parameters as described in 5.5.1 and 5.5.2 and has identified deficiencies but did not assess or correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access that did not technically or procedurally enforce one of the two password parameters as described in 5.5.1 and 5.5.2 and did not identify, assess, or correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 17 calendar months but less than or equal to 18 calendar months of the last password change and has identified deficiencies but did not assess or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 17 calendar months but less than or equal to 18 calendar months of the last password change and did not identify, assess, or correct the deficiencies. (5.6) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R5 and has identified deficiencies but did not assess or correct the deficiencies. (R5) or The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R5 and did not identify, assess, or correct the deficiencies. (R5) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access and has identified deficiencies but did not assess or correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access and did not identify, assess, or correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but did not, per device capability, change known default passwords and has identified deficiencies but did not assess or correct the deficiencies. (5.4) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but did not, per device capability, change known default passwords but did not identify, assess, or correct the deficiencies. (5.4) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but the Responsible Entity did not technically or procedurally enforce all of the password parameters described in 5.5.1 and 5.5.2 and has identified deficiencies but did not assess or correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but the Responsible Entity did not technically or procedurally enforce all of the password parameters described in 5.5.1 and 5.5.2 and did not identify, assess, or correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 18 calendar months of the last password change and has identified deficiencies but did not assess or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 18 calendar months of the last password change and did not identify, assess, or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for System Access Control but, where technically feasible, did not either limit the number of unsuccessful authentication attempts or generate alerts after a threshold of unsuccessful authentication attempts and has identified deficiencies but did not assess or correct the deficiencies. (5.7) or The Responsible Entity has implemented one or more documented process(es) for System Access Control but, where technically feasible, did not either limit the number of unsuccessful authentication attempts or generate alerts after a threshold of unsuccessful authentication attempts and did not identify, assess, or correct the deficiencies. (5.7) | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-007-5 (Saskatchewan) | 83750000000351 | R1. | 837500000004496 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R1 – Ports and Services. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | The Responsible Entity has implemented and documented processes for Ports and Services but had no methods to protect against unnecessary physical input/output ports used for network connectivity, console commands, or removable media and has identified deficiencies but did not assess or correct the deficiencies. (1.2) OR The Responsible Entity has implemented and documented processes for Ports and Services but had no methods to protect against unnecessary physical input/output ports used for network connectivity, console commands, or removable media but did not identify, assess, or correct the deficiencies. (1.2) | The Responsible Entity has implemented and documented processes for determining necessary Ports and Services but, where technically feasible, had one or more unneeded logical network accessible ports enabled and has identified deficiencies but did not assess or correct the deficiencies. (1.1) OR The Responsible Entity has implemented and documented processes for determining necessary Ports and Services but, where technically feasible, had one or more unneeded logical network accessible ports enabled but did not identify, assess, or correct the deficiencies. (1.1) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R1 and has identified deficiencies but did not assess or correct the deficiencies. (R1) OR The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R1 but did not identify, assess, or correct the deficiencies. (R1) | Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP007-5 Table R1 – Ports and Services and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 10000000
CIP-007-5 (Saskatchewan) | 83750000000351 | R2. | 837500000004497 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R2 – Security Patch Management. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 35 calendar days but less than 50 calendar days of the last evaluation for the source or sources identified and has identified deficiencies but did not assess or correct the deficiencies. (2.2) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 35 calendar days but less than 50 calendar days of the last evaluation for the source or sources identified but did not identify, assess, or correct the deficiencies. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 35 calendar days but less than 50 calendar days of the evaluation completion and has identified deficiencies but did not assess or correct the deficiencies. (2.3) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 35 calendar days but less than 50 calendar days of the evaluation completion but did not identify, assess, or correct the deficiencies. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes, including the identification of sources, for tracking or evaluating cyber security patches for applicable Cyber Assets and has identified deficiencies but did not assess or correct the deficiencies. (2.1) OR The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes, including the identification of sources, for tracking, or evaluating cyber security patches for applicable Cyber Assets but did not identify, assess, or correct the deficiencies. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 50 calendar days but less than 65 calendar days of the last evaluation for the source or sources identified and has identified deficiencies but did not assess or correct the deficiencies. (2.2) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 50 calendar days but less than 65 calendar days of the last evaluation for the source or sources identified but did not identify, assess, or correct the deficiencies. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 50 calendar days but less than 65 calendar days of the evaluation completion and has identified deficiencies but did not assess or correct the deficiencies. (2.3) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 50 calendar days but less than 65 calendar days of the evaluation completion but did not identify, assess, or correct the deficiencies. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for installing cyber security patches for applicable Cyber Assets and has identified deficiencies but did not assess or correct the deficiencies. (2.1) OR The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for installing cyber security patches for applicable Cyber Assets but did not identify, assess, or correct the deficiencies. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 65 calendar days of the last evaluation for the source or sources identified and has identified deficiencies but did not assess or correct the deficiencies. (2.2) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 65 calendar days of the last evaluation for the days source or sources identified but did not identify, assess, or correct the deficiencies. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 65 calendar days of the evaluation completion and has identified deficiencies but did not assess or correct the deficiencies. (2.3) OR Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 65 calendar days of the evaluation completion but did not identify, assess, or correct the deficiencies. (2.3) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R2 and has identified deficiencies but did not assess or correct the deficiencies. (R2) OR The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R2 but did not identify, assess, or correct the deficiencies. (R2) OR The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for tracking, evaluating, or installing cyber security patches for applicable Cyber Assets and has identified deficiencies but did not assess or correct the deficiencies. (2.1) OR The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for tracking, evaluating, or installing cyber security patches for applicable Cyber Assets but did not identify, assess, or correct the deficiencies. (2.1) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch and documented a revision or extension to the timeframe but did not obtain approval by the CIP Senior Manager or delegate and has identified deficiencies but did not assess or correct the deficiencies. (2.4) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch and documented a revision or extension to the timeframe but did not obtain approval by the CIP Senior Manager or delegate but did not identify, assess, or correct the deficiencies. (2.4) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch but did not implement the plan as created or revised within the timeframe specified in the plan and has identified deficiencies but did not assess or correct the deficiencies. (2.4) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch but did not implement the plan as created or revised within the timeframe specified in the plan but did not identify, assess, or correct the deficiencies. (2.4) | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R2 – Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 20000000
CIP-007-5 (Saskatchewan) | 83750000000351 | R3. | 837500000004498 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R3 – Malicious Code Prevention. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | The Responsible Entity has implemented one or more documented process(es), but, where signatures or patterns are used, the Responsible Entity did not address testing the signatures or patterns and has identified deficiencies but did not assess or correct the deficiencies. (3.3) OR The Responsible Entity has implemented one or more documented process(es), but, where signatures or patterns are used, the Responsible Entity did not address testing the signatures or patterns and did not identify, assess, or correct the deficiencies. (3.3) | The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not mitigate the threat of detected malicious code and has identified deficiencies but did not assess or correct the deficiencies. (3.2) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not mitigate the threat of detected malicious code and did not identify, assess, or correct the deficiencies. (3.2) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention, but where signatures or patterns are used, the Responsible Entity did not update malicious code protections and has identified deficiencies but did not assess or correct the deficiencies. (3.3) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention, but where signatures or patterns are used, the Responsible Entity did not update malicious code protections and did not identify, assess, or correct the deficiencies. (3.3) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R3 and has identified deficiencies but did not assess or correct the deficiencies. (R3) OR The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R3 and did not identify, assess, or correct the deficiencies. (R3) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not deploy method(s) to deter, detect, or prevent malicious code and has identified deficiencies but did not assess or correct the deficiencies. (3.1) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not deploy method(s) to deter, detect, or prevent malicious code and did not identify, assess, or correct the deficiencies. (3.1) | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 30000000
CIP-007-5 (Saskatchewan) | 83750000000351 | R4. | 837500000004499 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R4 – Security Event Monitoring. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Assessment, Same-Day Operations | Medium | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 22 calendar days of the prior review and has identified deficiencies but did not assess or correct the deficiencies. (4.4) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 22 calendar days of the prior review but did not identify, assess, or correct the deficiencies. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 30 calendar days of the prior review and has identified deficiencies but did not assess or correct the deficiencies. (4.4) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 30 calendar days of the prior review but did not identify, assess, or correct the deficiencies. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to generate alerts for necessary security events (as determined by the responsible entity) for the Applicable Systems (per device or system capability) but did not generate alerts for all of the required types of events described in 4.2.1 through 4.2.2 and has identified deficiencies but did not assess or correct the deficiencies. (4.2) OR The Responsible Entity has documented and implemented one or more process(es) to generate alerts for necessary security events (as determined by the responsible entity) for the Applicable Systems (per device or system capability) but did not generate alerts for all of the required types of events described in 4.2.1 through 4.2.2 and did not identify, assess, or correct the deficiencies. (4.2) OR The Responsible Entity has documented and implemented one or more process(es) to log applicable events identified in 4.1 (where technically feasible and except during CIP Exceptional Circumstances) but did not retain applicable event logs for at least the last 90 consecutive days and has identified deficiencies but did not assess or correct the deficiencies. (4.3) OR The Responsible Entity has documented and implemented one or more process(es) to log applicable events identified in 4.1 (where technically feasible and except during CIP Exceptional Circumstances) but did not retain applicable event logs for at least the last 90 consecutive days and did not identify, assess, or correct the deficiencies. (4.3) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed two or more intervals and has identified deficiencies but did not assess or correct the deficiencies. (4.4) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed two or more intervals and did not identify, assess, or correct the deficiencies. (4.4) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R4 and has identified deficiencies but did not assess or correct the deficiencies. (R4) OR The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R4 and did not identify, assess, or correct the deficiencies. (R4) OR The Responsible Entity has documented and implemented one or more process(es) to log events for the Applicable Systems (per device or system capability) but did not detect and log all of the required types of events described in 4.1.1 through 4.1.3 and has identified deficiencies but did not assess or correct the deficiencies. (4.1) or The Responsible Entity has documented and implemented one or more process(es) to log events for the Applicable Systems (per device or system capability) but did not detect and log all of the required types of events described in 4.1.1 through 4.1.3 and did not identify, assess, or correct the deficiencies. (4.1) | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 40000000
CIP-007-5 (Saskatchewan) | 83750000000351 | R5. | 837500000004500 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R5 – System Access Controls. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 15 calendar months but less than or equal to 16 calendar months of the last password change and has identified deficiencies but did not assess or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 15 calendar months but less than or equal to 16 calendar months of the last password change and did not identify, assess, or correct the deficiencies. (5.6) | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 16 calendar months but less than or equal to 17 calendar months of the last password change and has identified deficiencies but did not assess or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 16 calendar months but less than or equal to 17 calendar months of the last password change and did not identify, assess, or correct the deficiencies. (5.6) | The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification or inventory of all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s) and has identified deficiencies but did not assess or correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification or inventory of all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s) and did not identify, assess, or correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification of the individuals with authorized access to shared accounts and has identified deficiencies but did not assess or correct the deficiencies. (5.3) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification of the individuals with authorized access to shared accounts and did not identify, assess, or correct the deficiencies. (5.3) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access that did not technically or procedurally enforce one of the two password parameters as described in 5.5.1 and 5.5.2 and has identified deficiencies but did not assess or correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access that did not technically or procedurally enforce one of the two password parameters as described in 5.5.1 and 5.5.2 and did not identify, assess, or correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 17 calendar months but less than or equal to 18 calendar months of the last password change and has identified deficiencies but did not assess or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 17 calendar months but less than or equal to 18 calendar months of the last password change and did not identify, assess, or correct the deficiencies. (5.6) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R5 and has identified deficiencies but did not assess or correct the deficiencies. (R5) or The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R5 and did not identify, assess, or correct the deficiencies. (R5) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access and has identified deficiencies but did not assess or correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access and did not identify, assess, or correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but did not, per device capability, change known default passwords and has identified deficiencies but did not assess or correct the deficiencies. (5.4) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but did not, per device capability, change known default passwords but did not identify, assess, or correct the deficiencies. (5.4) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but the Responsible Entity did not technically or procedurally enforce all of the password parameters described in 5.5.1 and 5.5.2 and has identified deficiencies but did not assess or correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but the Responsible Entity did not technically or procedurally enforce all of the password parameters described in 5.5.1 and 5.5.2 and did not identify, assess, or correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 18 calendar months of the last password change and has identified deficiencies but did not assess or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 18 calendar months of the last password change and did not identify, assess, or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for System Access Control but, where technically feasible, did not either limit the number of unsuccessful authentication attempts or generate alerts after a threshold of unsuccessful authentication attempts and has identified deficiencies but did not assess or correct the deficiencies. (5.7) or The Responsible Entity has implemented one or more documented process(es) for System Access Control but, where technically feasible, did not either limit the number of unsuccessful authentication attempts or generate alerts after a threshold of unsuccessful authentication attempts and did not identify, assess, or correct the deficiencies. (5.7) | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. |  |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 50000000
CIP-007-6 | 513 | R1. | 6092 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R1 – Ports and Services. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | The Responsible Entity has implemented and documented processes for Ports and Services but had no methods to protect against unnecessary physical input/output ports used for network connectivity, console commands, or removable media. (1.2) | The Responsible Entity has implemented and documented processes for determining necessary Ports and Services but, where technically feasible, had one or more unneeded logical network accessible ports enabled. (1.1) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R1. (R1) | M1. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP007-6 Table R1 – Ports and Services and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-007-6 | 513 | R2. | 6093 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R2 – Security Patch Management. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 35 calendar days but less than 50 calendar days of the last evaluation for the source or sources identified. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 35 calendar days but less than 50 calendar days of the evaluation completion. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes, including the identification of sources, for tracking or evaluating cyber security patches for applicable Cyber Assets. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 50 calendar days but less than 65 calendar days of the last evaluation for the source or sources identified. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 50 calendar days but less than 65 calendar days of the evaluation completion. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for installing cyber security patches for applicable Cyber Assets. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 65 calendar days of the last evaluation for the source or sources identified. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 65 calendar days of the evaluation completion. (2.3) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R2. (R2) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch but did not implement the plan as created or revised within the timeframe specified in the plan. (2.4) | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R2 – Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-007-6 | 513 | R3. | 6094 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R3 – Malicious Code Prevention. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | The Responsible Entity has implemented one or more documented process(es), but, where signatures or patterns are used, the Responsible Entity did not address testing the signatures or patterns. (3.3) | The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not mitigate the threat of detected malicious code. (3.2) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention, but where signatures or patterns are used, the Responsible Entity did not update malicious code protections. (3.3). | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R3. (R3). OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not deploy method(s) to deter, detect, or prevent malicious code. (3.1) | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-007-6 | 513 | R4. | 6095 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Assessment, Same-Day Operations | Medium | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 22 calendar days of the prior review. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 30 calendar days of the prior review. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to generate alerts for necessary security events (as determined by the responsible entity) for the Applicable Systems (per device or system capability) but did not generate alerts for all of the required types of events described in 4.2.1 through 4.2.2. (4.2) OR The Responsible Entity has documented and implemented one or more process(es) to log applicable events identified in 4.1 (where technically feasible and except during CIP Exceptional Circumstances) but did not retain applicable event logs for at least the last 90 consecutive days. (4.3) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed two or more intervals. (4.4) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R4. (R4) OR The Responsible Entity has documented and implemented one or more process(es) to log events for the Applicable Systems (per device or system capability) but did not detect and log all of the required types of events described in 4.1.1 through 4.1.3. (4.1) | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-007-6 | 513 | R5. | 6096 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R5 – System Access Controls. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 15 calendar months but less than or equal to 16 calendar months of the last password change. (5.6) | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 16 calendar months but less than or equal to 17 calendar months of the last password change. (5.6) | The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification or inventory of all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s). (5.2) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification of the individuals with authorized access to shared accounts. (5.3) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access that did not technically or procedurally enforce one of the two password parameters as described in 5.5.1 and 5.5.2. (5.5) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 17 calendar months but less than or equal to 18 calendar months of the last password change. (5.6) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R5. (R5) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access. (5.1) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access. (5.1) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but did not, per device capability, change known default passwords. (5.4) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but the Responsible Entity did not technically or procedurally enforce all of the password parameters described in 5.5.1 and 5.5.2. (5.5) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 18 calendar months of the last password change. (5.6) OR The Responsible Entity has implemented one or more documented process(es) for System Access Control but, where technically feasible, did not either limit the number of unsuccessful authentication attempts or generate alerts after a threshold of unsuccessful authentication attempts. (5.7) | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-007-6 (British Columbia) | 666700000010055 | R1. | 666700000010639 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R1 – Ports and Services. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | The Responsible Entity has implemented and documented processes for Ports and Services but had no methods to protect against unnecessary physical input/output ports used for network connectivity, console commands, or removable media. (1.2) | The Responsible Entity has implemented and documented processes for determining necessary Ports and Services but, where technically feasible, had one or more unneeded logical network accessible ports enabled. (1.1) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R1. (R1) | M1. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP007-6 Table R1 – Ports and Services and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2018-10-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | WECC-BC | [6 empty] | 10000000
CIP-007-6 (British Columbia) | 666700000010055 | R2. | 666700000010640 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R2 – Security Patch Management. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 35 calendar days but less than 50 calendar days of the last evaluation for the source or sources identified. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 35 calendar days but less than 50 calendar days of the evaluation completion. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes, including the identification of sources, for tracking or evaluating cyber security patches for applicable Cyber Assets. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 50 calendar days but less than 65 calendar days of the last evaluation for the source or sources identified. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 50 calendar days but less than 65 calendar days of the evaluation completion. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for installing cyber security patches for applicable Cyber Assets. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 65 calendar days of the last evaluation for the source or sources identified. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 65 calendar days of the evaluation completion. (2.3) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R2. (R2) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch but did not implement the plan as created or revised within the timeframe specified in the plan. (2.4) | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R2 – Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2018-10-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | WECC-BC | [6 empty] | 20000000
CIP-007-6 (British Columbia) | 666700000010055 | R3. | 666700000010641 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R3 – Malicious Code Prevention. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | The Responsible Entity has implemented one or more documented process(es), but, where signatures or patterns are used, the Responsible Entity did not address testing the signatures or patterns. (3.3) | The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not mitigate the threat of detected malicious code. (3.2) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention, but where signatures or patterns are used, the Responsible Entity did not update malicious code protections. (3.3). | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R3. (R3). OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not deploy method(s) to deter, detect, or prevent malicious code. (3.1) | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2018-10-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | WECC-BC | [6 empty] | 30000000
CIP-007-6 (British Columbia) | 666700000010055 | R4. | 666700000010642 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Assessment, Same-Day Operations | Medium | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 22 calendar days of the prior review. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 30 calendar days of the prior review. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to generate alerts for necessary security events (as determined by the responsible entity) for the Applicable Systems (per device or system capability) but did not generate alerts for all of the required types of events described in 4.2.1 through 4.2.2. (4.2) OR The Responsible Entity has documented and implemented one or more process(es) to log applicable events identified in 4.1 (where technically feasible and except during CIP Exceptional Circumstances) but did not retain applicable event logs for at least the last 90 consecutive days. (4.3) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed two or more intervals. (4.4) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R4. (R4) OR The Responsible Entity has documented and implemented one or more process(es) to log events for the Applicable Systems (per device or system capability) but did not detect and log all of the required types of events described in 4.1.1 through 4.1.3. (4.1) | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2018-10-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | WECC-BC | [6 empty] | 40000000
CIP-007-6 (British Columbia) | 666700000010055 | R5. | 666700000010643 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R5 – System Access Controls. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 15 calendar months but less than or equal to 16 calendar months of the last password change. (5.6) | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 16 calendar months but less than or equal to 17 calendar months of the last password change. (5.6) | The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification or inventory of all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s). (5.2) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification of the individuals with authorized access to shared accounts. (5.3) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access that did not technically or procedurally enforce one of the two password parameters as described in 5.5.1 and 5.5.2. (5.5) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 17 calendar months but less than or equal to 18 calendar months of the last password change. (5.6) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R5. (R5) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access. (5.1) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access. (5.1) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but did not, per device capability, change known default passwords. (5.4) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but the Responsible Entity did not technically or procedurally enforce all of the password parameters described in 5.5.1 and 5.5.2. (5.5) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 18 calendar months of the last password change. (5.6) OR The Responsible Entity has implemented one or more documented process(es) for System Access Control but, where technically feasible, did not either limit the number of unsuccessful authentication attempts or generate alerts after a threshold of unsuccessful authentication attempts. (5.7) | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2018-10-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | WECC-BC | [6 empty] | 50000000
CIP-007-6 (Manitoba) | 77660000000513 | R1. | 776600000006092 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R1 – Ports and Services. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | The Responsible Entity has implemented and documented processes for Ports and Services but had no methods to protect against unnecessary physical input/output ports used for network connectivity, console commands, or removable media. (1.2) | The Responsible Entity has implemented and documented processes for determining necessary Ports and Services but, where technically feasible, had one or more unneeded logical network accessible ports enabled. (1.1) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R1. (R1) | M1. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP007-6 Table R1 – Ports and Services and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2017-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-MB | [6 empty] | 10000000
CIP-007-6 (Manitoba) | 77660000000513 | R2. | 776600000006093 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R2 – Security Patch Management. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 35 calendar days but less than 50 calendar days of the last evaluation for the source or sources identified. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 35 calendar days but less than 50 calendar days of the evaluation completion. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes, including the identification of sources, for tracking or evaluating cyber security patches for applicable Cyber Assets. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 50 calendar days but less than 65 calendar days of the last evaluation for the source or sources identified. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 50 calendar days but less than 65 calendar days of the evaluation completion. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for installing cyber security patches for applicable Cyber Assets. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 65 calendar days of the last evaluation for the source or sources identified. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 65 calendar days of the evaluation completion. (2.3) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R2. (R2) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch but did not implement the plan as created or revised within the timeframe specified in the plan. (2.4) | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R2 – Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2017-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-MB | [6 empty] | 20000000
CIP-007-6 (Manitoba) | 77660000000513 | R3. | 776600000006094 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R3 – Malicious Code Prevention. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | The Responsible Entity has implemented one or more documented process(es), but, where signatures or patterns are used, the Responsible Entity did not address testing the signatures or patterns. (3.3) | The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not mitigate the threat of detected malicious code. (3.2) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention, but where signatures or patterns are used, the Responsible Entity did not update malicious code protections. (3.3). | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R3. (R3). OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not deploy method(s) to deter, detect, or prevent malicious code. (3.1) | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2017-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-MB | [6 empty] | 30000000
CIP-007-6 (Manitoba) | 77660000000513 | R4. | 776600000006095 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Assessment, Same-Day Operations | Medium | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 22 calendar days of the prior review. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 30 calendar days of the prior review. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to generate alerts for necessary security events (as determined by the responsible entity) for the Applicable Systems (per device or system capability) but did not generate alerts for all of the required types of events described in 4.2.1 through 4.2.2. (4.2) OR The Responsible Entity has documented and implemented one or more process(es) to log applicable events identified in 4.1 (where technically feasible and except during CIP Exceptional Circumstances) but did not retain applicable event logs for at least the last 90 consecutive days. (4.3) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed two or more intervals. (4.4) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R4. (R4) OR The Responsible Entity has documented and implemented one or more process(es) to log events for the Applicable Systems (per device or system capability) but did not detect and log all of the required types of events described in 4.1.1 through 4.1.3. (4.1) | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2017-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-MB | [6 empty] | 40000000
CIP-007-6 (Manitoba) | 77660000000513 | R5. | 776600000006096 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R5 – System Access Controls. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 15 calendar months but less than or equal to 16 calendar months of the last password change. (5.6) | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 16 calendar months but less than or equal to 17 calendar months of the last password change. (5.6) | The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification or inventory of all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s). (5.2) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification of the individuals with authorized access to shared accounts. (5.3) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access that did not technically or procedurally enforce one of the two password parameters as described in 5.5.1 and 5.5.2. (5.5) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 17 calendar months but less than or equal to 18 calendar months of the last password change. (5.6) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R5. (R5) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access. (5.1) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access. (5.1) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but did not, per device capability, change known default passwords. (5.4) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but the Responsible Entity did not technically or procedurally enforce all of the password parameters described in 5.5.1 and 5.5.2. (5.5) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 18 calendar months of the last password change. (5.6) OR The Responsible Entity has implemented one or more documented process(es) for System Access Control but, where technically feasible, did not either limit the number of unsuccessful authentication attempts or generate alerts after a threshold of unsuccessful authentication attempts. (5.7) | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2017-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-MB | [6 empty] | 50000000
CIP-007-6 (Nova Scotia) | 78830000000513 | R1. | 788300000006092 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R1 – Ports and Services. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | The Responsible Entity has implemented and documented processes for Ports and Services but had no methods to protect against unnecessary physical input/output ports used for network connectivity, console commands, or removable media. (1.2) | The Responsible Entity has implemented and documented processes for determining necessary Ports and Services but, where technically feasible, had one or more unneeded logical network accessible ports enabled. (1.1) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R1. (R1) | M1. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP007-6 Table R1 – Ports and Services and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2017-01-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | NPCC-NS | [6 empty] | 10000000
CIP-007-6 (Nova Scotia) | 78830000000513 | R2. | 788300000006093 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R2 – Security Patch Management. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 35 calendar days but less than 50 calendar days of the last evaluation for the source or sources identified. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 35 calendar days but less than 50 calendar days of the evaluation completion. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes, including the identification of sources, for tracking or evaluating cyber security patches for applicable Cyber Assets. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 50 calendar days but less than 65 calendar days of the last evaluation for the source or sources identified. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 50 calendar days but less than 65 calendar days of the evaluation completion. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for installing cyber security patches for applicable Cyber Assets. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 65 calendar days of the last evaluation for the source or sources identified. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 65 calendar days of the evaluation completion. (2.3) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R2. (R2) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch but did not implement the plan as created or revised within the timeframe specified in the plan. (2.4) | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R2 – Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2017-01-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | NPCC-NS | [6 empty] | 20000000
CIP-007-6 (Nova Scotia) | 78830000000513 | R3. | 788300000006094 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R3 – Malicious Code Prevention. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | The Responsible Entity has implemented one or more documented process(es), but, where signatures or patterns are used, the Responsible Entity did not address testing the signatures or patterns. (3.3) | The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not mitigate the threat of detected malicious code. (3.2) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention, but where signatures or patterns are used, the Responsible Entity did not update malicious code protections. (3.3). | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R3. (R3). OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not deploy method(s) to deter, detect, or prevent malicious code. (3.1) | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2017-01-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | NPCC-NS | [6 empty] | 30000000
CIP-007-6 (Nova Scotia) | 78830000000513 | R4. | 788300000006095 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Assessment, Same-Day Operations | Medium | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 22 calendar days of the prior review. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 30 calendar days of the prior review. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to generate alerts for necessary security events (as determined by the responsible entity) for the Applicable Systems (per device or system capability) but did not generate alerts for all of the required types of events described in 4.2.1 through 4.2.2. (4.2) OR The Responsible Entity has documented and implemented one or more process(es) to log applicable events identified in 4.1 (where technically feasible and except during CIP Exceptional Circumstances) but did not retain applicable event logs for at least the last 90 consecutive days. (4.3) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed two or more intervals. (4.4) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R4. (R4) OR The Responsible Entity has documented and implemented one or more process(es) to log events for the Applicable Systems (per device or system capability) but did not detect and log all of the required types of events described in 4.1.1 through 4.1.3. (4.1) | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2017-01-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | NPCC-NS | [6 empty] | 40000000
CIP-007-6 (Nova Scotia) | 78830000000513 | R5. | 788300000006096 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R5 – System Access Controls. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 15 calendar months but less than or equal to 16 calendar months of the last password change. (5.6) | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 16 calendar months but less than or equal to 17 calendar months of the last password change. (5.6) | The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification or inventory of all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s). (5.2) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification of the individuals with authorized access to shared accounts. (5.3) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access that did not technically or procedurally enforce one of the two password parameters as described in 5.5.1 and 5.5.2. (5.5) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 17 calendar months but less than or equal to 18 calendar months of the last password change. (5.6) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R5. (R5) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access. (5.1) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access. (5.1) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but did not, per device capability, change known default passwords. (5.4) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but the Responsible Entity did not technically or procedurally enforce all of the password parameters described in 5.5.1 and 5.5.2. (5.5) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 18 calendar months of the last password change. (5.6) OR The Responsible Entity has implemented one or more documented process(es) for System Access Control but, where technically feasible, did not either limit the number of unsuccessful authentication attempts or generate alerts after a threshold of unsuccessful authentication attempts. (5.7) | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2017-01-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | NPCC-NS | [6 empty] | 50000000
CIP-007-6 (Ontario) | 79780000513 | R1. | 79780006092 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R1 – Ports and Services. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | The Responsible Entity has implemented and documented processes for Ports and Services but had no methods to protect against unnecessary physical input/output ports used for network connectivity, console commands, or removable media. (1.2) | The Responsible Entity has implemented and documented processes for determining necessary Ports and Services but, where technically feasible, had one or more unneeded logical network accessible ports enabled. (1.1) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R1. (R1) | &lt;p&gt;M1. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP007-6 Table R1 – Ports and Services and additional evidence to demonstrate implementation as described in the Measures column of the table.&lt;/p&gt; | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | NPCC-ON | [6 empty] | 10000000
CIP-007-6 (Ontario) | 79780000513 | R2. | 79780006093 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R2 – Security Patch Management. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 35 calendar days but less than 50 calendar days of the last evaluation for the source or sources identified. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 35 calendar days but less than 50 calendar days of the evaluation completion. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes, including the identification of sources, for tracking or evaluating cyber security patches for applicable Cyber Assets. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 50 calendar days but less than 65 calendar days of the last evaluation for the source or sources identified. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 50 calendar days but less than 65 calendar days of the evaluation completion. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for installing cyber security patches for applicable Cyber Assets. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 65 calendar days of the last evaluation for the source or sources identified. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 65 calendar days of the evaluation completion. (2.3) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R2. (R2) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch but did not implement the plan as created or revised within the timeframe specified in the plan. (2.4) | &lt;p&gt;Evidence must include each of the applicable documented processes that collectively include each of &lt;br/&gt;the applicable requirement parts in CIP-007-6 Table R2 – Security Patch Management and additional evidence to &lt;br/&gt;demonstrate implementation as described in the Measures column of the table.&lt;/p&gt; &lt;p/&gt; | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | NPCC-ON | [6 empty] | 20000000
CIP-007-6 (Ontario) | 79780000513 | R3. | 79780006094 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R3 – Malicious Code Prevention. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | The Responsible Entity has implemented one or more documented process(es), but, where signatures or patterns are used, the Responsible Entity did not address testing the signatures or patterns. (3.3) | The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not mitigate the threat of detected malicious code. (3.2) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention, but where signatures or patterns are used, the Responsible Entity did not update malicious code protections. (3.3). | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R3. (R3). OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not deploy method(s) to deter, detect, or prevent malicious code. (3.1) | &lt;p&gt;Evidence must include each of the documented processes that collectively include each of the &lt;br/&gt;applicable requirement parts in CIP-007-6 Table R3 – Malicious Code Prevention and additional evidence to demonstrate &lt;br/&gt;implementation as described in the Measures column of the table.&lt;/p&gt; &lt;p/&gt; | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | NPCC-ON | [6 empty] | 30000000
CIP-007-6 (Ontario) | 79780000513 | R4. | 79780006095 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Assessment, Same-Day Operations | Medium | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 22 calendar days of the prior review. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 30 calendar days of the prior review. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to generate alerts for necessary security events (as determined by the responsible entity) for the Applicable Systems (per device or system capability) but did not generate alerts for all of the required types of events described in 4.2.1 through 4.2.2. (4.2) OR The Responsible Entity has documented and implemented one or more process(es) to log applicable events identified in 4.1 (where technically feasible and except during CIP Exceptional Circumstances) but did not retain applicable event logs for at least the last 90 consecutive days. (4.3) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed two or more intervals. (4.4) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R4. (R4) OR The Responsible Entity has documented and implemented one or more process(es) to log events for the Applicable Systems (per device or system capability) but did not detect and log all of the required types of events described in 4.1.1 through 4.1.3. (4.1) | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | NPCC-ON | [6 empty] | 40000000
CIP-007-6 (Ontario) | 79780000513 | R5. | 79780006096 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R5 – System Access Controls. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 15 calendar months but less than or equal to 16 calendar months of the last password change. (5.6) | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 16 calendar months but less than or equal to 17 calendar months of the last password change. (5.6) | The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification or inventory of all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s). (5.2) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification of the individuals with authorized access to shared accounts. (5.3) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access that did not technically or procedurally enforce one of the two password parameters as described in 5.5.1 and 5.5.2. (5.5) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 17 calendar months but less than or equal to 18 calendar months of the last password change. (5.6) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R5. (R5) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access. (5.1) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access. (5.1) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but did not, per device capability, change known default passwords. (5.4) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but the Responsible Entity did not technically or procedurally enforce all of the password parameters described in 5.5.1 and 5.5.2. (5.5) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 18 calendar months of the last password change. (5.6) OR The Responsible Entity has implemented one or more documented process(es) for System Access Control but, where technically feasible, did not either limit the number of unsuccessful authentication attempts or generate alerts after a threshold of unsuccessful authentication attempts. (5.7) | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | NPCC-ON | [6 empty] | 50000000
CIP-007-6 (Saskatchewan) | 83750000000513 | R1. | 837500000006092 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R1 – Ports and Services. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | The Responsible Entity has implemented and documented processes for Ports and Services but had no methods to protect against unnecessary physical input/output ports used for network connectivity, console commands, or removable media. (1.2) | The Responsible Entity has implemented and documented processes for determining necessary Ports and Services but, where technically feasible, had one or more unneeded logical network accessible ports enabled. (1.1) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R1. (R1) | M1. Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP007-6 Table R1 – Ports and Services and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-SK | [6 empty] | 10000000
CIP-007-6 (Saskatchewan) | 83750000000513 | R2. | 837500000006093 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R2 – Security Patch Management. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 35 calendar days but less than 50 calendar days of the last evaluation for the source or sources identified. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 35 calendar days but less than 50 calendar days of the evaluation completion. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes, including the identification of sources, for tracking or evaluating cyber security patches for applicable Cyber Assets. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 50 calendar days but less than 65 calendar days of the last evaluation for the source or sources identified. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 50 calendar days but less than 65 calendar days of the evaluation completion. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for installing cyber security patches for applicable Cyber Assets. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 65 calendar days of the last evaluation for the source or sources identified. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 65 calendar days of the evaluation completion. (2.3) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R2. (R2) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch but did not implement the plan as created or revised within the timeframe specified in the plan. (2.4) | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R2 – Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-SK | [6 empty] | 20000000
CIP-007-6 (Saskatchewan) | 83750000000513 | R3. | 837500000006094 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R3 – Malicious Code Prevention. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | The Responsible Entity has implemented one or more documented process(es), but, where signatures or patterns are used, the Responsible Entity did not address testing the signatures or patterns. (3.3) | The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not mitigate the threat of detected malicious code. (3.2) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention, but where signatures or patterns are used, the Responsible Entity did not update malicious code protections. (3.3). | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R3. (R3). OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not deploy method(s) to deter, detect, or prevent malicious code. (3.1) | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-SK | [6 empty] | 30000000
CIP-007-6 (Saskatchewan) | 83750000000513 | R4. | 837500000006095 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Assessment, Same-Day Operations | Medium | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 22 calendar days of the prior review. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 30 calendar days of the prior review. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to generate alerts for necessary security events (as determined by the responsible entity) for the Applicable Systems (per device or system capability) but did not generate alerts for all of the required types of events described in 4.2.1 through 4.2.2. (4.2) OR The Responsible Entity has documented and implemented one or more process(es) to log applicable events identified in 4.1 (where technically feasible and except during CIP Exceptional Circumstances) but did not retain applicable event logs for at least the last 90 consecutive days. (4.3) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed two or more intervals. (4.4) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R4. (R4) OR The Responsible Entity has documented and implemented one or more process(es) to log events for the Applicable Systems (per device or system capability) but did not detect and log all of the required types of events described in 4.1.1 through 4.1.3. (4.1) | M4. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-SK | [6 empty] | 40000000
CIP-007-6 (Saskatchewan) | 83750000000513 | R5. | 837500000006096 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R5 – System Access Controls. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 15 calendar months but less than or equal to 16 calendar months of the last password change. (5.6) | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 16 calendar months but less than or equal to 17 calendar months of the last password change. (5.6) | The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification or inventory of all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s). (5.2) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification of the individuals with authorized access to shared accounts. (5.3) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access that did not technically or procedurally enforce one of the two password parameters as described in 5.5.1 and 5.5.2. (5.5) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 17 calendar months but less than or equal to 18 calendar months of the last password change. (5.6) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R5. (R5) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access. (5.1) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access. (5.1) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but did not, per device capability, change known default passwords. (5.4) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but the Responsible Entity did not technically or procedurally enforce all of the password parameters described in 5.5.1 and 5.5.2. (5.5) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 18 calendar months of the last password change. (5.6) OR The Responsible Entity has implemented one or more documented process(es) for System Access Control but, where technically feasible, did not either limit the number of unsuccessful authentication attempts or generate alerts after a threshold of unsuccessful authentication attempts. (5.7) | M5. Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-6 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | MRO-SK | [6 empty] | 50000000
CIP-007-7 | ST-2024-05-10-0000007 | R1. | RQ-2024-05-10-0000022 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-7 Table R1 – System Hardening. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | The Responsible Entity did not document one or more process(es) that included the applicable items in CIP-007-7 Table R1. (Requirement R1 | The Responsible Entity had no methods to protect against unnecessary physical input/output ports used for network connectivity, console commands, or Removable Media. (Part 1.2) | The Responsible Entity had one or more unneeded logical network accessible ports or network accessible services enabled. (Part 1.1) OR The Responsible Entity has not prevented the sharing of the CPU and memory resources between VCAs that are, or are associated with, a Medium or High Impact BCS, and VCAs that are not, or are not associated with a Medium or High Impact BCS. (Part 1.3) | The Responsible Entity neither implemented nor documented one or more process(es) that included the applicable items in CIP-007-6 Table R1. (Requirement R1) | Evidence must include the documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R1 – System Hardening and additional evidence to demonstrate implementation as described in the Measures column of the table. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-007-7 | ST-2024-05-10-0000007 | R2. | RQ-2024-05-10-0000023 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-7 Table R2 – Cyber Security Patch Management. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity did not evaluate the cyber security patches for applicability within 35 calendar days but less than 50 calendar days of the last evaluation for the source or sources identified. (Part 2.2) OR The Responsible Entity did not apply the applicable cyber security patches, create a dated mitigation plan, or revise an existing mitigation plan within 35 calendar days but less than 50 calendar days of the evaluation completion. (Part 2.3) | The Responsible Entity did not include any processes, including the identification of sources, for tracking or evaluating cyber security patches for Applicable Systems. (Part 2.1) OR The Responsible Entity did not evaluate the cyber security patches for applicability within 50 calendar days but less than 65 calendar days of the last evaluation for the source or sources identified. (Part 2.2) OR The Responsible Entity did not apply the applicable cyber security patches, create a dated mitigation plan, or revise an existing mitigation plan within 50 calendar days but less than 65 calendar days of the evaluation completion. (Part 2.3) | The Responsible Entity did not include any processes for installing cyber security patches for Applicable Systems. (Part 2.1) OR The Responsible Entity did not evaluate the cyber security patches for applicability within 65 calendar days of the last evaluation for the source or sources identified. (Part 2.2) OR The Responsible Entity did not apply the applicable cyber security patches, create a dated mitigation plan, or revise an existing mitigation plan within 65 calendar days of the evaluation completion. (Part 2.3) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-7 Table R2. (Requirement R2) OR The Responsible Entity did not include any processes for tracking, evaluating, or installing cyber security patches for applicable Cyber Assets. (Part 2.1) OR 1. The Responsible Entity did not obtain approval by the CIP Senior Manager or delegate. (Part 2.4) OR The Responsible Entity did not implement the plan as created or revised within the timeframe specified in the plan. (Part 2.4) | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R2 – Cyber Security Patch Management and additional evidence to demonstrate implementation as described in the Measures column of the table. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-007-7 | ST-2024-05-10-0000007 | R3. | RQ-2024-05-10-0000024 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-7 Table R3 – Malicious Code Prevention. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Same-Day Operations | Medium | N/A | The Responsible Entity, where signatures or patterns are used, the Responsible Entity did not address testing the signatures or patterns. (Part 3.3) | The Responsible Entity did not mitigate the threat of detected malicious code. (Part 3.2) OR The Responsible Entity, where signatures or patterns are used, the Responsible Entity did not update malicious code protections. (Part 3.3). | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R3. (Requirement R3). OR The Responsible Entity did not deploy method(s) to deter, detect, or prevent malicious code. (Part 3.1) | M1. Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R3 – Malicious Code Prevention and additional evidence to demonstrate implementation as described in the Measures column of the table. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-007-7 | ST-2024-05-10-0000007 | R4. | RQ-2024-05-10-0000025 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-7 Table R4 – Security Event Monitoring. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Assessment, Same-Day Operations | Medium | The Responsible Entity missed one of 15 calendar day interval and completed the review within 22 calendar days of the prior review. (Part 4.4) | The Responsible Entity missed one 15 calendar day interval and completed the review within 30 calendar days of the prior review. (Part 4.4) | The Responsible Entity did not generate alerts for all of the required types of security events described in 4.2.1 through 4.2.2. (Part 4.2) OR The Responsible Entity did not retain applicable security event logs for at least the last 90 consecutive days. (Part 4.3) OR The Responsible Entity missed two or more 15 calendar day intervals. (Part 4.4) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R4. (Requirement R4) OR The Responsible Entity, per system capability, did not detect and log all of the required types of events described in 4.1.1 through 4.1.3. (Part 4.1) | Evidence must include each of the documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table R4 – Security Event Monitoring and additional evidence to demonstrate implementation as described in the Measures column of the table. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-007-7 | ST-2024-05-10-0000007 | R5. | RQ-2024-05-10-0000026 | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-7 Table R5 – System Access Controls. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning | Medium | The Responsible Entity did not technically or procedurally enforce password changes or an obligation to change the password within 15 calendar months but less than or equal to 16 calendar months of the last password change. (Part 5.6) | The Responsible Entity did not technically or procedurally enforce password changes or an obligation to change the password within 16 calendar months but less than or equal to 17 calendar months of the last password change. (Part 5.6) | The Responsible Entity did not include the identification or inventory of all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s). (Part 5.2) OR The Responsible Entity did not include the identification of the individuals with authorized access to shared accounts. (Part 5.3) OR The Responsible Entity did not technically or procedurally enforce one of the two password parameters as described in 5.5.1 and 5.5.2. (Part 5.5) OR The Responsible Entity process(es) for password-only authentication for interactive user access did not technically or procedurally enforce one of the two password parameters as described in 5.5.1 and 5.5.2. (Part 5.5) OR The Responsible Entity did not technically or procedurally enforce password changes or an obligation to change the password within 17 calendar months but less than or equal to 18 calendar months of the last password change. (Part 5.6) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R5. (Requirement R5) OR The Responsible Entity does not have a method(s) to enforce authentication of interactive user access. (Part 5.1) OR The Responsible Entity does not have a method(s) to enforce authentication of interactive user access. (Part 5.1) OR The Responsible Entity did not, per device capability, change known default passwords. (Part 5.4) OR The Responsible Entity did not technically or procedurally enforce all of the password parameters described in 5.5.1 and 5.5.2. (Part 5.5) OR The Responsible Entity did not technically or procedurally enforce password changes or an obligation to change the password within 18 calendar months of the last password change. (Part 5.6) OR The Responsible Entity neither limited the number of unsuccessful authentication attempts nor generated alerts after a threshold of unsuccessful authentication attempts. (Part 5.7) | Evidence must include each of the applicable documented processes that collectively include each of the applicable requirement parts in CIP-007-7 Table 5 – System Access Controls and additional evidence to demonstrate implementation as described in the Measures column of the table. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-007-AB-5 (Alberta) | 656600000009011 | R1. | 656600000009106 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP]007-AB]5 Table R1 - Ports and Services. |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 10000000
CIP-007-AB-5 (Alberta) | 656600000009011 | R2. | 656600000009107 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP]007-AB]5 Table R2 - Security Patch Management. |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 20000000
CIP-007-AB-5 (Alberta) | 656600000009011 | R3. | 656600000009108 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP]007-AB]5 Table R3 - Malicious Code Prevention. |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 30000000
CIP-007-AB-5 (Alberta) | 656600000009011 | R4. | 656600000009109 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP]007-AB]5 Table R4 - Security Event Monitoring. |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 40000000
CIP-007-AB-5 (Alberta) | 656600000009011 | R5. | 656600000009110 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP]007-AB]5 Table R5 - System Access Controls. |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 50000000
CIP-008-1 | 30 | R1. | 427 | Cyber Security Incident Response Plan — The Responsible Entity shall develop and maintain a Cyber Security Incident response plan. The Cyber Security Incident Response plan shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-008-1 | 30 | R2. | 434 | Cyber Security Incident Documentation — The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-008-1 (British Columbia) | 666700000010056 | R1. | 666700000010644 | Cyber Security Incident Response Plan — The Responsible Entity shall develop and maintain a Cyber Security Incident response plan. The Cyber Security Incident Response plan shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-008-1 (British Columbia) | 666700000010056 | R2. | 666700000010645 | Cyber Security Incident Documentation — The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 20000000
CIP-008-1 (Ontario) | 79780000030 | R1. | 79780000427 | Cyber Security Incident Response Plan — The Responsible Entity shall develop and maintain a Cyber Security Incident response plan. The Cyber Security Incident Response plan shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | N/A | The Responsible Entity has developed but not maintained a Cyber Security Incident response plan. | The Responsible Entity has developed a Cyber Security Incident response plan but the plan does not address one or more of the subrequirements R1.1 through R1.6 | The Responsible Entity has not developed a Cyber Security Incident response plan. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-008-1 (Ontario) | 79780000030 | R2. | 79780000434 | Cyber Security Incident Documentation — The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity has kept relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for two but less than three calendar years. | The Responsible Entity has kept relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for less than two calendar years. | The Responsible Entity has kept relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for less than one calendar year. | The Responsible Entity has not kept relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-008-2 | 214 | R1. | 2505 | Cyber Security Incident Response Plan — The Responsible Entity shall develop and maintain a Cyber Security Incident response plan and implement the plan in response to Cyber Security Incidents. The Cyber Security Incident response plan shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-008-2 | 214 | R2. | 2512 | Cyber Security Incident Documentation — The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Planning, Real-Time Operations | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  | CIP-008-1 R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-008-2 (Ontario) | 79780000214 | R1. | 79780002505 | Cyber Security Incident Response Plan — The Responsible Entity shall develop and maintain a Cyber Security Incident response plan and implement the plan in response to Cyber Security Incidents. The Cyber Security Incident response plan shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-008-2 (Ontario) | 79780000214 | R2. | 79780002512 | Cyber Security Incident Documentation — The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Planning, Real-Time Operations | Low |  |  |  |  | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-5 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-008-3 | 228 | R1. | 2866 | Cyber Security Incident Response Plan — The Responsible Entity shall develop and maintain a Cyber Security Incident response plan and implement the plan in response to Cyber Security Incidents. The Cyber Security Incident response plan shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Planning, Real-Time Operations | Low |  |  |  |  | The Responsible Entity shall make available its Cyber Security Incident response plan as indicated in Requirement R1 and documentation of the review, updating, and testing of the plan. | 2010-10-01 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-008-3 | 228 | R2. | 2873 | Cyber Security Incident Documentation — The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Assessment | Low |  |  |  |  | The Responsible Entity shall make available all documentation as specified in Requirement R2. | 2010-10-01 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-008-3 (British Columbia) | 666700000010057 | R1. | 666700000010646 | Cyber Security Incident Response Plan — The Responsible Entity shall develop and maintain a Cyber Security Incident response plan and implement the plan in response to Cyber Security Incidents. The Cyber Security Incident response plan shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Planning, Real-Time Operations | Low |  |  |  |  | The Responsible Entity shall make available its Cyber Security Incident response plan as indicated in Requirement R1 and documentation of the review, updating, and testing of the plan. | 2012-07-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-008-3 (British Columbia) | 666700000010057 | R2. | 666700000010647 | Cyber Security Incident Documentation — The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Assessment | Low |  |  |  |  | The Responsible Entity shall make available all documentation as specified in Requirement R2. | 2012-07-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 20000000
CIP-008-3 (Manitoba) | 77660000000228 | R1. | 776600000002866 | Cyber Security Incident Response Plan — The Responsible Entity shall develop and maintain a Cyber Security Incident response plan and implement the plan in response to Cyber Security Incidents. The Cyber Security Incident response plan shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Planning, Real-Time Operations | Low |  |  |  |  | The Responsible Entity shall make available its Cyber Security Incident response plan as indicated in Requirement R1 and documentation of the review, updating, and testing of the plan. | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
CIP-008-3 (Manitoba) | 77660000000228 | R2. | 776600000002873 | Cyber Security Incident Documentation — The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Assessment | Low |  |  |  |  | The Responsible Entity shall make available all documentation as specified in Requirement R2. | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
CIP-008-3 (Ontario) | 79780000228 | R1. | 79780002866 | Cyber Security Incident Response Plan — The Responsible Entity shall develop and maintain a Cyber Security Incident response plan and implement the plan in response to Cyber Security Incidents. The Cyber Security Incident response plan shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Planning, Real-Time Operations | Low | N/A | N/A | The Responsible Entity has developed a Cyber Security Incident response plan that addresses all of the components required by R1.1 through R1.6 but has not maintained the plan in accordance with those components. | The Responsible Entity has not developed a Cyber Security Incident response plan that addresses all of the components required by R1.1 through R1.6, or has not implemented the plan in response to a Cyber Security Incident. | M2.1. Examples of evidence may include, but are not limited to, dated evidence of a lessons-learned report that includes a summary of the test or a compilation of notes, logs, and communication resulting from the test. Types of exercises may include discussion or operations based exercises. | 2010-10-01 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-008-3 (Ontario) | 79780000228 | R2. | 79780002873 | Cyber Security Incident Documentation — The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Assessment | Low | N/A | N/A | N/A | The Responsible Entity has not kept relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for at least three calendar years. |  | 2010-10-01 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-008-4 | 254 | R1. | 3355 | Cyber Security Incident Response Plan — The Responsible Entity shall develop and maintain a Cyber Security Incident response plan and implement the plan in response to Cyber Security Incidents. The Cyber Security Incident response plan shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Assessment | Low | N/A | N/A | The Responsible Entity has developed a Cyber Security Incident response plan that addresses all of the components required by R1.1 through R1.6 but has not maintained the plan in accordance with those components. | The Responsible Entity has not developed a Cyber Security Incident response plan that addresses all of the components required by R1.1 through R1.6, or has not implemented the plan in response to a Cyber Security Incident. | M3.2. An example of evidence may include, but is not limited to: 1. Dated and revised Cyber Security Incident response plan with changes to the roles or responsibilities, responders or technology; and 2. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-008-4 | 254 | R2. | 3362 | Cyber Security Incident Documentation — The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity has not kept relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for at least three calendar years. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-008-4 (Ontario) | 79780000254 | R1. | 79780003355 | Cyber Security Incident Response Plan — The Responsible Entity shall develop and maintain a Cyber Security Incident response plan and implement the plan in response to Cyber Security Incidents. The Cyber Security Incident response plan shall address, at a minimum, the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Operations Assessment | Low | N/A | N/A | The Responsible Entity has developed a Cyber Security Incident response plan that addresses all of the components required by R1.1 through R1.6 but has not maintained the plan in accordance with those components. | The Responsible Entity has not developed a Cyber Security Incident response plan that addresses all of the components required by R1.1 through R1.6, or has not implemented the plan in response to a Cyber Security Incident. | M3.2. An example of evidence may include, but is not limited to:&lt;br/&gt;1. Dated and revised Cyber Security Incident response plan with changes to the roles or responsibilities, responders or technology; and&lt;br/&gt;2. Evidence of plan update distribution including, but not limited to:&lt;br/&gt;• Emails;&lt;br/&gt;• USPS or other mail service;&lt;br/&gt;• Electronic distribution system; or &lt;br/&gt;• Training sign-in sheets. | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-008-4 (Ontario) | 79780000254 | R2. | 79780003362 | Cyber Security Incident Documentation — The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity has not kept relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for at least three calendar years. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-008-5 | 352 | R1. | 4501 | Each Responsible Entity shall document one or more Cyber Security Incident response plan(s) that collectively include each of the applicable requirement parts in CIP-008-5 Table R1 – Cyber Security Incident Response Plan Specifications. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Low | N/A | N/A | The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include the roles and responsibilities of Cyber Security Incident response groups or individuals. (1.3) OR The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include incident handling procedures for Cyber Security Incidents. (1.4) | The Responsible Entity has not developed a Cyber Security Incident response plan with one or more processes to identify, classify, and respond to Cyber Security Incidents. (1.1) OR The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes to identify Reportable Cyber Security Incidents. (1.2) OR The Responsible Entity has developed a Cyber Security Incident response plan, but did not provide at least preliminary notification to ES-ISAC within one hour from identification of a Reportable Cyber Security Incident. (1.2) | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-5 Table R1 – Cyber Security Incident Response Plan Specifications. | 2016-07-01 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-008-5 | 352 | R2. | 4502 | Each Responsible Entity shall implement each of its documented Cyber Security Incident response plans to collectively include each of the applicable requirement parts in CIP-008-5 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations | Low | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 15 calendar months, not exceeding 16 calendar months between tests of the plan. (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 16 calendar months, not exceeding 17 calendar months between tests of the plan. (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 17 calendar months, not exceeding 18 calendar months between tests of the plan. (2.1) OR The Responsible Entity did not document deviations, if any, from the plan during a test or when a Reportable Cyber Security Incident occurs. (2.2) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 19 calendar months between tests of the plan. (2.1) OR The Responsible Entity did not retain relevant records related to Reportable Cyber Security Incidents. (2.3) | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-5 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | 2016-07-01 |  | 2020-12-31 |  | 1.2 High Impact BES Cyber Systems and their associated: • EACMS Medium Impact BES Cyber Systems and their associated: • EACMS |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-008-5 | 352 | R3. | 4503 | Each Responsible Entity shall maintain each of its Cyber Security Incident response plans according to each of the applicable requirement parts in CIP-008-5 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Assessment | Low | The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within greater than 90 but less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) | The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) OR The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) OR The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 60 and less than 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) Roles or responsibilities, or Cyber Security Incident response groups or individuals, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) or The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) or The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) Roles or responsibilities, or Cyber Security Incident response groups or individuals, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) | Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-5 Table R3 – Cyber Security Incident. | 2016-07-01 |  | 2020-12-31 |  | 1.3 High Impact BES Cyber Systems and their associated: • EACMS Medium Impact BES Cyber Systems and their associated: • EACMS |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-008-5 (British Columbia) | 666700000010058 | R1. | 666700000010648 | Each Responsible Entity shall document one or more Cyber Security Incident response plan(s) that collectively include each of the applicable requirement parts in CIP-008-5 Table R1 – Cyber Security Incident Response Plan Specifications. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Low | N/A | N/A | The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include the roles and responsibilities of Cyber Security Incident response groups or individuals. (1.3) OR The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include incident handling procedures for Cyber Security Incidents. (1.4) | The Responsible Entity has not developed a Cyber Security Incident response plan with one or more processes to identify, classify, and respond to Cyber Security Incidents. (1.1) OR The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes to identify Reportable Cyber Security Incidents. (1.2) OR The Responsible Entity has developed a Cyber Security Incident response plan, but did not provide at least preliminary notification to ES-ISAC within one hour from identification of a Reportable Cyber Security Incident. (1.2) | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-5 Table R1 – Cyber Security Incident Response Plan Specifications. | 2018-10-01 |  | 2023-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | WECC-BC | [6 empty] | 10000000
CIP-008-5 (British Columbia) | 666700000010058 | R2. | 666700000010649 | Each Responsible Entity shall implement each of its documented Cyber Security Incident response plans to collectively include each of the applicable requirement parts in CIP-008-5 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations | Low | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 15 calendar months, not exceeding 16 calendar months between tests of the plan. (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 16 calendar months, not exceeding 17 calendar months between tests of the plan. (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 17 calendar months, not exceeding 18 calendar months between tests of the plan. (2.1) OR The Responsible Entity did not document deviations, if any, from the plan during a test or when a Reportable Cyber Security Incident occurs. (2.2) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 19 calendar months between tests of the plan. (2.1) OR The Responsible Entity did not retain relevant records related to Reportable Cyber Security Incidents. (2.3) | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-5 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | 2018-10-01 |  | 2023-03-31 |  | 1.2 High Impact BES Cyber Systems and their associated: • EACMS Medium Impact BES Cyber Systems and their associated: • EACMS |  | WECC-BC | [6 empty] | 20000000
CIP-008-5 (British Columbia) | 666700000010058 | R3. | 666700000010650 | Each Responsible Entity shall maintain each of its Cyber Security Incident response plans according to each of the applicable requirement parts in CIP-008-5 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Assessment | Low | The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within greater than 90 but less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) | The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) OR The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) OR The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 60 and less than 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) Roles or responsibilities, or Cyber Security Incident response groups or individuals, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) or The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) or The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) Roles or responsibilities, or Cyber Security Incident response groups or individuals, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) | Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-5 Table R3 – Cyber Security Incident. | 2018-10-01 |  | 2023-03-31 |  | 1.3 High Impact BES Cyber Systems and their associated: • EACMS Medium Impact BES Cyber Systems and their associated: • EACMS |  | WECC-BC | [6 empty] | 30000000
CIP-008-5 (Manitoba) | 77660000000352 | R1. | 776600000004501 | Each Responsible Entity shall document one or more Cyber Security Incident response plan(s) that collectively include each of the applicable requirement parts in CIP-008-5 Table R1 – Cyber Security Incident Response Plan Specifications. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Low | N/A | N/A | The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include the roles and responsibilities of Cyber Security Incident response groups or individuals. (1.3) OR The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include incident handling procedures for Cyber Security Incidents. (1.4) | The Responsible Entity has not developed a Cyber Security Incident response plan with one or more processes to identify, classify, and respond to Cyber Security Incidents. (1.1) OR The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes to identify Reportable Cyber Security Incidents. (1.2) OR The Responsible Entity has developed a Cyber Security Incident response plan, but did not provide at least preliminary notification to ES-ISAC within one hour from identification of a Reportable Cyber Security Incident. (1.2) | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-5 Table R1 – Cyber Security Incident Response Plan Specifications. | 2017-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | MRO-MB | [6 empty] | 10000000
CIP-008-5 (Manitoba) | 77660000000352 | R2. | 776600000004502 | Each Responsible Entity shall implement each of its documented Cyber Security Incident response plans to collectively include each of the applicable requirement parts in CIP-008-5 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations | Low | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 15 calendar months, not exceeding 16 calendar months between tests of the plan. (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 16 calendar months, not exceeding 17 calendar months between tests of the plan. (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 17 calendar months, not exceeding 18 calendar months between tests of the plan. (2.1) OR The Responsible Entity did not document deviations, if any, from the plan during a test or when a Reportable Cyber Security Incident occurs. (2.2) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 19 calendar months between tests of the plan. (2.1) OR The Responsible Entity did not retain relevant records related to Reportable Cyber Security Incidents. (2.3) | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-5 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | 2017-07-01 |  |  |  | 1.2 High Impact BES Cyber Systems and their associated: • EACMS Medium Impact BES Cyber Systems and their associated: • EACMS |  | MRO-MB | [6 empty] | 20000000
CIP-008-5 (Manitoba) | 77660000000352 | R3. | 776600000004503 | Each Responsible Entity shall maintain each of its Cyber Security Incident response plans according to each of the applicable requirement parts in CIP-008-5 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Assessment | Low | The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within greater than 90 but less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) | The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) OR The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) OR The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 60 and less than 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) Roles or responsibilities, or Cyber Security Incident response groups or individuals, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) or The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) or The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) Roles or responsibilities, or Cyber Security Incident response groups or individuals, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) | Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-5 Table R3 – Cyber Security Incident. | 2017-07-01 |  |  |  | 1.3 High Impact BES Cyber Systems and their associated: • EACMS Medium Impact BES Cyber Systems and their associated: • EACMS |  | MRO-MB | [6 empty] | 30000000
CIP-008-5 (Nova Scotia) | 78830000000352 | R1. | 788300000004501 | Each Responsible Entity shall document one or more Cyber Security Incident response plan(s) that collectively include each of the applicable requirement parts in CIP-008-5 Table R1 – Cyber Security Incident Response Plan Specifications. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Low | N/A | N/A | The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include the roles and responsibilities of Cyber Security Incident response groups or individuals. (1.3) OR The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include incident handling procedures for Cyber Security Incidents. (1.4) | The Responsible Entity has not developed a Cyber Security Incident response plan with one or more processes to identify, classify, and respond to Cyber Security Incidents. (1.1) OR The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes to identify Reportable Cyber Security Incidents. (1.2) OR The Responsible Entity has developed a Cyber Security Incident response plan, but did not provide at least preliminary notification to ES-ISAC within one hour from identification of a Reportable Cyber Security Incident. (1.2) | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-5 Table R1 – Cyber Security Incident Response Plan Specifications. | 2016-10-01 |  | 2021-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | NPCC-NS | [6 empty] | 10000000
CIP-008-5 (Nova Scotia) | 78830000000352 | R2. | 788300000004502 | Each Responsible Entity shall implement each of its documented Cyber Security Incident response plans to collectively include each of the applicable requirement parts in CIP-008-5 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations | Low | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 15 calendar months, not exceeding 16 calendar months between tests of the plan. (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 16 calendar months, not exceeding 17 calendar months between tests of the plan. (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 17 calendar months, not exceeding 18 calendar months between tests of the plan. (2.1) OR The Responsible Entity did not document deviations, if any, from the plan during a test or when a Reportable Cyber Security Incident occurs. (2.2) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 19 calendar months between tests of the plan. (2.1) OR The Responsible Entity did not retain relevant records related to Reportable Cyber Security Incidents. (2.3) | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-5 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | 2016-10-01 |  | 2021-06-30 |  | 1.2 High Impact BES Cyber Systems and their associated: • EACMS Medium Impact BES Cyber Systems and their associated: • EACMS |  | NPCC-NS | [6 empty] | 20000000
CIP-008-5 (Nova Scotia) | 78830000000352 | R3. | 788300000004503 | Each Responsible Entity shall maintain each of its Cyber Security Incident response plans according to each of the applicable requirement parts in CIP-008-5 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Assessment | Low | The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within greater than 90 but less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) | The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) OR The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) OR The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 60 and less than 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) Roles or responsibilities, or Cyber Security Incident response groups or individuals, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) or The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) or The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) Roles or responsibilities, or Cyber Security Incident response groups or individuals, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) | Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-5 Table R3 – Cyber Security Incident. | 2016-10-01 |  | 2021-06-30 |  | 1.3 High Impact BES Cyber Systems and their associated: • EACMS Medium Impact BES Cyber Systems and their associated: • EACMS |  | NPCC-NS | [6 empty] | 30000000
CIP-008-5 (Ontario) | 79780000352 | R1. | 79780004501 | Each Responsible Entity shall document one or more Cyber Security Incident response plan(s) that collectively include each of the applicable requirement parts in CIP-008-5 Table R1 – Cyber Security Incident Response Plan Specifications. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Low | N/A | N/A | The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include the roles and responsibilities of Cyber Security Incident response groups or individuals. (1.3) OR The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include incident handling procedures for Cyber Security Incidents. (1.4) | The Responsible Entity has not developed a Cyber Security Incident response plan with one or more processes to identify, classify, and respond to Cyber Security Incidents. (1.1) OR The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes to identify Reportable Cyber Security Incidents. (1.2) OR The Responsible Entity has developed a Cyber Security Incident response plan, but did not provide at least preliminary notification to ES-ISAC within one hour from identification of a Reportable Cyber Security Incident. (1.2) | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-5 Table R1 – Cyber Security Incident Response Plan Specifications. | 2016-07-01 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | NPCC-ON | [6 empty] | 10000000
CIP-008-5 (Ontario) | 79780000352 | R2. | 79780004502 | Each Responsible Entity shall implement each of its documented Cyber Security Incident response plans to collectively include each of the applicable requirement parts in CIP-008-5 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations | Low | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 15 calendar months, not exceeding 16 calendar months between tests of the plan. (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 16 calendar months, not exceeding 17 calendar months between tests of the plan. (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 17 calendar months, not exceeding 18 calendar months between tests of the plan. (2.1) OR The Responsible Entity did not document deviations, if any, from the plan during a test or when a Reportable Cyber Security Incident occurs. (2.2) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 19 calendar months between tests of the plan. (2.1) OR The Responsible Entity did not retain relevant records related to Reportable Cyber Security Incidents. (2.3) | &lt;p&gt;Evidence must include, but is not limited to, documentation that collectively demonstrates &lt;br/&gt;implementation of each of the applicable requirement parts in CIP-008-5 Table R2 – Cyber Security Incident Response Plan &lt;br/&gt;Implementation and Testing.&lt;/p&gt; &lt;p/&gt; | 2016-07-01 |  | 2020-12-31 |  | 1.2 High Impact BES Cyber Systems and their associated:&lt;br/&gt;• EACMS&lt;br/&gt;Medium Impact BES Cyber Systems and their associated:&lt;br/&gt;• EACMS |  | NPCC-ON | [6 empty] | 20000000
CIP-008-5 (Ontario) | 79780000352 | R3. | 79780004503 | Each Responsible Entity shall maintain each of its Cyber Security Incident response plans according to each of the applicable requirement parts in CIP-008-5 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Assessment | Low | The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within greater than 90 but less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) | The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) OR The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) OR The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 60 and less than 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) Roles or responsibilities, or Cyber Security Incident response groups or individuals, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) or The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) or The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) Roles or responsibilities, or Cyber Security Incident response groups or individuals, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) | &lt;p&gt;Evidence must include, but is not limited to, documentation that collectively demonstrates &lt;br/&gt;maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-5 Table R3 &lt;br/&gt;– Cyber Security Incident.&lt;/p&gt; &lt;p/&gt; | 2016-07-01 |  | 2020-12-31 |  | 1.3 High Impact BES Cyber Systems and their associated:&lt;br/&gt;• EACMS&lt;br/&gt;Medium Impact BES Cyber Systems and their associated:&lt;br/&gt;• EACMS |  | NPCC-ON | [6 empty] | 30000000
CIP-008-5 (Saskatchewan) | 83750000000352 | R1. | 837500000004501 | Each Responsible Entity shall document one or more Cyber Security Incident response plan(s) that collectively include each of the applicable requirement parts in CIP-008-5 Table R1 – Cyber Security Incident Response Plan Specifications. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Low | N/A | N/A | The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include the roles and responsibilities of Cyber Security Incident response groups or individuals. (1.3) OR The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include incident handling procedures for Cyber Security Incidents. (1.4) | The Responsible Entity has not developed a Cyber Security Incident response plan with one or more processes to identify, classify, and respond to Cyber Security Incidents. (1.1) OR The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes to identify Reportable Cyber Security Incidents. (1.2) OR The Responsible Entity has developed a Cyber Security Incident response plan, but did not provide at least preliminary notification to ES-ISAC within one hour from identification of a Reportable Cyber Security Incident. (1.2) | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-5 Table R1 – Cyber Security Incident Response Plan Specifications. | 2016-07-01 |  | 2021-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | MRO-SK | [6 empty] | 10000000
CIP-008-5 (Saskatchewan) | 83750000000352 | R2. | 837500000004502 | Each Responsible Entity shall implement each of its documented Cyber Security Incident response plans to collectively include each of the applicable requirement parts in CIP-008-5 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations | Low | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 15 calendar months, not exceeding 16 calendar months between tests of the plan. (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 16 calendar months, not exceeding 17 calendar months between tests of the plan. (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 17 calendar months, not exceeding 18 calendar months between tests of the plan. (2.1) OR The Responsible Entity did not document deviations, if any, from the plan during a test or when a Reportable Cyber Security Incident occurs. (2.2) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 19 calendar months between tests of the plan. (2.1) OR The Responsible Entity did not retain relevant records related to Reportable Cyber Security Incidents. (2.3) | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-5 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | 2016-07-01 |  | 2021-03-31 |  | 1.2 High Impact BES Cyber Systems and their associated: • EACMS Medium Impact BES Cyber Systems and their associated: • EACMS |  | MRO-SK | [6 empty] | 20000000
CIP-008-5 (Saskatchewan) | 83750000000352 | R3. | 837500000004503 | Each Responsible Entity shall maintain each of its Cyber Security Incident response plans according to each of the applicable requirement parts in CIP-008-5 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Assessment | Low | The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within greater than 90 but less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) | The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) OR The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) OR The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 60 and less than 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) Roles or responsibilities, or Cyber Security Incident response groups or individuals, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) or The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) or The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) Roles or responsibilities, or Cyber Security Incident response groups or individuals, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) | Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-5 Table R3 – Cyber Security Incident. | 2016-07-01 |  | 2021-03-31 |  | 1.3 High Impact BES Cyber Systems and their associated: • EACMS Medium Impact BES Cyber Systems and their associated: • EACMS |  | MRO-SK | [6 empty] | 30000000
CIP-008-6 | 590 | R1. | 8514 | Each Responsible Entity shall document one or more Cyber Security Incident response plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Low | N/A | N/A | The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include the roles and responsibilities of Cyber Security Incident response groups or individuals. (1.3) OR The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include incident handling procedures for Cyber Security Incidents. (1.4) The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes to provide notification per Requirement R4. (1.2) OR The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes that include criteria to evaluate and define attempts to compromise. (1.2) | The Responsible Entity has not developed a Cyber Security Incident response plan with one or more processes to identify, classify, and respond to Cyber Security Incidents. (1.1) OR The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes to identify Reportable Cyber Security Incidents or a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Part 1.2.1, a system identified in the “Applicable Systems” column for Part 1.2. (1.2) | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-008-6 | 590 | R2. | 8526 | Each Responsible Entity shall implement each of its documented Cyber Security Incident response plans to collectively include each of the applicable requirement parts in CIP-008-6 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations | Low | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 15 calendar months, not exceeding 16 calendar months between tests of the plan(s). (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 16 calendar months, not exceeding 17 calendar months between tests of the plan(s). (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 17 calendar months, not exceeding 18 calendar months between tests of the plan(s). (2.1) OR The Responsible Entity did not document deviations, if any, from the plan during a test or when a Reportable Cyber Security Incident or a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 2.2 occurs. (2.2) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 18 calendar months between tests of the plan(s). (2.1) OR The Responsible Entity did not retain relevant records related to Reportable Cyber Security Incidents or Cyber Security Incidents that were an attempt to compromise a system identified in the “Applicable Systems” column for Part 2.3. (2.3) | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-6 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-008-6 | 590 | R3. | 8530 | Each Responsible Entity shall maintain each of its Cyber Security Incident response plans according to each of the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Assessment | Low | The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within greater than 90 but less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) | The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) OR The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) OR The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 60 and less than 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) OR The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) OR The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-008-6 | 590 | R4. | 8531 | Each Responsible Entity shall notify the Electricity Information Sharing and Analysis Center (E-ISAC) and, if subject to the jurisdiction of the United States, the United States National Cybersecurity and Communications Integration Center (NCCIC), or their successors, of a Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Requirement R1, Part 1.2.1, a system identified in the “Applicable Systems” column, unless prohibited by law, in accordance with each of the applicable requirement parts in CIP-008-6 Table R4 – Notifications and Reporting for Cyber Security Incidents. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Assessment, Operations Planning | Low | The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 4.2 but failed to notify or update E-ISAC or NCCIC, or their successors, within the timelines pursuant to Part 4.2. (4.2) OR The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident or a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 4.3 but failed to report on one or more of the attributes within 7 days after determination of the attribute(s) not reported pursuant to Part 4.1. (4.3) OR The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident or a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 4.1 but failed to report on one or more of the attributes after determination pursuant to Part 4.1. (4.1) | The Responsible Entity failed to notify E-ISAC or NCCIC, or their successors, of a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Requirement R1, Part 1.2.1, a system identified in the “Applicable Systems” column. (R4) | The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident but failed to notify or update E-ISAC or NCCIC, or their successors, within the timelines pursuant to Part 4.2. (4.2) OR The Responsible Entity failed to notify E-ISAC or NCCIC, or their successors, of a Reportable Cyber Security Incident. (R4) | The Responsible Entity failed to notify E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident. (R4) | M4. Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column according to the applicable requirement parts in CIP-008-6 Table R4 – Notifications and Reporting for Cyber Security Incidents. | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-008-6 (British Columbia) | 666700000010059 | R1. | 666700000010651 | Each Responsible Entity shall document one or more Cyber Security Incident response plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Low | N/A | N/A | The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include the roles and responsibilities of Cyber Security Incident response groups or individuals. (1.3) OR The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include incident handling procedures for Cyber Security Incidents. (1.4) The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes to provide notification per Requirement R4. (1.2) OR The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes that include criteria to evaluate and define attempts to compromise. (1.2) | The Responsible Entity has not developed a Cyber Security Incident response plan with one or more processes to identify, classify, and respond to Cyber Security Incidents. (1.1) OR The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes to identify Reportable Cyber Security Incidents or a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Part 1.2.1, a system identified in the “Applicable Systems” column for Part 1.2. (1.2) | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. | 2023-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | WECC-BC | [6 empty] | 10000000
CIP-008-6 (British Columbia) | 666700000010059 | R2. | 666700000010652 | Each Responsible Entity shall implement each of its documented Cyber Security Incident response plans to collectively include each of the applicable requirement parts in CIP-008-6 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations | Low | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 15 calendar months, not exceeding 16 calendar months between tests of the plan(s). (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 16 calendar months, not exceeding 17 calendar months between tests of the plan(s). (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 17 calendar months, not exceeding 18 calendar months between tests of the plan(s). (2.1) OR The Responsible Entity did not document deviations, if any, from the plan during a test or when a Reportable Cyber Security Incident or a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 2.2 occurs. (2.2) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 18 calendar months between tests of the plan(s). (2.1) OR The Responsible Entity did not retain relevant records related to Reportable Cyber Security Incidents or Cyber Security Incidents that were an attempt to compromise a system identified in the “Applicable Systems” column for Part 2.3. (2.3) | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-6 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | 2023-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | WECC-BC | [6 empty] | 20000000
CIP-008-6 (British Columbia) | 666700000010059 | R3. | 666700000010653 | Each Responsible Entity shall maintain each of its Cyber Security Incident response plans according to each of the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Assessment | Low | The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within greater than 90 but less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) | The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) OR The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) OR The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 60 and less than 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) OR The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) OR The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | 2023-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | WECC-BC | [6 empty] | 30000000
CIP-008-6 (British Columbia) | 666700000010059 | R4. | 666700000010654 | Each Responsible Entity shall notify the Electricity Information Sharing and Analysis Center (E-ISAC) and, if subject to the jurisdiction of the United States, the United States National Cybersecurity and Communications Integration Center (NCCIC), or their successors, of a Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Requirement R1, Part 1.2.1, a system identified in the “Applicable Systems” column, unless prohibited by law, in accordance with each of the applicable requirement parts in CIP-008-6 Table R4 – Notifications and Reporting for Cyber Security Incidents. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Assessment, Operations Planning | Low | The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 4.2 but failed to notify or update E-ISAC or NCCIC, or their successors, within the timelines pursuant to Part 4.2. (4.2) OR The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident or a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 4.3 but failed to report on one or more of the attributes within 7 days after determination of the attribute(s) not reported pursuant to Part 4.1. (4.3) OR The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident or a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 4.1 but failed to report on one or more of the attributes after determination pursuant to Part 4.1. (4.1) | The Responsible Entity failed to notify E-ISAC or NCCIC, or their successors, of a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Requirement R1, Part 1.2.1, a system identified in the “Applicable Systems” column. (R4) | The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident but failed to notify or update E-ISAC or NCCIC, or their successors, within the timelines pursuant to Part 4.2. (4.2) OR The Responsible Entity failed to notify E-ISAC or NCCIC, or their successors, of a Reportable Cyber Security Incident. (R4) | The Responsible Entity failed to notify E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident. (R4) | M4. Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column according to the applicable requirement parts in CIP-008-6 Table R4 – Notifications and Reporting for Cyber Security Incidents. | 2023-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | WECC-BC | [6 empty] | 40000000
CIP-008-6 (Manitoba) | 77660000000590 | R1. | 776600000008514 | Each Responsible Entity shall document one or more Cyber Security Incident response plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Low | N/A | N/A | The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include the roles and responsibilities of Cyber Security Incident response groups or individuals. (1.3) OR The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include incident handling procedures for Cyber Security Incidents. (1.4) The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes to provide notification per Requirement R4. (1.2) OR The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes that include criteria to evaluate and define attempts to compromise. (1.2) | The Responsible Entity has not developed a Cyber Security Incident response plan with one or more processes to identify, classify, and respond to Cyber Security Incidents. (1.1) OR The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes to identify Reportable Cyber Security Incidents or a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Part 1.2.1, a system identified in the “Applicable Systems” column for Part 1.2. (1.2) | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. | 2022-07-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | MRO-MB | [6 empty] | 10000000
CIP-008-6 (Manitoba) | 77660000000590 | R2. | 776600000008526 | Each Responsible Entity shall implement each of its documented Cyber Security Incident response plans to collectively include each of the applicable requirement parts in CIP-008-6 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations | Low | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 15 calendar months, not exceeding 16 calendar months between tests of the plan(s). (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 16 calendar months, not exceeding 17 calendar months between tests of the plan(s). (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 17 calendar months, not exceeding 18 calendar months between tests of the plan(s). (2.1) OR The Responsible Entity did not document deviations, if any, from the plan during a test or when a Reportable Cyber Security Incident or a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 2.2 occurs. (2.2) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 18 calendar months between tests of the plan(s). (2.1) OR The Responsible Entity did not retain relevant records related to Reportable Cyber Security Incidents or Cyber Security Incidents that were an attempt to compromise a system identified in the “Applicable Systems” column for Part 2.3. (2.3) | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-6 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | 2022-07-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | MRO-MB | [6 empty] | 20000000
CIP-008-6 (Manitoba) | 77660000000590 | R3. | 776600000008530 | Each Responsible Entity shall maintain each of its Cyber Security Incident response plans according to each of the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Assessment | Low | The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within greater than 90 but less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) | The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) OR The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) OR The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 60 and less than 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) OR The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) OR The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | 2022-07-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | MRO-MB | [6 empty] | 30000000
CIP-008-6 (Manitoba) | 77660000000590 | R4. | 776600000008531 | Each Responsible Entity shall notify the Electricity Information Sharing and Analysis Center (E-ISAC) and, if subject to the jurisdiction of the United States, the United States National Cybersecurity and Communications Integration Center (NCCIC), or their successors, of a Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Requirement R1, Part 1.2.1, a system identified in the “Applicable Systems” column, unless prohibited by law, in accordance with each of the applicable requirement parts in CIP-008-6 Table R4 – Notifications and Reporting for Cyber Security Incidents. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Assessment, Operations Planning | Low | The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 4.2 but failed to notify or update E-ISAC or NCCIC, or their successors, within the timelines pursuant to Part 4.2. (4.2) OR The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident or a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 4.3 but failed to report on one or more of the attributes within 7 days after determination of the attribute(s) not reported pursuant to Part 4.1. (4.3) OR The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident or a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 4.1 but failed to report on one or more of the attributes after determination pursuant to Part 4.1. (4.1) | The Responsible Entity failed to notify E-ISAC or NCCIC, or their successors, of a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Requirement R1, Part 1.2.1, a system identified in the “Applicable Systems” column. (R4) | The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident but failed to notify or update E-ISAC or NCCIC, or their successors, within the timelines pursuant to Part 4.2. (4.2) OR The Responsible Entity failed to notify E-ISAC or NCCIC, or their successors, of a Reportable Cyber Security Incident. (R4) | The Responsible Entity failed to notify E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident. (R4) | M4. Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column according to the applicable requirement parts in CIP-008-6 Table R4 – Notifications and Reporting for Cyber Security Incidents. | 2022-07-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | MRO-MB | [6 empty] | 40000000
CIP-008-6 (Nova Scotia) | 78830000000590 | R1. | 788300000008514 | Each Responsible Entity shall document one or more Cyber Security Incident response plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Low | N/A | N/A | The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include the roles and responsibilities of Cyber Security Incident response groups or individuals. (1.3) OR The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include incident handling procedures for Cyber Security Incidents. (1.4) The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes to provide notification per Requirement R4. (1.2) OR The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes that include criteria to evaluate and define attempts to compromise. (1.2) | The Responsible Entity has not developed a Cyber Security Incident response plan with one or more processes to identify, classify, and respond to Cyber Security Incidents. (1.1) OR The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes to identify Reportable Cyber Security Incidents or a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Part 1.2.1, a system identified in the “Applicable Systems” column for Part 1.2. (1.2) | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. | 2021-07-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | NPCC-NS | [6 empty] | 10000000
CIP-008-6 (Nova Scotia) | 78830000000590 | R2. | 788300000008526 | Each Responsible Entity shall implement each of its documented Cyber Security Incident response plans to collectively include each of the applicable requirement parts in CIP-008-6 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations | Low | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 15 calendar months, not exceeding 16 calendar months between tests of the plan(s). (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 16 calendar months, not exceeding 17 calendar months between tests of the plan(s). (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 17 calendar months, not exceeding 18 calendar months between tests of the plan(s). (2.1) OR The Responsible Entity did not document deviations, if any, from the plan during a test or when a Reportable Cyber Security Incident or a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 2.2 occurs. (2.2) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 18 calendar months between tests of the plan(s). (2.1) OR The Responsible Entity did not retain relevant records related to Reportable Cyber Security Incidents or Cyber Security Incidents that were an attempt to compromise a system identified in the “Applicable Systems” column for Part 2.3. (2.3) | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-6 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | 2021-07-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | NPCC-NS | [6 empty] | 20000000
CIP-008-6 (Nova Scotia) | 78830000000590 | R3. | 788300000008530 | Each Responsible Entity shall maintain each of its Cyber Security Incident response plans according to each of the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Assessment | Low | The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within greater than 90 but less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) | The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) OR The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) OR The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 60 and less than 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) OR The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) OR The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | 2021-07-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | NPCC-NS | [6 empty] | 30000000
CIP-008-6 (Nova Scotia) | 78830000000590 | R4. | 788300000008531 | Each Responsible Entity shall notify the Electricity Information Sharing and Analysis Center (E-ISAC) and, if subject to the jurisdiction of the United States, the United States National Cybersecurity and Communications Integration Center (NCCIC), or their successors, of a Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Requirement R1, Part 1.2.1, a system identified in the “Applicable Systems” column, unless prohibited by law, in accordance with each of the applicable requirement parts in CIP-008-6 Table R4 – Notifications and Reporting for Cyber Security Incidents. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Assessment, Operations Planning | Low | The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 4.2 but failed to notify or update E-ISAC or NCCIC, or their successors, within the timelines pursuant to Part 4.2. (4.2) OR The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident or a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 4.3 but failed to report on one or more of the attributes within 7 days after determination of the attribute(s) not reported pursuant to Part 4.1. (4.3) OR The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident or a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 4.1 but failed to report on one or more of the attributes after determination pursuant to Part 4.1. (4.1) | The Responsible Entity failed to notify E-ISAC or NCCIC, or their successors, of a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Requirement R1, Part 1.2.1, a system identified in the “Applicable Systems” column. (R4) | The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident but failed to notify or update E-ISAC or NCCIC, or their successors, within the timelines pursuant to Part 4.2. (4.2) OR The Responsible Entity failed to notify E-ISAC or NCCIC, or their successors, of a Reportable Cyber Security Incident. (R4) | The Responsible Entity failed to notify E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident. (R4) | M4. Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column according to the applicable requirement parts in CIP-008-6 Table R4 – Notifications and Reporting for Cyber Security Incidents. | 2021-07-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | NPCC-NS | [6 empty] | 40000000
CIP-008-6 (Ontario) | 79780000590 | R1. | 79780008514 | Each Responsible Entity shall document one or more Cyber Security Incident response plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Low | N/A | N/A | The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include the roles and responsibilities of Cyber Security Incident response groups or individuals. (1.3) OR The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include incident handling procedures for Cyber Security Incidents. (1.4) The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes to provide notification per Requirement R4. (1.2) OR The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes that include criteria to evaluate and define attempts to compromise. (1.2) | The Responsible Entity has not developed a Cyber Security Incident response plan with one or more processes to identify, classify, and respond to Cyber Security Incidents. (1.1) OR The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes to identify Reportable Cyber Security Incidents or a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Part 1.2.1, a system identified in the “Applicable Systems” column for Part 1.2. (1.2) | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | NPCC-ON | [6 empty] | 10000000
CIP-008-6 (Ontario) | 79780000590 | R2. | 79780008526 | Each Responsible Entity shall implement each of its documented Cyber Security Incident response plans to collectively include each of the applicable requirement parts in CIP-008-6 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations | Low | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 15 calendar months, not exceeding 16 calendar months between tests of the plan(s). (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 16 calendar months, not exceeding 17 calendar months between tests of the plan(s). (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 17 calendar months, not exceeding 18 calendar months between tests of the plan(s). (2.1) OR The Responsible Entity did not document deviations, if any, from the plan during a test or when a Reportable Cyber Security Incident or a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 2.2 occurs. (2.2) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 18 calendar months between tests of the plan(s). (2.1) OR The Responsible Entity did not retain relevant records related to Reportable Cyber Security Incidents or Cyber Security Incidents that were an attempt to compromise a system identified in the “Applicable Systems” column for Part 2.3. (2.3) | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-6 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | NPCC-ON | [6 empty] | 20000000
CIP-008-6 (Ontario) | 79780000590 | R3. | 79780008530 | Each Responsible Entity shall maintain each of its Cyber Security Incident response plans according to each of the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Assessment | Low | The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within greater than 90 but less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) | The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) OR The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) OR The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 60 and less than 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) OR The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) OR The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | NPCC-ON | [6 empty] | 30000000
CIP-008-6 (Ontario) | 79780000590 | R4. | 79780008531 | Each Responsible Entity shall notify the Electricity Information Sharing and Analysis Center (E-ISAC) and, if subject to the jurisdiction of the United States, the United States National Cybersecurity and Communications Integration Center (NCCIC), or their successors, of a Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Requirement R1, Part 1.2.1, a system identified in the “Applicable Systems” column, unless prohibited by law, in accordance with each of the applicable requirement parts in CIP-008-6 Table R4 – Notifications and Reporting for Cyber Security Incidents. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Assessment, Operations Planning | Low | The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 4.2 but failed to notify or update E-ISAC or NCCIC, or their successors, within the timelines pursuant to Part 4.2. (4.2) OR The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident or a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 4.3 but failed to report on one or more of the attributes within 7 days after determination of the attribute(s) not reported pursuant to Part 4.1. (4.3) OR The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident or a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 4.1 but failed to report on one or more of the attributes after determination pursuant to Part 4.1. (4.1) | The Responsible Entity failed to notify E-ISAC or NCCIC, or their successors, of a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Requirement R1, Part 1.2.1, a system identified in the “Applicable Systems” column. (R4) | The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident but failed to notify or update E-ISAC or NCCIC, or their successors, within the timelines pursuant to Part 4.2. (4.2) OR The Responsible Entity failed to notify E-ISAC or NCCIC, or their successors, of a Reportable Cyber Security Incident. (R4) | The Responsible Entity failed to notify E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident. (R4) | M4. Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column according to the applicable requirement parts in CIP-008-6 Table R4 – Notifications and Reporting for Cyber Security Incidents. | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | NPCC-ON | [6 empty] | 40000000
CIP-008-6 (Saskatchewan) | 83750000000590 | R1. | 837500000008514 | Each Responsible Entity shall document one or more Cyber Security Incident response plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Low | N/A | N/A | The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include the roles and responsibilities of Cyber Security Incident response groups or individuals. (1.3) OR The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include incident handling procedures for Cyber Security Incidents. (1.4) The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes to provide notification per Requirement R4. (1.2) OR The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes that include criteria to evaluate and define attempts to compromise. (1.2) | The Responsible Entity has not developed a Cyber Security Incident response plan with one or more processes to identify, classify, and respond to Cyber Security Incidents. (1.1) OR The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes to identify Reportable Cyber Security Incidents or a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Part 1.2.1, a system identified in the “Applicable Systems” column for Part 1.2. (1.2) | M1. Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | MRO-SK | [6 empty] | 10000000
CIP-008-6 (Saskatchewan) | 83750000000590 | R2. | 837500000008526 | Each Responsible Entity shall implement each of its documented Cyber Security Incident response plans to collectively include each of the applicable requirement parts in CIP-008-6 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations | Low | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 15 calendar months, not exceeding 16 calendar months between tests of the plan(s). (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 16 calendar months, not exceeding 17 calendar months between tests of the plan(s). (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 17 calendar months, not exceeding 18 calendar months between tests of the plan(s). (2.1) OR The Responsible Entity did not document deviations, if any, from the plan during a test or when a Reportable Cyber Security Incident or a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 2.2 occurs. (2.2) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 18 calendar months between tests of the plan(s). (2.1) OR The Responsible Entity did not retain relevant records related to Reportable Cyber Security Incidents or Cyber Security Incidents that were an attempt to compromise a system identified in the “Applicable Systems” column for Part 2.3. (2.3) | M2. Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-6 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | MRO-SK | [6 empty] | 20000000
CIP-008-6 (Saskatchewan) | 83750000000590 | R3. | 837500000008530 | Each Responsible Entity shall maintain each of its Cyber Security Incident response plans according to each of the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Assessment | Low | The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within greater than 90 but less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) | The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) OR The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) OR The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 60 and less than 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) OR The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) OR The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) | M3. Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | MRO-SK | [6 empty] | 30000000
CIP-008-6 (Saskatchewan) | 83750000000590 | R4. | 837500000008531 | Each Responsible Entity shall notify the Electricity Information Sharing and Analysis Center (E-ISAC) and, if subject to the jurisdiction of the United States, the United States National Cybersecurity and Communications Integration Center (NCCIC), or their successors, of a Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Requirement R1, Part 1.2.1, a system identified in the “Applicable Systems” column, unless prohibited by law, in accordance with each of the applicable requirement parts in CIP-008-6 Table R4 – Notifications and Reporting for Cyber Security Incidents. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Assessment, Operations Planning | Low | The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 4.2 but failed to notify or update E-ISAC or NCCIC, or their successors, within the timelines pursuant to Part 4.2. (4.2) OR The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident or a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 4.3 but failed to report on one or more of the attributes within 7 days after determination of the attribute(s) not reported pursuant to Part 4.1. (4.3) OR The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident or a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 4.1 but failed to report on one or more of the attributes after determination pursuant to Part 4.1. (4.1) | The Responsible Entity failed to notify E-ISAC or NCCIC, or their successors, of a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Requirement R1, Part 1.2.1, a system identified in the “Applicable Systems” column. (R4) | The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident but failed to notify or update E-ISAC or NCCIC, or their successors, within the timelines pursuant to Part 4.2. (4.2) OR The Responsible Entity failed to notify E-ISAC or NCCIC, or their successors, of a Reportable Cyber Security Incident. (R4) | The Responsible Entity failed to notify E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident. (R4) | M4. Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column according to the applicable requirement parts in CIP-008-6 Table R4 – Notifications and Reporting for Cyber Security Incidents. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | MRO-SK | [6 empty] | 40000000
CIP-008-7 | ST-2024-05-10-0000008 | R1. | RQ-2024-05-10-0000027 | Each Responsible Entity shall document one or more Cyber Security Incident response plan(s) that collectively include each of the applicable requirement parts in CIP-008-7 Table R1 – Cyber Security Incident Response Plan Specifications. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Low | N/A | N/A | The Responsible Entity did not include the roles and responsibilities of Cyber Security Incident response groups or individuals. (Part 1.3) OR The Responsible Entity did not include incident handling procedures for Cyber Security Incidents. (Part 1.4) OR The Responsible Entity’s plan did not include one or more processes to provide notification per Requirement R4. (Part 1.2) OR The Responsible Entity’s plan did not include one or more processes that include criteria to evaluate and define attempts to compromise. (Part 1.2) | The Responsible Entity did not develop a Cyber Security Incident response plan with one or more processes to identify, classify, and respond to Cyber Security Incidents. (Part 1.1) OR The Responsible Entity’s plan did not include one or more processes to identify Reportable Cyber Security Incidents or a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Part 1.2.1, a system identified in the Applicable Systems column for Part 1.2. (Part 1.2) | Evidence must include each of the documented plan(s) that collectively include each of the applicable requirement parts in CIP-008-7 Table R1 – Cyber Security Incident Response Plan Specifications. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-008-7 | ST-2024-05-10-0000008 | R2. | RQ-2024-05-10-0000028 | Each Responsible Entity shall implement each of its documented Cyber Security Incident response plans to collectively include each of the applicable requirement parts in CIP-008-7 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations | Low | The Responsible Entity did not test the Cyber Security Incident response plan(s) within 15 calendar months, not exceeding 16 calendar months between tests of the plan(s). (Par 2.1) | The Responsible Entity did not test the Cyber Security Incident response plan(s) within 16 calendar months, not exceeding 17 calendar months between tests of the plan(s). (Part 2.1) | The Responsible Entity did not test the Cyber Security Incident response plan(s) within 17 calendar months, not exceeding 18 calendar months between tests of the plan(s). (Part 2.1) OR The Responsible Entity did not document deviations, if any, from the plan during a test or when a Reportable Cyber Security Incident or a Cyber Security Incident that was an attempt to compromise a system identified in the Applicable Systems column for Part 2.2 occurs. (Part 2.2) | The Responsible Entity did not test the Cyber Security Incident response plan(s) within 18 calendar months between tests of the plan(s). (Part 2.1) OR The Responsible Entity did not retain relevant records related to Reportable Cyber Security Incidents or Cyber Security Incidents that were an attempt to compromise a system identified in the Applicable Systems column for Part 2.3. (Part 2.3) | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-008-7 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-008-7 | ST-2024-05-10-0000008 | R3. | RQ-2024-05-10-0000029 | Each Responsible Entity shall maintain each of its Cyber Security Incident response plans according to each of the applicable requirement parts in CIP-008-7 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Assessment | Low | The Responsible Entity did not notify each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within greater than 90 but less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (Part 3.1.3) | The Responsible Entity did not update the Cyber Security Incident response plan based on any documented lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (Part 3.1.2) OR The Responsible Entity did not notify each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (Part 3.1.3) OR The Responsible Entity did not update the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 60 and less than 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: • Roles or responsibilities, or • Cyber Security Incident response groups or individuals, or • Technology changes. (Part 3.2) | The Responsible Entity neither documented lessons learned nor documented the absence of any lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (Part 3.1.1) OR The Responsible Entity did not update the Cyber Security Incident response plan based on any documented lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (Part 3.1.2) OR The Responsible Entity did not update the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: • Roles or responsibilities, or • Cyber Security Incident response groups or individuals, or • Technology changes. (Part 3.2) | The Responsible Entity neither documented lessons learned nor documented the absence of any lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (Part 3.1.1) | Evidence must include, but is not limited to, documentation that collectively demonstrates maintenance of each Cyber Security Incident response plan according to the applicable requirement parts in CIP-008-7 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-008-7 | ST-2024-05-10-0000008 | R4. | RQ-2024-05-10-0000030 | Each Responsible Entity shall notify the Electricity Information Sharing and Analysis Center (E-ISAC) and, if subject to the jurisdiction of the United States, the United States Cybersecurity & Infrastructure Security Agency (CISA), or their successors, of a Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Requirement R1, Part 1.2.1, a system identified in the Applicable Systems column, unless prohibited by law, in accordance with each of the applicable requirement parts in CIP-008-7 Table R4 – Notifications and Reporting for Cyber Security Incidents. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Operations Assessment | Low | The Responsible Entity did not notify or update E-ISAC or CISA, or their successors, within the timelines pursuant to Part 4.2. (Part 4.2) OR The Responsible Entity did not report on one or more of the attributes within 7 days after determination of the attribute(s) not reported pursuant to Part 4.1. (Part 4.3) OR The Responsible Entity did not report on one or more of the attributes after determination pursuant to Part 4.1. (Part 4.1) | The Responsible Entity did not notify E-ISAC or CISA, or their successors, of a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Requirement R1, Part 1.2.1, a system identified in the Applicable Systems column. (Requirement R4) | The Responsible Entity did not notify or update E-ISAC or CISA, or their successors, within the timelines pursuant to Part 4.2. (Part 4.2) OR The Responsible Entity did not notify E-ISAC or CISA, or their successors, of a Reportable Cyber Security Incident. (Requirement R4) | The Responsible Entity did not notify E-ISAC and CISA, or their successors, of a Reportable Cyber Security Incident. (Requirement R4) | Evidence must include, but is not limited to, documentation that collectively demonstrates notification of each determined Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise a system identified in the Applicable Systems column according to the applicable requirement parts in CIP-008-7 Table R4 – Notifications and Reporting for Cyber Security Incidents. | [6 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-008-AB-5 (Alberta) | 656600000009012 | R1. | 656600000009111 | Each Responsible Entity shall document one or more cyber security incident response plan(s) that collectively include each of the applicable requirement parts in CIP]008-AB]5 Table R1 - Cyber Security Incident Response Plan Specifications. |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 10000000
CIP-008-AB-5 (Alberta) | 656600000009012 | R2. | 656600000009112 | Each Responsible Entity shall implement each of its documented cyber security incident response plans to collectively include each of the applicable requirement parts in CIP]008-AB]5 Table R2 - Cyber Security Incident Response Plan Implementation and Testing. |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 20000000
CIP-008-AB-5 (Alberta) | 656600000009012 | R3. | 656600000009113 | Each Responsible Entity shall maintain each of its cyber security incident response plans according to each of the applicable requirement parts in CIP]008-AB]5 Table R3 - Cyber Security Incident Response Plan Review, Update, and Communication. |  | ISO | [28 empty] | 2017-10-01 | [5 empty] | WECC-AB | [6 empty] | 30000000
CIP-009-1 | 31 | R1. | 435 | Recovery Plans — The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity has not annually reviewed recovery plan(s) for Critical Cyber Assets. | The Responsible Entity has created recovery plan(s) for Critical Cyber Assets but did not address one of the requirements CIP-009-1 R1.1 or R1.2. | The Responsible Entity has not created recovery plan(s) for Critical Cyber Assets that address at a minimum both requirements CIP-009-1 R1.1 and R1.2. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-009-1 | 31 | R2. | 438 | Exercises — The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity's recovery plan(s) have not been exercised at least annually. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-009-1 | 31 | R3. | 439 | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity's recovery plan(s) have been updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident but the updates were communicated to personnel responsible for the activation and impl | The Responsible Entity's recovery plan(s) have been updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident but the updates were communicated to personnel responsible for the activation and impl | The Responsible Entity's recovery plan(s) have been updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident but the updates were communicated to personnel responsible for the activation and impl | The Responsible Entity's recovery plan(s) have not been updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. OR The Responsible Entity's recovery plan(s) have been updated to reflect any ch |  | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-009-1 | 31 | R4. | 440 | Backup and Restore — The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity's recovery plan(s) do not include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-009-1 | 31 | R5. | 441 | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity's information essential to recovery that is stored on backup media has not been tested at least annually to ensure that the information is available. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-009-1 (British Columbia) | 666700000010060 | R1. | 666700000010655 | Recovery Plans — The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity has not annually reviewed recovery plan(s) for Critical Cyber Assets. | The Responsible Entity has created recovery plan(s) for Critical Cyber Assets but did not address one of the requirements CIP-009-1 R1.1 or R1.2. | The Responsible Entity has not created recovery plan(s) for Critical Cyber Assets that address at a minimum both requirements CIP-009-1 R1.1 and R1.2. |  | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-009-1 (British Columbia) | 666700000010060 | R2. | 666700000010656 | Exercises — The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity's recovery plan(s) have not been exercised at least annually. |  | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 20000000
CIP-009-1 (British Columbia) | 666700000010060 | R3. | 666700000010657 | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity's recovery plan(s) have been updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident but the updates were communicated to personnel responsible for the activation and impl | The Responsible Entity's recovery plan(s) have been updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident but the updates were communicated to personnel responsible for the activation and impl | The Responsible Entity's recovery plan(s) have been updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident but the updates were communicated to personnel responsible for the activation and impl | The Responsible Entity's recovery plan(s) have not been updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. OR The Responsible Entity's recovery plan(s) have been updated to reflect any ch |  | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 30000000
CIP-009-1 (British Columbia) | 666700000010060 | R4. | 666700000010658 | Backup and Restore — The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity's recovery plan(s) do not include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. |  | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 40000000
CIP-009-1 (British Columbia) | 666700000010060 | R5. | 666700000010659 | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity's information essential to recovery that is stored on backup media has not been tested at least annually to ensure that the information is available. |  | 2010-11-01 |  | 2012-06-30 |  |  |  | WECC-BC | [6 empty] | 50000000
CIP-009-1 (Ontario) | 79780000031 | R1. | 79780000435 | Recovery Plans — The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Medium | N/A | The Responsible Entity has not annually reviewed recovery plan(s) for Critical Cyber Assets. | The Responsible Entity has created recovery plan(s) for Critical Cyber Assets but did not address one of the requirements CIP-009-1 R1.1 or R1.2. | The Responsible Entity has not created recovery plan(s) for Critical Cyber Assets that address at a minimum both requirements CIP-009-1 R1.1 and R1.2. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-009-1 (Ontario) | 79780000031 | R2. | 79780000438 | Exercises — The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity's recovery plan(s) have not been exercised at least annually. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-009-1 (Ontario) | 79780000031 | R3. | 79780000439 | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | The Responsible Entity's recovery plan(s) have been updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident but the updates were communicated to personnel responsible for the activation and impl | The Responsible Entity's recovery plan(s) have been updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident but the updates were communicated to personnel responsible for the activation and impl | The Responsible Entity's recovery plan(s) have been updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident but the updates were communicated to personnel responsible for the activation and impl | The Responsible Entity's recovery plan(s) have not been updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. &lt;br/&gt;OR&lt;br/&gt;The Responsible Entity's recovery plan(s) have been updated to reflect any ch |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-009-1 (Ontario) | 79780000031 | R4. | 79780000440 | Backup and Restore — The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity's recovery plan(s) do not include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-009-1 (Ontario) | 79780000031 | R5. | 79780000441 | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity's information essential to recovery that is stored on backup media has not been tested at least annually to ensure that the information is available. |  | 2008-07-01 |  | 2010-03-31 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-009-2 | 215 | R1. | 2513 | Recovery Plans — The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  | CIP-009-1 R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-009-2 | 215 | R2. | 2516 | Exercises — The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-009-2 | 215 | R3. | 2517 | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-009-2 | 215 | R4. | 2518 | Backup and Restore — The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-009-2 | 215 | R5. | 2519 | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-009-2 (Ontario) | 79780000215 | R1. | 79780002513 | Recovery Plans — The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-009-2 (Ontario) | 79780000215 | R2. | 79780002516 | Exercises — The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-009-2 (Ontario) | 79780000215 | R3. | 79780002517 | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-009-2 (Ontario) | 79780000215 | R4. | 79780002518 | Backup and Restore — The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-009-2 (Ontario) | 79780000215 | R5. | 79780002519 | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | [5 empty] | 2010-04-01 |  | 2010-09-30 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-009-3 | 229 | R1. | 2874 | Recovery Plans — The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | The Responsible Entity shall make available its recovery plan(s) as specified in Requirement R1. | 2010-10-01 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-009-3 | 229 | R2. | 2877 | Exercises — The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | The Responsible Entity shall make available its records documenting required exercises as specified in Requirement R2. | 2010-10-01 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-009-3 | 229 | R3. | 2878 | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | The Responsible Entity shall make available its documentation of changes to the recovery plan(s), and documentation of all communications, as specified in Requirement R3. | 2010-10-01 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-009-3 | 229 | R4. | 2879 | Backup and Restore — The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | The Responsible Entity shall make available its documentation regarding backup and storage of information as specified in Requirement R4. | 2010-10-01 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-009-3 | 229 | R5. | 2880 | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | The Responsible Entity shall make available its documentation of testing of backup media as specified in Requirement R5. | 2010-10-01 |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-009-3 (British Columbia) | 666700000010061 | R1. | 666700000010660 | Recovery Plans — The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | The Responsible Entity shall make available its recovery plan(s) as specified in Requirement R1. | 2012-07-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-009-3 (British Columbia) | 666700000010061 | R2. | 666700000010661 | Exercises — The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | The Responsible Entity shall make available its records documenting required exercises as specified in Requirement R2. | 2012-07-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 20000000
CIP-009-3 (British Columbia) | 666700000010061 | R3. | 666700000010662 | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | The Responsible Entity shall make available its documentation of changes to the recovery plan(s), and documentation of all communications, as specified in Requirement R3. | 2012-07-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 30000000
CIP-009-3 (British Columbia) | 666700000010061 | R4. | 666700000010663 | Backup and Restore — The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | The Responsible Entity shall make available its documentation regarding backup and storage of information as specified in Requirement R4. | 2012-07-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 40000000
CIP-009-3 (British Columbia) | 666700000010061 | R5. | 666700000010664 | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | The Responsible Entity shall make available its documentation of testing of backup media as specified in Requirement R5. | 2012-07-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 50000000
CIP-009-3 (Manitoba) | 77660000000229 | R1. | 776600000002874 | Recovery Plans — The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium |  |  |  |  | The Responsible Entity shall make available its recovery plan(s) as specified in Requirement R1. | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
CIP-009-3 (Manitoba) | 77660000000229 | R2. | 776600000002877 | Exercises — The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | The Responsible Entity shall make available its records documenting required exercises as specified in Requirement R2. | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
CIP-009-3 (Manitoba) | 77660000000229 | R3. | 776600000002878 | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | The Responsible Entity shall make available its documentation of changes to the recovery plan(s), and documentation of all communications, as specified in Requirement R3. | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
CIP-009-3 (Manitoba) | 77660000000229 | R4. | 776600000002879 | Backup and Restore — The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | The Responsible Entity shall make available its documentation regarding backup and storage of information as specified in Requirement R4. | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 40000000
CIP-009-3 (Manitoba) | 77660000000229 | R5. | 776600000002880 | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low |  |  |  |  | The Responsible Entity shall make available its documentation of testing of backup media as specified in Requirement R5. | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 50000000
CIP-009-3 (Ontario) | 79780000229 | R1. | 79780002874 | Recovery Plans — The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity has not created or has not annually reviewed their recovery plan(s) for Critical Cyber Assets OR has created a plan but did not address one or more of the requirements CIP- 009-1 R1.1 and R1.2. |  | 2010-10-01 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-009-3 (Ontario) | 79780000229 | R2. | 79780002877 | Exercises — The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity's recovery plan(s) have not been exercised at least annually |  | 2010-10-01 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-009-3 (Ontario) | 79780000229 | R3. | 79780002878 | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity's recovery plan(s) have not been updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. OR The Responsible Entity's recovery plan(s) have been updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident but the updates were not communicated to personnel responsible for the activation and implementation of the recovery plan(s) within thirty calendar days of the change. |  | 2010-10-01 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-009-3 (Ontario) | 79780000229 | R4. | 79780002879 | Backup and Restore — The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity's recovery plan(s) do not include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. |  | 2010-10-01 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-009-3 (Ontario) | 79780000229 | R5. | 79780002880 | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Low | N/A | N/A | N/A | The Responsible Entity's information essential to recovery that is stored on backup media has not been tested at least annually to ensure that the information is available. |  | 2010-10-01 |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-009-4 | 255 | R1. | 3363 | Recovery Plans — The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity has not created or has not annually reviewed their recovery plan(s) for Critical Cyber Assets OR has created a plan but did not address one or more of the requirements CIP- 009-4 R1.1 and R1.2. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-009-4 | 255 | R2. | 3366 | Exercises — The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Long-Term Planning | Low | N/A | N/A | N/A | The Responsible Entity's recovery plan(s) have not been exercised at least annually. | M1. Evidence must include the documented recovery plan(s) that collectively include the applicable requirement parts in CIP-009-6 Table R1 – Recovery Plan Specifications. | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-009-4 | 255 | R3. | 3367 | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Long-Term Planning | Low | N/A | N/A | N/A | The Responsible Entity's recovery plan(s) have not been updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. OR The Responsible Entity's recovery plan(s) have been updated to reflect any c | M1.1. An example of evidence may include, but is not limited to, one or more plans that include language identifying conditions for activation of the recovery plan(s). | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-009-4 | 255 | R4. | 3368 | Backup and Restore — The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Long-Term Planning | Low | N/A | N/A | N/A | The Responsible Entity's recovery plan(s) do not include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. | M1.2. An example of evidence may include, but is not limited to, one or more recovery plans that include language identifying the roles and responsibilities of responders. | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
CIP-009-4 | 255 | R5. | 3369 | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Long-Term Planning | Low | N/A | N/A | N/A | The Responsible Entity's information essential to recovery that is stored on backup media has not been tested at least annually to ensure that the information is available. | M1.3. An example of evidence may include, but is not limited to, documentation of specific processes for the backup and storage of information required to recover BES Cyber System functionality. | 2014-10-01 |  | 2014-02-03 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
CIP-009-4 (Ontario) | 79780000255 | R1. | 79780003363 | Recovery Plans — The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | Medium | N/A | N/A | N/A | The Responsible Entity has not created or has not annually reviewed their recovery plan(s) for Critical Cyber Assets OR has created a plan but did not address one or more of the requirements CIP- 009-4 R1.1 and R1.2. |  | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-009-4 (Ontario) | 79780000255 | R2. | 79780003366 | Exercises — The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Long-Term Planning | Low | N/A | N/A | N/A | The Responsible Entity's recovery plan(s) have not been exercised at least annually. | M1. Evidence must include the documented recovery plan(s) that collectively include the applicable requirement parts in CIP-009-6 Table R1 – Recovery Plan Specifications. | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-009-4 (Ontario) | 79780000255 | R3. | 79780003367 | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within thirty calendar days of the change being completed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Long-Term Planning | Low | N/A | N/A | N/A | The Responsible Entity's recovery plan(s) have not been updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. OR The Responsible Entity's recovery plan(s) have been updated to reflect any c | M1.1. An example of evidence may include, but is not limited to, one or more plans that include language identifying conditions for activation of the recovery plan(s). | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-009-4 (Ontario) | 79780000255 | R4. | 79780003368 | Backup and Restore — The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Long-Term Planning | Low | N/A | N/A | N/A | The Responsible Entity's recovery plan(s) do not include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. | M1.2. An example of evidence may include, but is not limited to, one or more recovery plans that include language identifying the roles and responsibilities of responders. | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 40000000
CIP-009-4 (Ontario) | 79780000255 | R5. | 79780003369 | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | Long-Term Planning | Low | N/A | N/A | N/A | The Responsible Entity's information essential to recovery that is stored on backup media has not been tested at least annually to ensure that the information is available. | M1.3. An example of evidence may include, but is not limited to, documentation of specific processes for the backup and storage of information required to recover BES Cyber System functionality. | 2014-10-01 |  | 2014-02-03 |  |  |  | NPCC-ON | [6 empty] | 50000000
CIP-009-5 | 353 | R1. | 4504 | Each Responsible Entity shall have one or more documented recovery plans that collectively include each of the applicable requirement parts in CIP-009-5 Table R1 – Recovery Plan Specifications. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Medium | N/A | The Responsible Entity has developed recovery plan(s), but the plan(s) do not address one of the requirements included in Parts 1.2 through 1.5. | The Responsible Entity has developed recovery plan(s), but the plan(s) do not address two of the requirements included in Parts 1.2 through 1.5. | The Responsible Entity has not created recovery plan(s) for BES Cyber Systems. or The Responsible Entity has created recovery plan(s) for BES Cyber Systems, but the plan(s) does not address the conditions for activation in Part 1.1. or The Responsible Entity has created recovery plan(s) for BES Cyber Systems, but the plan(s) does not address three or more of the requirements in Parts 1.2 through 1.5. | Evidence must include the documented recovery plan(s) that collectively include the applicable requirement parts in CIP009-5 Table R1 – Recovery Plan Specifications. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
CIP-009-5 | 353 | R2. | 4505 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, its documented recovery plan(s) to collectively include each of the applicable requirement parts in CIP-009-5 Table R2 – Recovery Plan Implementation and Testing. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations | Low | The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.1 within 15 calendar months, not exceeding 16 calendar months between tests of the plan, and when tested, any deficiencies were identified, assessed, and corrected. (2.1) or The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 15 calendar months, not exceeding 16 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.2) or The Responsible Entity has not tested the recovery plan according to R2 Part 2.3 within 36 calendar months, not exceeding 37 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.3) | The Responsible Entity has not tested the recovery plan(s) within 16 calendar months, not exceeding 17 calendar months between tests of the plan, and when tested, any deficiencies were identified, assessed, and corrected. (2.1) or The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 16 calendar months, not exceeding 17 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.2) or The Responsible Entity has not tested the recovery plan according to R2 Part 2.3 within 37 calendar months, not exceeding 38 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.3) | The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.1 within 17 calendar months, not exceeding 18 calendar months between tests of the plan, and when tested, any deficiencies were identified, assessed, and corrected. (2.1) or The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 17 calendar months, not exceeding 18 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.2) or The Responsible Entity has not tested the recovery plan according to R2 Part 2.3 within 38 calendar months, not exceeding 39 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.3) | The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.1 within 18 calendar months between tests of the plan. (2.1) or The Responsible Entity has tested the recovery plan(s) according to R2 Part 2.1 and identified deficiencies, but did not assess or correct the deficiencies. (2.1) or The Responsible Entity has tested the recovery plan(s) according to R2 Part 2.1 but did not identify, assess, or correct the deficiencies. (2.1) or The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 18 calendar months between tests. (2.2) or The Responsible Entity has tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 and identified deficiencies, but did not assess or correct the deficiencies. (2.2) or The Responsible Entity has tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 but did not identify, assess, or correct the deficiencies. (2.2) or The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.3 within 39 calendar months between tests of the plan. (2.3) or The Responsible Entity has tested the recovery plan(s) according to R2 Part 2.3 and identified deficiencies, but did not assess or correct the deficiencies. (2.3) or The Responsible Entity has tested the recovery plan(s) according to R2 Part 2.3 but did not identify, assess, or correct the deficiencies. (2.3) | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-009-5 Table R2 – Recovery Plan Implementation and Testing. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
CIP-009-5 | 353 | R3. | 4506 | Each Responsible Entity shall maintain each of its recovery plans in accordance with each of the applicable requirement parts in CIP-009-5 Table R3 – Recovery Plan Review, Update and Communication. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Assessment | Low | The Responsible Entity has not notified each person or group with a defined role in the recovery plan(s) of updates within 90 and less than 210 calendar days of the update being completed. (3.1.3) | The Responsible Entity has not updated the recovery plan(s) based on any documented lessons learned within 90 and less than 210 calendar days of each recovery plan test or actual recovery. (3.1.2) or The Responsible Entity has not notified each person or group with a defined role in the recovery plan(s) of updates within 120 calendar days of the update being completed. (3.1.3) or The Responsible Entity has not updated the recovery plan(s) or notified each person or group with a defined role within 60 and less than 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) Roles or responsibilities, or Responders, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 90 and less than 210 calendar days of each recovery plan test or actual recovery. (3.1.1) or The Responsible Entity has not updated the recovery plan(s) based on any documented lessons learned within 120 calendar days of each recovery plan test or actual recovery. (3.1.2) or The Responsible Entity has not updated the recovery plan(s) or notified each person or group with a defined role within 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) Roles or responsibilities, or Responders, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 210 calendar days of each recovery plan test or actual recovery. (3.1.1) | Acceptable evidence includes, but is not limited to, each of the applicable requirement parts in CIP-009-5 Table R3 – Recovery Plan Review, Update and Communication. |  |  | 2016-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
CIP-009-5 (British Columbia) | 666700000010062 | R1. | 666700000010665 | Each Responsible Entity shall have one or more documented recovery plans that collectively include each of the applicable requirement parts in CIP-009-5 Table R1 – Recovery Plan Specifications. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Medium | N/A | The Responsible Entity has developed recovery plan(s), but the plan(s) do not address one of the requirements included in Parts 1.2 through 1.5. | The Responsible Entity has developed recovery plan(s), but the plan(s) do not address two of the requirements included in Parts 1.2 through 1.5. | The Responsible Entity has not created recovery plan(s) for BES Cyber Systems. or The Responsible Entity has created recovery plan(s) for BES Cyber Systems, but the plan(s) does not address the conditions for activation in Part 1.1. or The Responsible Entity has created recovery plan(s) for BES Cyber Systems, but the plan(s) does not address three or more of the requirements in Parts 1.2 through 1.5. | Evidence must include the documented recovery plan(s) that collectively include the applicable requirement parts in CIP009-5 Table R1 – Recovery Plan Specifications. |  |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
CIP-009-5 (British Columbia) | 666700000010062 | R2. | 666700000010666 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, its documented recovery plan(s) to collectively include each of the applicable requirement parts in CIP-009-5 Table R2 – Recovery Plan Implementation and Testing. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations | Low | The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.1 within 15 calendar months, not exceeding 16 calendar months between tests of the plan, and when tested, any deficiencies were identified, assessed, and corrected. (2.1) or The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 15 calendar months, not exceeding 16 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.2) or The Responsible Entity has not tested the recovery plan according to R2 Part 2.3 within 36 calendar months, not exceeding 37 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.3) | The Responsible Entity has not tested the recovery plan(s) within 16 calendar months, not exceeding 17 calendar months between tests of the plan, and when tested, any deficiencies were identified, assessed, and corrected. (2.1) or The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 16 calendar months, not exceeding 17 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.2) or The Responsible Entity has not tested the recovery plan according to R2 Part 2.3 within 37 calendar months, not exceeding 38 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.3) | The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.1 within 17 calendar months, not exceeding 18 calendar months between tests of the plan, and when tested, any deficiencies were identified, assessed, and corrected. (2.1) or The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 17 calendar months, not exceeding 18 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.2) or The Responsible Entity has not tested the recovery plan according to R2 Part 2.3 within 38 calendar months, not exceeding 39 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.3) | The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.1 within 18 calendar months between tests of the plan. (2.1) or The Responsible Entity has tested the recovery plan(s) according to R2 Part 2.1 and identified deficiencies, but did not assess or correct the deficiencies. (2.1) or The Responsible Entity has tested the recovery plan(s) according to R2 Part 2.1 but did not identify, assess, or correct the deficiencies. (2.1) or The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 18 calendar months between tests. (2.2) or The Responsible Entity has tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 and identified deficiencies, but did not assess or correct the deficiencies. (2.2) or The Responsible Entity has tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 but did not identify, assess, or correct the deficiencies. (2.2) or The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.3 within 39 calendar months between tests of the plan. (2.3) or The Responsible Entity has tested the recovery plan(s) according to R2 Part 2.3 and identified deficiencies, but did not assess or correct the deficiencies. (2.3) or The Responsible Entity has tested the recovery plan(s) according to R2 Part 2.3 but did not identify, assess, or correct the deficiencies. (2.3) | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-009-5 Table R2 – Recovery Plan Implementation and Testing. |  |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 20000000
CIP-009-5 (British Columbia) | 666700000010062 | R3. | 666700000010667 | Each Responsible Entity shall maintain each of its recovery plans in accordance with each of the applicable requirement parts in CIP-009-5 Table R3 – Recovery Plan Review, Update and Communication. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Assessment | Low | The Responsible Entity has not notified each person or group with a defined role in the recovery plan(s) of updates within 90 and less than 210 calendar days of the update being completed. (3.1.3) | The Responsible Entity has not updated the recovery plan(s) based on any documented lessons learned within 90 and less than 210 calendar days of each recovery plan test or actual recovery. (3.1.2) or The Responsible Entity has not notified each person or group with a defined role in the recovery plan(s) of updates within 120 calendar days of the update being completed. (3.1.3) or The Responsible Entity has not updated the recovery plan(s) or notified each person or group with a defined role within 60 and less than 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) Roles or responsibilities, or Responders, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 90 and less than 210 calendar days of each recovery plan test or actual recovery. (3.1.1) or The Responsible Entity has not updated the recovery plan(s) based on any documented lessons learned within 120 calendar days of each recovery plan test or actual recovery. (3.1.2) or The Responsible Entity has not updated the recovery plan(s) or notified each person or group with a defined role within 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) Roles or responsibilities, or Responders, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 210 calendar days of each recovery plan test or actual recovery. (3.1.1) | Acceptable evidence includes, but is not limited to, each of the applicable requirement parts in CIP-009-5 Table R3 – Recovery Plan Review, Update and Communication. |  |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 30000000
CIP-009-5 (Ontario) | 79780000353 | R1. | 79780004504 | Each Responsible Entity shall have one or more documented recovery plans that collectively include each of the applicable requirement parts in CIP-009-5 Table R1 – Recovery Plan Specifications. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Medium | N/A | The Responsible Entity has developed recovery plan(s), but the plan(s) do not address one of the requirements included in Parts 1.2 through 1.5. | The Responsible Entity has developed recovery plan(s), but the plan(s) do not address two of the requirements included in Parts 1.2 through 1.5. | The Responsible Entity has not created recovery plan(s) for BES Cyber Systems. or The Responsible Entity has created recovery plan(s) for BES Cyber Systems, but the plan(s) does not address the conditions for activation in Part 1.1. or The Responsible Entity has created recovery plan(s) for BES Cyber Systems, but the plan(s) does not address three or more of the requirements in Parts 1.2 through 1.5. | M1.4. An example of evidence may include, but is not limited to, logs, workflow or other documentation confirming that the backup process completed successfully and backup failures, if any, were addressed. |  |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
CIP-009-5 (Ontario) | 79780000353 | R2. | 79780004505 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, its documented recovery plan(s) to collectively include each of the applicable requirement parts in CIP-009-5 Table R2 – Recovery Plan Implementation and Testing. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Assessment | Low | The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.1 within 15 calendar months, not exceeding 16 calendar months between tests of the plan, and when tested, any deficiencies were identified, assessed, and corrected. (2.1) or The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 15 calendar months, not exceeding 16 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.2) or The Responsible Entity has not tested the recovery plan according to R2 Part 2.3 within 36 calendar months, not exceeding 37 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.3) | The Responsible Entity has not tested the recovery plan(s) within 16 calendar months, not exceeding 17 calendar months between tests of the plan, and when tested, any deficiencies were identified, assessed, and corrected. (2.1) or The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 16 calendar months, not exceeding 17 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.2) or The Responsible Entity has not tested the recovery plan according to R2 Part 2.3 within 37 calendar months, not exceeding 38 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.3) | The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.1 within 17 calendar months, not exceeding 18 calendar months between tests of the plan, and when tested, any deficiencies were identified, assessed, and corrected. (2.1) or The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 17 calendar months, not exceeding 18 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.2) or The Responsible Entity has not tested the recovery plan according to R2 Part 2.3 within 38 calendar months, not exceeding 39 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.3) | The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.1 within 18 calendar months between tests of the plan. (2.1) or The Responsible Entity has tested the recovery plan(s) according to R2 Part 2.1 and identified deficiencies, but did not assess or correct the deficiencies. (2.1) or The Responsible Entity has tested the recovery plan(s) according to R2 Part 2.1 but did not identify, assess, or correct the deficiencies. (2.1) or The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 18 calendar months between tests. (2.2) or The Responsible Entity has tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 and identified deficiencies, but did not assess or correct the deficiencies. (2.2) or The Responsible Entity has tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 but did not identify, assess, or correct the deficiencies. (2.2) or The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.3 within 39 calendar months between tests of the plan. (2.3) or The Responsible Entity has tested the recovery plan(s) according to R2 Part 2.3 and identified deficiencies, but did not assess or correct the deficiencies. (2.3) or The Responsible Entity has tested the recovery plan(s) according to R2 Part 2.3 but did not identify, assess, or correct the deficiencies. (2.3) | M3. Acceptable evidence includes, but is not limited to, each of the applicable requirement parts in CIP-009-6 Table R3 – Recovery Plan Review, Update and Communication. |  |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
CIP-009-5 (Ontario) | 79780000353 | R3. | 79780004506 | Each Responsible Entity shall maintain each of its recovery plans in accordance with each of the applicable requirement parts in CIP-009-5 Table R3 – Recovery Plan Review, Update and Communication. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Assessment | Low | The Responsible Entity has not notified each person or group with a defined role in the recovery plan(s) of updates within 90 and less than 210 calendar days of the update being completed. (3.1.3) | The Responsible Entity has not updated the recovery plan(s) based on any documented lessons learned within 90 and less than 210 calendar days of each recovery plan test or actual recovery. (3.1.2) or The Responsible Entity has not notified each person or group with a defined role in the recovery plan(s) of updates within 120 calendar days of the update being completed. (3.1.3) or The Responsible Entity has not updated the recovery plan(s) or notified each person or group with a defined role within 60 and less than 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) Roles or responsibilities, or Responders, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 90 and less than 210 calendar days of each recovery plan test or actual recovery. (3.1.1) or The Responsible Entity has not updated the recovery plan(s) based on any documented lessons learned within 120 calendar days of each recovery plan test or actual recovery. (3.1.2) or The Responsible Entity has not updated the recovery plan(s) or notified each person or group with a defined role within 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) Roles or responsibilities, or Responders, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 210 calendar days of each recovery plan test or actual recovery. (3.1.1) |  |  |  | 2016-06-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
CIP-009-5 (Saskatchewan) | 83750000000353 | R1. | 837500000004504 | Each Responsible Entity shall have one or more documented recovery plans that collectively include each of the applicable requirement parts in CIP-009-5 Table R1 – Recovery Plan Specifications. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Long-Term Planning | Medium | N/A | The Responsible Entity has developed recovery plan(s), but the plan(s) do not address one of the requirements included in Parts 1.2 through 1.5. | The Responsible Entity has developed recovery plan(s), but the plan(s) do not address two of the requirements included in Parts 1.2 through 1.5. | The Responsible Entity has not created recovery plan(s) for BES Cyber Systems. or The Responsible Entity has created recovery plan(s) for BES Cyber Systems, but the plan(s) does not address the conditions for activation in Part 1.1. or The Responsible Entity has created recovery plan(s) for BES Cyber Systems, but the plan(s) does not address three or more of the requirements in Parts 1.2 through 1.5. | Evidence must include the documented recovery plan(s) that collectively include the applicable requirement parts in CIP009-5 Table R1 – Recovery Plan Specifications. |  |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 10000000
CIP-009-5 (Saskatchewan) | 83750000000353 | R2. | 837500000004505 | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, its documented recovery plan(s) to collectively include each of the applicable requirement parts in CIP-009-5 Table R2 – Recovery Plan Implementation and Testing. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations | Low | The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.1 within 15 calendar months, not exceeding 16 calendar months between tests of the plan, and when tested, any deficiencies were identified, assessed, and corrected. (2.1) or The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 15 calendar months, not exceeding 16 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.2) or The Responsible Entity has not tested the recovery plan according to R2 Part 2.3 within 36 calendar months, not exceeding 37 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.3) | The Responsible Entity has not tested the recovery plan(s) within 16 calendar months, not exceeding 17 calendar months between tests of the plan, and when tested, any deficiencies were identified, assessed, and corrected. (2.1) or The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 16 calendar months, not exceeding 17 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.2) or The Responsible Entity has not tested the recovery plan according to R2 Part 2.3 within 37 calendar months, not exceeding 38 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.3) | The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.1 within 17 calendar months, not exceeding 18 calendar months between tests of the plan, and when tested, any deficiencies were identified, assessed, and corrected. (2.1) or The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 17 calendar months, not exceeding 18 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.2) or The Responsible Entity has not tested the recovery plan according to R2 Part 2.3 within 38 calendar months, not exceeding 39 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.3) | The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.1 within 18 calendar months between tests of the plan. (2.1) or The Responsible Entity has tested the recovery plan(s) according to R2 Part 2.1 and identified deficiencies, but did not assess or correct the deficiencies. (2.1) or The Responsible Entity has tested the recovery plan(s) according to R2 Part 2.1 but did not identify, assess, or correct the deficiencies. (2.1) or The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 18 calendar months between tests. (2.2) or The Responsible Entity has tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 and identified deficiencies, but did not assess or correct the deficiencies. (2.2) or The Responsible Entity has tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 but did not identify, assess, or correct the deficiencies. (2.2) or The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.3 within 39 calendar months between tests of the plan. (2.3) or The Responsible Entity has tested the recovery plan(s) according to R2 Part 2.3 and identified deficiencies, but did not assess or correct the deficiencies. (2.3) or The Responsible Entity has tested the recovery plan(s) according to R2 Part 2.3 but did not identify, assess, or correct the deficiencies. (2.3) | Evidence must include, but is not limited to, documentation that collectively demonstrates implementation of each of the applicable requirement parts in CIP-009-5 Table R2 – Recovery Plan Implementation and Testing. |  |  | 2016-06-30 |  |  |  | MRO-SK | [6 empty] | 20000000