TOP-001-4 (Manitoba) | 77660000000565 | R9. | 776600000008020 | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity did not notify one known impacted interconnected entity or 5% or less of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify two known impacted interconnected entities or more than 5% and less than or equal to 10% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify three known impacted interconnected entities or more than 10% and less than or equal to 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify its Reliability Coordinator of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. OR The responsible entity did not notify four or more known impacted interconnected entities or more than 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | Each Balancing Authority and Transmission Operator shall make available upon request, evidence that it notified its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Balancing Authority or Transmission Operator may provide an attestation. | 2019-07-01 | [5 empty] | MRO-MB | [6 empty] | 90000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R1. | 788300000008012 | Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator failed to act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Each Transmission Operator shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 10000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R10. | 788300000008021 | Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | The Transmission Operator did not monitor, obtain, or utilize one of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize two of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize three of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize four or more of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10 Part 10.1 through 10.6. | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 100000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R11. | 788300000008022 | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. |  | BA | BA | [20 empty] | Real-Time Operations | High | N/A | N/A | The Balancing Authority did not monitor the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | The Balancing Authority did not monitor its Balancing Authority Area, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 110000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R12. | 788300000008029 | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator exceeded an identified Interconnection Reliability Operating Limit (IROL) for a continuous duration greater than its associated IROL Tv. | Each Transmission Operator shall make available evidence to show that for any occasion in which it operated outside any identified Interconnection Reliability Operating Limit (IROL), the continuous duration did not exceed its associated IROL Tv. Such evidence could include but is not limited to dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If such a situation has not occurred, the Transmission Operator may provide an attestation that an event has not occurred. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 120000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R13. | 788300000008030 | Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for one 30-minute period within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for two 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for three 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for four or more 30-minute periods within that 24-hour period. | Each Transmission Operator shall have, and make available upon request, evidence to show it ensured that a Real-Time Assessment was performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 130000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R14. | 788300000008031 | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator did not initiate its Operating Plan for mitigating a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment | Each Transmission Operator shall have evidence that it initiated its Operating Plan for mitigating SOL exceedances identified as part of its Real-time monitoring or Real-time Assessments. This evidence could include but is not limited to dated computer logs showing times the Operating Plan was initiated, dated checklists, or other evidence. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 140000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R15. | 788300000008032 | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | N/A | The Transmission Operator did not inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL had been exceeded. | M15. Each Transmission Operator shall make available evidence that it informed its Reliability Coordinator of actions taken to return the System to within limits when a SOL was exceeded. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, or dated computer printouts. If such a situation has not occurred, the Transmission Operator may provide an attestation. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 150000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R16. | 788300000008033 | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M16. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Transmission Operator has provided its System Operators with the authority to approve planned outages and maintenance of telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 160000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R17. | 788300000008034 | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | BA | BA | [20 empty] | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Balancing Authority did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M17. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Balancing Authority has provided its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 170000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R18. | 788300000008035 | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator failed to operate to the most limiting parameter in instances where there was a difference in SOLs. | M18. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to operator logs, voice recordings, electronic communications, or equivalent evidence that will be used to determine if it operated to the most limiting parameter in instances where there is a difference in SOLs. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 180000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R19. | 788300000008036 | Each Transmission Operator shall have data exchange capabilities with the entities it has identified it needs data from in order to perform its Operational Planning Analyses. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | The Transmission Operator did not have data exchange capabilities for performing its Operational Planning Analyses with one identified entity, or 5% or less of the applicable entities, whichever is greater. | The Transmission Operator did not have data exchange capabilities for performing its Operational Planning Analyses with two identified entities, or more than 5% or less than or equal to 10% of the applicable entities, whichever is greater. | The Transmission Operator did not have data exchange capabilities for performing its Operational Planning Analyses with three identified entities, or more than 10% or less than or equal to 15% of the applicable entities, whichever is greater. | The Transmission Operator did not have data exchange capabilities for performing its Operational Planning Analyses with four or more identified entities or greater than 15% of the applicable entities, whichever is greater. | Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, operator logs, system specifications, system diagrams, or other evidence that it has data exchange capabilities with the entities it has identified it needs data from in order to perform its Operational Planning Analyses. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 190000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R2. | 788300000008013 | Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. |  | BA | BA | [20 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Balancing Authority failed to act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Each Balancing Authority shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 20000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R20. | 788300000008037 | Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator had data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments, but did not have redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, as specified in the Requirement. | The Transmission Operator did not have data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments as specified in the Requirement. | M20. Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order to perform its Real-time monitoring and Real-time Assessments as specified in the requirement. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 200000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R21. | 788300000008038 | Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 180 calendar days since the previous test; OR The Transmission Operator did not test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | M21. Each Transmission Operator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R20 for the redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R21. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 210000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R22. | 788300000008039 | Each Balancing Authority shall have data exchange capabilities with the entities it has identified it needs data from in order to develop its Operating Plan for next-day operations. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority did not have data exchange capabilities for developing its Operating Plan with one identified entity, or 5% or less of the applicable entities, whichever is greater. | The Balancing Authority did not have data exchange capabilities for developing its Operating Plan with two identified entities, or more than 5% or less than or equal to 10% of the applicable entities, whichever is greater. | The Balancing Authority did not have data exchange capabilities for developing its Operating Plan with three identified entities, or more than 10% or less than or equal to 15% of the applicable entities, whichever is greater. | The Balancing Authority did not have data exchange capabilities for developing its Operating Plan with four or more identified entities or greater than 15% of the applicable entities, whichever is greater. | M22. Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, operator logs, system specifications, system diagrams, or other evidence that it has data exchange capabilities with the entities it has identified it needs data from in order to develop its Operating Plan for next-day operations. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 220000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R23. | 788300000008040 | Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. |  | BA | BA | [20 empty] | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Balancing Authority had data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions, but did not have redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, as specified in the Requirement. | The Balancing Authority did not have data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions as specified in the Requirement. | M23. Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order to perform its Real-time monitoring and analysis functions as specified in the requirement. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 230000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R24. | 788300000008041 | Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 180 calendar days since the previous test OR The Balancing Authority did not test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | Each Balancing Authority shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R24. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 240000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R3. | 788300000008014 | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. |  | BA, DP, GOP | BA | DP |  |  |  | GOP | [15 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Transmission Operator, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by the Transmission Operator(s) unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Balancing Authority, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Transmission Operator’s Operating Instruction. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 30000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R4. | 788300000008015 | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. |  | BA, DP, GOP | BA | DP |  |  |  | GOP | [15 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Transmission Operator of its inability to comply with its Operating Instruction issued. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 40000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R5. | 788300000008016 | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. |  | DP, GOP, TOP |  | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Balancing Authority, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by its Balancing Authority unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Transmission Operator, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Balancing Authority’s Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 50000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R6. | 788300000008017 | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. |  | DP, GOP, TOP |  | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Balancing Authority of its inability to comply with its Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 60000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R7. | 788300000008018 | Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator did not provide comparable assistance to other Transmission Operators within its Reliability Coordinator Area, when requested and able, and the requesting entity had implemented its Emergency procedures, and such actions could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | Each Transmission Operator shall make available upon request, evidence that comparable requested assistance, if able, was provided to other Transmission Operators within its Reliability Coordinator Area unless such assistance could not be physically implemented or would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no request for assistance was received, the Transmission Operator may provide an attestation. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 70000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R8. | 788300000008019 | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | The Transmission Operator did not inform one known impacted Transmission Operator or 5% or less of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform one known impacted Balancing Authorities or 5% or less of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform two known impacted Transmission Operators or more than 5% and less than or equal to 10% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform two known impacted Balancing Authorities or more than 5% and less than or equal to 10% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas | The Transmission Operator did not inform three known impacted Transmission Operators or more than 10% and less than or equal to 15% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform three known impacted Balancing Authorities or more than 10% and less than or equal to 15% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform its Reliability Coordinator of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Transmission Operators or more than 15% of the known impacted Transmission Operators of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Balancing Authorities or more than 15% of the known impacted Balancing Authorities of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | Each Transmission Operator shall make available upon request, evidence that it informed its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If no such situations have occurred, the Transmission Operator may provide an attestation. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 80000000
TOP-001-4 (Nova Scotia) | 78830000000565 | R9. | 788300000008020 | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity did not notify one known impacted interconnected entity or 5% or less of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify two known impacted interconnected entities or more than 5% and less than or equal to 10% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify three known impacted interconnected entities or more than 10% and less than or equal to 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify its Reliability Coordinator of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. OR The responsible entity did not notify four or more known impacted interconnected entities or more than 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | Each Balancing Authority and Transmission Operator shall make available upon request, evidence that it notified its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Balancing Authority or Transmission Operator may provide an attestation. | 2018-10-01 |  | 2021-06-30 |  |  |  | NPCC-NS | [6 empty] | 90000000
TOP-001-4 (Ontario) | 79780000565 | R1. | 79780008012 | Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator failed to act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | &lt;p&gt;Each Transmission Operator shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions.&lt;/p&gt; &lt;p/&gt; | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-001-4 (Ontario) | 79780000565 | R10. | 79780008021 | Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | The Transmission Operator did not monitor, obtain, or utilize one of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize two of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize three of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize four or more of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10 Part 10.1 through 10.6. | &lt;p&gt;Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area.&lt;/p&gt; &lt;p/&gt; | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 100000000
TOP-001-4 (Ontario) | 79780000565 | R11. | 79780008022 | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. |  | BA | BA | [20 empty] | Real-Time Operations | High | N/A | N/A | The Balancing Authority did not monitor the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | The Balancing Authority did not monitor its Balancing Authority Area, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | &lt;p&gt;Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency.&lt;/p&gt; &lt;p/&gt; | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 110000000
TOP-001-4 (Ontario) | 79780000565 | R12. | 79780008029 | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator exceeded an identified Interconnection Reliability Operating Limit (IROL) for a continuous duration greater than its associated IROL Tv. | &lt;p&gt;Each Transmission Operator shall make available evidence to show that for any occasion in which it operated outside any identified Interconnection Reliability Operating Limit (IROL), the continuous duration did not exceed its associated IROL Tv. Such evidence could include but is not limited to dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If such a situation has not occurred, the Transmission Operator may provide an attestation that an event has not occurred.&lt;/p&gt; &lt;p/&gt; | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 120000000
TOP-001-4 (Ontario) | 79780000565 | R13. | 79780008030 | Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for one 30-minute period within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for two 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for three 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for four or more 30-minute periods within that 24-hour period. | &lt;p&gt;Each Transmission Operator shall have, and make available upon request, evidence to show it ensured that a Real-Time Assessment was performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence.&lt;/p&gt; &lt;p/&gt; | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 130000000
TOP-001-4 (Ontario) | 79780000565 | R14. | 79780008031 | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator did not initiate its Operating Plan for mitigating a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment | &lt;p&gt;Each Transmission Operator shall have evidence that it initiated its Operating Plan for mitigating SOL exceedances identified as part of its Real-time monitoring or Real-time Assessments. This evidence could include but is not limited to dated computer logs showing times the Operating Plan was initiated, dated checklists, or other evidence.&lt;/p&gt; &lt;p/&gt; | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 140000000
TOP-001-4 (Ontario) | 79780000565 | R15. | 79780008032 | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | N/A | The Transmission Operator did not inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL had been exceeded. | M15. Each Transmission Operator shall make available evidence that it informed its Reliability Coordinator of actions taken to return the System to within limits when a SOL was exceeded. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, or dated computer printouts. If such a situation has not occurred, the Transmission Operator may provide an attestation. | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 150000000
TOP-001-4 (Ontario) | 79780000565 | R16. | 79780008033 | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M16. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Transmission Operator has provided its System Operators with the authority to approve planned outages and maintenance of telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 160000000
TOP-001-4 (Ontario) | 79780000565 | R17. | 79780008034 | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | BA | BA | [20 empty] | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Balancing Authority did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M17. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Balancing Authority has provided its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 170000000
TOP-001-4 (Ontario) | 79780000565 | R18. | 79780008035 | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator failed to operate to the most limiting parameter in instances where there was a difference in SOLs. | M18. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to operator logs, voice recordings, electronic communications, or equivalent evidence that will be used to determine if it operated to the most limiting parameter in instances where there is a difference in SOLs. | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 180000000
TOP-001-4 (Ontario) | 79780000565 | R19. | 79780008036 | Each Transmission Operator shall have data exchange capabilities with the entities it has identified it needs data from in order to perform its Operational Planning Analyses. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | The Transmission Operator did not have data exchange capabilities for performing its Operational Planning Analyses with one identified entity, or 5% or less of the applicable entities, whichever is greater. | The Transmission Operator did not have data exchange capabilities for performing its Operational Planning Analyses with two identified entities, or more than 5% or less than or equal to 10% of the applicable entities, whichever is greater. | The Transmission Operator did not have data exchange capabilities for performing its Operational Planning Analyses with three identified entities, or more than 10% or less than or equal to 15% of the applicable entities, whichever is greater. | The Transmission Operator did not have data exchange capabilities for performing its Operational Planning Analyses with four or more identified entities or greater than 15% of the applicable entities, whichever is greater. | &lt;p&gt;Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, operator logs, system specifications, system diagrams, or other evidence that it has data exchange capabilities with the entities it has identified it needs data from in order to perform its Operational Planning Analyses.&lt;/p&gt; &lt;p/&gt; | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 190000000
TOP-001-4 (Ontario) | 79780000565 | R2. | 79780008013 | Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. |  | BA | BA | [20 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Balancing Authority failed to act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | &lt;p&gt;Each Balancing Authority shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions.&lt;/p&gt; | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-001-4 (Ontario) | 79780000565 | R20. | 79780008037 | Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator had data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments, but did not have redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, as specified in the Requirement. | The Transmission Operator did not have data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments as specified in the Requirement. | M20. Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order to perform its Real-time monitoring and Real-time Assessments as specified in the requirement. | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 200000000
TOP-001-4 (Ontario) | 79780000565 | R21. | 79780008038 | Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 180 calendar days since the previous test; OR The Transmission Operator did not test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | M21. Each Transmission Operator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R20 for the redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R21. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 210000000
TOP-001-4 (Ontario) | 79780000565 | R22. | 79780008039 | Each Balancing Authority shall have data exchange capabilities with the entities it has identified it needs data from in order to develop its Operating Plan for next-day operations. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority did not have data exchange capabilities for developing its Operating Plan with one identified entity, or 5% or less of the applicable entities, whichever is greater. | The Balancing Authority did not have data exchange capabilities for developing its Operating Plan with two identified entities, or more than 5% or less than or equal to 10% of the applicable entities, whichever is greater. | The Balancing Authority did not have data exchange capabilities for developing its Operating Plan with three identified entities, or more than 10% or less than or equal to 15% of the applicable entities, whichever is greater. | The Balancing Authority did not have data exchange capabilities for developing its Operating Plan with four or more identified entities or greater than 15% of the applicable entities, whichever is greater. | M22. Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, operator logs, system specifications, system diagrams, or other evidence that it has data exchange capabilities with the entities it has identified it needs data from in order to develop its Operating Plan for next-day operations. | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 220000000
TOP-001-4 (Ontario) | 79780000565 | R23. | 79780008040 | Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. |  | BA | BA | [20 empty] | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Balancing Authority had data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions, but did not have redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, as specified in the Requirement. | The Balancing Authority did not have data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions as specified in the Requirement. | M23. Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order to perform its Real-time monitoring and analysis functions as specified in the requirement. | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 230000000
TOP-001-4 (Ontario) | 79780000565 | R24. | 79780008041 | Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 180 calendar days since the previous test OR The Balancing Authority did not test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | &lt;p&gt;&lt;br/&gt;Each Balancing Authority shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R24. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications.&lt;/p&gt; &lt;p/&gt; | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 240000000
TOP-001-4 (Ontario) | 79780000565 | R3. | 79780008014 | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. |  | BA, DP, GOP | BA | DP |  |  |  | GOP | [15 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Transmission Operator, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | &lt;p&gt;&lt;br/&gt;Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by the &lt;br/&gt;Transmission Operator(s) unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Balancing Authority, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Transmission Operator’s Operating Instruction. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation.&lt;/p&gt; &lt;p/&gt; | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-001-4 (Ontario) | 79780000565 | R4. | 79780008015 | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. |  | BA, DP, GOP | BA | DP |  |  |  | GOP | [15 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | &lt;p&gt;Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Transmission Operator of its inability to comply with its Operating Instruction issued. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation.&lt;/p&gt; &lt;p/&gt; | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-001-4 (Ontario) | 79780000565 | R5. | 79780008016 | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. |  | DP, GOP, TOP |  | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Balancing Authority, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | &lt;p&gt;Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by its Balancing Authority unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Transmission Operator, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Balancing Authority’s Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation.&lt;/p&gt; &lt;p/&gt; | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 50000000
TOP-001-4 (Ontario) | 79780000565 | R6. | 79780008017 | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. |  | DP, GOP, TOP |  | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | &lt;p&gt;Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Balancing Authority of its inability to comply with its Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation.&lt;/p&gt; | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 60000000
TOP-001-4 (Ontario) | 79780000565 | R7. | 79780008018 | Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator did not provide comparable assistance to other Transmission Operators within its Reliability Coordinator Area, when requested and able, and the requesting entity had implemented its Emergency procedures, and such actions could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | &lt;p&gt;Each Transmission Operator shall make available upon request, evidence that comparable requested assistance, if able, was provided to other Transmission Operators within its Reliability Coordinator Area unless such assistance could not be physically implemented or would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no request for assistance was received, the Transmission Operator may provide an attestation.&lt;/p&gt; &lt;p/&gt; | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 70000000
TOP-001-4 (Ontario) | 79780000565 | R8. | 79780008019 | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | The Transmission Operator did not inform one known impacted Transmission Operator or 5% or less of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform one known impacted Balancing Authorities or 5% or less of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform two known impacted Transmission Operators or more than 5% and less than or equal to 10% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform two known impacted Balancing Authorities or more than 5% and less than or equal to 10% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas | The Transmission Operator did not inform three known impacted Transmission Operators or more than 10% and less than or equal to 15% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform three known impacted Balancing Authorities or more than 10% and less than or equal to 15% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform its Reliability Coordinator of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Transmission Operators or more than 15% of the known impacted Transmission Operators of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Balancing Authorities or more than 15% of the known impacted Balancing Authorities of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | &lt;p&gt;Each Transmission Operator shall make available upon request, evidence that it informed its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If no such situations have occurred, the Transmission Operator may provide an attestation.&lt;/p&gt; | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 80000000
TOP-001-4 (Ontario) | 79780000565 | R9. | 79780008020 | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity did not notify one known impacted interconnected entity or 5% or less of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify two known impacted interconnected entities or more than 5% and less than or equal to 10% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify three known impacted interconnected entities or more than 10% and less than or equal to 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify its Reliability Coordinator of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. OR The responsible entity did not notify four or more known impacted interconnected entities or more than 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | &lt;p&gt;Each Balancing Authority and Transmission Operator shall make available upon request, evidence that it notified its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Balancing Authority or Transmission Operator may provide an attestation.&lt;/p&gt; | 2018-07-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 90000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R1. | 837500000008012 | Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator failed to act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Each Transmission Operator shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 10000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R10. | 837500000008021 | Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | The Transmission Operator did not monitor, obtain, or utilize one of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize two of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize three of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize four or more of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10 Part 10.1 through 10.6. | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 100000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R11. | 837500000008022 | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. |  | BA | BA | [20 empty] | Real-Time Operations | High | N/A | N/A | The Balancing Authority did not monitor the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | The Balancing Authority did not monitor its Balancing Authority Area, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 110000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R12. | 837500000008029 | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator exceeded an identified Interconnection Reliability Operating Limit (IROL) for a continuous duration greater than its associated IROL Tv. | Each Transmission Operator shall make available evidence to show that for any occasion in which it operated outside any identified Interconnection Reliability Operating Limit (IROL), the continuous duration did not exceed its associated IROL Tv. Such evidence could include but is not limited to dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If such a situation has not occurred, the Transmission Operator may provide an attestation that an event has not occurred. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 120000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R13. | 837500000008030 | Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for one 30-minute period within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for two 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for three 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for four or more 30-minute periods within that 24-hour period. | Each Transmission Operator shall have, and make available upon request, evidence to show it ensured that a Real-Time Assessment was performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 130000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R14. | 837500000008031 | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator did not initiate its Operating Plan for mitigating a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment | Each Transmission Operator shall have evidence that it initiated its Operating Plan for mitigating SOL exceedances identified as part of its Real-time monitoring or Real-time Assessments. This evidence could include but is not limited to dated computer logs showing times the Operating Plan was initiated, dated checklists, or other evidence. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 140000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R15. | 837500000008032 | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | N/A | The Transmission Operator did not inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL had been exceeded. | M15. Each Transmission Operator shall make available evidence that it informed its Reliability Coordinator of actions taken to return the System to within limits when a SOL was exceeded. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, or dated computer printouts. If such a situation has not occurred, the Transmission Operator may provide an attestation. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 150000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R16. | 837500000008033 | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M16. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Transmission Operator has provided its System Operators with the authority to approve planned outages and maintenance of telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 160000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R17. | 837500000008034 | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | BA | BA | [20 empty] | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Balancing Authority did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M17. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Balancing Authority has provided its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 170000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R18. | 837500000008035 | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator failed to operate to the most limiting parameter in instances where there was a difference in SOLs. | M18. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to operator logs, voice recordings, electronic communications, or equivalent evidence that will be used to determine if it operated to the most limiting parameter in instances where there is a difference in SOLs. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 180000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R19. | 837500000008036 | Each Transmission Operator shall have data exchange capabilities with the entities it has identified it needs data from in order to perform its Operational Planning Analyses. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | The Transmission Operator did not have data exchange capabilities for performing its Operational Planning Analyses with one identified entity, or 5% or less of the applicable entities, whichever is greater. | The Transmission Operator did not have data exchange capabilities for performing its Operational Planning Analyses with two identified entities, or more than 5% or less than or equal to 10% of the applicable entities, whichever is greater. | The Transmission Operator did not have data exchange capabilities for performing its Operational Planning Analyses with three identified entities, or more than 10% or less than or equal to 15% of the applicable entities, whichever is greater. | The Transmission Operator did not have data exchange capabilities for performing its Operational Planning Analyses with four or more identified entities or greater than 15% of the applicable entities, whichever is greater. | Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, operator logs, system specifications, system diagrams, or other evidence that it has data exchange capabilities with the entities it has identified it needs data from in order to perform its Operational Planning Analyses. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 190000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R2. | 837500000008013 | Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. |  | BA | BA | [20 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Balancing Authority failed to act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Each Balancing Authority shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 20000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R20. | 837500000008037 | Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator had data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments, but did not have redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, as specified in the Requirement. | The Transmission Operator did not have data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments as specified in the Requirement. | M20. Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order to perform its Real-time monitoring and Real-time Assessments as specified in the requirement. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 200000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R21. | 837500000008038 | Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 180 calendar days since the previous test; OR The Transmission Operator did not test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | M21. Each Transmission Operator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R20 for the redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R21. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 210000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R22. | 837500000008039 | Each Balancing Authority shall have data exchange capabilities with the entities it has identified it needs data from in order to develop its Operating Plan for next-day operations. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority did not have data exchange capabilities for developing its Operating Plan with one identified entity, or 5% or less of the applicable entities, whichever is greater. | The Balancing Authority did not have data exchange capabilities for developing its Operating Plan with two identified entities, or more than 5% or less than or equal to 10% of the applicable entities, whichever is greater. | The Balancing Authority did not have data exchange capabilities for developing its Operating Plan with three identified entities, or more than 10% or less than or equal to 15% of the applicable entities, whichever is greater. | The Balancing Authority did not have data exchange capabilities for developing its Operating Plan with four or more identified entities or greater than 15% of the applicable entities, whichever is greater. | M22. Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, operator logs, system specifications, system diagrams, or other evidence that it has data exchange capabilities with the entities it has identified it needs data from in order to develop its Operating Plan for next-day operations. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 220000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R23. | 837500000008040 | Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. |  | BA | BA | [20 empty] | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Balancing Authority had data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions, but did not have redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, as specified in the Requirement. | The Balancing Authority did not have data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions as specified in the Requirement. | M23. Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order to perform its Real-time monitoring and analysis functions as specified in the requirement. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 230000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R24. | 837500000008041 | Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 180 calendar days since the previous test OR The Balancing Authority did not test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | Each Balancing Authority shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R24. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 240000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R3. | 837500000008014 | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. |  | BA, DP, GOP | BA | DP |  |  |  | GOP | [15 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Transmission Operator, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by the Transmission Operator(s) unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Balancing Authority, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Transmission Operator’s Operating Instruction. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 30000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R4. | 837500000008015 | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. |  | BA, DP, GOP | BA | DP |  |  |  | GOP | [15 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Transmission Operator of its inability to comply with its Operating Instruction issued. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 40000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R5. | 837500000008016 | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. |  | DP, GOP, TOP |  | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Balancing Authority, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by its Balancing Authority unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Transmission Operator, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Balancing Authority’s Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 50000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R6. | 837500000008017 | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. |  | DP, GOP, TOP |  | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Balancing Authority of its inability to comply with its Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 60000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R7. | 837500000008018 | Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator did not provide comparable assistance to other Transmission Operators within its Reliability Coordinator Area, when requested and able, and the requesting entity had implemented its Emergency procedures, and such actions could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | Each Transmission Operator shall make available upon request, evidence that comparable requested assistance, if able, was provided to other Transmission Operators within its Reliability Coordinator Area unless such assistance could not be physically implemented or would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no request for assistance was received, the Transmission Operator may provide an attestation. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 70000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R8. | 837500000008019 | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | The Transmission Operator did not inform one known impacted Transmission Operator or 5% or less of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform one known impacted Balancing Authorities or 5% or less of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform two known impacted Transmission Operators or more than 5% and less than or equal to 10% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform two known impacted Balancing Authorities or more than 5% and less than or equal to 10% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas | The Transmission Operator did not inform three known impacted Transmission Operators or more than 10% and less than or equal to 15% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform three known impacted Balancing Authorities or more than 10% and less than or equal to 15% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform its Reliability Coordinator of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Transmission Operators or more than 15% of the known impacted Transmission Operators of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Balancing Authorities or more than 15% of the known impacted Balancing Authorities of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | Each Transmission Operator shall make available upon request, evidence that it informed its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If no such situations have occurred, the Transmission Operator may provide an attestation. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 80000000
TOP-001-4 (Saskatchewan) | 83750000000565 | R9. | 837500000008020 | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity did not notify one known impacted interconnected entity or 5% or less of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify two known impacted interconnected entities or more than 5% and less than or equal to 10% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify three known impacted interconnected entities or more than 10% and less than or equal to 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify its Reliability Coordinator of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. OR The responsible entity did not notify four or more known impacted interconnected entities or more than 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | Each Balancing Authority and Transmission Operator shall make available upon request, evidence that it notified its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Balancing Authority or Transmission Operator may provide an attestation. | 2018-10-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 90000000
TOP-001-5 | 603 | R1. | 8762 | Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator failed to act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Each Transmission Operator shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time‐stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-001-5 | 603 | R10. | 8771 | Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | The Transmission Operator did not monitor, obtain, or utilize one of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize two of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize three of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize four or more of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10 Part 10.1 through 10.6. | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 100000000
TOP-001-5 | 603 | R11. | 8778 | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. |  | BA | BA | [20 empty] | Real-Time Operations | High | N/A | N/A | The Balancing Authority did not monitor the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | The Balancing Authority did not monitor its Balancing Authority Area, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | M11. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 110000000
TOP-001-5 | 603 | R12. | 8779 | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator exceeded an identified Interconnection Reliability Operating Limit (IROL) for a continuous duration greater than its associated IROL Tv. | M12. Each Transmission Operator shall make available evidence to show that for any occasion in which it operated outside any identified Interconnection Reliability Operating Limit (IROL), the continuous duration did not exceed its associated IROL Tv. Such evidence could include but is not limited to dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If such a situation has not occurred, the Transmission Operator may provide an attestation that an event has not occurred. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 120000000
TOP-001-5 | 603 | R13. | 8780 | Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for one 30-minute period within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for two 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for three 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for four or more 30-minute periods within that 24-hour period. | M13. Each Transmission Operator shall have, and make available upon request, evidence to show it ensured that a Real-Time Assessment was performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 130000000
TOP-001-5 | 603 | R14. | 8781 | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator did not initiate its Operating Plan for mitigating a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment | M14. Each Transmission Operator shall have evidence that it initiated its Operating Plan for mitigating SOL exceedances identified as part of its Real-time monitoring or Real-time Assessments. This evidence could include but is not limited to dated computer logs showing times the Operating Plan was initiated, dated checklists, or other evidence. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 140000000
TOP-001-5 | 603 | R15. | 8782 | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | N/A | The Transmission Operator did not inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL had been exceeded. | M15. Each Transmission Operator shall make available evidence that it informed its Reliability Coordinator of actions taken to return the System to within limits when a SOL was exceeded. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, or dated computer printouts. If such a situation has not occurred, the Transmission Operator may provide an attestation. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 150000000
TOP-001-5 | 603 | R16. | 8783 | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M16. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Transmission Operator has provided its System Operators with the authority to approve planned outages and maintenance of telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 160000000
TOP-001-5 | 603 | R17. | 8784 | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | BA | BA | [20 empty] | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Balancing Authority did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M17. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Balancing Authority has provided its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 170000000
TOP-001-5 | 603 | R18. | 8785 | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator failed to operate to the most limiting parameter in instances where there was a difference in SOLs. | M18. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to operator logs, voice recordings, electronic communications, or equivalent evidence that will be used to determine if it operated to the most limiting parameter in instances where there is a difference in SOLs. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 180000000
TOP-001-5 | 603 | R19. | RQ-2021-09-20-0000001 | Reserved. | [29 empty] | Reserved. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 190000000
TOP-001-5 | 603 | R2. | 8763 | Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. |  | BA | BA | [20 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Balancing Authority failed to act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Each Balancing Authority shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time‐stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-001-5 | 603 | R20. | 8787 | Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator had data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments, but did not have redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, as specified in the Requirement. | The Transmission Operator did not have data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments as specified in the Requirement. | M20. Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order to perform its Real-time monitoring and Real-time Assessments as specified in the requirement. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 200000000
TOP-001-5 | 603 | R21. | 8788 | Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 180 calendar days since the previous test; OR The Transmission Operator did not test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | M21. Each Transmission Operator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R20 for the redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R21. Evidence could include, but is not limited to: dated and time‐stamped test records, operator logs, voice recordings, or electronic communications. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 210000000
TOP-001-5 | 603 | R22. | RQ-2021-09-20-0000002 | Reserved. | [29 empty] | Reserved. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 220000000
TOP-001-5 | 603 | R23. | 8790 | Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. |  | BA | BA | [20 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Balancing Authority had data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions, but did not have redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, as specified in the Requirement. | The Balancing Authority did not have data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions as specified in the Requirement. | M23. Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order to perform its Real-time monitoring and analysis functions as specified in the requirement. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 230000000
TOP-001-5 | 603 | R24. | 8791 | Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 180 calendar days since the previous test OR The Balancing Authority did not test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | M24. Each Balancing Authority shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R24. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 240000000
TOP-001-5 | 603 | R3. | 8764 | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. |  | BA, DP, GOP, TOP | BA | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Transmission Operator, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | M3. Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by the Transmission Operator(s) unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Balancing Authority, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Transmission Operator’s Operating Instruction. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-001-5 | 603 | R4. | 8765 | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. |  | BA, DP, GOP, TOP | BA | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Transmission Operator of its inability to comply with its Operating Instruction issued. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-001-5 | 603 | R5. | 8766 | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. |  | DP, GOP, TOP |  | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Balancing Authority, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | . Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by its Balancing Authority unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Transmission Operator, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Balancing Authority’s Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-001-5 | 603 | R6. | 8767 | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. |  | DP, GOP, TOP |  | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | M6. Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Balancing Authority of its inability to comply with its Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TOP-001-5 | 603 | R7. | 8768 | Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator did not provide comparable assistance to other Transmission Operators within its Reliability Coordinator Area, when requested and able, and the requesting entity had implemented its Emergency procedures, and such actions could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | Each Transmission Operator shall make available upon request, evidence that comparable requested assistance, if able, was provided to other Transmission Operators within its Reliability Coordinator Area unless such assistance could not be physically implemented or would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no request for assistance was received, the Transmission Operator may provide an attestation. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
TOP-001-5 | 603 | R8. | 8769 | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | The Transmission Operator did not inform one known impacted Transmission Operator or 5% or less of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform one known impacted Balancing Authorities or 5% or less of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform two known impacted Transmission Operators or more than 5% and less than or equal to 10% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform two known impacted Balancing Authorities or more than 5% and less than or equal to 10% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas | The Transmission Operator did not inform three known impacted Transmission Operators or more than 10% and less than or equal to 15% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform three known impacted Balancing Authorities or more than 10% and less than or equal to 15% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform its Reliability Coordinator of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Transmission Operators or more than 15% of the known impacted Transmission Operators of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Balancing Authorities or more than 15% of the known impacted Balancing Authorities of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | Each Transmission Operator shall make available upon request, evidence that it informed its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If no such situations have occurred, the Transmission Operator may provide an attestation. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
TOP-001-5 | 603 | R9. | 8770 | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity did not notify one known impacted interconnected entity or 5% or less of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify two known impacted interconnected entities or more than 5% and less than or equal to 10% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify three known impacted interconnected entities or more than 10% and less than or equal to 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify its Reliability Coordinator of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. OR The responsible entity did not notify four or more known impacted interconnected entities or more than 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | M9. Each Balancing Authority and Transmission Operator shall make available upon request, evidence that it notified its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Balancing Authority or Transmission Operator may provide an attestation. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
TOP-001-5 (British Columbia) | 666700000010332 | R1. | 666700000014859 | Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator failed to act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Each Transmission Operator shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time‐stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 10000000
TOP-001-5 (British Columbia) | 666700000010332 | R10. | 666700000014845 | Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | The Transmission Operator did not monitor, obtain, or utilize one of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize two of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize three of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize four or more of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10 Part 10.1 through 10.6. | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 100000000
TOP-001-5 (British Columbia) | 666700000010332 | R11. | 666700000014846 | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. |  | BA | BA | [20 empty] | Real-Time Operations | High | N/A | N/A | The Balancing Authority did not monitor the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | The Balancing Authority did not monitor its Balancing Authority Area, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | M11. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 110000000
TOP-001-5 (British Columbia) | 666700000010332 | R12. | 666700000014847 | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator exceeded an identified Interconnection Reliability Operating Limit (IROL) for a continuous duration greater than its associated IROL Tv. | M12. Each Transmission Operator shall make available evidence to show that for any occasion in which it operated outside any identified Interconnection Reliability Operating Limit (IROL), the continuous duration did not exceed its associated IROL Tv. Such evidence could include but is not limited to dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If such a situation has not occurred, the Transmission Operator may provide an attestation that an event has not occurred. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 120000000
TOP-001-5 (British Columbia) | 666700000010332 | R13. | 666700000014848 | Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for one 30-minute period within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for two 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for three 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for four or more 30-minute periods within that 24-hour period. | M13. Each Transmission Operator shall have, and make available upon request, evidence to show it ensured that a Real-Time Assessment was performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 130000000
TOP-001-5 (British Columbia) | 666700000010332 | R14. | 666700000014849 | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator did not initiate its Operating Plan for mitigating a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment | M14. Each Transmission Operator shall have evidence that it initiated its Operating Plan for mitigating SOL exceedances identified as part of its Real-time monitoring or Real-time Assessments. This evidence could include but is not limited to dated computer logs showing times the Operating Plan was initiated, dated checklists, or other evidence. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 140000000
TOP-001-5 (British Columbia) | 666700000010332 | R15. | 666700000014850 | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | N/A | The Transmission Operator did not inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL had been exceeded. | M15. Each Transmission Operator shall make available evidence that it informed its Reliability Coordinator of actions taken to return the System to within limits when a SOL was exceeded. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, or dated computer printouts. If such a situation has not occurred, the Transmission Operator may provide an attestation. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 150000000
TOP-001-5 (British Columbia) | 666700000010332 | R16. | 666700000014851 | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M16. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Transmission Operator has provided its System Operators with the authority to approve planned outages and maintenance of telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 160000000
TOP-001-5 (British Columbia) | 666700000010332 | R17. | 666700000014852 | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | BA | BA | [20 empty] | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Balancing Authority did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M17. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Balancing Authority has provided its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 170000000
TOP-001-5 (British Columbia) | 666700000010332 | R18. | 666700000014853 | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator failed to operate to the most limiting parameter in instances where there was a difference in SOLs. | M18. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to operator logs, voice recordings, electronic communications, or equivalent evidence that will be used to determine if it operated to the most limiting parameter in instances where there is a difference in SOLs. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 180000000
TOP-001-5 (British Columbia) | 666700000010332 | R19. | 666700000014870 | Reserved. | [29 empty] | Reserved. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 190000000
TOP-001-5 (British Columbia) | 666700000010332 | R2. | 666700000014860 | Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. |  | BA | BA | [20 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Balancing Authority failed to act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Each Balancing Authority shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time‐stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 20000000
TOP-001-5 (British Columbia) | 666700000010332 | R20. | 666700000014854 | Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator had data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments, but did not have redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, as specified in the Requirement. | The Transmission Operator did not have data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments as specified in the Requirement. | M20. Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order to perform its Real-time monitoring and Real-time Assessments as specified in the requirement. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 200000000
TOP-001-5 (British Columbia) | 666700000010332 | R21. | 666700000014855 | Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 180 calendar days since the previous test; OR The Transmission Operator did not test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | M21. Each Transmission Operator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R20 for the redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R21. Evidence could include, but is not limited to: dated and time‐stamped test records, operator logs, voice recordings, or electronic communications. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 210000000
TOP-001-5 (British Columbia) | 666700000010332 | R22. | 666700000014871 | Reserved. | [29 empty] | Reserved. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 220000000
TOP-001-5 (British Columbia) | 666700000010332 | R23. | 666700000014856 | Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. |  | BA | BA | [20 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Balancing Authority had data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions, but did not have redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, as specified in the Requirement. | The Balancing Authority did not have data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions as specified in the Requirement. | M23. Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order to perform its Real-time monitoring and analysis functions as specified in the requirement. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 230000000
TOP-001-5 (British Columbia) | 666700000010332 | R24. | 666700000014857 | Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 180 calendar days since the previous test OR The Balancing Authority did not test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | M24. Each Balancing Authority shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R24. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 240000000
TOP-001-5 (British Columbia) | 666700000010332 | R3. | 666700000014838 | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. |  | BA, DP, GOP, TOP | BA | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Transmission Operator, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | M3. Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by the Transmission Operator(s) unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Balancing Authority, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Transmission Operator’s Operating Instruction. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 30000000
TOP-001-5 (British Columbia) | 666700000010332 | R4. | 666700000014839 | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. |  | BA, DP, GOP, TOP | BA | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Transmission Operator of its inability to comply with its Operating Instruction issued. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 40000000
TOP-001-5 (British Columbia) | 666700000010332 | R5. | 666700000014840 | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. |  | DP, GOP, TOP |  | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Balancing Authority, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | . Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by its Balancing Authority unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Transmission Operator, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Balancing Authority’s Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 50000000
TOP-001-5 (British Columbia) | 666700000010332 | R6. | 666700000014841 | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. |  | DP, GOP, TOP |  | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | M6. Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Balancing Authority of its inability to comply with its Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 60000000
TOP-001-5 (British Columbia) | 666700000010332 | R7. | 666700000014842 | Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator did not provide comparable assistance to other Transmission Operators within its Reliability Coordinator Area, when requested and able, and the requesting entity had implemented its Emergency procedures, and such actions could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | Each Transmission Operator shall make available upon request, evidence that comparable requested assistance, if able, was provided to other Transmission Operators within its Reliability Coordinator Area unless such assistance could not be physically implemented or would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no request for assistance was received, the Transmission Operator may provide an attestation. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 70000000
TOP-001-5 (British Columbia) | 666700000010332 | R8. | 666700000014843 | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | The Transmission Operator did not inform one known impacted Transmission Operator or 5% or less of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform one known impacted Balancing Authorities or 5% or less of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform two known impacted Transmission Operators or more than 5% and less than or equal to 10% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform two known impacted Balancing Authorities or more than 5% and less than or equal to 10% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas | The Transmission Operator did not inform three known impacted Transmission Operators or more than 10% and less than or equal to 15% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform three known impacted Balancing Authorities or more than 10% and less than or equal to 15% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform its Reliability Coordinator of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Transmission Operators or more than 15% of the known impacted Transmission Operators of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Balancing Authorities or more than 15% of the known impacted Balancing Authorities of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | Each Transmission Operator shall make available upon request, evidence that it informed its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If no such situations have occurred, the Transmission Operator may provide an attestation. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 80000000
TOP-001-5 (British Columbia) | 666700000010332 | R9. | 666700000014844 | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity did not notify one known impacted interconnected entity or 5% or less of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify two known impacted interconnected entities or more than 5% and less than or equal to 10% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify three known impacted interconnected entities or more than 10% and less than or equal to 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify its Reliability Coordinator of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. OR The responsible entity did not notify four or more known impacted interconnected entities or more than 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | M9. Each Balancing Authority and Transmission Operator shall make available upon request, evidence that it notified its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Balancing Authority or Transmission Operator may provide an attestation. | 2022-10-29 | [5 empty] | WECC-BC | [6 empty] | 90000000
TOP-001-5 (Manitoba) | 77660000000603 | R1. | 776600000008762 | Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator failed to act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Each Transmission Operator shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time‐stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 10000000
TOP-001-5 (Manitoba) | 77660000000603 | R10. | 776600000008771 | Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | The Transmission Operator did not monitor, obtain, or utilize one of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize two of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize three of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize four or more of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10 Part 10.1 through 10.6. | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 100000000
TOP-001-5 (Manitoba) | 77660000000603 | R11. | 776600000008778 | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. |  | BA | BA | [20 empty] | Real-Time Operations | High | N/A | N/A | The Balancing Authority did not monitor the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | The Balancing Authority did not monitor its Balancing Authority Area, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | M11. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 110000000
TOP-001-5 (Manitoba) | 77660000000603 | R12. | 776600000008779 | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator exceeded an identified Interconnection Reliability Operating Limit (IROL) for a continuous duration greater than its associated IROL Tv. | M12. Each Transmission Operator shall make available evidence to show that for any occasion in which it operated outside any identified Interconnection Reliability Operating Limit (IROL), the continuous duration did not exceed its associated IROL Tv. Such evidence could include but is not limited to dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If such a situation has not occurred, the Transmission Operator may provide an attestation that an event has not occurred. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 120000000
TOP-001-5 (Manitoba) | 77660000000603 | R13. | 776600000008780 | Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for one 30-minute period within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for two 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for three 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for four or more 30-minute periods within that 24-hour period. | M13. Each Transmission Operator shall have, and make available upon request, evidence to show it ensured that a Real-Time Assessment was performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 130000000
TOP-001-5 (Manitoba) | 77660000000603 | R14. | 776600000008781 | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator did not initiate its Operating Plan for mitigating a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment | M14. Each Transmission Operator shall have evidence that it initiated its Operating Plan for mitigating SOL exceedances identified as part of its Real-time monitoring or Real-time Assessments. This evidence could include but is not limited to dated computer logs showing times the Operating Plan was initiated, dated checklists, or other evidence. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 140000000
TOP-001-5 (Manitoba) | 77660000000603 | R15. | 776600000008782 | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | N/A | The Transmission Operator did not inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL had been exceeded. | M15. Each Transmission Operator shall make available evidence that it informed its Reliability Coordinator of actions taken to return the System to within limits when a SOL was exceeded. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, or dated computer printouts. If such a situation has not occurred, the Transmission Operator may provide an attestation. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 150000000
TOP-001-5 (Manitoba) | 77660000000603 | R16. | 776600000008783 | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M16. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Transmission Operator has provided its System Operators with the authority to approve planned outages and maintenance of telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 160000000
TOP-001-5 (Manitoba) | 77660000000603 | R17. | 776600000008784 | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | BA | BA | [20 empty] | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Balancing Authority did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M17. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Balancing Authority has provided its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 170000000
TOP-001-5 (Manitoba) | 77660000000603 | R18. | 776600000008785 | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator failed to operate to the most limiting parameter in instances where there was a difference in SOLs. | M18. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to operator logs, voice recordings, electronic communications, or equivalent evidence that will be used to determine if it operated to the most limiting parameter in instances where there is a difference in SOLs. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 180000000
TOP-001-5 (Manitoba) | 77660000000603 | R19. | RQ-2021-09-20-0000001-MB | Reserved. | [29 empty] | Reserved. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 190000000
TOP-001-5 (Manitoba) | 77660000000603 | R2. | 776600000008763 | Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. |  | BA | BA | [20 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Balancing Authority failed to act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Each Balancing Authority shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time‐stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 20000000
TOP-001-5 (Manitoba) | 77660000000603 | R20. | 776600000008787 | Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator had data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments, but did not have redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, as specified in the Requirement. | The Transmission Operator did not have data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments as specified in the Requirement. | M20. Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order to perform its Real-time monitoring and Real-time Assessments as specified in the requirement. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 200000000
TOP-001-5 (Manitoba) | 77660000000603 | R21. | 776600000008788 | Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 180 calendar days since the previous test; OR The Transmission Operator did not test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | M21. Each Transmission Operator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R20 for the redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R21. Evidence could include, but is not limited to: dated and time‐stamped test records, operator logs, voice recordings, or electronic communications. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 210000000
TOP-001-5 (Manitoba) | 77660000000603 | R22. | RQ-2021-09-20-0000002-MB | Reserved. | [29 empty] | Reserved. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 220000000
TOP-001-5 (Manitoba) | 77660000000603 | R23. | 776600000008790 | Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. |  | BA | BA | [20 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Balancing Authority had data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions, but did not have redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, as specified in the Requirement. | The Balancing Authority did not have data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions as specified in the Requirement. | M23. Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order to perform its Real-time monitoring and analysis functions as specified in the requirement. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 230000000
TOP-001-5 (Manitoba) | 77660000000603 | R24. | 776600000008791 | Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 180 calendar days since the previous test OR The Balancing Authority did not test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | M24. Each Balancing Authority shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R24. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 240000000
TOP-001-5 (Manitoba) | 77660000000603 | R3. | 776600000008764 | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. |  | BA, DP, GOP | BA | DP |  |  |  | GOP | [15 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Transmission Operator, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | M3. Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by the Transmission Operator(s) unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Balancing Authority, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Transmission Operator’s Operating Instruction. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 30000000
TOP-001-5 (Manitoba) | 77660000000603 | R4. | 776600000008765 | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. |  | BA, DP, GOP | BA | DP |  |  |  | GOP | [15 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Transmission Operator of its inability to comply with its Operating Instruction issued. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 40000000
TOP-001-5 (Manitoba) | 77660000000603 | R5. | 776600000008766 | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. |  | DP, GOP, TOP |  | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Balancing Authority, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | . Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by its Balancing Authority unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Transmission Operator, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Balancing Authority’s Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 50000000
TOP-001-5 (Manitoba) | 77660000000603 | R6. | 776600000008767 | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. |  | DP, GOP, TOP |  | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | M6. Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Balancing Authority of its inability to comply with its Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 60000000
TOP-001-5 (Manitoba) | 77660000000603 | R7. | 776600000008768 | Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator did not provide comparable assistance to other Transmission Operators within its Reliability Coordinator Area, when requested and able, and the requesting entity had implemented its Emergency procedures, and such actions could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | Each Transmission Operator shall make available upon request, evidence that comparable requested assistance, if able, was provided to other Transmission Operators within its Reliability Coordinator Area unless such assistance could not be physically implemented or would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no request for assistance was received, the Transmission Operator may provide an attestation. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 70000000
TOP-001-5 (Manitoba) | 77660000000603 | R8. | 776600000008769 | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | The Transmission Operator did not inform one known impacted Transmission Operator or 5% or less of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform one known impacted Balancing Authorities or 5% or less of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform two known impacted Transmission Operators or more than 5% and less than or equal to 10% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform two known impacted Balancing Authorities or more than 5% and less than or equal to 10% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas | The Transmission Operator did not inform three known impacted Transmission Operators or more than 10% and less than or equal to 15% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform three known impacted Balancing Authorities or more than 10% and less than or equal to 15% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform its Reliability Coordinator of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Transmission Operators or more than 15% of the known impacted Transmission Operators of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Balancing Authorities or more than 15% of the known impacted Balancing Authorities of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | Each Transmission Operator shall make available upon request, evidence that it informed its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If no such situations have occurred, the Transmission Operator may provide an attestation. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 80000000
TOP-001-5 (Manitoba) | 77660000000603 | R9. | 776600000008770 | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity did not notify one known impacted interconnected entity or 5% or less of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify two known impacted interconnected entities or more than 5% and less than or equal to 10% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify three known impacted interconnected entities or more than 10% and less than or equal to 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify its Reliability Coordinator of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. OR The responsible entity did not notify four or more known impacted interconnected entities or more than 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | M9. Each Balancing Authority and Transmission Operator shall make available upon request, evidence that it notified its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Balancing Authority or Transmission Operator may provide an attestation. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 90000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R1. | 788300000008762 | Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator failed to act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Each Transmission Operator shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time‐stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 10000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R10. | 788300000008771 | Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | The Transmission Operator did not monitor, obtain, or utilize one of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize two of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize three of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize four or more of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10 Part 10.1 through 10.6. | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 100000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R11. | 788300000008778 | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. |  | BA | BA | [20 empty] | Real-Time Operations | High | N/A | N/A | The Balancing Authority did not monitor the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | The Balancing Authority did not monitor its Balancing Authority Area, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | M11. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 110000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R12. | 788300000008779 | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator exceeded an identified Interconnection Reliability Operating Limit (IROL) for a continuous duration greater than its associated IROL Tv. | M12. Each Transmission Operator shall make available evidence to show that for any occasion in which it operated outside any identified Interconnection Reliability Operating Limit (IROL), the continuous duration did not exceed its associated IROL Tv. Such evidence could include but is not limited to dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If such a situation has not occurred, the Transmission Operator may provide an attestation that an event has not occurred. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 120000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R13. | 788300000008780 | Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for one 30-minute period within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for two 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for three 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for four or more 30-minute periods within that 24-hour period. | M13. Each Transmission Operator shall have, and make available upon request, evidence to show it ensured that a Real-Time Assessment was performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 130000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R14. | 788300000008781 | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator did not initiate its Operating Plan for mitigating a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment | M14. Each Transmission Operator shall have evidence that it initiated its Operating Plan for mitigating SOL exceedances identified as part of its Real-time monitoring or Real-time Assessments. This evidence could include but is not limited to dated computer logs showing times the Operating Plan was initiated, dated checklists, or other evidence. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 140000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R15. | 788300000008782 | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | N/A | The Transmission Operator did not inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL had been exceeded. | M15. Each Transmission Operator shall make available evidence that it informed its Reliability Coordinator of actions taken to return the System to within limits when a SOL was exceeded. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, or dated computer printouts. If such a situation has not occurred, the Transmission Operator may provide an attestation. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 150000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R16. | 788300000008783 | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M16. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Transmission Operator has provided its System Operators with the authority to approve planned outages and maintenance of telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 160000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R17. | 788300000008784 | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | BA | BA | [20 empty] | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Balancing Authority did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M17. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Balancing Authority has provided its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 170000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R18. | 788300000008785 | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator failed to operate to the most limiting parameter in instances where there was a difference in SOLs. | M18. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to operator logs, voice recordings, electronic communications, or equivalent evidence that will be used to determine if it operated to the most limiting parameter in instances where there is a difference in SOLs. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 180000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R19. | RQ-2021-09-20-0000001-NS | Reserved. | [29 empty] | Reserved. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 190000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R2. | 788300000008763 | Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. |  | BA | BA | [20 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Balancing Authority failed to act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Each Balancing Authority shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time‐stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 20000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R20. | 788300000008787 | Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator had data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments, but did not have redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, as specified in the Requirement. | The Transmission Operator did not have data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments as specified in the Requirement. | M20. Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order to perform its Real-time monitoring and Real-time Assessments as specified in the requirement. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 200000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R21. | 788300000008788 | Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 180 calendar days since the previous test; OR The Transmission Operator did not test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | M21. Each Transmission Operator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R20 for the redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R21. Evidence could include, but is not limited to: dated and time‐stamped test records, operator logs, voice recordings, or electronic communications. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 210000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R22. | RQ-2021-09-20-0000002-NS | Reserved. | [29 empty] | Reserved. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 220000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R23. | 788300000008790 | Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. |  | BA | BA | [20 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Balancing Authority had data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions, but did not have redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, as specified in the Requirement. | The Balancing Authority did not have data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions as specified in the Requirement. | M23. Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order to perform its Real-time monitoring and analysis functions as specified in the requirement. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 230000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R24. | 788300000008791 | Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 180 calendar days since the previous test OR The Balancing Authority did not test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | M24. Each Balancing Authority shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R24. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 240000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R3. | 788300000008764 | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. |  | BA, DP, GOP | BA | DP |  |  |  | GOP | [15 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Transmission Operator, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | M3. Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by the Transmission Operator(s) unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Balancing Authority, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Transmission Operator’s Operating Instruction. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 30000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R4. | 788300000008765 | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. |  | BA, DP, GOP | BA | DP |  |  |  | GOP | [15 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Transmission Operator of its inability to comply with its Operating Instruction issued. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 40000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R5. | 788300000008766 | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. |  | DP, GOP, TOP |  | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Balancing Authority, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | . Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by its Balancing Authority unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Transmission Operator, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Balancing Authority’s Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 50000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R6. | 788300000008767 | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. |  | DP, GOP, TOP |  | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | M6. Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Balancing Authority of its inability to comply with its Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 60000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R7. | 788300000008768 | Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator did not provide comparable assistance to other Transmission Operators within its Reliability Coordinator Area, when requested and able, and the requesting entity had implemented its Emergency procedures, and such actions could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | Each Transmission Operator shall make available upon request, evidence that comparable requested assistance, if able, was provided to other Transmission Operators within its Reliability Coordinator Area unless such assistance could not be physically implemented or would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no request for assistance was received, the Transmission Operator may provide an attestation. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 70000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R8. | 788300000008769 | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | The Transmission Operator did not inform one known impacted Transmission Operator or 5% or less of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform one known impacted Balancing Authorities or 5% or less of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform two known impacted Transmission Operators or more than 5% and less than or equal to 10% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform two known impacted Balancing Authorities or more than 5% and less than or equal to 10% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas | The Transmission Operator did not inform three known impacted Transmission Operators or more than 10% and less than or equal to 15% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform three known impacted Balancing Authorities or more than 10% and less than or equal to 15% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform its Reliability Coordinator of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Transmission Operators or more than 15% of the known impacted Transmission Operators of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Balancing Authorities or more than 15% of the known impacted Balancing Authorities of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | Each Transmission Operator shall make available upon request, evidence that it informed its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If no such situations have occurred, the Transmission Operator may provide an attestation. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 80000000
TOP-001-5 (Nova Scotia) | 78830000000603 | R9. | 788300000008770 | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity did not notify one known impacted interconnected entity or 5% or less of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify two known impacted interconnected entities or more than 5% and less than or equal to 10% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify three known impacted interconnected entities or more than 10% and less than or equal to 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify its Reliability Coordinator of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. OR The responsible entity did not notify four or more known impacted interconnected entities or more than 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | M9. Each Balancing Authority and Transmission Operator shall make available upon request, evidence that it notified its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Balancing Authority or Transmission Operator may provide an attestation. | 2021-07-01 |  | 2024-09-30 |  |  |  | NPCC-NS | [6 empty] | 90000000
TOP-001-5 (Ontario) | 79780000603 | R1. | 79780008762 | Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator failed to act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | &lt;p&gt;&lt;br/&gt;Each Transmission Operator shall have and provide evidence which may include but is not limited to &lt;br/&gt;dated operator logs, dated records, dated and time‐stamped voice recordings or dated transcripts of &lt;br/&gt;voice recordings, electronic communications, or equivalent documentation, that will be used to &lt;br/&gt;determine that it acted to maintain the reliability of its Transmission Operator Area via its own &lt;br/&gt;actions or by issuing&lt;br/&gt;Operating Instructions.&lt;/p&gt; | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 10000000
TOP-001-5 (Ontario) | 79780000603 | R10. | 79780008771 | Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | The Transmission Operator did not monitor, obtain, or utilize one of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize two of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize three of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize four or more of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10 Part 10.1 through 10.6. | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 100000000
TOP-001-5 (Ontario) | 79780000603 | R11. | 79780008778 | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. |  | BA | BA | [20 empty] | Real-Time Operations | High | N/A | N/A | The Balancing Authority did not monitor the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | The Balancing Authority did not monitor its Balancing Authority Area, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | M11. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 110000000
TOP-001-5 (Ontario) | 79780000603 | R12. | 79780008779 | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator exceeded an identified Interconnection Reliability Operating Limit (IROL) for a continuous duration greater than its associated IROL Tv. | M12. Each Transmission Operator shall make available evidence to show that for any occasion in which it operated outside any identified Interconnection Reliability Operating Limit (IROL), the continuous duration did not exceed its associated IROL Tv. Such evidence could include but is not limited to dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If such a situation has not occurred, the Transmission Operator may provide an attestation that an event has not occurred. | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 120000000
TOP-001-5 (Ontario) | 79780000603 | R13. | 79780008780 | Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for one 30-minute period within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for two 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for three 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for four or more 30-minute periods within that 24-hour period. | M13. Each Transmission Operator shall have, and make available upon request, evidence to show it ensured that a Real-Time Assessment was performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence. | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 130000000
TOP-001-5 (Ontario) | 79780000603 | R14. | 79780008781 | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator did not initiate its Operating Plan for mitigating a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment | M14. Each Transmission Operator shall have evidence that it initiated its Operating Plan for mitigating SOL exceedances identified as part of its Real-time monitoring or Real-time Assessments. This evidence could include but is not limited to dated computer logs showing times the Operating Plan was initiated, dated checklists, or other evidence. | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 140000000
TOP-001-5 (Ontario) | 79780000603 | R15. | 79780008782 | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | N/A | The Transmission Operator did not inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL had been exceeded. | M15. Each Transmission Operator shall make available evidence that it informed its Reliability Coordinator of actions taken to return the System to within limits when a SOL was exceeded. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, or dated computer printouts. If such a situation has not occurred, the Transmission Operator may provide an attestation. | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 150000000
TOP-001-5 (Ontario) | 79780000603 | R16. | 79780008783 | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M16. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Transmission Operator has provided its System Operators with the authority to approve planned outages and maintenance of telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 160000000
TOP-001-5 (Ontario) | 79780000603 | R17. | 79780008784 | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | BA | BA | [20 empty] | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Balancing Authority did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M17. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Balancing Authority has provided its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 170000000
TOP-001-5 (Ontario) | 79780000603 | R18. | 79780008785 | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator failed to operate to the most limiting parameter in instances where there was a difference in SOLs. | M18. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to operator logs, voice recordings, electronic communications, or equivalent evidence that will be used to determine if it operated to the most limiting parameter in instances where there is a difference in SOLs. | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 180000000
TOP-001-5 (Ontario) | 79780000603 | R2. | 79780008763 | Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. |  | BA | BA | [20 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Balancing Authority failed to act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | &lt;p&gt;&lt;br/&gt;Each Balancing Authority shall have and provide evidence which may include but is not limited to &lt;br/&gt;dated operator logs, dated records, dated and time‐stamped voice recordings or dated transcripts of &lt;br/&gt;voice recordings, electronic communications, or equivalent documentation, that will be used to &lt;br/&gt;determine that it acted to maintain the reliability of its Balancing Authority Area via its own &lt;br/&gt;actions or by issuing&lt;br/&gt;Operating Instructions.&lt;/p&gt; | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 20000000
TOP-001-5 (Ontario) | 79780000603 | R20. | 79780008787 | Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator had data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments, but did not have redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, as specified in the Requirement. | The Transmission Operator did not have data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments as specified in the Requirement. | M20. Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order to perform its Real-time monitoring and Real-time Assessments as specified in the requirement. | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 200000000
TOP-001-5 (Ontario) | 79780000603 | R21. | 79780008788 | Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 180 calendar days since the previous test; OR The Transmission Operator did not test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | &lt;p&gt;M21. Each Transmission Operator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R20 for the redundant functionality, or experienced an event that demonstrated the &lt;br/&gt;redundant functionality; and, if the test was unsuccessful, initiated action within two hours to &lt;br/&gt;restore redundant functionality as specified in Requirement R21. Evidence could include, but is not &lt;br/&gt;limited to: dated and time‐stamped test records, operator&lt;br/&gt;logs, voice recordings, or electronic communications.&lt;/p&gt; | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 210000000
TOP-001-5 (Ontario) | 79780000603 | R23. | 79780008790 | Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. |  | BA | BA | [20 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Balancing Authority had data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions, but did not have redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, as specified in the Requirement. | The Balancing Authority did not have data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions as specified in the Requirement. | M23. Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order to perform its Real-time monitoring and analysis functions as specified in the requirement. | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 230000000
TOP-001-5 (Ontario) | 79780000603 | R24. | 79780008791 | Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 180 calendar days since the previous test OR The Balancing Authority did not test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | M24. Each Balancing Authority shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R24. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 240000000
TOP-001-5 (Ontario) | 79780000603 | R3. | 79780008764 | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. |  | BA, DP, GOP | BA | DP |  |  |  | GOP | [15 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Transmission Operator, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | M3. Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by the Transmission Operator(s) unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Balancing Authority, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Transmission Operator’s Operating Instruction. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 30000000
TOP-001-5 (Ontario) | 79780000603 | R4. | 79780008765 | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. |  | BA, DP, GOP | BA | DP |  |  |  | GOP | [15 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | M20. Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order to perform its Real-time monitoring and Real-time Assessments as specified in the requirement. | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 40000000
TOP-001-5 (Ontario) | 79780000603 | R5. | 79780008766 | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. |  | DP, GOP, TOP |  | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Balancing Authority, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | M21. Each Transmission Operator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R20 for the redundant functionality, or experienced an event that demonstrated the | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 50000000
TOP-001-5 (Ontario) | 79780000603 | R6. | 79780008767 | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. |  | DP, GOP, TOP |  | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | M6. Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Balancing Authority of its inability to comply with its Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 60000000
TOP-001-5 (Ontario) | 79780000603 | R7. | 79780008768 | Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator did not provide comparable assistance to other Transmission Operators within its Reliability Coordinator Area, when requested and able, and the requesting entity had implemented its Emergency procedures, and such actions could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | M23. Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order to perform its Real-time monitoring and analysis functions as specified in the requirement. | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 70000000
TOP-001-5 (Ontario) | 79780000603 | R8. | 79780008769 | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | The Transmission Operator did not inform one known impacted Transmission Operator or 5% or less of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform one known impacted Balancing Authorities or 5% or less of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform two known impacted Transmission Operators or more than 5% and less than or equal to 10% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform two known impacted Balancing Authorities or more than 5% and less than or equal to 10% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas | The Transmission Operator did not inform three known impacted Transmission Operators or more than 10% and less than or equal to 15% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform three known impacted Balancing Authorities or more than 10% and less than or equal to 15% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform its Reliability Coordinator of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Transmission Operators or more than 15% of the known impacted Transmission Operators of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Balancing Authorities or more than 15% of the known impacted Balancing Authorities of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | M24. Each Balancing Authority shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R24. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 80000000
TOP-001-5 (Ontario) | 79780000603 | R9. | 79780008770 | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity did not notify one known impacted interconnected entity or 5% or less of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify two known impacted interconnected entities or more than 5% and less than or equal to 10% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify three known impacted interconnected entities or more than 10% and less than or equal to 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify its Reliability Coordinator of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. OR The responsible entity did not notify four or more known impacted interconnected entities or more than 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | M9. Each Balancing Authority and Transmission Operator shall make available upon request, evidence that it notified its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Balancing Authority or Transmission Operator may provide an attestation. | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 90000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R1. | 837500000008762 | Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator failed to act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Each Transmission Operator shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time‐stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 10000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R10. | 837500000008771 | Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | The Transmission Operator did not monitor, obtain, or utilize one of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize two of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize three of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize four or more of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10 Part 10.1 through 10.6. | M10. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 100000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R11. | 837500000008778 | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. |  | BA | BA | [20 empty] | Real-Time Operations | High | N/A | N/A | The Balancing Authority did not monitor the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | The Balancing Authority did not monitor its Balancing Authority Area, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | M11. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 110000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R12. | 837500000008779 | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator exceeded an identified Interconnection Reliability Operating Limit (IROL) for a continuous duration greater than its associated IROL Tv. | M12. Each Transmission Operator shall make available evidence to show that for any occasion in which it operated outside any identified Interconnection Reliability Operating Limit (IROL), the continuous duration did not exceed its associated IROL Tv. Such evidence could include but is not limited to dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If such a situation has not occurred, the Transmission Operator may provide an attestation that an event has not occurred. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 120000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R13. | 837500000008780 | Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for one 30-minute period within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for two 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for three 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for four or more 30-minute periods within that 24-hour period. | M13. Each Transmission Operator shall have, and make available upon request, evidence to show it ensured that a Real-Time Assessment was performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 130000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R14. | 837500000008781 | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator did not initiate its Operating Plan for mitigating a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment | M14. Each Transmission Operator shall have evidence that it initiated its Operating Plan for mitigating SOL exceedances identified as part of its Real-time monitoring or Real-time Assessments. This evidence could include but is not limited to dated computer logs showing times the Operating Plan was initiated, dated checklists, or other evidence. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 140000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R15. | 837500000008782 | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | N/A | The Transmission Operator did not inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL had been exceeded. | M15. Each Transmission Operator shall make available evidence that it informed its Reliability Coordinator of actions taken to return the System to within limits when a SOL was exceeded. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, or dated computer printouts. If such a situation has not occurred, the Transmission Operator may provide an attestation. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 150000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R16. | 837500000008783 | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M16. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Transmission Operator has provided its System Operators with the authority to approve planned outages and maintenance of telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 160000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R17. | 837500000008784 | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | BA | BA | [20 empty] | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Balancing Authority did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | M17. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Balancing Authority has provided its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 170000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R18. | 837500000008785 | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator failed to operate to the most limiting parameter in instances where there was a difference in SOLs. | M18. Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to operator logs, voice recordings, electronic communications, or equivalent evidence that will be used to determine if it operated to the most limiting parameter in instances where there is a difference in SOLs. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 180000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R19. | RQ-2021-09-20-0000001-SK | Reserved. | [29 empty] | Reserved. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 190000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R2. | 837500000008763 | Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. |  | BA | BA | [20 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Balancing Authority failed to act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Each Balancing Authority shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time‐stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 20000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R20. | 837500000008787 | Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator had data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments, but did not have redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, as specified in the Requirement. | The Transmission Operator did not have data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments as specified in the Requirement. | M20. Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order to perform its Real-time monitoring and Real-time Assessments as specified in the requirement. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 200000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R21. | 837500000008788 | Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 180 calendar days since the previous test; OR The Transmission Operator did not test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | M21. Each Transmission Operator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R20 for the redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R21. Evidence could include, but is not limited to: dated and time‐stamped test records, operator logs, voice recordings, or electronic communications. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 210000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R22. | RQ-2021-09-20-0000002-SK | Reserved. | [29 empty] | Reserved. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 220000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R23. | 837500000008790 | Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. |  | BA | BA | [20 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Balancing Authority had data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions, but did not have redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, as specified in the Requirement. | The Balancing Authority did not have data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions as specified in the Requirement. | M23. Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order to perform its Real-time monitoring and analysis functions as specified in the requirement. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 230000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R24. | 837500000008791 | Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 180 calendar days since the previous test OR The Balancing Authority did not test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | M24. Each Balancing Authority shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R24. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 240000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R3. | 837500000008764 | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. |  | BA, DP, GOP, TOP | BA | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Transmission Operator, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | M3. Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by the Transmission Operator(s) unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Balancing Authority, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Transmission Operator’s Operating Instruction. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 30000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R4. | 837500000008765 | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. |  | BA, DP, GOP, TOP | BA | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Transmission Operator of its inability to comply with its Operating Instruction issued. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 40000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R5. | 837500000008766 | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. |  | DP, GOP, TOP |  | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Balancing Authority, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | . Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by its Balancing Authority unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Transmission Operator, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Balancing Authority’s Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 50000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R6. | 837500000008767 | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. |  | DP, GOP, TOP |  | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | M6. Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Balancing Authority of its inability to comply with its Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 60000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R7. | 837500000008768 | Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator did not provide comparable assistance to other Transmission Operators within its Reliability Coordinator Area, when requested and able, and the requesting entity had implemented its Emergency procedures, and such actions could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | Each Transmission Operator shall make available upon request, evidence that comparable requested assistance, if able, was provided to other Transmission Operators within its Reliability Coordinator Area unless such assistance could not be physically implemented or would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no request for assistance was received, the Transmission Operator may provide an attestation. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 70000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R8. | 837500000008769 | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | The Transmission Operator did not inform one known impacted Transmission Operator or 5% or less of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform one known impacted Balancing Authorities or 5% or less of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform two known impacted Transmission Operators or more than 5% and less than or equal to 10% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform two known impacted Balancing Authorities or more than 5% and less than or equal to 10% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas | The Transmission Operator did not inform three known impacted Transmission Operators or more than 10% and less than or equal to 15% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform three known impacted Balancing Authorities or more than 10% and less than or equal to 15% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform its Reliability Coordinator of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Transmission Operators or more than 15% of the known impacted Transmission Operators of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Balancing Authorities or more than 15% of the known impacted Balancing Authorities of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | Each Transmission Operator shall make available upon request, evidence that it informed its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If no such situations have occurred, the Transmission Operator may provide an attestation. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 80000000
TOP-001-5 (Saskatchewan) | 83750000000603 | R9. | 837500000008770 | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity did not notify one known impacted interconnected entity or 5% or less of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify two known impacted interconnected entities or more than 5% and less than or equal to 10% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify three known impacted interconnected entities or more than 10% and less than or equal to 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify its Reliability Coordinator of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. OR The responsible entity did not notify four or more known impacted interconnected entities or more than 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | M9. Each Balancing Authority and Transmission Operator shall make available upon request, evidence that it notified its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Balancing Authority or Transmission Operator may provide an attestation. | 2021-04-01 |  | 2024-03-31 |  |  |  | MRO-SK | [6 empty] | 90000000
TOP-001-6 | ST-2021-07-12-0000001 | R1. | RQ-2021-07-12-0000002 | Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator failed to act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Each Transmission Operator shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-001-6 | ST-2021-07-12-0000001 | R10. | RQ-2021-07-13-0000002 | Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | The Transmission Operator did not monitor, obtain, or utilize one of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize two of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize three of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize four or more of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10 Part 10.1 through 10.6. | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 100000000
TOP-001-6 | ST-2021-07-12-0000001 | R11. | RQ-2021-07-13-0000003 | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. |  | BA | BA | [20 empty] | Real-Time Operations | High | N/A | N/A | The Balancing Authority did not monitor the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load- interchange balance within its Balancing Authority Area and support Interconnection frequency. | The Balancing Authority did not monitor its Balancing Authority Area, in order to maintain generation-Load- interchange balance within its Balancing Authority Area and support Interconnection frequency. | Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 110000000
TOP-001-6 | ST-2021-07-12-0000001 | R12. | RQ-2021-07-13-0000004 | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator exceeded an identified Interconnection Reliability Operating Limit (IROL) for a continuous duration greater than its associated IROL Tv. | Each Transmission Operator shall make available evidence to show that for any occasion in which it operated outside any identified Interconnection Reliability Operating Limit (IROL), the continuous duration did not exceed its associated IROL Tv. Such evidence could include but is not limited to dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If such a situation has not occurred, the Transmission Operator may provide an attestation that an event has not occurred. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 120000000
TOP-001-6 | ST-2021-07-12-0000001 | R13. | RQ-2021-07-13-0000005 | Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for one 30- minute period within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for two 30- minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for three 30- minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for four or more 30-minute periods within that 24-hour period. | Each Transmission Operator shall have, and make available upon request, evidence to show it ensured that a Real-Time Assessment was performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 130000000
TOP-001-6 | ST-2021-07-12-0000001 | R14. | RQ-2021-07-13-0000006 | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator did not initiate its Operating Plan for mitigating a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. | Each Transmission Operator shall have evidence that it initiated its Operating Plan for mitigating SOL exceedances identified as part of its Real-time monitoring or Real-time Assessments. This evidence could include but is not limited to dated computer logs showing times the Operating Plan was initiated, dated checklists, or other evidence. Other evidence could include but is not limited to: Reliability Coordinator’s SOL methodology, system logs/records showing successfully mitigated SOL exceedances in conjunction with Operating Plans (e.g. mutually agreed operating protocols between TOPs and their Reliability Coordinator, Operating Procedures, Operating Processes, operating policies, generator redispatch logs, equipment settings for automatically switched equipment and reactive power/voltage control devices, switching schedules, etc.). | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 140000000
TOP-001-6 | ST-2021-07-12-0000001 | R15. | RQ-2021-07-13-0000007 | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded in accordance with its Reliability Coordinator’s SOL methodology. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | N/A | The Transmission Operator did not inform in accordance with its Reliability Coordinator’s SOL methodology its Reliability Coordinator of actions taken to return the System to within limits when a SOL had been exceeded. | Each Transmission Operator shall make available evidence that it informed its Reliability Coordinator of actions taken to return the System to within limits when a SOL was exceeded in accordance with its Reliability Coordinator’s SOL methodology. Such evidence could include but is not limited to dated operator logs, electronic communications, voice recordings or transcripts of voice recordings, or dated computer printouts. If such a situation has not occurred, the Transmission Operator may provide an attestation. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 150000000
TOP-001-6 | ST-2021-07-12-0000001 | R16. | RQ-2021-07-13-0000008 | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Transmission Operator has provided its System Operators with the authority to approve planned outages and maintenance of telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 160000000
TOP-001-6 | ST-2021-07-12-0000001 | R17. | RQ-2021-07-13-0000009 | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | BA | BA | [20 empty] | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Balancing Authority did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Balancing Authority has provided its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 170000000
TOP-001-6 | ST-2021-07-12-0000001 | R18. | RQ-2021-07-13-0000010 | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator failed to operate to the most limiting parameter in instances where there was a difference in SOLs. | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to operator logs, voice recordings, electronic communications, or equivalent evidence that will be used to determine if it operated to the most limiting parameter in instances where there is a difference in SOLs. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 180000000
TOP-001-6 | ST-2021-07-12-0000001 | R19. | RQ-2021-07-13-0000011 | Reserved. | [29 empty] | Reserved. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 190000000
TOP-001-6 | ST-2021-07-12-0000001 | R2. | RQ-2021-07-12-0000003 | Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. |  | BA | BA | [20 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Balancing Authority failed to act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Each Balancing Authority shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-001-6 | ST-2021-07-12-0000001 | R20. | RQ-2021-07-13-0000012 | Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator had data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments, but did not have redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, as specified in the Requirement. | The Transmission Operator did not have data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments as specified in the Requirement. | Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order to perform its Real-time monitoring and Real-time Assessments as specified in the requirement. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 200000000
TOP-001-6 | ST-2021-07-12-0000001 | R21. | RQ-2021-07-13-0000013 | Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 180 calendar days since the previous test; OR The Transmission Operator did not test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | Each Transmission Operator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R20 for the redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R21. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 210000000
TOP-001-6 | ST-2021-07-12-0000001 | R22. | RQ-2021-07-13-0000014 | Reserved. | [29 empty] | Reserved. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 220000000
TOP-001-6 | ST-2021-07-12-0000001 | R23. | RQ-2021-07-13-0000015 | Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Balancing Authority had data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real- time monitoring and analysis functions, but did not have redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, as specified in the Requirement. | The Balancing Authority did not have data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions as specified in the Requirement. | Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order to perform its Real-time monitoring and analysis functions as specified in the requirement. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 230000000
TOP-001-6 | ST-2021-07-12-0000001 | R24. | RQ-2021-07-13-0000016 | Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 180 calendar days since the previous test; OR The Balancing Authority did not test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | Each Balancing Authority shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R24. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 240000000
TOP-001-6 | ST-2021-07-12-0000001 | R25. | RQ-2021-07-13-0000017 | Each Transmission Operator shall use the applicable Reliability Coordinator’s SOL methodology when determining SOL exceedances for Real-time Assessments, Real- time monitoring, and Operational Planning Analysis. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High |  |  |  | The Transmission Operator failed to use the applicable Reliability Coordinator’s SOL methodology when determining SOL exceedances for Real-time Assessments, Real-time monitoring, and Operational Planning Analysis. | Each Transmission Operator shall have, and provide upon request, evidence that it used the applicable Reliability Coordinator’s SOL methodology when determining SOL exceedances for Real-time Assessments, Real-time monitoring, and Operational Planning Analysis. Evidence could include, but is not limited to: Reliability Coordinator’s SOL methodology, Operating Plans, contingency sets, alarming and study reporting thresholds, operator logs, voice recordings or other equivalent evidence. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 250000000
TOP-001-6 | ST-2021-07-12-0000001 | R3. | RQ-2021-07-12-0000004 | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. |  | BA, DP, GOP, TOP | BA | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Transmission Operator, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by the Transmission Operator(s) unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Balancing Authority, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Transmission Operator’s Operating Instruction. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-001-6 | ST-2021-07-12-0000001 | R4. | RQ-2021-07-12-0000005 | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. |  | BA, DP, GOP, TOP | BA | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Transmission Operator of its inability to comply with its Operating Instruction issued. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-001-6 | ST-2021-07-12-0000001 | R5. | RQ-2021-07-12-0000006 | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. |  | DP, GOP, TOP |  | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Balancing Authority, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by its Balancing Authority unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Transmission Operator, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Balancing Authority’s Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-001-6 | ST-2021-07-12-0000001 | R6. | RQ-2021-07-12-0000007 | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. |  | DP, GOP, TOP |  | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Balancing Authority of its inability to comply with its Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TOP-001-6 | ST-2021-07-12-0000001 | R7. | RQ-2021-07-12-0000008 | Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator did not provide comparable assistance to other Transmission Operators within its Reliability Coordinator Area, when requested and able, and the requesting entity had implemented its Emergency procedures, and such actions could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | Each Transmission Operator shall make available upon request, evidence that comparable requested assistance, if able, was provided to other Transmission Operators within its Reliability Coordinator Area unless such assistance could not be physically implemented or would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no request for assistance was received, the Transmission Operator may provide an attestation. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
TOP-001-6 | ST-2021-07-12-0000001 | R8. | RQ-2021-07-12-0000009 | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | The Transmission Operator did not inform one known impacted Transmission Operator or 5% or less of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR, The Transmission Operator did not inform one known impacted Balancing Authorities or 5% or less of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform two known impacted Transmission Operators or more than 5% and less than or equal to 10% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR, The Transmission Operator did not inform two known impacted Balancing Authorities or more than 5% and less than or equal to 10% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform three known impacted Transmission Operators or more than 10% and less than or equal to 15% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR, The Transmission Operator did not inform three known impacted Balancing Authorities or more than 10% and less than or equal to 15% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform its Reliability Coordinator of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Transmission Operators or more than 15% of the known impacted Transmission Operators of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR, The Transmission Operator did not inform four or more known impacted Balancing Authorities or more than 15% of the known impacted Balancing Authorities of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | Each Transmission Operator shall make available upon request, evidence that it informed its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If no such situations have occurred, the Transmission Operator may provide an attestation. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
TOP-001-6 | ST-2021-07-12-0000001 | R9. | RQ-2021-07-13-0000001 | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity did not notify one known impacted interconnected entity or 5% or less of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify two known impacted interconnected entities or more than 5% and less than or equal to 10% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify three known impacted interconnected entities or more than 10% and less than or equal to 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify its Reliability Coordinator of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. OR, The responsible entity did not notify four or more known impacted interconnected entities or more than 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | Each Balancing Authority and Transmission Operator shall make available upon request, evidence that it notified its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Balancing Authority or Transmission Operator may provide an attestation. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R1. | RQ-2021-07-12-0000002-NS | Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator failed to act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Each Transmission Operator shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 10000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R10. | RQ-2021-07-13-0000002-NS | Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | The Transmission Operator did not monitor, obtain, or utilize one of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize two of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize three of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize four or more of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10 Part 10.1 through 10.6. | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 100000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R11. | RQ-2021-07-13-0000003-NS | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. |  | BA | BA | [20 empty] | Real-Time Operations | High | N/A | N/A | The Balancing Authority did not monitor the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load- interchange balance within its Balancing Authority Area and support Interconnection frequency. | The Balancing Authority did not monitor its Balancing Authority Area, in order to maintain generation-Load- interchange balance within its Balancing Authority Area and support Interconnection frequency. | Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 110000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R12. | RQ-2021-07-13-0000004-NS | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator exceeded an identified Interconnection Reliability Operating Limit (IROL) for a continuous duration greater than its associated IROL Tv. | Each Transmission Operator shall make available evidence to show that for any occasion in which it operated outside any identified Interconnection Reliability Operating Limit (IROL), the continuous duration did not exceed its associated IROL Tv. Such evidence could include but is not limited to dated computer logs or reports in electronic or hard copy format specifying the date, time, duration, and details of the excursion. If such a situation has not occurred, the Transmission Operator may provide an attestation that an event has not occurred. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 120000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R13. | RQ-2021-07-13-0000005-NS | Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for one 30- minute period within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for two 30- minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for three 30- minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for four or more 30-minute periods within that 24-hour period. | Each Transmission Operator shall have, and make available upon request, evidence to show it ensured that a Real-Time Assessment was performed at least once every 30 minutes. This evidence could include but is not limited to dated computer logs showing times the assessment was conducted, dated checklists, or other evidence. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 130000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R14. | RQ-2021-07-13-0000006-NS | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator did not initiate its Operating Plan for mitigating a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. | Each Transmission Operator shall have evidence that it initiated its Operating Plan for mitigating SOL exceedances identified as part of its Real-time monitoring or Real-time Assessments. This evidence could include but is not limited to dated computer logs showing times the Operating Plan was initiated, dated checklists, or other evidence. Other evidence could include but is not limited to: Reliability Coordinator’s SOL methodology, system logs/records showing successfully mitigated SOL exceedances in conjunction with Operating Plans (e.g. mutually agreed operating protocols between TOPs and their Reliability Coordinator, Operating Procedures, Operating Processes, operating policies, generator redispatch logs, equipment settings for automatically switched equipment and reactive power/voltage control devices, switching schedules, etc.). | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 140000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R15. | RQ-2021-07-13-0000007-NS | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded in accordance with its Reliability Coordinator’s SOL methodology. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | N/A | The Transmission Operator did not inform in accordance with its Reliability Coordinator’s SOL methodology its Reliability Coordinator of actions taken to return the System to within limits when a SOL had been exceeded. | Each Transmission Operator shall make available evidence that it informed its Reliability Coordinator of actions taken to return the System to within limits when a SOL was exceeded in accordance with its Reliability Coordinator’s SOL methodology. Such evidence could include but is not limited to dated operator logs, electronic communications, voice recordings or transcripts of voice recordings, or dated computer printouts. If such a situation has not occurred, the Transmission Operator may provide an attestation. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 150000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R16. | RQ-2021-07-13-0000008-NS | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Transmission Operator has provided its System Operators with the authority to approve planned outages and maintenance of telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 160000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R17. | RQ-2021-07-13-0000009-NS | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | BA | BA | [20 empty] | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Balancing Authority did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to a documented procedure or equivalent evidence that will be used to confirm that the Balancing Authority has provided its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 170000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R18. | RQ-2021-07-13-0000010-NS | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Transmission Operator failed to operate to the most limiting parameter in instances where there was a difference in SOLs. | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to operator logs, voice recordings, electronic communications, or equivalent evidence that will be used to determine if it operated to the most limiting parameter in instances where there is a difference in SOLs. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 180000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R19. | RQ-2021-07-13-0000011-NS | Reserved. |  | BA, DP, GOP, TOP | BA | DP |  |  |  | GOP | [12 empty] | TOP | [8 empty] | Reserved. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 190000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R2. | RQ-2021-07-12-0000003-NS | Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. |  | BA | BA | [20 empty] | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The Balancing Authority failed to act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Each Balancing Authority shall have and provide evidence which may include but is not limited to dated operator logs, dated records, dated and time-stamped voice recordings or dated transcripts of voice recordings, electronic communications, or equivalent documentation, that will be used to determine that it acted to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 20000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R20. | RQ-2021-07-13-0000012-NS | Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator had data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments, but did not have redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, as specified in the Requirement. | The Transmission Operator did not have data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments as specified in the Requirement. | Each Transmission Operator shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order to perform its Real-time monitoring and Real-time Assessments as specified in the requirement. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 200000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R21. | RQ-2021-07-13-0000013-NS | Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 180 calendar days since the previous test; OR The Transmission Operator did not test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | Each Transmission Operator shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R20 for the redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R21. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 210000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R22. | RQ-2021-07-13-0000014-NS | Reserved. |  | BA, DP, GOP, TOP | BA | DP |  |  |  | GOP | [12 empty] | TOP | [8 empty] | Reserved. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 220000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R23. | RQ-2021-07-13-0000015-NS | Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Balancing Authority had data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real- time monitoring and analysis functions, but did not have redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, as specified in the Requirement. | The Balancing Authority did not have data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions as specified in the Requirement. | Each Balancing Authority shall have, and provide upon request, evidence that could include, but is not limited to, system specifications, system diagrams, or other documentation that lists its data exchange capabilities, including redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order to perform its Real-time monitoring and analysis functions as specified in the requirement. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 230000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R24. | RQ-2021-07-13-0000016-NS | Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 180 calendar days since the previous test; OR The Balancing Authority did not test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | Each Balancing Authority shall have, and provide upon request, evidence that it tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, or experienced an event that demonstrated the redundant functionality; and, if the test was unsuccessful, initiated action within two hours to restore redundant functionality as specified in Requirement R24. Evidence could include, but is not limited to: dated and time-stamped test records, operator logs, voice recordings, or electronic communications. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 240000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R25. | RQ-2021-07-13-0000017-NS | Each Transmission Operator shall use the applicable Reliability Coordinator’s SOL methodology when determining SOL exceedances for Real-time Assessments, Real- time monitoring, and Operational Planning Analysis. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High |  |  |  | The Transmission Operator failed to use the applicable Reliability Coordinator’s SOL methodology when determining SOL exceedances for Real-time Assessments, Real-time monitoring, and Operational Planning Analysis. | Each Transmission Operator shall have, and provide upon request, evidence that it used the applicable Reliability Coordinator’s SOL methodology when determining SOL exceedances for Real-time Assessments, Real-time monitoring, and Operational Planning Analysis. Evidence could include, but is not limited to: Reliability Coordinator’s SOL methodology, Operating Plans, contingency sets, alarming and study reporting thresholds, operator logs, voice recordings or other equivalent evidence. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 250000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R3. | RQ-2021-07-12-0000004-NS | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. |  | BA, DP, GOP, TOP | BA | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Transmission Operator, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by the Transmission Operator(s) unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Balancing Authority, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Transmission Operator’s Operating Instruction. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 30000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R4. | RQ-2021-07-12-0000005-NS | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. |  | BA, DP, GOP, TOP | BA | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | Each Balancing Authority, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Transmission Operator of its inability to comply with its Operating Instruction issued. If such a situation has not occurred, the Balancing Authority, Generator Operator, or Distribution Provider may provide an attestation. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 40000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R5. | RQ-2021-07-12-0000006-NS | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. |  | BA, DP, GOP, TOP | BA | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Balancing Authority, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence that it complied with each Operating Instruction issued by its Balancing Authority unless such action could not be physically implemented or it would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. In such cases, the Transmission Operator, Generator Operator, and Distribution Provider shall have and provide copies of the safety, equipment, regulatory, or statutory requirements as evidence for not complying with the Balancing Authority’s Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 50000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R6. | RQ-2021-07-12-0000007-NS | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. |  | BA, DP, GOP, TOP | BA | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Real-Time Operations, Same-Day Operations | High | N/A | N/A | N/A | The responsible entity did not inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | Each Transmission Operator, Generator Operator, and Distribution Provider shall make available upon request, evidence which may include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or equivalent evidence in electronic or hard copy format, that it informed its Balancing Authority of its inability to comply with its Operating Instruction. If such a situation has not occurred, the Transmission Operator, Generator Operator, or Distribution Provider may provide an attestation. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 60000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R7. | RQ-2021-07-12-0000008-NS | Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The Transmission Operator did not provide comparable assistance to other Transmission Operators within its Reliability Coordinator Area, when requested and able, and the requesting entity had implemented its Emergency procedures, and such actions could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | Each Transmission Operator shall make available upon request, evidence that comparable requested assistance, if able, was provided to other Transmission Operators within its Reliability Coordinator Area unless such assistance could not be physically implemented or would have violated safety, equipment, regulatory, or statutory requirements. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence in electronic or hard copy format. If no request for assistance was received, the Transmission Operator may provide an attestation. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 70000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R8. | RQ-2021-07-12-0000009-NS | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | The Transmission Operator did not inform one known impacted Transmission Operator or 5% or less of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR, The Transmission Operator did not inform one known impacted Balancing Authorities or 5% or less of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform two known impacted Transmission Operators or more than 5% and less than or equal to 10% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR, The Transmission Operator did not inform two known impacted Balancing Authorities or more than 5% and less than or equal to 10% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform three known impacted Transmission Operators or more than 10% and less than or equal to 15% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR, The Transmission Operator did not inform three known impacted Balancing Authorities or more than 10% and less than or equal to 15% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform its Reliability Coordinator of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Transmission Operators or more than 15% of the known impacted Transmission Operators of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR, The Transmission Operator did not inform four or more known impacted Balancing Authorities or more than 15% of the known impacted Balancing Authorities of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | Each Transmission Operator shall make available upon request, evidence that it informed its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If no such situations have occurred, the Transmission Operator may provide an attestation. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 80000000
TOP-001-6 (Nova Scotia) | ST-2021-07-12-0000001-NS | R9. | RQ-2021-07-13-0000001-NS | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity did not notify one known impacted interconnected entity or 5% or less of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify two known impacted interconnected entities or more than 5% and less than or equal to 10% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify three known impacted interconnected entities or more than 10% and less than or equal to 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify its Reliability Coordinator of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. OR, The responsible entity did not notify four or more known impacted interconnected entities or more than 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | Each Balancing Authority and Transmission Operator shall make available upon request, evidence that it notified its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence. If such a situation has not occurred, the Balancing Authority or Transmission Operator may provide an attestation. | 2024-10-01 | [5 empty] | NPCC-NS | [6 empty] | 90000000
TOP-002-0 | 418 | R1. | 5155 | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-08-07 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-002-0 | 418 | R10. | 5156 | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-08-07 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 100000000
TOP-002-0 | 418 | R11. | 5157 | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject confidentiality requirements), and to its Reliability Coordinator. |  | TOP | [18 empty] | TOP | [11 empty] | 2007-08-07 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 110000000
TOP-002-0 | 418 | R12. | 5158 | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  | TSP | [20 empty] | TSP | [9 empty] | 2007-08-07 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 120000000
TOP-002-0 | 418 | R13. | 5159 | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP | [11 empty] | 2007-08-07 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 130000000
TOP-002-0 | 418 | R14. | 5160 | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  | GOP | [5 empty] | GOP | [24 empty] | 2007-08-07 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 140000000
TOP-002-0 | 418 | R15. | 5163 | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | GOP | [5 empty] | GOP | [24 empty] | 2007-08-07 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 150000000
TOP-002-0 | 418 | R16. | 5164 | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  | TOP | [18 empty] | TOP | [11 empty] | 2007-08-07 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 160000000
TOP-002-0 | 418 | R17. | 5167 | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-08-07 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 170000000
TOP-002-0 | 418 | R18. | 5168 | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers and Load Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | BA, GOP, LSE, TOP, TSP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP | [9 empty] | 2007-08-07 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 180000000
TOP-002-0 | 418 | R19. | 5177 | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-08-07 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 190000000
TOP-002-0 | 418 | R2. | 5169 | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-08-07 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-002-0 | 418 | R3. | 5170 | Each Load Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  | GOP, LSE | [5 empty] | GOP |  | LSE | [22 empty] | 2007-08-07 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-002-0 | 418 | R4. | 5171 | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-08-07 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-002-0 | 418 | R5. | 5172 | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-08-07 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-002-0 | 418 | R6. | 5173 | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-08-07 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TOP-002-0 | 418 | R7. | 5174 | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | BA | BA | [29 empty] | 2007-08-07 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
TOP-002-0 | 418 | R8. | 5175 | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | BA | BA | [29 empty] | 2007-08-07 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
TOP-002-0 | 418 | R9. | 5176 | Each Balancing Authority shall plan to meet Interchange Schedules and ramps. |  | BA | BA | [29 empty] | 2007-08-07 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
TOP-002-0 (Ontario) | 79780000418 | R1. | 79780005155 |  |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-08-07 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-002-0 (Ontario) | 79780000418 | R10. | 79780005156 |  |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-08-07 |  |  |  | NPCC-ON | [6 empty] | 100000000
TOP-002-0 (Ontario) | 79780000418 | R11. | 79780005157 |  |  | TOP | [18 empty] | TOP | [11 empty] | 2007-08-07 |  |  |  | NPCC-ON | [6 empty] | 110000000
TOP-002-0 (Ontario) | 79780000418 | R12. | 79780005158 |  |  | TSP | [20 empty] | TSP | [9 empty] | 2007-08-07 |  |  |  | NPCC-ON | [6 empty] | 120000000
TOP-002-0 (Ontario) | 79780000418 | R13. | 79780005159 |  |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP | [11 empty] | 2007-08-07 |  |  |  | NPCC-ON | [6 empty] | 130000000
TOP-002-0 (Ontario) | 79780000418 | R14. | 79780005160 |  |  | GOP | [5 empty] | GOP | [24 empty] | 2007-08-07 |  |  |  | NPCC-ON | [6 empty] | 140000000
TOP-002-0 (Ontario) | 79780000418 | R15. | 79780005163 |  |  | GOP | [5 empty] | GOP | [24 empty] | 2007-08-07 |  |  |  | NPCC-ON | [6 empty] | 150000000
TOP-002-0 (Ontario) | 79780000418 | R16. | 79780005164 |  |  | TOP | [18 empty] | TOP | [11 empty] | 2007-08-07 |  |  |  | NPCC-ON | [6 empty] | 160000000
TOP-002-0 (Ontario) | 79780000418 | R17. | 79780005167 |  |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-08-07 |  |  |  | NPCC-ON | [6 empty] | 170000000
TOP-002-0 (Ontario) | 79780000418 | R18. | 79780005168 |  |  | BA, GOP, LSE, TOP, TSP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP | [9 empty] | 2007-08-07 |  |  |  | NPCC-ON | [6 empty] | 180000000
TOP-002-0 (Ontario) | 79780000418 | R19. | 79780005177 |  |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-08-07 |  |  |  | NPCC-ON | [6 empty] | 190000000
TOP-002-0 (Ontario) | 79780000418 | R2. | 79780005169 |  |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-08-07 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-002-0 (Ontario) | 79780000418 | R3. | 79780005170 |  |  | GOP, LSE | [5 empty] | GOP |  | LSE | [22 empty] | 2007-08-07 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-002-0 (Ontario) | 79780000418 | R4. | 79780005171 |  |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-08-07 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-002-0 (Ontario) | 79780000418 | R5. | 79780005172 |  |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-08-07 |  |  |  | NPCC-ON | [6 empty] | 50000000
TOP-002-0 (Ontario) | 79780000418 | R6. | 79780005173 |  |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-08-07 |  |  |  | NPCC-ON | [6 empty] | 60000000
TOP-002-0 (Ontario) | 79780000418 | R7. | 79780005174 |  |  | BA | BA | [29 empty] | 2007-08-07 |  |  |  | NPCC-ON | [6 empty] | 70000000
TOP-002-0 (Ontario) | 79780000418 | R8. | 79780005175 |  |  | BA | BA | [29 empty] | 2007-08-07 |  |  |  | NPCC-ON | [6 empty] | 80000000
TOP-002-0 (Ontario) | 79780000418 | R9. | 79780005176 |  |  | BA | BA | [29 empty] | 2007-08-07 |  |  |  | NPCC-ON | [6 empty] | 90000000
TOP-002-1 | 419 | R1. | 5178 | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-002-1 | 419 | R10. | 5179 | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 100000000
TOP-002-1 | 419 | R11. | 5180 | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject confidentiality requirements), and to its Reliability Coordinator. |  | TOP | [18 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 110000000
TOP-002-1 | 419 | R12. | 5181 | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  | TSP | [20 empty] | TSP | [9 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 120000000
TOP-002-1 | 419 | R13. | 5182 | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 130000000
TOP-002-1 | 419 | R14. | 5183 | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  | GOP | [5 empty] | GOP | [24 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 140000000
TOP-002-1 | 419 | R15. | 5185 | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | GOP | [5 empty] | GOP | [24 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 150000000
TOP-002-1 | 419 | R16. | 5186 | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  | TOP | [18 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 160000000
TOP-002-1 | 419 | R17. | 5189 | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 170000000
TOP-002-1 | 419 | R18. | 5190 | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers and Load Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | BA, GOP, TOP, TSP | BA |  |  |  |  | GOP | [12 empty] | TOP |  | TSP | [9 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 180000000
TOP-002-1 | 419 | R19. | 5199 | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 190000000
TOP-002-1 | 419 | R2. | 5191 | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-002-1 | 419 | R3. | 5192 | Each Load Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  | GOP, LSE | [5 empty] | GOP |  | LSE | [22 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-002-1 | 419 | R4. | 5193 | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-002-1 | 419 | R5. | 5194 | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-002-1 | 419 | R6. | 5195 | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TOP-002-1 | 419 | R7. | 5196 | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | BA | BA | [29 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
TOP-002-1 | 419 | R8. | 5197 | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | BA | BA | [29 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
TOP-002-1 | 419 | R9. | 5198 | Each Balancing Authority shall plan to meet Interchange Schedules and ramps. |  | BA | BA | [29 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
TOP-002-1 (Ontario) | 79780000419 | R1. | 79780005178 |  |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-002-1 (Ontario) | 79780000419 | R10. | 79780005179 |  |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 100000000
TOP-002-1 (Ontario) | 79780000419 | R11. | 79780005180 |  |  | TOP | [18 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 110000000
TOP-002-1 (Ontario) | 79780000419 | R12. | 79780005181 |  |  | TSP | [20 empty] | TSP | [9 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 120000000
TOP-002-1 (Ontario) | 79780000419 | R13. | 79780005182 |  |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 130000000
TOP-002-1 (Ontario) | 79780000419 | R14. | 79780005183 |  |  | GOP | [5 empty] | GOP | [24 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 140000000
TOP-002-1 (Ontario) | 79780000419 | R15. | 79780005185 |  |  | GOP | [5 empty] | GOP | [24 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 150000000
TOP-002-1 (Ontario) | 79780000419 | R16. | 79780005186 |  |  | TOP | [18 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 160000000
TOP-002-1 (Ontario) | 79780000419 | R17. | 79780005189 |  |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 170000000
TOP-002-1 (Ontario) | 79780000419 | R18. | 79780005190 |  |  | BA, GOP, TOP, TSP | BA |  |  |  |  | GOP | [12 empty] | TOP |  | TSP | [9 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 180000000
TOP-002-1 (Ontario) | 79780000419 | R19. | 79780005199 |  |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 190000000
TOP-002-1 (Ontario) | 79780000419 | R2. | 79780005191 |  |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-002-1 (Ontario) | 79780000419 | R3. | 79780005192 |  |  | GOP, LSE | [5 empty] | GOP |  | LSE | [22 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-002-1 (Ontario) | 79780000419 | R4. | 79780005193 |  |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-002-1 (Ontario) | 79780000419 | R5. | 79780005194 |  |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 50000000
TOP-002-1 (Ontario) | 79780000419 | R6. | 79780005195 |  |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 60000000
TOP-002-1 (Ontario) | 79780000419 | R7. | 79780005196 |  |  | BA | BA | [29 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 70000000
TOP-002-1 (Ontario) | 79780000419 | R8. | 79780005197 |  |  | BA | BA | [29 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 80000000
TOP-002-1 (Ontario) | 79780000419 | R9. | 79780005198 |  |  | BA | BA | [29 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 90000000
TOP-002-2 | 169 | R1. | 1903 | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2009-12-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-002-2 | 169 | R10. | 1904 | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2009-12-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 100000000
TOP-002-2 | 169 | R11. | 1905 | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2009-12-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 110000000
TOP-002-2 | 169 | R12. | 1906 | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  | TSP | [20 empty] | TSP |  | Medium | [5 empty] | 2007-06-18 |  | 2009-12-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 120000000
TOP-002-2 | 169 | R13. | 1907 | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2007-06-18 |  | 2009-12-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 130000000
TOP-002-2 | 169 | R14. | 1908 | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2007-06-18 |  | 2009-12-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 140000000
TOP-002-2 | 169 | R15. | 1911 | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | GOP | [5 empty] | GOP | [16 empty] | Low | [5 empty] | 2007-06-18 |  | 2009-12-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 150000000
TOP-002-2 | 169 | R16. | 1912 | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2009-12-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 160000000
TOP-002-2 | 169 | R17. | 1915 | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High | [5 empty] | 2007-06-18 |  | 2009-12-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 170000000
TOP-002-2 | 169 | R18. | 1916 | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | BA, GOP, LSE, TOP, TSP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP |  | Medium | [5 empty] | 2007-06-18 |  | 2009-12-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 180000000
TOP-002-2 | 169 | R19. | 1917 | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2009-12-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 190000000
TOP-002-2 | 169 | R2. | 1918 | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2009-12-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-002-2 | 169 | R3. | 1919 | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  | BA, GOP, LSE, TSP | BA |  |  |  |  | GOP |  | LSE | [12 empty] | TSP |  | Medium | [5 empty] | 2007-06-18 |  | 2009-12-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-002-2 | 169 | R4. | 1920 | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2009-12-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-002-2 | 169 | R5. | 1921 | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2009-12-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-002-2 | 169 | R6. | 1922 | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2009-12-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TOP-002-2 | 169 | R7. | 1923 | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2007-06-18 |  | 2009-12-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
TOP-002-2 | 169 | R8. | 1924 | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2007-06-18 |  | 2009-12-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
TOP-002-2 | 169 | R9. | 1925 | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. |  | BA | BA | [21 empty] | Low | [5 empty] | 2007-06-18 |  | 2009-12-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
TOP-002-2.1b | 318 | R1. | 4145 | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M1. Each Balancing Authority and Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, documented planning procedures, copies of current day plans, copies of seasonal operations plans, or other equivalent evidence that will be used to confirm that it maintained a set of current plans. (Requirement 1 Part 1). | 2012-09-13 |  | 2017-03-31 |  |  | TOP-002-2 R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-002-2.1b | 318 | R10. | 4153 | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M10. Each Balancing Authority, Transmission Operator, Generator Operator, Transmission Service Provider and Load Serving Entity shall have and provide upon request evidence that could include, but is not limited to, a list of interconnected transmission facilities and their line identifiers at each end or other equivalent evidence that will be used to confirm that it used uniform line identifiers when referring to transmission facilities of an interconnected network. (Requirement 18) | 2012-09-13 |  | 2017-03-31 |  |  | TOP-002-2 R10. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 100000000
TOP-002-2.1b | 318 | R11. | 4154 | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-09-13 |  | 2017-03-31 |  |  | TOP-002-2 R11. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 110000000
TOP-002-2.1b | 318 | R12. | 4155 | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  | TSP | [20 empty] | TSP |  | Medium | [5 empty] | 2012-09-13 |  | 2017-03-31 |  |  | TOP-002-2 R12. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 120000000
TOP-002-2.1b | 318 | R13. | 4156 | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2012-09-13 |  | 2017-03-31 |  |  | TOP-002-2 R13. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 130000000
TOP-002-2.1b | 318 | R14. | 4157 | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2012-09-13 |  | 2017-03-31 |  |  | TOP-002-2 R14. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 140000000
TOP-002-2.1b | 318 | R15. | 4158 | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | GOP | [5 empty] | GOP | [16 empty] | Low | [5 empty] | 2012-09-13 |  | 2017-03-31 |  |  | TOP-002-2 R15. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 150000000
TOP-002-2.1b | 318 | R16. | 4159 | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-09-13 |  | 2017-03-31 |  |  | TOP-002-2 R16. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 160000000
TOP-002-2.1b | 318 | R17. | 4160 | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High | [5 empty] | 2012-09-13 |  | 2017-03-31 |  |  | TOP-002-2 R17. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 170000000
TOP-002-2.1b | 318 | R18. | 4161 | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | BA, GOP, LSE, TOP, TSP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP |  | Medium | [5 empty] | 2012-09-13 |  | 2017-03-31 |  |  | TOP-002-2 R18. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 180000000
TOP-002-2.1b | 318 | R19. | 4162 | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-09-13 |  | 2017-03-31 |  |  | TOP-002-2 R19. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 190000000
TOP-002-2.1b | 318 | R2. | 4148 | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M2. Each Balancing Authority and Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, copies of current day plans or other equivalent evidence that will be used to confirm that its plans address Requirements 5, 6, and 10. | 2012-09-13 |  | 2017-03-31 |  |  | TOP-002-2 R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-002-2.1b | 318 | R3. | 4144 | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  | BA, GOP, LSE, TSP | BA |  |  |  |  | GOP |  | LSE | [12 empty] | TSP |  | Medium |  |  |  |  | M3. Each Balancing Authority shall have and provide upon request evidence that could include, but is not limited to, copies of current day plans or other equivalent evidence that will be used to confirm that its plans address Requirements 7, 8, and 9. | 2012-09-13 |  | 2017-03-31 |  |  | TOP-002-2 R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-002-2.1b | 318 | R4. | 4146 | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M4. Each Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, its next-day, and current-day Bulk Electric System studies used to determine SOLs or other equivalent evidence that will be used to confirm that its studies reflect current system conditions. (Requirement 11 Part 1) | 2012-09-13 |  | 2017-03-31 |  |  | TOP-002-2 R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-002-2.1b | 318 | R5. | 4147 | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M5. Each Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that the results of Bulk Electric System studies were made available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. (Requirement 11 Part 2) | 2012-09-13 |  | 2017-03-31 |  |  | TOP-002-2 R5. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-002-2.1b | 318 | R6. | 4151 | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M6. Each Generator Operator shall have and provide upon request evidence that, when requested by either a Transmission Operator or Balancing Authority, it performed a generating real and reactive capability verification and provided the results to the requesting entity in accordance with Requirement 13. | 2012-09-13 |  | 2017-03-31 |  |  | TOP-002-2 R6. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TOP-002-2.1b | 318 | R7. | 4152 | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | BA | BA | [21 empty] | Medium |  |  |  |  | M7. Each Generator Operator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that without any intentional time delay, it notified its Balancing Authority and Transmission Operator of changes in real capabilities. (Requirement 14) | 2012-09-13 |  | 2017-03-31 |  |  | TOP-002-2 R7. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
TOP-002-2.1b | 318 | R8. | 4150 | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | BA | BA | [21 empty] | Medium |  |  |  |  | M8. Each Generator Operator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that, on request, it provided a forecast of expected real power output to assist in operations planning. (Requirement 15) | 2012-09-13 |  | 2017-03-31 |  |  | TOP-002-2 R8. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
TOP-002-2.1b | 318 | R9. | 4149 | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. |  | BA | BA | [21 empty] | Low |  |  |  |  | M9. Each Transmission Operators shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that, without any intentional time delay, it notified its Balancing Authority and Reliability Coordinator of changes in capabilities and characteristics. (Requirement16) | 2012-09-13 |  | 2017-03-31 |  |  | TOP-002-2 R9. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
TOP-002-2.1b (British Columbia) | 666700000010277 | R1. | 666700000011679 | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M1. Each Balancing Authority and Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, documented planning procedures, copies of current day plans, copies of seasonal operations plans, or other equivalent evidence that will be used to confirm that it maintained a set of current plans. (Requirement 1 Part 1). | 2013-12-12 |  | 2021-03-31 |  |  |  | WECC-BC | [6 empty] | 10000000
TOP-002-2.1b (British Columbia) | 666700000010277 | R10. | 666700000011680 | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M10. Each Balancing Authority, Transmission Operator, Generator Operator, Transmission Service Provider and Load Serving Entity shall have and provide upon request evidence that could include, but is not limited to, a list of interconnected transmission facilities and their line identifiers at each end or other equivalent evidence that will be used to confirm that it used uniform line identifiers when referring to transmission facilities of an interconnected network. (Requirement 18) | 2013-12-12 |  | 2021-03-31 |  |  |  | WECC-BC | [6 empty] | 100000000
TOP-002-2.1b (British Columbia) | 666700000010277 | R11. | 666700000011681 | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2013-12-12 |  | 2021-03-31 |  |  |  | WECC-BC | [6 empty] | 110000000
TOP-002-2.1b (British Columbia) | 666700000010277 | R12. | 666700000011682 | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  | TSP | [20 empty] | TSP |  | Medium | [5 empty] | 2013-12-12 |  | 2021-03-31 |  |  |  | WECC-BC | [6 empty] | 120000000
TOP-002-2.1b (British Columbia) | 666700000010277 | R13. | 666700000011683 | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2013-12-12 |  | 2021-03-31 |  |  |  | WECC-BC | [6 empty] | 130000000
TOP-002-2.1b (British Columbia) | 666700000010277 | R14. | 666700000011684 | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2013-12-12 |  | 2021-03-31 |  |  |  | WECC-BC | [6 empty] | 140000000
TOP-002-2.1b (British Columbia) | 666700000010277 | R15. | 666700000011685 | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | GOP | [5 empty] | GOP | [16 empty] | Low | [5 empty] | 2013-12-12 |  | 2021-03-31 |  |  |  | WECC-BC | [6 empty] | 150000000
TOP-002-2.1b (British Columbia) | 666700000010277 | R16. | 666700000011686 | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2013-12-12 |  | 2021-03-31 |  |  |  | WECC-BC | [6 empty] | 160000000
TOP-002-2.1b (British Columbia) | 666700000010277 | R17. | 666700000011687 | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High | [5 empty] | 2013-12-12 |  | 2021-03-31 |  |  |  | WECC-BC | [6 empty] | 170000000
TOP-002-2.1b (British Columbia) | 666700000010277 | R18. | 666700000011688 | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | BA, GOP, LSE, TOP, TSP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP |  | Medium | [5 empty] | 2013-12-12 |  | 2021-03-31 |  |  |  | WECC-BC | [6 empty] | 180000000
TOP-002-2.1b (British Columbia) | 666700000010277 | R19. | 666700000011689 | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2013-12-12 |  | 2021-03-31 |  |  |  | WECC-BC | [6 empty] | 190000000
TOP-002-2.1b (British Columbia) | 666700000010277 | R2. | 666700000011690 | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M2. Each Balancing Authority and Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, copies of current day plans or other equivalent evidence that will be used to confirm that its plans address Requirements 5, 6, and 10. | 2013-12-12 |  | 2021-03-31 |  |  |  | WECC-BC | [6 empty] | 20000000
TOP-002-2.1b (British Columbia) | 666700000010277 | R3. | 666700000011691 | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  | BA, GOP, LSE, TSP | BA |  |  |  |  | GOP |  | LSE | [12 empty] | TSP |  | Medium |  |  |  |  | M3. Each Balancing Authority shall have and provide upon request evidence that could include, but is not limited to, copies of current day plans or other equivalent evidence that will be used to confirm that its plans address Requirements 7, 8, and 9. | 2013-12-12 |  | 2021-03-31 |  |  |  | WECC-BC | [6 empty] | 30000000
TOP-002-2.1b (British Columbia) | 666700000010277 | R4. | 666700000011692 | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M4. Each Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, its next-day, and current-day Bulk Electric System studies used to determine SOLs or other equivalent evidence that will be used to confirm that its studies reflect current system conditions. (Requirement 11 Part 1) | 2013-12-12 |  | 2021-03-31 |  |  |  | WECC-BC | [6 empty] | 40000000
TOP-002-2.1b (British Columbia) | 666700000010277 | R5. | 666700000011693 | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M5. Each Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that the results of Bulk Electric System studies were made available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. (Requirement 11 Part 2) | 2013-12-12 |  | 2021-03-31 |  |  |  | WECC-BC | [6 empty] | 50000000
TOP-002-2.1b (British Columbia) | 666700000010277 | R6. | 666700000011694 | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M6. Each Generator Operator shall have and provide upon request evidence that, when requested by either a Transmission Operator or Balancing Authority, it performed a generating real and reactive capability verification and provided the results to the requesting entity in accordance with Requirement 13. | 2013-12-12 |  | 2021-03-31 |  |  |  | WECC-BC | [6 empty] | 60000000
TOP-002-2.1b (British Columbia) | 666700000010277 | R7. | 666700000011695 | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | BA | BA | [21 empty] | Medium |  |  |  |  | M7. Each Generator Operator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that without any intentional time delay, it notified its Balancing Authority and Transmission Operator of changes in real capabilities. (Requirement 14) | 2013-12-12 |  | 2021-03-31 |  |  |  | WECC-BC | [6 empty] | 70000000
TOP-002-2.1b (British Columbia) | 666700000010277 | R8. | 666700000011696 | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | BA | BA | [21 empty] | Medium |  |  |  |  | M8. Each Generator Operator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that, on request, it provided a forecast of expected real power output to assist in operations planning. (Requirement 15) | 2013-12-12 |  | 2021-03-31 |  |  |  | WECC-BC | [6 empty] | 80000000
TOP-002-2.1b (British Columbia) | 666700000010277 | R9. | 666700000011697 | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. |  | BA | BA | [21 empty] | Low |  |  |  |  | M9. Each Transmission Operators shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that, without any intentional time delay, it notified its Balancing Authority and Reliability Coordinator of changes in capabilities and characteristics. (Requirement16) | 2013-12-12 |  | 2021-03-31 |  |  |  | WECC-BC | [6 empty] | 90000000
TOP-002-2.1b (Manitoba) | 77660000000318 | R1. | 776600000004145 | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M1. Each Balancing Authority and Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, documented planning procedures, copies of current day plans, copies of seasonal operations plans, or other equivalent evidence that will be used to confirm that it maintained a set of current plans. (Requirement 1 Part 1). | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
TOP-002-2.1b (Manitoba) | 77660000000318 | R10. | 776600000004153 | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M10. Each Balancing Authority, Transmission Operator, Generator Operator, Transmission Service Provider and Load Serving Entity shall have and provide upon request evidence that could include, but is not limited to, a list of interconnected transmission facilities and their line identifiers at each end or other equivalent evidence that will be used to confirm that it used uniform line identifiers when referring to transmission facilities of an interconnected network. (Requirement 18) | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 100000000
TOP-002-2.1b (Manitoba) | 77660000000318 | R11. | 776600000004154 | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 110000000
TOP-002-2.1b (Manitoba) | 77660000000318 | R12. | 776600000004155 | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  | TSP | [20 empty] | TSP |  | Medium | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 120000000
TOP-002-2.1b (Manitoba) | 77660000000318 | R13. | 776600000004156 | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 130000000
TOP-002-2.1b (Manitoba) | 77660000000318 | R14. | 776600000004157 | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 140000000
TOP-002-2.1b (Manitoba) | 77660000000318 | R15. | 776600000004158 | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | GOP | [5 empty] | GOP | [16 empty] | Low | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 150000000
TOP-002-2.1b (Manitoba) | 77660000000318 | R16. | 776600000004159 | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 160000000
TOP-002-2.1b (Manitoba) | 77660000000318 | R17. | 776600000004160 | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 170000000
TOP-002-2.1b (Manitoba) | 77660000000318 | R18. | 776600000004161 | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | BA, GOP, LSE, TOP, TSP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP |  | Medium | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 180000000
TOP-002-2.1b (Manitoba) | 77660000000318 | R19. | 776600000004162 | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 190000000
TOP-002-2.1b (Manitoba) | 77660000000318 | R2. | 776600000004148 | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M2. Each Balancing Authority and Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, copies of current day plans or other equivalent evidence that will be used to confirm that its plans address Requirements 5, 6, and 10. | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
TOP-002-2.1b (Manitoba) | 77660000000318 | R3. | 776600000004144 | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  | BA, GOP, LSE, TSP | BA |  |  |  |  | GOP |  | LSE | [12 empty] | TSP |  | Medium |  |  |  |  | M3. Each Balancing Authority shall have and provide upon request evidence that could include, but is not limited to, copies of current day plans or other equivalent evidence that will be used to confirm that its plans address Requirements 7, 8, and 9. | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
TOP-002-2.1b (Manitoba) | 77660000000318 | R4. | 776600000004146 | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M4. Each Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, its next-day, and current-day Bulk Electric System studies used to determine SOLs or other equivalent evidence that will be used to confirm that its studies reflect current system conditions. (Requirement 11 Part 1) | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 40000000
TOP-002-2.1b (Manitoba) | 77660000000318 | R5. | 776600000004147 | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M5. Each Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that the results of Bulk Electric System studies were made available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. (Requirement 11 Part 2) | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 50000000
TOP-002-2.1b (Manitoba) | 77660000000318 | R6. | 776600000004151 | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M6. Each Generator Operator shall have and provide upon request evidence that, when requested by either a Transmission Operator or Balancing Authority, it performed a generating real and reactive capability verification and provided the results to the requesting entity in accordance with Requirement 13. | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 60000000
TOP-002-2.1b (Manitoba) | 77660000000318 | R7. | 776600000004152 | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | BA | BA | [21 empty] | Medium |  |  |  |  | M7. Each Generator Operator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that without any intentional time delay, it notified its Balancing Authority and Transmission Operator of changes in real capabilities. (Requirement 14) | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 70000000
TOP-002-2.1b (Manitoba) | 77660000000318 | R8. | 776600000004150 | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | BA | BA | [21 empty] | Medium |  |  |  |  | M8. Each Generator Operator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that, on request, it provided a forecast of expected real power output to assist in operations planning. (Requirement 15) | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 80000000
TOP-002-2.1b (Manitoba) | 77660000000318 | R9. | 776600000004149 | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. |  | BA | BA | [21 empty] | Low |  |  |  |  | M9. Each Transmission Operators shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that, without any intentional time delay, it notified its Balancing Authority and Reliability Coordinator of changes in capabilities and characteristics. (Requirement16) | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 90000000
TOP-002-2.1b (Ontario) | 79780000318 | R1. | 79780004145 | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  | The responsible entity maintained a set of current plans that were designed to evaluate options and set procedures for reliable operation through a reasonable future time period, but failed utilize all available personnel and system equipment to implement | The responsible entity failed to maintain a set of current plans that were designed to evaluate options and set procedures for reliable operation through a reasonable future time period. | M1. Each Balancing Authority and Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, documented planning procedures, copies of current day plans, copies of seasonal operations plans, or other equivalent evidence that will be used to confirm that it maintained a set of current plans. (Requirement 1 Part 1). | 2012-09-13 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-002-2.1b (Ontario) | 79780000318 | R10. | 79780004153 | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). | M10. Each Balancing Authority, Transmission Operator, Generator Operator, Transmission Service Provider and Load Serving Entity shall have and provide upon request evidence that could include, but is not limited to, a list of interconnected transmission facilities and their line identifiers at each end or other equivalent evidence that will be used to confirm that it used uniform line identifiers when referring to transmission facilities of an interconnected network. (Requirement 18) | 2012-09-13 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 100000000
TOP-002-2.1b (Ontario) | 79780000318 | R11. | 79780004154 | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | Medium |  |  | The Transmission Operator performed seasonal, next-day, and current-day Bulk Electric System studies, reflecting current system conditions, to determine SOLs, but failed to make the results of Bulk Electric System studies available to all of the Transmiss | The Transmission Operator failed to perform seasonal, next-day, or current-day Bulk Electric System studies, reflecting current system conditions, to determine SOLs. |  | 2012-09-13 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 110000000
TOP-002-2.1b (Ontario) | 79780000318 | R12. | 79780004155 | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  | TSP | [20 empty] | TSP |  | Medium |  |  |  | The Transmission Service Provider failed to include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer |  | 2012-09-13 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 120000000
TOP-002-2.1b (Ontario) | 79780000318 | R13. | 79780004156 | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  | GOP | [5 empty] | GOP | [16 empty] | Medium |  |  |  | The Generator Operator failed to perform generating real and reactive capability verification that included, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, or failed to provide the results of generating re |  | 2012-09-13 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 130000000
TOP-002-2.1b (Ontario) | 79780000318 | R14. | 79780004157 | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  | GOP | [5 empty] | GOP | [16 empty] | Medium |  |  |  | The Generator Operator failed to notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics. |  | 2012-09-13 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 140000000
TOP-002-2.1b (Ontario) | 79780000318 | R15. | 79780004158 | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | GOP | [5 empty] | GOP | [16 empty] | Low |  |  |  | The Generation Operator failed to provide, at the request of the Balancing Authority or Transmission Operator, a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | 2012-09-13 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 150000000
TOP-002-2.1b (Ontario) | 79780000318 | R16. | 79780004159 | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  | TOP | [18 empty] | TOP |  |  |  | Medium |  |  |  | The Transmission Operator failed to notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics, within the terms and conditions of standards of conduct and confidentiality agreements. |  | 2012-09-13 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 160000000
TOP-002-2.1b (Ontario) | 79780000318 | R17. | 79780004160 | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High |  |  |  | The responsible entity failed to communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | 2012-09-13 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 170000000
TOP-002-2.1b (Ontario) | 79780000318 | R18. | 79780004161 | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | BA, GOP, LSE, TOP, TSP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP |  | Medium |  |  |  | The responsible entity failed to use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | 2012-09-13 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 180000000
TOP-002-2.1b (Ontario) | 79780000318 | R19. | 79780004162 | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to maintain accurate computer models utilized for analyzing and planning system operations. |  | 2012-09-13 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 190000000
TOP-002-2.1b (Ontario) | 79780000318 | R2. | 79780004148 | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to ensure its operating personnel participated in the system planning and design study processes. | M2. Each Balancing Authority and Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, copies of current day plans or other equivalent evidence that will be used to confirm that its plans address Requirements 5, 6, and 10. | 2012-09-13 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-002-2.1b (Ontario) | 79780000318 | R3. | 79780004144 | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  | BA, GOP, LSE, TSP | BA |  |  |  |  | GOP |  | LSE | [12 empty] | TSP |  | Medium |  | The Load-Serving Entity or Generator Operator failed to coordinate (where confidentiality agreements allow) its seasonal operations with its Host Balancing Authority and Transmission Service Provider, or the Balancing Authority or Transmission Service Pro |  | The Load-Serving Entity or Generator Operator failed to coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider, or the Balancing Authority | M3. Each Balancing Authority shall have and provide upon request evidence that could include, but is not limited to, copies of current day plans or other equivalent evidence that will be used to confirm that its plans address Requirements 7, 8, and 9. | 2012-09-13 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-002-2.1b (Ontario) | 79780000318 | R4. | 79780004146 | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  | The responsible entity failed to coordinate (where confidentiality agreements allow) its seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator. |  | The responsible entity failed to coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator. | M4. Each Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, its next-day, and current-day Bulk Electric System studies used to determine SOLs or other equivalent evidence that will be used to confirm that its studies reflect current system conditions. (Requirement 11 Part 1) | 2012-09-13 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-002-2.1b (Ontario) | 79780000318 | R5. | 79780004147 | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. | M5. Each Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that the results of Bulk Electric System studies were made available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. (Requirement 11 Part 2) | 2012-09-13 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 50000000
TOP-002-2.1b (Ontario) | 79780000318 | R6. | 79780004151 | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requir | M6. Each Generator Operator shall have and provide upon request evidence that, when requested by either a Transmission Operator or Balancing Authority, it performed a generating real and reactive capability verification and provided the results to the requesting entity in accordance with Requirement 13. | 2012-09-13 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 60000000
TOP-002-2.1b (Ontario) | 79780000318 | R7. | 79780004152 | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority failed to plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. | M7. Each Generator Operator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that without any intentional time delay, it notified its Balancing Authority and Transmission Operator of changes in real capabilities. (Requirement 14) | 2012-09-13 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 70000000
TOP-002-2.1b (Ontario) | 79780000318 | R8. | 79780004150 | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority failed to plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. | M8. Each Generator Operator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that, on request, it provided a forecast of expected real power output to assist in operations planning. (Requirement 15) | 2012-09-13 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 80000000
TOP-002-2.1b (Ontario) | 79780000318 | R9. | 79780004149 | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority failed to plan to meet Interchange Schedules and Ramps. | M9. Each Transmission Operators shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that, without any intentional time delay, it notified its Balancing Authority and Reliability Coordinator of changes in capabilities and characteristics. (Requirement16) | 2012-09-13 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 90000000
TOP-002-2.1b (Saskatchewan) | 83750000000318 | R1. | 837500000004145 | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M1. Each Balancing Authority and Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, documented planning procedures, copies of current day plans, copies of seasonal operations plans, or other equivalent evidence that will be used to confirm that it maintained a set of current plans. (Requirement 1 Part 1). | 2014-04-01 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 10000000
TOP-002-2.1b (Saskatchewan) | 83750000000318 | R10. | 837500000004153 | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M10. Each Balancing Authority, Transmission Operator, Generator Operator, Transmission Service Provider and Load Serving Entity shall have and provide upon request evidence that could include, but is not limited to, a list of interconnected transmission facilities and their line identifiers at each end or other equivalent evidence that will be used to confirm that it used uniform line identifiers when referring to transmission facilities of an interconnected network. (Requirement 18) | 2014-04-01 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 100000000
TOP-002-2.1b (Saskatchewan) | 83750000000318 | R11. | 837500000004154 | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2014-04-01 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 110000000
TOP-002-2.1b (Saskatchewan) | 83750000000318 | R12. | 837500000004155 | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  | TSP | [20 empty] | TSP |  | Medium | [5 empty] | 2014-04-01 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 120000000
TOP-002-2.1b (Saskatchewan) | 83750000000318 | R13. | 837500000004156 | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2014-04-01 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 130000000
TOP-002-2.1b (Saskatchewan) | 83750000000318 | R14. | 837500000004157 | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2014-04-01 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 140000000
TOP-002-2.1b (Saskatchewan) | 83750000000318 | R15. | 837500000004158 | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | GOP | [5 empty] | GOP | [16 empty] | Low | [5 empty] | 2014-04-01 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 150000000
TOP-002-2.1b (Saskatchewan) | 83750000000318 | R16. | 837500000004159 | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2014-04-01 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 160000000
TOP-002-2.1b (Saskatchewan) | 83750000000318 | R17. | 837500000004160 | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High | [5 empty] | 2014-04-01 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 170000000
TOP-002-2.1b (Saskatchewan) | 83750000000318 | R18. | 837500000004161 | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | BA, GOP, LSE, TOP, TSP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP |  | Medium | [5 empty] | 2014-04-01 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 180000000
TOP-002-2.1b (Saskatchewan) | 83750000000318 | R19. | 837500000004162 | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2014-04-01 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 190000000
TOP-002-2.1b (Saskatchewan) | 83750000000318 | R2. | 837500000004148 | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M2. Each Balancing Authority and Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, copies of current day plans or other equivalent evidence that will be used to confirm that its plans address Requirements 5, 6, and 10. | 2014-04-01 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 20000000
TOP-002-2.1b (Saskatchewan) | 83750000000318 | R3. | 837500000004144 | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  | BA, GOP, LSE, TSP | BA |  |  |  |  | GOP |  | LSE | [12 empty] | TSP |  | Medium |  |  |  |  | M3. Each Balancing Authority shall have and provide upon request evidence that could include, but is not limited to, copies of current day plans or other equivalent evidence that will be used to confirm that its plans address Requirements 7, 8, and 9. | 2014-04-01 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 30000000
TOP-002-2.1b (Saskatchewan) | 83750000000318 | R4. | 837500000004146 | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M4. Each Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, its next-day, and current-day Bulk Electric System studies used to determine SOLs or other equivalent evidence that will be used to confirm that its studies reflect current system conditions. (Requirement 11 Part 1) | 2014-04-01 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 40000000
TOP-002-2.1b (Saskatchewan) | 83750000000318 | R5. | 837500000004147 | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M5. Each Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that the results of Bulk Electric System studies were made available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. (Requirement 11 Part 2) | 2014-04-01 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 50000000
TOP-002-2.1b (Saskatchewan) | 83750000000318 | R6. | 837500000004151 | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M6. Each Generator Operator shall have and provide upon request evidence that, when requested by either a Transmission Operator or Balancing Authority, it performed a generating real and reactive capability verification and provided the results to the requesting entity in accordance with Requirement 13. | 2014-04-01 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 60000000
TOP-002-2.1b (Saskatchewan) | 83750000000318 | R7. | 837500000004152 | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | BA | BA | [21 empty] | Medium |  |  |  |  | M7. Each Generator Operator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that without any intentional time delay, it notified its Balancing Authority and Transmission Operator of changes in real capabilities. (Requirement 14) | 2014-04-01 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 70000000
TOP-002-2.1b (Saskatchewan) | 83750000000318 | R8. | 837500000004150 | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | BA | BA | [21 empty] | Medium |  |  |  |  | M8. Each Generator Operator shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that, on request, it provided a forecast of expected real power output to assist in operations planning. (Requirement 15) | 2014-04-01 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 80000000
TOP-002-2.1b (Saskatchewan) | 83750000000318 | R9. | 837500000004149 | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. |  | BA | BA | [21 empty] | Low |  |  |  |  | M9. Each Transmission Operators shall have and provide upon request evidence that could include, but is not limited to, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that, without any intentional time delay, it notified its Balancing Authority and Reliability Coordinator of changes in capabilities and characteristics. (Requirement16) | 2014-04-01 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 90000000
TOP-002-2a | 170 | R1. | 1926 | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2 R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-002-2a | 170 | R10. | 1927 | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2 R10. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 100000000
TOP-002-2a | 170 | R11. | 1928 | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2 R11. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 110000000
TOP-002-2a | 170 | R12. | 1929 | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  | TSP | [20 empty] | TSP |  | Medium | [5 empty] | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2 R12. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 120000000
TOP-002-2a | 170 | R13. | 1930 | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2 R13. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 130000000
TOP-002-2a | 170 | R14. | 1931 | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2 R14. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 140000000
TOP-002-2a | 170 | R15. | 1934 | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | GOP | [5 empty] | GOP | [16 empty] | Low | [5 empty] | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2 R15. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 150000000
TOP-002-2a | 170 | R16. | 1935 | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2 R16. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 160000000
TOP-002-2a | 170 | R17. | 1938 | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High | [5 empty] | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2 R17. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 170000000
TOP-002-2a | 170 | R18. | 1939 | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | BA, GOP, LSE, TOP, TSP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP |  | Medium | [5 empty] | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2 R18. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 180000000
TOP-002-2a | 170 | R19. | 1940 | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2 R19. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 190000000
TOP-002-2a | 170 | R2. | 1941 | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2 R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-002-2a | 170 | R3. | 1942 | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  | BA, GOP, LSE, TSP | BA |  |  |  |  | GOP |  | LSE | [12 empty] | TSP |  | Medium | [5 empty] | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2 R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-002-2a | 170 | R4. | 1943 | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2 R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-002-2a | 170 | R5. | 1944 | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2 R5. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-002-2a | 170 | R6. | 1945 | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2 R6. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TOP-002-2a | 170 | R7. | 1946 | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2 R7. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
TOP-002-2a | 170 | R8. | 1947 | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2 R8. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
TOP-002-2a | 170 | R9. | 1948 | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. |  | BA | BA | [21 empty] | Low | [5 empty] | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2 R9. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
TOP-002-2a (British Columbia) | 666700000010278 | R1. | 666700000011698 | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-30 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 10000000
TOP-002-2a (British Columbia) | 666700000010278 | R10. | 666700000011699 | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-30 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 100000000
TOP-002-2a (British Columbia) | 666700000010278 | R11. | 666700000011700 | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-30 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 110000000
TOP-002-2a (British Columbia) | 666700000010278 | R12. | 666700000011701 | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  | TSP | [20 empty] | TSP |  | Medium | [5 empty] | 2011-10-30 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 120000000
TOP-002-2a (British Columbia) | 666700000010278 | R13. | 666700000011702 | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2011-10-30 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 130000000
TOP-002-2a (British Columbia) | 666700000010278 | R14. | 666700000011703 | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2011-10-30 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 140000000
TOP-002-2a (British Columbia) | 666700000010278 | R15. | 666700000011704 | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | GOP | [5 empty] | GOP | [16 empty] | Low | [5 empty] | 2011-10-30 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 150000000
TOP-002-2a (British Columbia) | 666700000010278 | R16. | 666700000011705 | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-30 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 160000000
TOP-002-2a (British Columbia) | 666700000010278 | R17. | 666700000011706 | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High | [5 empty] | 2011-10-30 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 170000000
TOP-002-2a (British Columbia) | 666700000010278 | R18. | 666700000011707 | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | BA, GOP, LSE, TOP, TSP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP |  | Medium | [5 empty] | 2011-10-30 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 180000000
TOP-002-2a (British Columbia) | 666700000010278 | R19. | 666700000011708 | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-30 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 190000000
TOP-002-2a (British Columbia) | 666700000010278 | R2. | 666700000011709 | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-30 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 20000000
TOP-002-2a (British Columbia) | 666700000010278 | R3. | 666700000011710 | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  | BA, GOP, LSE, TSP | BA |  |  |  |  | GOP |  | LSE | [12 empty] | TSP |  | Medium | [5 empty] | 2011-10-30 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 30000000
TOP-002-2a (British Columbia) | 666700000010278 | R4. | 666700000011711 | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-30 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 40000000
TOP-002-2a (British Columbia) | 666700000010278 | R5. | 666700000011712 | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-30 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 50000000
TOP-002-2a (British Columbia) | 666700000010278 | R6. | 666700000011713 | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-30 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 60000000
TOP-002-2a (British Columbia) | 666700000010278 | R7. | 666700000011714 | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2011-10-30 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 70000000
TOP-002-2a (British Columbia) | 666700000010278 | R8. | 666700000011715 | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2011-10-30 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 80000000
TOP-002-2a (British Columbia) | 666700000010278 | R9. | 666700000011716 | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. |  | BA | BA | [21 empty] | Low | [5 empty] | 2011-10-30 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 90000000
TOP-002-2a (Ontario) | 79780000170 | R1. | 79780001926 | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  | The responsible entity maintained a set of current plans that were designed to evaluate options and set procedures for reliable operation through a reasonable future time period, but failed utilize all available personnel and system equipment to implement | The responsible entity failed to maintain a set of current plans that were designed to evaluate options and set procedures for reliable operation through a reasonable future time period. |  | 2009-12-02 |  | 2011-10-19 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-002-2a (Ontario) | 79780000170 | R10. | 79780001927 | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | 2009-12-02 |  | 2011-10-19 |  |  |  | NPCC-ON | [6 empty] | 100000000
TOP-002-2a (Ontario) | 79780000170 | R11. | 79780001928 | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | Medium |  |  | The Transmission Operator performed seasonal, next-day, and current-day Bulk Electric System studies, reflecting current system conditions, to determine SOLs, but failed to make the results of Bulk Electric System studies available to all of the Transmiss | The Transmission Operator failed to perform seasonal, next-day, or current-day Bulk Electric System studies, reflecting current system conditions, to determine SOLs. |  | 2009-12-02 |  | 2011-10-19 |  |  |  | NPCC-ON | [6 empty] | 110000000
TOP-002-2a (Ontario) | 79780000170 | R12. | 79780001929 | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  | TSP | [20 empty] | TSP |  | Medium |  |  |  | The Transmission Service Provider failed to include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer |  | 2009-12-02 |  | 2011-10-19 |  |  |  | NPCC-ON | [6 empty] | 120000000
TOP-002-2a (Ontario) | 79780000170 | R13. | 79780001930 | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  | GOP | [5 empty] | GOP | [16 empty] | Medium |  |  |  | The Generator Operator failed to perform generating real and reactive capability verification that included, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, or failed to provide the results of generating re |  | 2009-12-02 |  | 2011-10-19 |  |  |  | NPCC-ON | [6 empty] | 130000000
TOP-002-2a (Ontario) | 79780000170 | R14. | 79780001931 | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  | GOP | [5 empty] | GOP | [16 empty] | Medium |  |  |  | The Generator Operator failed to notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics. |  | 2009-12-02 |  | 2011-10-19 |  |  |  | NPCC-ON | [6 empty] | 140000000
TOP-002-2a (Ontario) | 79780000170 | R15. | 79780001934 | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | GOP | [5 empty] | GOP | [16 empty] | Low |  |  |  | The Generation Operator failed to provide, at the request of the Balancing Authority or Transmission Operator, a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | 2009-12-02 |  | 2011-10-19 |  |  |  | NPCC-ON | [6 empty] | 150000000
TOP-002-2a (Ontario) | 79780000170 | R16. | 79780001935 | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  | TOP | [18 empty] | TOP |  |  |  | Medium |  |  |  | The Transmission Operator failed to notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics, within the terms and conditions of standards of conduct and confidentiality agreements. |  | 2009-12-02 |  | 2011-10-19 |  |  |  | NPCC-ON | [6 empty] | 160000000
TOP-002-2a (Ontario) | 79780000170 | R17. | 79780001938 | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High |  |  |  | The responsible entity failed to communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | 2009-12-02 |  | 2011-10-19 |  |  |  | NPCC-ON | [6 empty] | 170000000
TOP-002-2a (Ontario) | 79780000170 | R18. | 79780001939 | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | BA, GOP, LSE, TOP, TSP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP |  | Medium |  |  |  | The responsible entity failed to use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | 2009-12-02 |  | 2011-10-19 |  |  |  | NPCC-ON | [6 empty] | 180000000
TOP-002-2a (Ontario) | 79780000170 | R19. | 79780001940 | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to maintain accurate computer models utilized for analyzing and planning system operations. |  | 2009-12-02 |  | 2011-10-19 |  |  |  | NPCC-ON | [6 empty] | 190000000
TOP-002-2a (Ontario) | 79780000170 | R2. | 79780001941 | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to ensure its operating personnel participated in the system planning and design study processes. |  | 2009-12-02 |  | 2011-10-19 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-002-2a (Ontario) | 79780000170 | R3. | 79780001942 | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  | BA, GOP, LSE, TSP | BA |  |  |  |  | GOP |  | LSE | [12 empty] | TSP |  | Medium |  | The Load-Serving Entity or Generator Operator failed to coordinate (where confidentiality agreements allow) its seasonal operations with its Host Balancing Authority and Transmission Service Provider, or the Balancing Authority or Transmission Service Pro |  | The Load-Serving Entity or Generator Operator failed to coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider, or the Balancing Authority |  | 2009-12-02 |  | 2011-10-19 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-002-2a (Ontario) | 79780000170 | R4. | 79780001943 | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  | The responsible entity failed to coordinate (where confidentiality agreements allow) its seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator. |  | The responsible entity failed to coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator. |  | 2009-12-02 |  | 2011-10-19 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-002-2a (Ontario) | 79780000170 | R5. | 79780001944 | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | 2009-12-02 |  | 2011-10-19 |  |  |  | NPCC-ON | [6 empty] | 50000000
TOP-002-2a (Ontario) | 79780000170 | R6. | 79780001945 | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requir |  | 2009-12-02 |  | 2011-10-19 |  |  |  | NPCC-ON | [6 empty] | 60000000
TOP-002-2a (Ontario) | 79780000170 | R7. | 79780001946 | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority failed to plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | 2009-12-02 |  | 2011-10-19 |  |  |  | NPCC-ON | [6 empty] | 70000000
TOP-002-2a (Ontario) | 79780000170 | R8. | 79780001947 | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority failed to plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | 2009-12-02 |  | 2011-10-19 |  |  |  | NPCC-ON | [6 empty] | 80000000
TOP-002-2a (Ontario) | 79780000170 | R9. | 79780001948 | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority failed to plan to meet Interchange Schedules and Ramps. |  | 2009-12-02 |  | 2011-10-19 |  |  |  | NPCC-ON | [6 empty] | 90000000
TOP-002-2b | 288 | R1. | 3768 | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-20 |  | 2012-09-12 |  |  | TOP-002-2 R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-002-2b | 288 | R10. | 3776 | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-20 |  | 2012-09-12 |  |  | TOP-002-2 R10. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 100000000
TOP-002-2b | 288 | R11. | 3777 | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-20 |  | 2012-09-12 |  |  | TOP-002-2 R11. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 110000000
TOP-002-2b | 288 | R12. | 3778 | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  | TSP | [20 empty] | TSP |  | Medium | [5 empty] | 2011-10-20 |  | 2012-09-12 |  50% compliant two years after initial issuance of regional requirements per RELIABILITY STANDARD PRC-002 Requirement 5.  75% compliant three years after initial issuance of regional requirements per reliability standard PRC-002 R5.  100% compliant four years after initial issuance of regional requirements per reliability standard PRC-002 R5. |  | TOP-002-2 R12. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 120000000
TOP-002-2b | 288 | R13. | 3779 | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2011-10-20 |  | 2012-09-12 |  |  | TOP-002-2 R13. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 130000000
TOP-002-2b | 288 | R14. | 3780 | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2011-10-20 |  | 2012-09-12 |  |  | TOP-002-2 R14. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 140000000
TOP-002-2b | 288 | R15. | 3781 | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | GOP | [5 empty] | GOP | [16 empty] | Low | [5 empty] | 2011-10-20 |  | 2012-09-12 |  |  | TOP-002-2 R15. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 150000000
TOP-002-2b | 288 | R16. | 3782 | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-20 |  | 2012-09-12 |  |  | TOP-002-2 R16. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 160000000
TOP-002-2b | 288 | R17. | 3783 | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High | [5 empty] | 2011-10-20 |  | 2012-09-12 |  |  | TOP-002-2 R17. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 170000000
TOP-002-2b | 288 | R18. | 3784 | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | BA, GOP, LSE, TOP, TSP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP |  | Medium | [5 empty] | 2011-10-20 |  | 2012-09-12 |  |  | TOP-002-2 R18. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 180000000
TOP-002-2b | 288 | R19. | 3785 | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-20 |  | 2012-09-12 |  |  | TOP-002-2 R19. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 190000000
TOP-002-2b | 288 | R2. | 3771 | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-20 |  | 2012-09-12 |  |  | TOP-002-2 R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-002-2b | 288 | R3. | 3767 | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  | BA, GOP, LSE, TSP | BA |  |  |  |  | GOP |  | LSE | [12 empty] | TSP |  | Medium | [5 empty] | 2011-10-20 |  | 2012-09-12 |  |  | TOP-002-2 R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-002-2b | 288 | R4. | 3769 | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-20 |  | 2012-09-12 |  |  | TOP-002-2 R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-002-2b | 288 | R5. | 3770 | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-20 |  | 2012-09-12 |  |  | TOP-002-2 R5. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-002-2b | 288 | R6. | 3774 | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-20 |  | 2012-09-12 |  |  | TOP-002-2 R6. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TOP-002-2b | 288 | R7. | 3775 | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2011-10-20 |  | 2012-09-12 |  |  | TOP-002-2 R7. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
TOP-002-2b | 288 | R8. | 3773 | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2011-10-20 |  | 2012-09-12 |  |  | TOP-002-2 R8. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
TOP-002-2b | 288 | R9. | 3772 | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. |  | BA | BA | [21 empty] | Low | [5 empty] | 2011-10-20 |  | 2012-09-12 |  |  | TOP-002-2 R9. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
TOP-002-2b (British Columbia) | 666700000010279 | R1. | 666700000011717 | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2013-01-15 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 10000000
TOP-002-2b (British Columbia) | 666700000010279 | R10. | 666700000011718 | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2013-01-15 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 100000000
TOP-002-2b (British Columbia) | 666700000010279 | R11. | 666700000011719 | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2013-01-15 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 110000000
TOP-002-2b (British Columbia) | 666700000010279 | R12. | 666700000011720 | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  | TSP | [20 empty] | TSP |  | Medium | [5 empty] | 2013-01-15 |  | 2013-12-11 |  50% compliant two years after initial issuance of regional requirements per RELIABILITY STANDARD PRC-002 Requirement 5.  75% compliant three years after initial issuance of regional requirements per reliability standard PRC-002 R5.  100% compliant four years after initial issuance of regional requirements per reliability standard PRC-002 R5. |  |  | WECC-BC | [6 empty] | 120000000
TOP-002-2b (British Columbia) | 666700000010279 | R13. | 666700000011721 | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2013-01-15 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 130000000
TOP-002-2b (British Columbia) | 666700000010279 | R14. | 666700000011722 | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2013-01-15 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 140000000
TOP-002-2b (British Columbia) | 666700000010279 | R15. | 666700000011723 | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | GOP | [5 empty] | GOP | [16 empty] | Low | [5 empty] | 2013-01-15 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 150000000
TOP-002-2b (British Columbia) | 666700000010279 | R16. | 666700000011724 | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2013-01-15 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 160000000
TOP-002-2b (British Columbia) | 666700000010279 | R17. | 666700000011725 | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High | [5 empty] | 2013-01-15 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 170000000
TOP-002-2b (British Columbia) | 666700000010279 | R18. | 666700000011726 | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | BA, GOP, LSE, TOP, TSP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP |  | Medium | [5 empty] | 2013-01-15 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 180000000
TOP-002-2b (British Columbia) | 666700000010279 | R19. | 666700000011727 | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2013-01-15 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 190000000
TOP-002-2b (British Columbia) | 666700000010279 | R2. | 666700000011728 | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2013-01-15 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 20000000
TOP-002-2b (British Columbia) | 666700000010279 | R3. | 666700000011729 | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  | BA, GOP, LSE, TSP | BA |  |  |  |  | GOP |  | LSE | [12 empty] | TSP |  | Medium | [5 empty] | 2013-01-15 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 30000000
TOP-002-2b (British Columbia) | 666700000010279 | R4. | 666700000011730 | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2013-01-15 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 40000000
TOP-002-2b (British Columbia) | 666700000010279 | R5. | 666700000011731 | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2013-01-15 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 50000000
TOP-002-2b (British Columbia) | 666700000010279 | R6. | 666700000011732 | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2013-01-15 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 60000000
TOP-002-2b (British Columbia) | 666700000010279 | R7. | 666700000011733 | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2013-01-15 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 70000000
TOP-002-2b (British Columbia) | 666700000010279 | R8. | 666700000011734 | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2013-01-15 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 80000000
TOP-002-2b (British Columbia) | 666700000010279 | R9. | 666700000011735 | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. |  | BA | BA | [21 empty] | Low | [5 empty] | 2013-01-15 |  | 2013-12-11 |  |  |  | WECC-BC | [6 empty] | 90000000
TOP-002-2b (Ontario) | 79780000288 | R1. | 79780003768 | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  | The responsible entity maintained a set of current plans that were designed to evaluate options and set procedures for reliable operation through a reasonable future time period, but failed utilize all available personnel and system equipment to implement | The responsible entity failed to maintain a set of current plans that were designed to evaluate options and set procedures for reliable operation through a reasonable future time period. |  | 2011-10-20 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-002-2b (Ontario) | 79780000288 | R10. | 79780003776 | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | 2011-10-20 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 100000000
TOP-002-2b (Ontario) | 79780000288 | R11. | 79780003777 | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | Medium |  |  | The Transmission Operator performed seasonal, next-day, and current-day Bulk Electric System studies, reflecting current system conditions, to determine SOLs, but failed to make the results of Bulk Electric System studies available to all of the Transmiss | The Transmission Operator failed to perform seasonal, next-day, or current-day Bulk Electric System studies, reflecting current system conditions, to determine SOLs. | M2. The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have evidence it provided documentation of the program and its implementation to the appropriate Regional Reliability Organizations and NERC on request (within 30 calendar days). | 2011-10-20 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 110000000
TOP-002-2b (Ontario) | 79780000288 | R12. | 79780003778 | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  | TSP | [20 empty] | TSP |  | Medium |  |  |  | The Transmission Service Provider failed to include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer | M1. The Transmission Owner and Generator Owner shall each have evidence that DMEs it is required to have meet the functional requirements specified in Requirement 1 and are installed in accordance with its associated Regional Reliability Organization’s requirements (R2). | 2011-10-20 |  | 2012-09-12 |  50% compliant two years after initial issuance of regional requirements per RELIABILITY STANDARD PRC-002 Requirement 5.&lt;br/&gt; 75% compliant three years after initial issuance of regional requirements per reliability standard PRC-002 R5. &lt;br/&gt; 100% compliant four years after initial issuance of regional requirements per reliability standard PRC-002 R5. |  |  | NPCC-ON | [6 empty] | 120000000
TOP-002-2b (Ontario) | 79780000288 | R13. | 79780003779 | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  | GOP | [5 empty] | GOP | [16 empty] | Medium |  |  |  | The Generator Operator failed to perform generating real and reactive capability verification that included, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, or failed to provide the results of generating re |  | 2011-10-20 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 130000000
TOP-002-2b (Ontario) | 79780000288 | R14. | 79780003780 | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  | GOP | [5 empty] | GOP | [16 empty] | Medium |  |  |  | The Generator Operator failed to notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics. |  | 2011-10-20 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 140000000
TOP-002-2b (Ontario) | 79780000288 | R15. | 79780003781 | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | GOP | [5 empty] | GOP | [16 empty] | Low |  |  |  | The Generation Operator failed to provide, at the request of the Balancing Authority or Transmission Operator, a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | 2011-10-20 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 150000000
TOP-002-2b (Ontario) | 79780000288 | R16. | 79780003782 | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  | TOP | [18 empty] | TOP |  |  |  | Medium |  |  |  | The Transmission Operator failed to notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics, within the terms and conditions of standards of conduct and confidentiality agreements. |  | 2011-10-20 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 160000000
TOP-002-2b (Ontario) | 79780000288 | R17. | 79780003783 | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High |  |  |  | The responsible entity failed to communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | 2011-10-20 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 170000000
TOP-002-2b (Ontario) | 79780000288 | R18. | 79780003784 | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | BA, GOP, LSE, TOP, TSP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP |  | Medium |  |  |  | The responsible entity failed to use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | 2011-10-20 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 180000000
TOP-002-2b (Ontario) | 79780000288 | R19. | 79780003785 | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to maintain accurate computer models utilized for analyzing and planning system operations. |  | 2011-10-20 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 190000000
TOP-002-2b (Ontario) | 79780000288 | R2. | 79780003771 | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to ensure its operating personnel participated in the system planning and design study processes. |  | 2011-10-20 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-002-2b (Ontario) | 79780000288 | R3. | 79780003767 | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  | BA, GOP, LSE, TSP | BA |  |  |  |  | GOP |  | LSE | [12 empty] | TSP |  | Medium |  | The Load-Serving Entity or Generator Operator failed to coordinate (where confidentiality agreements allow) its seasonal operations with its Host Balancing Authority and Transmission Service Provider, or the Balancing Authority or Transmission Service Pro |  | The Load-Serving Entity or Generator Operator failed to coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider, or the Balancing Authority |  | 2011-10-20 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-002-2b (Ontario) | 79780000288 | R4. | 79780003769 | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  | The responsible entity failed to coordinate (where confidentiality agreements allow) its seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator. |  | The responsible entity failed to coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator. |  | 2011-10-20 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-002-2b (Ontario) | 79780000288 | R5. | 79780003770 | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | 2011-10-20 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 50000000
TOP-002-2b (Ontario) | 79780000288 | R6. | 79780003774 | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requir |  | 2011-10-20 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 60000000
TOP-002-2b (Ontario) | 79780000288 | R7. | 79780003775 | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority failed to plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | 2011-10-20 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 70000000
TOP-002-2b (Ontario) | 79780000288 | R8. | 79780003773 | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority failed to plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | 2011-10-20 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 80000000
TOP-002-2b (Ontario) | 79780000288 | R9. | 79780003772 | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority failed to plan to meet Interchange Schedules and Ramps. |  | 2011-10-20 |  | 2012-09-12 |  |  |  | NPCC-ON | [6 empty] | 90000000
TOP-002-2 (British Columbia) | 666700000010276 | R1. | 666700000011660 | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 10000000
TOP-002-2 (British Columbia) | 666700000010276 | R10. | 666700000011661 | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 100000000
TOP-002-2 (British Columbia) | 666700000010276 | R11. | 666700000011662 | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 110000000
TOP-002-2 (British Columbia) | 666700000010276 | R12. | 666700000011663 | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  | TSP | [20 empty] | TSP |  | Medium | [5 empty] | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 120000000
TOP-002-2 (British Columbia) | 666700000010276 | R13. | 666700000011664 | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 130000000
TOP-002-2 (British Columbia) | 666700000010276 | R14. | 666700000011665 | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 140000000
TOP-002-2 (British Columbia) | 666700000010276 | R15. | 666700000011666 | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | GOP | [5 empty] | GOP | [16 empty] | Low | [5 empty] | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 150000000
TOP-002-2 (British Columbia) | 666700000010276 | R16. | 666700000011667 | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 160000000
TOP-002-2 (British Columbia) | 666700000010276 | R17. | 666700000011668 | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High | [5 empty] | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 170000000
TOP-002-2 (British Columbia) | 666700000010276 | R18. | 666700000011669 | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | BA, GOP, LSE, TOP, TSP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP |  | Medium | [5 empty] | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 180000000
TOP-002-2 (British Columbia) | 666700000010276 | R19. | 666700000011670 | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 190000000
TOP-002-2 (British Columbia) | 666700000010276 | R2. | 666700000011671 | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 20000000
TOP-002-2 (British Columbia) | 666700000010276 | R3. | 666700000011672 | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  | BA, GOP, LSE, TSP | BA |  |  |  |  | GOP |  | LSE | [12 empty] | TSP |  | Medium | [5 empty] | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 30000000
TOP-002-2 (British Columbia) | 666700000010276 | R4. | 666700000011673 | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 40000000
TOP-002-2 (British Columbia) | 666700000010276 | R5. | 666700000011674 | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 50000000
TOP-002-2 (British Columbia) | 666700000010276 | R6. | 666700000011675 | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 60000000
TOP-002-2 (British Columbia) | 666700000010276 | R7. | 666700000011676 | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 70000000
TOP-002-2 (British Columbia) | 666700000010276 | R8. | 666700000011677 | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 80000000
TOP-002-2 (British Columbia) | 666700000010276 | R9. | 666700000011678 | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. |  | BA | BA | [21 empty] | Low | [5 empty] | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 90000000
TOP-002-2 (Manitoba) | 77660000000169 | R1. | 776600000001903 | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 10000000
TOP-002-2 (Manitoba) | 77660000000169 | R10. | 776600000001904 | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 100000000
TOP-002-2 (Manitoba) | 77660000000169 | R11. | 776600000001905 | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 110000000
TOP-002-2 (Manitoba) | 77660000000169 | R12. | 776600000001906 | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  | TSP | [20 empty] | TSP |  | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 120000000
TOP-002-2 (Manitoba) | 77660000000169 | R13. | 776600000001907 | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 130000000
TOP-002-2 (Manitoba) | 77660000000169 | R14. | 776600000001908 | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 140000000
TOP-002-2 (Manitoba) | 77660000000169 | R15. | 776600000001911 | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | GOP | [5 empty] | GOP | [16 empty] | Low | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 150000000
TOP-002-2 (Manitoba) | 77660000000169 | R16. | 776600000001912 | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 160000000
TOP-002-2 (Manitoba) | 77660000000169 | R17. | 776600000001915 | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 170000000
TOP-002-2 (Manitoba) | 77660000000169 | R18. | 776600000001916 | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | BA, GOP, LSE, TOP, TSP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP |  | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 180000000
TOP-002-2 (Manitoba) | 77660000000169 | R19. | 776600000001917 | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 190000000
TOP-002-2 (Manitoba) | 77660000000169 | R2. | 776600000001918 | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 20000000
TOP-002-2 (Manitoba) | 77660000000169 | R3. | 776600000001919 | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  | BA, GOP, LSE, TSP | BA |  |  |  |  | GOP |  | LSE | [12 empty] | TSP |  | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 30000000
TOP-002-2 (Manitoba) | 77660000000169 | R4. | 776600000001920 | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 40000000
TOP-002-2 (Manitoba) | 77660000000169 | R5. | 776600000001921 | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 50000000
TOP-002-2 (Manitoba) | 77660000000169 | R6. | 776600000001922 | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 60000000
TOP-002-2 (Manitoba) | 77660000000169 | R7. | 776600000001923 | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 70000000
TOP-002-2 (Manitoba) | 77660000000169 | R8. | 776600000001924 | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 80000000
TOP-002-2 (Manitoba) | 77660000000169 | R9. | 776600000001925 | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. |  | BA | BA | [21 empty] | Low | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 90000000
TOP-002-2 (Ontario) | 79780000169 | R1. | 79780001903 | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  | The responsible entity maintained a set of current plans that were designed to evaluate options and set procedures for reliable operation through a reasonable future time period, but failed utilize all available personnel and system equipment to implement | The responsible entity failed to maintain a set of current plans that were designed to evaluate options and set procedures for reliable operation through a reasonable future time period. |  | 2007-06-18 |  | 2009-12-01 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-002-2 (Ontario) | 79780000169 | R10. | 79780001904 | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | 2007-06-18 |  | 2009-12-01 |  |  |  | NPCC-ON | [6 empty] | 100000000
TOP-002-2 (Ontario) | 79780000169 | R11. | 79780001905 | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | Medium |  |  | The Transmission Operator performed seasonal, next-day, and current-day Bulk Electric System studies, reflecting current system conditions, to determine SOLs, but failed to make the results of Bulk Electric System studies available to all of the Transmiss | The Transmission Operator failed to perform seasonal, next-day, or current-day Bulk Electric System studies, reflecting current system conditions, to determine SOLs. |  | 2007-06-18 |  | 2009-12-01 |  |  |  | NPCC-ON | [6 empty] | 110000000
TOP-002-2 (Ontario) | 79780000169 | R12. | 79780001906 | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  | TSP | [20 empty] | TSP |  | Medium |  |  |  | The Transmission Service Provider failed to include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer |  | 2007-06-18 |  | 2009-12-01 |  |  |  | NPCC-ON | [6 empty] | 120000000
TOP-002-2 (Ontario) | 79780000169 | R13. | 79780001907 | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  | GOP | [5 empty] | GOP | [16 empty] | Medium |  |  |  | The Generator Operator failed to perform generating real and reactive capability verification that included, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, or failed to provide the results of generating re |  | 2007-06-18 |  | 2009-12-01 |  |  |  | NPCC-ON | [6 empty] | 130000000
TOP-002-2 (Ontario) | 79780000169 | R14. | 79780001908 | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  | GOP | [5 empty] | GOP | [16 empty] | Medium |  |  |  | The Generator Operator failed to notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics. |  | 2007-06-18 |  | 2009-12-01 |  |  |  | NPCC-ON | [6 empty] | 140000000
TOP-002-2 (Ontario) | 79780000169 | R15. | 79780001911 | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | GOP | [5 empty] | GOP | [16 empty] | Low |  |  |  | The Generation Operator failed to provide, at the request of the Balancing Authority or Transmission Operator, a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | 2007-06-18 |  | 2009-12-01 |  |  |  | NPCC-ON | [6 empty] | 150000000
TOP-002-2 (Ontario) | 79780000169 | R16. | 79780001912 | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  | TOP | [18 empty] | TOP |  |  |  | Medium |  |  |  | The Transmission Operator failed to notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics, within the terms and conditions of standards of conduct and confidentiality agreements. |  | 2007-06-18 |  | 2009-12-01 |  |  |  | NPCC-ON | [6 empty] | 160000000
TOP-002-2 (Ontario) | 79780000169 | R17. | 79780001915 | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High |  |  |  | The responsible entity failed to communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | 2007-06-18 |  | 2009-12-01 |  |  |  | NPCC-ON | [6 empty] | 170000000
TOP-002-2 (Ontario) | 79780000169 | R18. | 79780001916 | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | BA, GOP, LSE, TOP, TSP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP |  | Medium |  |  |  | The responsible entity failed to use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | 2007-06-18 |  | 2009-12-01 |  |  |  | NPCC-ON | [6 empty] | 180000000
TOP-002-2 (Ontario) | 79780000169 | R19. | 79780001917 | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to maintain accurate computer models utilized for analyzing and planning system operations. |  | 2007-06-18 |  | 2009-12-01 |  |  |  | NPCC-ON | [6 empty] | 190000000
TOP-002-2 (Ontario) | 79780000169 | R2. | 79780001918 | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to ensure its operating personnel participated in the system planning and design study processes. |  | 2007-06-18 |  | 2009-12-01 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-002-2 (Ontario) | 79780000169 | R3. | 79780001919 | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  | BA, GOP, LSE, TSP | BA |  |  |  |  | GOP |  | LSE | [12 empty] | TSP |  | Medium |  | The Load-Serving Entity or Generator Operator failed to coordinate (where confidentiality agreements allow) its seasonal operations with its Host Balancing Authority and Transmission Service Provider, or the Balancing Authority or Transmission Service Pro |  | The Load-Serving Entity or Generator Operator failed to coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider, or the Balancing Authority |  | 2007-06-18 |  | 2009-12-01 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-002-2 (Ontario) | 79780000169 | R4. | 79780001920 | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  | The responsible entity failed to coordinate (where confidentiality agreements allow) its seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator. |  | The responsible entity failed to coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator. |  | 2007-06-18 |  | 2009-12-01 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-002-2 (Ontario) | 79780000169 | R5. | 79780001921 | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | 2007-06-18 |  | 2009-12-01 |  |  |  | NPCC-ON | [6 empty] | 50000000
TOP-002-2 (Ontario) | 79780000169 | R6. | 79780001922 | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requir |  | 2007-06-18 |  | 2009-12-01 |  |  |  | NPCC-ON | [6 empty] | 60000000
TOP-002-2 (Ontario) | 79780000169 | R7. | 79780001923 | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority failed to plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | 2007-06-18 |  | 2009-12-01 |  |  |  | NPCC-ON | [6 empty] | 70000000
TOP-002-2 (Ontario) | 79780000169 | R8. | 79780001924 | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | BA | BA | [21 empty] | Medium |  |  |  | The Balancing Authority failed to plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | 2007-06-18 |  | 2009-12-01 |  |  |  | NPCC-ON | [6 empty] | 80000000
TOP-002-2 (Ontario) | 79780000169 | R9. | 79780001925 | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. |  | BA | BA | [21 empty] | Low |  |  |  | The Balancing Authority failed to plan to meet Interchange Schedules and Ramps. |  | 2007-06-18 |  | 2009-12-01 |  |  |  | NPCC-ON | [6 empty] | 90000000
TOP-002-2 (Saskatchewan) | 83750000000169 | R1. | 837500000001903 | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 10000000
TOP-002-2 (Saskatchewan) | 83750000000169 | R10. | 837500000001904 | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 100000000
TOP-002-2 (Saskatchewan) | 83750000000169 | R11. | 837500000001905 | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 110000000
TOP-002-2 (Saskatchewan) | 83750000000169 | R12. | 837500000001906 | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  | TSP | [20 empty] | TSP |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 120000000
TOP-002-2 (Saskatchewan) | 83750000000169 | R13. | 837500000001907 | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 130000000
TOP-002-2 (Saskatchewan) | 83750000000169 | R14. | 837500000001908 | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 140000000
TOP-002-2 (Saskatchewan) | 83750000000169 | R15. | 837500000001911 | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | GOP | [5 empty] | GOP | [16 empty] | Low | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 150000000
TOP-002-2 (Saskatchewan) | 83750000000169 | R16. | 837500000001912 | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 160000000
TOP-002-2 (Saskatchewan) | 83750000000169 | R17. | 837500000001915 | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 170000000
TOP-002-2 (Saskatchewan) | 83750000000169 | R18. | 837500000001916 | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | BA, GOP, LSE, TOP, TSP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 180000000
TOP-002-2 (Saskatchewan) | 83750000000169 | R19. | 837500000001917 | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 190000000
TOP-002-2 (Saskatchewan) | 83750000000169 | R2. | 837500000001918 | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 20000000
TOP-002-2 (Saskatchewan) | 83750000000169 | R3. | 837500000001919 | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  | BA, GOP, LSE, TSP | BA |  |  |  |  | GOP |  | LSE | [12 empty] | TSP |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 30000000
TOP-002-2 (Saskatchewan) | 83750000000169 | R4. | 837500000001920 | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 40000000
TOP-002-2 (Saskatchewan) | 83750000000169 | R5. | 837500000001921 | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 50000000
TOP-002-2 (Saskatchewan) | 83750000000169 | R6. | 837500000001922 | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 60000000
TOP-002-2 (Saskatchewan) | 83750000000169 | R7. | 837500000001923 | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 70000000
TOP-002-2 (Saskatchewan) | 83750000000169 | R8. | 837500000001924 | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | BA | BA | [21 empty] | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 80000000
TOP-002-2 (Saskatchewan) | 83750000000169 | R9. | 837500000001925 | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. |  | BA | BA | [21 empty] | Low | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 90000000
TOP-002-3 | 326 | R1. | 4304 | Each Transmission Operator shall have an Operational Planning Analysis that represents projected System conditions that will allow it to assess whether the planned operations for the next day within its Transmission Operator Area will exceed any of its Facility Ratings or Stability Limits during anticipated normal and Contingency event conditions. |  | TOP | [18 empty] | TOP |  |  |  | Medium | N/A | N/A | N/A | The Transmission Operator did not have an Operational Planning Analysis that represented projected System conditions allowing it to assess whether the planned operations for the next day within its Transmission Operator Area will exceed any of its Facility Ratings or Stability Limits during anticipated normal and Contingency event conditions. |  |  |  | 2016-01-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-002-3 | 326 | R2. | 4305 | Each Transmission Operator shall develop a plan to operate within each Interconnection Reliability Operating Limit (IROL) and each System Operating Limit (SOL) which, while not an IROL, has been identified by the Transmission Operator as supporting reliability internal to its Transmission Operator Area, identified as a result of the Operational Planning Analysis performed in Requirement R1. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not develop a plan to operate within those IROLs and each SOL which, while not an IROL, has been identified by the Transmission Operator as supporting its internal area reliability, identified as a result of the Operational Planning Analysis performed in Requirement R1. | Each Transmission Operator shall have evidence that it has developed a plan to operate within each IROL and each SOL which, while not an IROL, has been identified by the Transmission Operator as supporting its internal area reliability, identified as a result of the Operational Planning Analysis performed in Requirement R1 in accordance with Requirement R2. Such evidence could include, but it is not limited to, plans for precluding operating in excess of each IROL and each SOL which, while not an IROL, was identified as a result of the Operational Planning Analysis |  |  | 2016-01-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-002-3 | 326 | R3. | 4306 | Each Transmission Operator shall notify all NERC registered entities identified in the plan(s) cited in Requirement R2 as to their role in those plan(s). |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | The Transmission Operator did not notify one NERC-registered entity, or 5% or less of the NERC-registered entities, whichever is less identified in the plan(s) cited, as to their role in the plan(s). | The Transmission Operator did not notify two NERC-registered entities, or more than 5%, and less than or equal to 10% of the NERC-registered entities, whichever is less, identified in the plan(s) as to their role in the plan(s). | The Transmission Operator did not notify three NERC-registered entities, or more than 10% and less than or equal to 15% of the NERC-registered entities, whichever is less, identified in the plan(s) as to their role in the plan(s). | The Transmission Operator did not notify four or more NERC-registered entities, or more than15% of the NERC-registered entities identified in the plan(s) as to their role in the plan(s). | Each Transmission Operator shall have evidence that it notified all NERC registered entities identified in the plan(s) cited in Requirement R2 as to their role in the plan(s) in accordance with Requirement R3. Such evidence could include but is not limited to dated operator logs, voice recordings, or e-mail records. |  |  | 2016-01-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-002-3 (Ontario) | 79780000326 | R1. | 79780004304 | Each Transmission Operator shall have an Operational Planning Analysis that represents projected System conditions that will allow it to assess whether the planned operations for the next day within its Transmission Operator Area will exceed any of its Facility Ratings or Stability Limits during anticipated normal and Contingency event conditions. |  | TOP | [18 empty] | TOP |  |  |  | Medium | N/A | N/A | N/A | The Transmission Operator did not have an Operational Planning Analysis that represented projected System conditions allowing it to assess whether the planned operations for the next day within its Transmission Operator Area will exceed any of its Facilit | M1. Evidence that the Generator Operator, Transmission Operator, and Balancing Authority reported and coordinated scheduled outage information as indicated in the requirements above. |  |  | 2016-01-26 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-002-3 (Ontario) | 79780000326 | R2. | 79780004305 | Each Transmission Operator shall develop a plan to operate within each Interconnection Reliability Operating Limit (IROL) and each System Operating Limit (SOL) which, while not an IROL, has been identified by the Transmission Operator as supporting reliability internal to its Transmission Operator Area, identified as a result of the Operational Planning Analysis performed in Requirement R1. |  | TOP | [18 empty] | TOP |  |  |  | Medium | N/A | N/A | N/A | The Transmission Operator did not develop a plan to operate within those IROLs and each SOL which, while not an IROL, has been identified by the Transmission Operator as supporting its internal area reliability, identified as a result of the Operational P |  |  |  | 2016-01-26 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-002-3 (Ontario) | 79780000326 | R3. | 79780004306 | Each Transmission Operator shall notify all NERC registered entities identified in the plan(s) cited in Requirement R2 as to their role in those plan(s). |  | TOP | [18 empty] | TOP |  |  |  | Medium | The Transmission Operator did not notify one NERC-registered entity, or 5% or less of the NERC-registered entities, whichever is less identified in the plan(s) cited, as to their role in the plan(s). | The Transmission Operator did not notify two NERC-registered entities, or more than 5%, and less than or equal to 10% of the NERC-registered entities, whichever is less, identified in the plan(s) as to their role in the plan(s). | The Transmission Operator did not notify three NERC-registered entities, or more than 10% and less than or equal to 15% of the NERC-registered entities, whichever is less, identified in the plan(s) as to their role in the plan(s). | The Transmission Operator did not notify four or more NERC-registered entities, or more than15% of the NERC-registered entities identified in the plan(s) as to their role in the plan(s). |  |  |  | 2016-01-26 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-002-3 (Saskatchewan) | 83750000000326 | R1. | 837500000004304 | Each Transmission Operator shall have an Operational Planning Analysis that represents projected System conditions that will allow it to assess whether the planned operations for the next day within its Transmission Operator Area will exceed any of its Facility Ratings or Stability Limits during anticipated normal and Contingency event conditions. |  | TOP | [18 empty] | TOP |  |  |  | Medium | N/A | N/A | N/A | The Transmission Operator did not have an Operational Planning Analysis that represented projected System conditions allowing it to assess whether the planned operations for the next day within its Transmission Operator Area will exceed any of its Facility Ratings or Stability Limits during anticipated normal and Contingency event conditions. |  | 2012-05-09 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 10000000
TOP-002-3 (Saskatchewan) | 83750000000326 | R2. | 837500000004305 | Each Transmission Operator shall develop a plan to operate within each Interconnection Reliability Operating Limit (IROL) and each System Operating Limit (SOL) which, while not an IROL, has been identified by the Transmission Operator as supporting reliability internal to its Transmission Operator Area, identified as a result of the Operational Planning Analysis performed in Requirement R1. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not develop a plan to operate within those IROLs and each SOL which, while not an IROL, has been identified by the Transmission Operator as supporting its internal area reliability, identified as a result of the Operational Planning Analysis performed in Requirement R1. | Each Transmission Operator shall have evidence that it has developed a plan to operate within each IROL and each SOL which, while not an IROL, has been identified by the Transmission Operator as supporting its internal area reliability, identified as a result of the Operational Planning Analysis performed in Requirement R1 in accordance with Requirement R2. Such evidence could include, but it is not limited to, plans for precluding operating in excess of each IROL and each SOL which, while not an IROL, was identified as a result of the Operational Planning Analysis | 2012-05-09 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 20000000
TOP-002-3 (Saskatchewan) | 83750000000326 | R3. | 837500000004306 | Each Transmission Operator shall notify all NERC registered entities identified in the plan(s) cited in Requirement R2 as to their role in those plan(s). |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | The Transmission Operator did not notify one NERC-registered entity, or 5% or less of the NERC-registered entities, whichever is less identified in the plan(s) cited, as to their role in the plan(s). | The Transmission Operator did not notify two NERC-registered entities, or more than 5%, and less than or equal to 10% of the NERC-registered entities, whichever is less, identified in the plan(s) as to their role in the plan(s). | The Transmission Operator did not notify three NERC-registered entities, or more than 10% and less than or equal to 15% of the NERC-registered entities, whichever is less, identified in the plan(s) as to their role in the plan(s). | The Transmission Operator did not notify four or more NERC-registered entities, or more than15% of the NERC-registered entities identified in the plan(s) as to their role in the plan(s). | Each Transmission Operator shall have evidence that it notified all NERC registered entities identified in the plan(s) cited in Requirement R2 as to their role in the plan(s) in accordance with Requirement R3. Such evidence could include but is not limited to dated operator logs, voice recordings, or e-mail records. | 2012-05-09 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 30000000
TOP-002-4 | 520 | R1. | 6125 | Each Transmission Operator shall have an Operational Planning Analysis that will allow it to assess whether its planned operations for the next day within its Transmission Operator Area will exceed any of its System Operating Limits (SOLs). |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not have an Operational Planning Analysis allowing it to assess whether its planned operations for the next day within its Transmission Operator Area exceeded any of its System Operating Limits (SOLs). | Each Transmission Operator shall have evidence of a completed Operational Planning Analysis. Such evidence could include but is not limited to dated power flow study results. | 2017-04-01 |  | 2025-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-002-4 | 520 | R2. | 6126 | Each Transmission Operator shall have an Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) exceedances identified as a result of its Operational Planning Analysis as required in Requirement R1. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not have an Operating Plan to address potential System Operating Limit (SOL) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1. | Each Transmission Operator shall have evidence that it has an Operating Plan to address potential System Operating Limits (SOLs) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1. Such evidence could include but it is not limited to plans for precluding operating in excess of each SOL that was identified as a result of the Operational Planning Analysis. | 2017-04-01 |  | 2025-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-002-4 | 520 | R3. | 6127 | Each Transmission Operator shall notify entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in those plan(s). |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | The Transmission Operator did not notify one impacted entity or 5% or less of the entities, whichever is greater identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify two entities or more than 5% and less than or equal to 10% of the impacted entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify three impacted entities or more than 10% and less than or equal to 15% of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify four or more entities or more than 15% of the impacted NERC identified in the Operating Plan(s) as to their role in the plan(s). For the Requirement R3 and R5 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size of entity. If a small entity has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. | M3. Each Transmission Operator shall have evidence that it notified entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in the plan(s). Such evidence could include but is not limited to dated operator logs, or e-mail records. | 2017-04-01 |  | 2025-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-002-4 | 520 | R4. | 6128 | Each Balancing Authority shall have an Operating Plan(s) for the next-day that addresses: |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority has an Operating Plan but it does not address one of the criteria in Requirement R4. | The Balancing Authority has an Operating Plan but it does not address two of the criteria in Requirement R4. | The Balancing Authority has an Operating Plan but it does not address three of the criteria in Requirement R4. | The Balancing Authority did not have an Operating Plan. | M4. Each Balancing Authority shall have evidence that it has developed a plan to operate within the criteria identified. Such evidence could include but is not limited to dated operator logs or e-mail records. | 2017-04-01 |  | 2025-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-002-4 | 520 | R5. | 6129 | Each Balancing Authority shall notify entities identified in the Operating Plan(s) cited in Requirement R4 as to their role in those plan(s). |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority did not notify one impacted entity or 5% or less of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify two entities or more than 5% and less than or equal to 10% of the impacted entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify three impacted entities or more than 10% and less than or equal to 15% of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify four or more entities or more than 15% of the impacted entities identified in the Operating Plan(s) as to their role in the plan(s). For the Requirement R3 and R5 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size of entity. If a small entity has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. | Each Balancing Authority shall have evidence that it notified entities identified in the plan(s) cited in Requirement R4 as to their role in the plan(s). Such evidence could include but is not limited to dated operator logs or e-mail records. | 2017-04-01 |  | 2025-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-002-4 | 520 | R6. | 6130 | Each Transmission Operator shall provide its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not provide its Operating Plan(s) for next-day operations as identified in Requirement R2 to its Reliability Coordinator. | M6. Each Transmission Operator shall have evidence that it provided its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. Such evidence could include but is not limited to dated operator logs or e-mail records. | 2017-04-01 |  | 2025-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TOP-002-4 | 520 | R7. | 6131 | Each Balancing Authority shall provide its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. |  | BA | BA | [20 empty] | Operations Planning | Medium | N/A | N/A | N/A | The Balancing Authority did not provide its Operating Plan(s) for next-day operations as identified in Requirement R4 to its Reliability Coordinator. | M7. Each Balancing Authority shall have evidence that it provided its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. Such evidence could include but is not limited to dated operator logs or e-mail records. | 2017-04-01 |  | 2025-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
TOP-002-4 (British Columbia) | 666700000010280 | R1. | 666700000011736 | Each Transmission Operator shall have an Operational Planning Analysis that will allow it to assess whether its planned operations for the next day within its Transmission Operator Area will exceed any of its System Operating Limits (SOLs). |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not have an Operational Planning Analysis allowing it to assess whether its planned operations for the next day within its Transmission Operator Area exceeded any of its System Operating Limits (SOLs). | Each Transmission Operator shall have evidence of a completed Operational Planning Analysis. Such evidence could include but is not limited to dated power flow study results. | 2021-04-01 | [5 empty] | WECC-BC | [6 empty] | 10000000
TOP-002-4 (British Columbia) | 666700000010280 | R2. | 666700000011737 | Each Transmission Operator shall have an Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) exceedances identified as a result of its Operational Planning Analysis as required in Requirement R1. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not have an Operating Plan to address potential System Operating Limit (SOL) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1. | Each Transmission Operator shall have evidence that it has an Operating Plan to address potential System Operating Limits (SOLs) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1. Such evidence could include but it is not limited to plans for precluding operating in excess of each SOL that was identified as a result of the Operational Planning Analysis. | 2021-04-01 | [5 empty] | WECC-BC | [6 empty] | 20000000
TOP-002-4 (British Columbia) | 666700000010280 | R3. | 666700000011738 | Each Transmission Operator shall notify entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in those plan(s). |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | The Transmission Operator did not notify one impacted entity or 5% or less of the entities, whichever is greater identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify two entities or more than 5% and less than or equal to 10% of the impacted entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify three impacted entities or more than 10% and less than or equal to 15% of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify four or more entities or more than 15% of the impacted NERC identified in the Operating Plan(s) as to their role in the plan(s). For the Requirement R3 and R5 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size of entity. If a small entity has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. | M3. Each Transmission Operator shall have evidence that it notified entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in the plan(s). Such evidence could include but is not limited to dated operator logs, or e-mail records. | 2021-04-01 | [5 empty] | WECC-BC | [6 empty] | 30000000
TOP-002-4 (British Columbia) | 666700000010280 | R4. | 666700000011739 | Each Balancing Authority shall have an Operating Plan(s) for the next-day that addresses: |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority has an Operating Plan but it does not address one of the criteria in Requirement R4. | The Balancing Authority has an Operating Plan but it does not address two of the criteria in Requirement R4. | The Balancing Authority has an Operating Plan but it does not address three of the criteria in Requirement R4. | The Balancing Authority did not have an Operating Plan. | M4. Each Balancing Authority shall have evidence that it has developed a plan to operate within the criteria identified. Such evidence could include but is not limited to dated operator logs or e-mail records. | 2021-04-01 | [5 empty] | WECC-BC | [6 empty] | 40000000
TOP-002-4 (British Columbia) | 666700000010280 | R5. | 666700000011740 | Each Balancing Authority shall notify entities identified in the Operating Plan(s) cited in Requirement R4 as to their role in those plan(s). |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority did not notify one impacted entity or 5% or less of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify two entities or more than 5% and less than or equal to 10% of the impacted entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify three impacted entities or more than 10% and less than or equal to 15% of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify four or more entities or more than 15% of the impacted entities identified in the Operating Plan(s) as to their role in the plan(s). For the Requirement R3 and R5 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size of entity. If a small entity has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. | Each Balancing Authority shall have evidence that it notified entities identified in the plan(s) cited in Requirement R4 as to their role in the plan(s). Such evidence could include but is not limited to dated operator logs or e-mail records. | 2021-04-01 | [5 empty] | WECC-BC | [6 empty] | 50000000
TOP-002-4 (British Columbia) | 666700000010280 | R6. | 666700000011741 | Each Transmission Operator shall provide its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not provide its Operating Plan(s) for next-day operations as identified in Requirement R2 to its Reliability Coordinator. | M6. Each Transmission Operator shall have evidence that it provided its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. Such evidence could include but is not limited to dated operator logs or e-mail records. | 2021-04-01 | [5 empty] | WECC-BC | [6 empty] | 60000000
TOP-002-4 (British Columbia) | 666700000010280 | R7. | 666700000011742 | Each Balancing Authority shall provide its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. |  | BA | BA | [20 empty] | Operations Planning | Medium | N/A | N/A | N/A | The Balancing Authority did not provide its Operating Plan(s) for next-day operations as identified in Requirement R4 to its Reliability Coordinator. | M7. Each Balancing Authority shall have evidence that it provided its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. Such evidence could include but is not limited to dated operator logs or e-mail records. | 2021-04-01 | [5 empty] | WECC-BC | [6 empty] | 70000000
TOP-002-4 (Manitoba) | 77660000000520 | R1. | 776600000006125 | Each Transmission Operator shall have an Operational Planning Analysis that will allow it to assess whether its planned operations for the next day within its Transmission Operator Area will exceed any of its System Operating Limits (SOLs). |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not have an Operational Planning Analysis allowing it to assess whether its planned operations for the next day within its Transmission Operator Area exceeded any of its System Operating Limits (SOLs). | Each Transmission Operator shall have evidence of a completed Operational Planning Analysis. Such evidence could include but is not limited to dated power flow study results. | 2017-07-01 | [5 empty] | MRO-MB | [6 empty] | 10000000
TOP-002-4 (Manitoba) | 77660000000520 | R2. | 776600000006126 | Each Transmission Operator shall have an Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) exceedances identified as a result of its Operational Planning Analysis as required in Requirement R1. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not have an Operating Plan to address potential System Operating Limit (SOL) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1. | Each Transmission Operator shall have evidence that it has an Operating Plan to address potential System Operating Limits (SOLs) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1. Such evidence could include but it is not limited to plans for precluding operating in excess of each SOL that was identified as a result of the Operational Planning Analysis. | 2017-07-01 | [5 empty] | MRO-MB | [6 empty] | 20000000
TOP-002-4 (Manitoba) | 77660000000520 | R3. | 776600000006127 | Each Transmission Operator shall notify entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in those plan(s). |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | The Transmission Operator did not notify one impacted entity or 5% or less of the entities, whichever is greater identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify two entities or more than 5% and less than or equal to 10% of the impacted entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify three impacted entities or more than 10% and less than or equal to 15% of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify four or more entities or more than 15% of the impacted NERC identified in the Operating Plan(s) as to their role in the plan(s). For the Requirement R3 and R5 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size of entity. If a small entity has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. | M3. Each Transmission Operator shall have evidence that it notified entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in the plan(s). Such evidence could include but is not limited to dated operator logs, or e-mail records. | 2017-07-01 | [5 empty] | MRO-MB | [6 empty] | 30000000
TOP-002-4 (Manitoba) | 77660000000520 | R4. | 776600000006128 | Each Balancing Authority shall have an Operating Plan(s) for the next-day that addresses: |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority has an Operating Plan but it does not address one of the criteria in Requirement R4. | The Balancing Authority has an Operating Plan but it does not address two of the criteria in Requirement R4. | The Balancing Authority has an Operating Plan but it does not address three of the criteria in Requirement R4. | The Balancing Authority did not have an Operating Plan. | M4. Each Balancing Authority shall have evidence that it has developed a plan to operate within the criteria identified. Such evidence could include but is not limited to dated operator logs or e-mail records. | 2017-07-01 | [5 empty] | MRO-MB | [6 empty] | 40000000
TOP-002-4 (Manitoba) | 77660000000520 | R5. | 776600000006129 | Each Balancing Authority shall notify entities identified in the Operating Plan(s) cited in Requirement R4 as to their role in those plan(s). |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority did not notify one impacted entity or 5% or less of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify two entities or more than 5% and less than or equal to 10% of the impacted entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify three impacted entities or more than 10% and less than or equal to 15% of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify four or more entities or more than 15% of the impacted entities identified in the Operating Plan(s) as to their role in the plan(s). For the Requirement R3 and R5 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size of entity. If a small entity has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. | Each Balancing Authority shall have evidence that it notified entities identified in the plan(s) cited in Requirement R4 as to their role in the plan(s). Such evidence could include but is not limited to dated operator logs or e-mail records. | 2017-07-01 | [5 empty] | MRO-MB | [6 empty] | 50000000
TOP-002-4 (Manitoba) | 77660000000520 | R6. | 776600000006130 | Each Transmission Operator shall provide its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not provide its Operating Plan(s) for next-day operations as identified in Requirement R2 to its Reliability Coordinator. | M6. Each Transmission Operator shall have evidence that it provided its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. Such evidence could include but is not limited to dated operator logs or e-mail records. | 2017-07-01 | [5 empty] | MRO-MB | [6 empty] | 60000000
TOP-002-4 (Manitoba) | 77660000000520 | R7. | 776600000006131 | Each Balancing Authority shall provide its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. |  | BA | BA | [20 empty] | Operations Planning | Medium | N/A | N/A | N/A | The Balancing Authority did not provide its Operating Plan(s) for next-day operations as identified in Requirement R4 to its Reliability Coordinator. | M7. Each Balancing Authority shall have evidence that it provided its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. Such evidence could include but is not limited to dated operator logs or e-mail records. | 2017-07-01 | [5 empty] | MRO-MB | [6 empty] | 70000000
TOP-002-4 (Nova Scotia) | 78830000000520 | R1. | 788300000006125 | Each Transmission Operator shall have an Operational Planning Analysis that will allow it to assess whether its planned operations for the next day within its Transmission Operator Area will exceed any of its System Operating Limits (SOLs). |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not have an Operational Planning Analysis allowing it to assess whether its planned operations for the next day within its Transmission Operator Area exceeded any of its System Operating Limits (SOLs). | Each Transmission Operator shall have evidence of a completed Operational Planning Analysis. Such evidence could include but is not limited to dated power flow study results. | 2017-10-01 | [5 empty] | NPCC-NS | [6 empty] | 10000000
TOP-002-4 (Nova Scotia) | 78830000000520 | R2. | 788300000006126 | Each Transmission Operator shall have an Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) exceedances identified as a result of its Operational Planning Analysis as required in Requirement R1. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not have an Operating Plan to address potential System Operating Limit (SOL) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1. | Each Transmission Operator shall have evidence that it has an Operating Plan to address potential System Operating Limits (SOLs) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1. Such evidence could include but it is not limited to plans for precluding operating in excess of each SOL that was identified as a result of the Operational Planning Analysis. | 2017-10-01 | [5 empty] | NPCC-NS | [6 empty] | 20000000
TOP-002-4 (Nova Scotia) | 78830000000520 | R3. | 788300000006127 | Each Transmission Operator shall notify entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in those plan(s). |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | The Transmission Operator did not notify one impacted entity or 5% or less of the entities, whichever is greater identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify two entities or more than 5% and less than or equal to 10% of the impacted entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify three impacted entities or more than 10% and less than or equal to 15% of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify four or more entities or more than 15% of the impacted NERC identified in the Operating Plan(s) as to their role in the plan(s). For the Requirement R3 and R5 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size of entity. If a small entity has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. | M3. Each Transmission Operator shall have evidence that it notified entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in the plan(s). Such evidence could include but is not limited to dated operator logs, or e-mail records. | 2017-10-01 | [5 empty] | NPCC-NS | [6 empty] | 30000000
TOP-002-4 (Nova Scotia) | 78830000000520 | R4. | 788300000006128 | Each Balancing Authority shall have an Operating Plan(s) for the next-day that addresses: |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority has an Operating Plan but it does not address one of the criteria in Requirement R4. | The Balancing Authority has an Operating Plan but it does not address two of the criteria in Requirement R4. | The Balancing Authority has an Operating Plan but it does not address three of the criteria in Requirement R4. | The Balancing Authority did not have an Operating Plan. | M4. Each Balancing Authority shall have evidence that it has developed a plan to operate within the criteria identified. Such evidence could include but is not limited to dated operator logs or e-mail records. | 2017-10-01 | [5 empty] | NPCC-NS | [6 empty] | 40000000
TOP-002-4 (Nova Scotia) | 78830000000520 | R5. | 788300000006129 | Each Balancing Authority shall notify entities identified in the Operating Plan(s) cited in Requirement R4 as to their role in those plan(s). |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority did not notify one impacted entity or 5% or less of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify two entities or more than 5% and less than or equal to 10% of the impacted entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify three impacted entities or more than 10% and less than or equal to 15% of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify four or more entities or more than 15% of the impacted entities identified in the Operating Plan(s) as to their role in the plan(s). For the Requirement R3 and R5 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size of entity. If a small entity has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. | Each Balancing Authority shall have evidence that it notified entities identified in the plan(s) cited in Requirement R4 as to their role in the plan(s). Such evidence could include but is not limited to dated operator logs or e-mail records. | 2017-10-01 | [5 empty] | NPCC-NS | [6 empty] | 50000000
TOP-002-4 (Nova Scotia) | 78830000000520 | R6. | 788300000006130 | Each Transmission Operator shall provide its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not provide its Operating Plan(s) for next-day operations as identified in Requirement R2 to its Reliability Coordinator. | M6. Each Transmission Operator shall have evidence that it provided its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. Such evidence could include but is not limited to dated operator logs or e-mail records. | 2017-10-01 | [5 empty] | NPCC-NS | [6 empty] | 60000000
TOP-002-4 (Nova Scotia) | 78830000000520 | R7. | 788300000006131 | Each Balancing Authority shall provide its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. |  | BA | BA | [20 empty] | Operations Planning | Medium | N/A | N/A | N/A | The Balancing Authority did not provide its Operating Plan(s) for next-day operations as identified in Requirement R4 to its Reliability Coordinator. | M7. Each Balancing Authority shall have evidence that it provided its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. Such evidence could include but is not limited to dated operator logs or e-mail records. | 2017-10-01 | [5 empty] | NPCC-NS | [6 empty] | 70000000
TOP-002-4 (Ontario) | 79780000520 | R1. | 79780006125 | Each Transmission Operator shall have an Operational Planning Analysis that will allow it to assess whether its planned operations for the next day within its Transmission Operator Area will exceed any of its System Operating Limits (SOLs). |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not have an Operational Planning Analysis allowing it to assess whether its planned operations for the next day within its Transmission Operator Area exceeded any of its System Operating Limits (SOLs). | &lt;p&gt;Each Transmission Operator shall have evidence of a completed Operational Planning Analysis. Such evidence could include but is not limited to dated power flow study results.&lt;/p&gt; &lt;p/&gt; | 2017-04-01 | [5 empty] | NPCC-ON | [6 empty] | 10000000
TOP-002-4 (Ontario) | 79780000520 | R2. | 79780006126 | Each Transmission Operator shall have an Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) exceedances identified as a result of its Operational Planning Analysis as required in Requirement R1. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not have an Operating Plan to address potential System Operating Limit (SOL) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1. | &lt;p&gt;Each Transmission Operator shall have evidence that it has an Operating Plan to address potential System Operating Limits (SOLs) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1. Such evidence could include but it is not limited to plans for precluding operating in excess of each SOL that was identified as a result of the Operational Planning Analysis.&lt;/p&gt; &lt;p/&gt; | 2017-04-01 | [5 empty] | NPCC-ON | [6 empty] | 20000000
TOP-002-4 (Ontario) | 79780000520 | R3. | 79780006127 | Each Transmission Operator shall notify entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in those plan(s). |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The Transmission Operator did not notify one impacted entity or 5% or less of the entities, whichever is greater identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify two entities or more than 5% and less than or equal to 10% of the impacted entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify three impacted entities or more than 10% and less than or equal to 15% of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify four or more entities or more than 15% of the impacted NERC identified in the Operating Plan(s) as to their role in the plan(s). For the Requirement R3 and R5 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size of entity. If a small entity has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. | M3. Each Transmission Operator shall have evidence that it notified entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in the plan(s). Such evidence could include but is not limited to dated operator logs, or e-mail records. | 2017-04-01 | [5 empty] | NPCC-ON | [6 empty] | 30000000
TOP-002-4 (Ontario) | 79780000520 | R4. | 79780006128 | Each Balancing Authority shall have an Operating Plan(s) for the next-day that addresses: |  | BA | BA | [20 empty] | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The Balancing Authority has an Operating Plan but it does not address one of the criteria in Requirement R4. | The Balancing Authority has an Operating Plan but it does not address two of the criteria in Requirement R4. | The Balancing Authority has an Operating Plan but it does not address three of the criteria in Requirement R4. | The Balancing Authority did not have an Operating Plan. | M4. Each Balancing Authority shall have evidence that it has developed a plan to operate within the criteria identified. Such evidence could include but is not limited to dated operator logs or e-mail records. | 2017-04-01 | [5 empty] | NPCC-ON | [6 empty] | 40000000
TOP-002-4 (Ontario) | 79780000520 | R5. | 79780006129 | Each Balancing Authority shall notify entities identified in the Operating Plan(s) cited in Requirement R4 as to their role in those plan(s). |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority did not notify one impacted entity or 5% or less of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify two entities or more than 5% and less than or equal to 10% of the impacted entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify three impacted entities or more than 10% and less than or equal to 15% of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify four or more entities or more than 15% of the impacted entities identified in the Operating Plan(s) as to their role in the plan(s). For the Requirement R3 and R5 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size of entity. If a small entity has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. | &lt;p&gt;&lt;br/&gt;Each Balancing Authority shall have evidence that it notified entities identified in the plan(s) cited in Requirement R4 as to their role in the plan(s). Such evidence could include but is not limited to dated operator logs or e-mail records.&lt;/p&gt; &lt;p/&gt; | 2017-04-01 | [5 empty] | NPCC-ON | [6 empty] | 50000000
TOP-002-4 (Ontario) | 79780000520 | R6. | 79780006130 | Each Transmission Operator shall provide its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not provide its Operating Plan(s) for next-day operations as identified in Requirement R2 to its Reliability Coordinator. | M6. Each Transmission Operator shall have evidence that it provided its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. Such evidence could include but is not limited to dated operator logs or e-mail records. | 2017-04-01 | [5 empty] | NPCC-ON | [6 empty] | 60000000
TOP-002-4 (Ontario) | 79780000520 | R7. | 79780006131 | Each Balancing Authority shall provide its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. |  | BA | BA | [20 empty] | Operations Planning | Medium | N/A | N/A | N/A | The Balancing Authority did not provide its Operating Plan(s) for next-day operations as identified in Requirement R4 to its Reliability Coordinator. | M7. Each Balancing Authority shall have evidence that it provided its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. Such evidence could include but is not limited to dated operator logs or e-mail records. | 2017-04-01 | [5 empty] | NPCC-ON | [6 empty] | 70000000
TOP-002-4 (Saskatchewan) | 83750000000520 | R1. | 837500000006125 | Each Transmission Operator shall have an Operational Planning Analysis that will allow it to assess whether its planned operations for the next day within its Transmission Operator Area will exceed any of its System Operating Limits (SOLs). |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not have an Operational Planning Analysis allowing it to assess whether its planned operations for the next day within its Transmission Operator Area exceeded any of its System Operating Limits (SOLs). | Each Transmission Operator shall have evidence of a completed Operational Planning Analysis. Such evidence could include but is not limited to dated power flow study results. | 2017-04-01 | [5 empty] | MRO-SK | [6 empty] | 10000000
TOP-002-4 (Saskatchewan) | 83750000000520 | R2. | 837500000006126 | Each Transmission Operator shall have an Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) exceedances identified as a result of its Operational Planning Analysis as required in Requirement R1. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not have an Operating Plan to address potential System Operating Limit (SOL) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1. | Each Transmission Operator shall have evidence that it has an Operating Plan to address potential System Operating Limits (SOLs) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1. Such evidence could include but it is not limited to plans for precluding operating in excess of each SOL that was identified as a result of the Operational Planning Analysis. | 2017-04-01 | [5 empty] | MRO-SK | [6 empty] | 20000000
TOP-002-4 (Saskatchewan) | 83750000000520 | R3. | 837500000006127 | Each Transmission Operator shall notify entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in those plan(s). |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | The Transmission Operator did not notify one impacted entity or 5% or less of the entities, whichever is greater identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify two entities or more than 5% and less than or equal to 10% of the impacted entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify three impacted entities or more than 10% and less than or equal to 15% of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify four or more entities or more than 15% of the impacted NERC identified in the Operating Plan(s) as to their role in the plan(s). For the Requirement R3 and R5 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size of entity. If a small entity has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. | M3. Each Transmission Operator shall have evidence that it notified entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in the plan(s). Such evidence could include but is not limited to dated operator logs, or e-mail records. | 2017-04-01 | [5 empty] | MRO-SK | [6 empty] | 30000000
TOP-002-4 (Saskatchewan) | 83750000000520 | R4. | 837500000006128 | Each Balancing Authority shall have an Operating Plan(s) for the next-day that addresses: |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority has an Operating Plan but it does not address one of the criteria in Requirement R4. | The Balancing Authority has an Operating Plan but it does not address two of the criteria in Requirement R4. | The Balancing Authority has an Operating Plan but it does not address three of the criteria in Requirement R4. | The Balancing Authority did not have an Operating Plan. | M4. Each Balancing Authority shall have evidence that it has developed a plan to operate within the criteria identified. Such evidence could include but is not limited to dated operator logs or e-mail records. | 2017-04-01 | [5 empty] | MRO-SK | [6 empty] | 40000000
TOP-002-4 (Saskatchewan) | 83750000000520 | R5. | 837500000006129 | Each Balancing Authority shall notify entities identified in the Operating Plan(s) cited in Requirement R4 as to their role in those plan(s). |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority did not notify one impacted entity or 5% or less of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify two entities or more than 5% and less than or equal to 10% of the impacted entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify three impacted entities or more than 10% and less than or equal to 15% of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify four or more entities or more than 15% of the impacted entities identified in the Operating Plan(s) as to their role in the plan(s). For the Requirement R3 and R5 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size of entity. If a small entity has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. | Each Balancing Authority shall have evidence that it notified entities identified in the plan(s) cited in Requirement R4 as to their role in the plan(s). Such evidence could include but is not limited to dated operator logs or e-mail records. | 2017-04-01 | [5 empty] | MRO-SK | [6 empty] | 50000000
TOP-002-4 (Saskatchewan) | 83750000000520 | R6. | 837500000006130 | Each Transmission Operator shall provide its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not provide its Operating Plan(s) for next-day operations as identified in Requirement R2 to its Reliability Coordinator. | M6. Each Transmission Operator shall have evidence that it provided its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. Such evidence could include but is not limited to dated operator logs or e-mail records. | 2017-04-01 | [5 empty] | MRO-SK | [6 empty] | 60000000
TOP-002-4 (Saskatchewan) | 83750000000520 | R7. | 837500000006131 | Each Balancing Authority shall provide its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. |  | BA | BA | [20 empty] | Operations Planning | Medium | N/A | N/A | N/A | The Balancing Authority did not provide its Operating Plan(s) for next-day operations as identified in Requirement R4 to its Reliability Coordinator. | M7. Each Balancing Authority shall have evidence that it provided its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. Such evidence could include but is not limited to dated operator logs or e-mail records. | 2017-04-01 | [5 empty] | MRO-SK | [6 empty] | 70000000
TOP-002-5 | ST-2023-10-31-0000001 | R1. | RQ-2023-10-31-0000001 | Each Transmission Operator shall have an Operational Planning Analysis that will allow it to assess whether its planned operations for the next day within its Transmission Operator Area will exceed any of its System Operating Limits (SOLs) |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not have an Operational Planning Analysis allowing it to assess whether its planned operations for the next day within its Transmission Operator Area exceeded any of its System Operating Limits (SOLs). | Each Transmission Operator shall have evidence of a completed Operational Planning Analysis. Such evidence could include, but is not limited to dated power flow study results. | 2025-10-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-002-5 | ST-2023-10-31-0000001 | R2. | RQ-2023-10-31-0000002 | Each Transmission Operator shall have an Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) exceedances identified as a result of its Operational Planning Analysis as required in Requirement R1. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not have an Operating Plan to address potential System Operating Limit (SOL) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1. | Each Transmission Operator shall have evidence that it has an Operating Plan to address potential System Operating Limits (SOLs) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1. Such evidence could include, but it is not limited to plans for precluding operating in excess of each SOL that was identified as a result of the Operational Planning Analysis. | 2025-10-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-002-5 | ST-2023-10-31-0000001 | R3. | RQ-2023-10-31-0000003 | Each Transmission Operator shall notify entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in those plan(s). |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | The Transmission Operator did not notify one impacted entity or 5% or less of the entities, whichever is greater identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify two entities or more than 5% and less than or equal to 10% of the impacted entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify three impacted entities or more than 10% and less than or equal to 15% of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify four or more entities or more than 15% of the impacted NERC identified in the Operating Plan(s) as to their role in the plan(s). | Each Transmission Operator shall have evidence that it notified entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in the plan(s). Such evidence could include, but is not limited to dated operator logs, or email records. | 2025-10-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-002-5 | ST-2023-10-31-0000001 | R4. | RQ-2023-10-31-0000004 | Each Balancing Authority shall have an Operating Plan(s) for the next day that addresses: |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority has an Operating Plan, but it does not address one of the criteria in Requirement R4. | The Balancing Authority has an Operating Plan, but it does not address two of the criteria in Requirement R4. | The Balancing Authority has an Operating Plan, but it does not address three of the criteria in Requirement R4. | The Balancing Authority did not have an Operating Plan. | Each Balancing Authority shall have evidence that it has developed a plan to operate within the criteria identified. Such evidence could include, but is not limited to dated operator logs or email records. | 2025-10-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-002-5 | ST-2023-10-31-0000001 | R5. | RQ-2023-10-31-0000005 | Each Balancing Authority shall notify entities identified in the Operating Plan(s) cited in Requirement R4 as to their role in those plan(s) |  | BA | BA | [20 empty] | Operations Planning | Medium | The Balancing Authority did not notify one impacted entity or 5% or less of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify two entities or more than 5% and less than or equal to 10% of the impacted entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify three impacted entities or more than 10% and less than or equal to 15% of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify four or more entities or more than 15% of the impacted entities identified in the Operating Plan(s) as to their role in the plan(s). | Each Balancing Authority shall have evidence that it notified entities identified in the plan(s) cited in Requirement R4 as to their role in the plan(s). Such evidence could include, but is not limited to dated operator logs or email records. | 2025-10-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-002-5 | ST-2023-10-31-0000001 | R6. | RQ-2023-10-31-0000006 | Each Transmission Operator shall provide its Operating Plan(s) for next day operations identified in Requirement R2 to its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not provide its Operating Plan(s) for next day operations as identified in Requirement R2 to its Reliability Coordinator. | Each Transmission Operator shall have evidence that it provided its Operating Plan(s) for next day operations identified in Requirement R2 to its Reliability Coordinator. Such evidence could include, but is not limited to dated operator logs or email records. | 2025-10-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TOP-002-5 | ST-2023-10-31-0000001 | R7. | RQ-2023-10-31-0000007 | Each Balancing Authority shall provide its Operating Plan(s) for next day operations identified in Requirement R4 to its Reliability Coordinator. |  | BA | BA | [20 empty] | Operations Planning | Medium | N/A | N/A | N/A | The Transmission Operator did not provide its Operating Plan(s) for next day operations as identified in Requirement R2 to its Reliability Coordinator. | Each Balancing Authority shall have evidence that it provided its Operating Plan(s) for next day operations identified in Requirement R4 to its Reliability Coordinator. Such evidence could include, but is not limited to dated operator logs or email records. | 2025-10-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
TOP-002-5 | ST-2023-10-31-0000001 | R8. | RQ-2023-10-31-0000008 | Each Balancing Authority shall have an extreme cold weather Operating Process for its Balancing Authority Area, addressing preparations for and operations during extreme cold weather periods. The extreme cold weather Operating Process shall include, but is not limited to: |  | BA | BA | [20 empty] | Operations Planning | Medium | N/A | The Balancing Authority had an extreme cold weather Operating Process addressing preparations for and operations during extreme cold weather periods, but it did not address one of the Requirements or sub- Requirements of R8 Parts 8.1 through 8.3 | The Balancing Authority had an extreme cold weather Operating Process addressing preparations for and operations during extreme cold weather periods, but it did not address two of the Requirements or sub- Requirements of R8 Parts 8.1 through 8.3. | The Balancing Authority did not have an extreme cold weather Operating Process addressing preparations for and operations during extreme cold weather periods. | Each Balancing Authority shall have evidence that it has developed an extreme cold weather Operating Process in accordance with Requirement R8. | 2025-10-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
TOP-003-0 | 171 | R1. | 1949 | Generator Operators and Transmission Operators shall provide planned outage information. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-003-0 | 171 | R2. | 1953 | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of system voltage regulating equipment, such as automatic voltage regulators on generators, supplementary excitation control, synchronous condensers, shunt and series capacitors, reactors, etc., among affected Balancing Authorities and Transmission Operators as required. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-003-0 | 171 | R3. | 1954 | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of telemetering and control equipment and associated communication channels between the affected areas. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2011-09-30 |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-003-0 | 171 | R4. | 1955 | Each Reliability Coordinator shall resolve any scheduling of potential reliability conflicts. |  | RC | [11 empty] | RC | [10 empty] | Medium | [5 empty] | 2007-06-18 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-003-0 (British Columbia) | 666700000010281 | R1. | 666700000011743 | Generator Operators and Transmission Operators shall provide planned outage information. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-11-01 |  | 2013-04-14 |  |  |  | WECC-BC | [6 empty] | 10000000
TOP-003-0 (British Columbia) | 666700000010281 | R2. | 666700000011744 | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of system voltage regulating equipment, such as automatic voltage regulators on generators, supplementary excitation control, synchronous condensers, shunt and series capacitors, reactors, etc., among affected Balancing Authorities and Transmission Operators as required. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-11-01 |  | 2013-04-14 |  |  |  | WECC-BC | [6 empty] | 20000000
TOP-003-0 (British Columbia) | 666700000010281 | R3. | 666700000011745 | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of telemetering and control equipment and associated communication channels between the affected areas. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-11-01 |  | 2013-04-14 |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  |  | WECC-BC | [6 empty] | 30000000
TOP-003-0 (British Columbia) | 666700000010281 | R4. | 666700000011746 | Each Reliability Coordinator shall resolve any scheduling of potential reliability conflicts. |  | RC | [11 empty] | RC | [10 empty] | Medium | [5 empty] | 2010-11-01 |  | 2013-04-14 |  |  |  | WECC-BC | [6 empty] | 40000000
TOP-003-0 (Manitoba) | 77660000000171 | R1. | 776600000001949 | Generator Operators and Transmission Operators shall provide planned outage information. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 10000000
TOP-003-0 (Manitoba) | 77660000000171 | R2. | 776600000001953 | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of system voltage regulating equipment, such as automatic voltage regulators on generators, supplementary excitation control, synchronous condensers, shunt and series capacitors, reactors, etc., among affected Balancing Authorities and Transmission Operators as required. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 20000000
TOP-003-0 (Manitoba) | 77660000000171 | R3. | 776600000001954 | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of telemetering and control equipment and associated communication channels between the affected areas. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  |  | MRO-MB | [6 empty] | 30000000
TOP-003-0 (Manitoba) | 77660000000171 | R4. | 776600000001955 | Each Reliability Coordinator shall resolve any scheduling of potential reliability conflicts. |  | RC | [11 empty] | RC | [10 empty] | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 40000000
TOP-003-0 (Ontario) | 79780000171 | R1. | 79780001949 | Generator Operators and Transmission Operators shall provide planned outage information. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-003-0 (Ontario) | 79780000171 | R2. | 79780001953 | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of system voltage regulating equipment, such as automatic voltage regulators on generators, supplementary excitation control, synchronous condensers, shunt and series capacitors, reactors, etc., among affected Balancing Authorities and Transmission Operators as required. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to plan or coordinate scheduled outages of system voltage regulating equipment, such as automatic voltage regulators on generators, supplementary excitation control, synchronous condensers, shunt and series capacitors, reacto |  | 2007-06-18 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-003-0 (Ontario) | 79780000171 | R3. | 79780001954 | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of telemetering and control equipment and associated communication channels between the affected areas. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium | The responsible entity planned and coordinated scheduled outages of telemetering and control equipment and associated communication channels with its Reliability Coordinator, but failed to coordinate with affected neighboring Transmission Operators, Balan |  |  | The responsible entity failed to plan and coordinate scheduled outages of telemetering and control equipment and associated communication channels between the affected areas. | M3. The Transmission Owner and Generator Owner shall each have evidence it retained and provided recorded Disturbance data to entities in accordance with its associated Regional Reliability Organization’s Disturbance data reporting requirements. (R4 R5) | 2007-06-18 |  | 2011-09-30 |  100% compliant six months after BOT adoption for already installed DME.&lt;br/&gt; 100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  |  | NPCC-ON | [6 empty] | 30000000
TOP-003-0 (Ontario) | 79780000171 | R4. | 79780001955 | Each Reliability Coordinator shall resolve any scheduling of potential reliability conflicts. |  | RC | [11 empty] | RC | [10 empty] | Medium |  |  |  | The Reliability Coordinator failed to resolve any scheduling of potential reliability conflicts. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-003-1 | 172 | R1. | 1956 | Generator Operators and Transmission Operators shall provide planned outage information. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP | [8 empty] | Evidence that the Generator Operator, Transmission Operator, and Balancing Authority reported and coordinated scheduled outage information as indicated in the requirements above. | 2011-10-01 |  | 2017-03-31 |  |  | TOP-003-0 R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-003-1 | 172 | R2. | 1960 | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of system voltage regulating equipment, such as automatic voltage regulators on generators, supplementary excitation control, synchronous condensers, shunt and series capacitors, reactors, etc., among affected Balancing Authorities and Transmission Operators as required. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-01 |  | 2017-03-31 |  |  | TOP-003-0 R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-003-1 | 172 | R3. | 1961 | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of telemetering and control equipment and associated communication channels between the affected areas. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-01 |  | 2017-03-31 |  |  | TOP-003-0 R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-003-1 | 172 | R4. | 1962 | Each Reliability Coordinator shall resolve any scheduling of potential reliability conflicts. |  | RC | [11 empty] | RC | [10 empty] | Medium | [5 empty] | 2011-10-01 |  | 2017-03-31 |  |  | TOP-003-0 R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-003-1 (British Columbia) | 666700000010282 | R1. | 666700000011747 | Generator Operators and Transmission Operators shall provide planned outage information. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP | [8 empty] | Evidence that the Generator Operator, Transmission Operator, and Balancing Authority reported and coordinated scheduled outage information as indicated in the requirements above. | 2013-04-15 |  | 2019-03-31 |  |  |  | WECC-BC | [6 empty] | 10000000
TOP-003-1 (British Columbia) | 666700000010282 | R2. | 666700000011748 | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of system voltage regulating equipment, such as automatic voltage regulators on generators, supplementary excitation control, synchronous condensers, shunt and series capacitors, reactors, etc., among affected Balancing Authorities and Transmission Operators as required. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium | [5 empty] | 2013-04-15 |  | 2019-03-31 |  |  |  | WECC-BC | [6 empty] | 20000000
TOP-003-1 (British Columbia) | 666700000010282 | R3. | 666700000011749 | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of telemetering and control equipment and associated communication channels between the affected areas. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium | [5 empty] | 2013-04-15 |  | 2019-03-31 |  |  |  | WECC-BC | [6 empty] | 30000000
TOP-003-1 (British Columbia) | 666700000010282 | R4. | 666700000011750 | Each Reliability Coordinator shall resolve any scheduling of potential reliability conflicts. |  | RC | [11 empty] | RC | [10 empty] | Medium | [5 empty] | 2013-04-15 |  | 2019-03-31 |  |  |  | WECC-BC | [6 empty] | 40000000
TOP-003-1 (Manitoba) | 77660000000172 | R1. | 776600000001956 | Generator Operators and Transmission Operators shall provide planned outage information. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP | [8 empty] | Evidence that the Generator Operator, Transmission Operator, and Balancing Authority reported and coordinated scheduled outage information as indicated in the requirements above. | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
TOP-003-1 (Manitoba) | 77660000000172 | R2. | 776600000001960 | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of system voltage regulating equipment, such as automatic voltage regulators on generators, supplementary excitation control, synchronous condensers, shunt and series capacitors, reactors, etc., among affected Balancing Authorities and Transmission Operators as required. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
TOP-003-1 (Manitoba) | 77660000000172 | R3. | 776600000001961 | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of telemetering and control equipment and associated communication channels between the affected areas. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
TOP-003-1 (Manitoba) | 77660000000172 | R4. | 776600000001962 | Each Reliability Coordinator shall resolve any scheduling of potential reliability conflicts. |  | RC | [11 empty] | RC | [10 empty] | Medium | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 40000000
TOP-003-1 (Ontario) | 79780000172 | R1. | 79780001956 | Generator Operators and Transmission Operators shall provide planned outage information. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP | [9 empty] | 2011-10-01 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-003-1 (Ontario) | 79780000172 | R2. | 79780001960 | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of system voltage regulating equipment, such as automatic voltage regulators on generators, supplementary excitation control, synchronous condensers, shunt and series capacitors, reactors, etc., among affected Balancing Authorities and Transmission Operators as required. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-01 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-003-1 (Ontario) | 79780000172 | R3. | 79780001961 | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of telemetering and control equipment and associated communication channels between the affected areas. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-01 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-003-1 (Ontario) | 79780000172 | R4. | 79780001962 | Each Reliability Coordinator shall resolve any scheduling of potential reliability conflicts. |  | RC | [11 empty] | RC | [10 empty] | Medium | [5 empty] | 2011-10-01 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-003-1 (Saskatchewan) | 83750000000172 | R1. | 837500000001956 | Generator Operators and Transmission Operators shall provide planned outage information. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP | [8 empty] | Evidence that the Generator Operator, Transmission Operator, and Balancing Authority reported and coordinated scheduled outage information as indicated in the requirements above. | 2015-04-15 |  | 2012-05-08 |  |  |  | MRO-SK | [6 empty] | 10000000
TOP-003-1 (Saskatchewan) | 83750000000172 | R2. | 837500000001960 | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of system voltage regulating equipment, such as automatic voltage regulators on generators, supplementary excitation control, synchronous condensers, shunt and series capacitors, reactors, etc., among affected Balancing Authorities and Transmission Operators as required. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium | [5 empty] | 2015-04-15 |  | 2012-05-08 |  |  |  | MRO-SK | [6 empty] | 20000000
TOP-003-1 (Saskatchewan) | 83750000000172 | R3. | 837500000001961 | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of telemetering and control equipment and associated communication channels between the affected areas. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium | [5 empty] | 2015-04-15 |  | 2012-05-08 |  |  |  | MRO-SK | [6 empty] | 30000000
TOP-003-1 (Saskatchewan) | 83750000000172 | R4. | 837500000001962 | Each Reliability Coordinator shall resolve any scheduling of potential reliability conflicts. |  | RC | [11 empty] | RC | [10 empty] | Medium | [5 empty] | 2015-04-15 |  | 2012-05-08 |  |  |  | MRO-SK | [6 empty] | 40000000
TOP-003-2 | 327 | R1. | 4299 | Each Transmission Operator shall create a documented specification for the data necessary for it to perform its Operational Planning Analyses and Real-time monitoring. The specification shall include: [See Standard pdf for further information] |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not include one of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses and Real-time monitoring. | The Transmission Operator did not include two of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses and Real-time monitoring. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for them to perform their Operational Planning Analyses and Real-time monitoring. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for them to perform their Operational Planning Analyses and Real-time monitoring. |  |  |  | 2016-01-26 |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-003-2 | 327 | R2. | 4300 | Each Balancing Authority shall create a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The specification shall include: [See Standard pdf for further information] |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not include one of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include two of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for them to perform their analysis functions and Real-time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for them to perform their analysis functions and Real-time monitoring. |  |  |  | 2016-01-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-003-2 | 327 | R3. | 4301 | Each Transmission Operator shall distribute its data specification, as developed in Requirement R1,to entities that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not distribute its data specification, as developed in Requirement R1 to one entity, or 5% or less of the entities, whichever is less, that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | The Transmission Operator did not distribute its data specification, as developed in requirement R1 to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is less, that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | The Transmission Operator did not distribute its data specification, as developed in Requirement R1 to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is less, that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | The Transmission Operator did not distribute its data specification, as developed in Requirement R1 to four or more entities, or more than 15% of the entities, whichever is less, that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | M3. Each Transmission Operator shall make available evidence that it has distributed its data specification, as developed in Requirement R1, to entities that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements in accordance with Requirement R3. Such evidence could include, but is not limited to, web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. |  |  | 2016-01-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-003-2 | 327 | R4. | 4302 | Each Balancing Authority shall distribute its data specification, as developed in Requirement R2, to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not distribute its data specification, as developed in Requirement R2 to one entity, or 5% or less of the entities, whichever is less, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | The Balancing Authority did not distribute its data specification, as developed in Requirement R2 to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is less, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | The Balancing Authority did not distribute its data specification, as developed in Requirement R2 to three entities, or more than 10% and less than or equal to 15% of the entities, whichever is less, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring process used in meeting its NERC-mandated reliability requirements . | The Balancing Authority did not distribute its data specification, as developed in Requirement R2 to four or more entities, or more than 15% of the entities, whichever is less,that have data required by the Balancing Authority’s analysis functions and Realtime monitoring process used in meeting its NERC-mandated reliability requirements. | M4. Each Balancing Authority shall make available evidence that it has distributed its data specification, as developed in Requirement R2, to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring process used in meeting its NERC-mandated reliability requirements, in accordance with Requirement R4. Such evidence could include, but is not limited to, web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. |  |  | 2016-01-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-003-2 | 327 | R5. | 4303 | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Interchange Authority, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications for data. |  | BA, DP, GO, GOP, IA, LSE, TO, TOP | BA | DP |  |  | GO | GOP | IA | LSE | [9 empty] | TO | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The responsible entity receiving a data specification in Requirement R3 or R4 did not satisfy the obligations of the documented specifications for data. | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Interchange Authority, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications for data, in accordance with Requirement R5. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. |  |  | 2016-01-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-003-2 (Ontario) | 79780000327 | R1. | 79780004299 | Each Transmission Operator shall create a documented specification for the data necessary for it to perform its Operational Planning Analyses and Real-time monitoring. The specification shall include: [See Standard pdf for further information] |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not include one of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses and Real-time monitoring. | The Transmission Operator did not include two of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses and Real-time monitoring. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for them to perform their Operational Planning Analyses and Real-time monitoring. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for them to perform their Operational Planning Analyses and Real-time monitoring. | M4. Each Transmission Owner and Generator Owner that is required to install DMEs to meet its Regional Reliability Organization’s DME installation requirements, shall have an associated DME maintenance and testing program as defined in Requirement 6. |  |  | 2016-01-26 |  100% compliant six months after BOT adoption for already installed DME.&lt;br/&gt; 100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  |  | NPCC-ON | [6 empty] | 10000000
TOP-003-2 (Ontario) | 79780000327 | R2. | 79780004300 | Each Balancing Authority shall create a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The specification shall include: [See Standard pdf for further information] |  | BA | BA | [20 empty] | Long-Term Planning, Operations Planning | Low | The Balancing Authority did not include one of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include two of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for them to perform their analysis functions and Real-time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for them to perform their analysis functions and Real-time monitoring. | M1. Each Generator Owner and Transmission Owner with applicable Facilities will have evidence (such as examples provided in PRC-019 Section G) that it coordinated the voltage regulating system controls, including in-service limiters and protection functions, with the applicable equipment capabilities and settings of the applicable Protection System devices and functions as specified in Requirement R1. This evidence should include dated documentation that demonstrates the coordination was performed. |  |  | 2016-01-26 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-003-2 (Ontario) | 79780000327 | R3. | 79780004301 | Each Transmission Operator shall distribute its data specification, as developed in Requirement R1,to entities that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not distribute its data specification, as developed in Requirement R1 to one entity, or 5% or less of the entities, whichever is less, that have data required by the Transmission Operator’s Operational Planning Analysis and R | The Transmission Operator did not distribute its data specification, as developed in requirement R1 to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is less, that have data required by the Transmission O | The Transmission Operator did not distribute its data specification, as developed in Requirement R1 to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is less, that have data required by the Transmissi | The Transmission Operator did not distribute its data specification, as developed in Requirement R1 to four or more entities, or more than 15% of the entities, whichever is less, that have data required by the Transmission Operator’s Operational Planning | M3. Each Transmission Operator shall make available evidence that it has distributed its data specification, as developed in Requirement R1, to entities that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements in accordance with Requirement R3. Such evidence could include, but is not limited to, web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. |  |  | 2016-01-26 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-003-2 (Ontario) | 79780000327 | R4. | 79780004302 | Each Balancing Authority shall distribute its data specification, as developed in Requirement R2, to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not distribute its data specification, as developed in Requirement R2 to one entity, or 5% or less of the entities, whichever is less, that have data required by the Balancing Authority’s analysis functions and Real-time monito | The Balancing Authority did not distribute its data specification, as developed in Requirement R2 to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is less, that have data required by the Balancing Authority’s analy | The Balancing Authority did not distribute its data specification, as developed in Requirement R2 to three entities, or more than 10% and less than or equal to 15% of the entities, whichever is less, that have data required by the Balancing Authority’s an | The Balancing Authority did not distribute its data specification, as developed in Requirement R2 to four or more entities, or more than 15% of the entities, whichever is less,that have data required by the Balancing Authority’s analysis functions and Rea | M4. Each Balancing Authority shall make available evidence that it has distributed its data specification, as developed in Requirement R2, to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring process used in meeting its NERC-mandated reliability requirements, in accordance with Requirement R4. Such evidence could include, but is not limited to, web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. |  |  | 2016-01-26 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-003-2 (Ontario) | 79780000327 | R5. | 79780004303 | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Interchange Authority, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications for data. |  | BA, DP, GO, GOP, IA, LSE, TO, TOP | BA | DP |  |  | GO | GOP | IA | LSE | [9 empty] | TO | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The responsible entity receiving a data specification in Requirement R3 or R4 did not satisfy the obligations of the documented specifications for data. | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Interchange Authority, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications for data, in accordance with Requirement R5. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. |  |  | 2016-01-26 |  |  |  | NPCC-ON | [6 empty] | 50000000
TOP-003-2 (Saskatchewan) | 83750000000327 | R1. | 837500000004299 | Each Transmission Operator shall create a documented specification for the data necessary for it to perform its Operational Planning Analyses and Real-time monitoring. The specification shall include: [See Standard pdf for further information] |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not include one of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses and Real-time monitoring. | The Transmission Operator did not include two of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses and Real-time monitoring. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for them to perform their Operational Planning Analyses and Real-time monitoring. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for them to perform their Operational Planning Analyses and Real-time monitoring. |  | 2012-05-09 |  | 2016-12-31 |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  |  | MRO-SK | [6 empty] | 10000000
TOP-003-2 (Saskatchewan) | 83750000000327 | R2. | 837500000004300 | Each Balancing Authority shall create a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The specification shall include: [See Standard pdf for further information] |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not include one of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include two of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for them to perform their analysis functions and Real-time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for them to perform their analysis functions and Real-time monitoring. |  | 2012-05-09 |  | 2016-12-31 |  |  |  | MRO-SK | [6 empty] | 20000000
TOP-003-2 (Saskatchewan) | 83750000000327 | R3. | 837500000004301 | Each Transmission Operator shall distribute its data specification, as developed in Requirement R1,to entities that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not distribute its data specification, as developed in Requirement R1 to one entity, or 5% or less of the entities, whichever is less, that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | The Transmission Operator did not distribute its data specification, as developed in requirement R1 to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is less, that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | The Transmission Operator did not distribute its data specification, as developed in Requirement R1 to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is less, that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | The Transmission Operator did not distribute its data specification, as developed in Requirement R1 to four or more entities, or more than 15% of the entities, whichever is less, that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | M3. Each Transmission Operator shall make available evidence that it has distributed its data specification, as developed in Requirement R1, to entities that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements in accordance with Requirement R3. Such evidence could include, but is not limited to, web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | 2012-05-09 |  | 2016-12-31 |  |  |  | MRO-SK | [6 empty] | 30000000
TOP-003-2 (Saskatchewan) | 83750000000327 | R4. | 837500000004302 | Each Balancing Authority shall distribute its data specification, as developed in Requirement R2, to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not distribute its data specification, as developed in Requirement R2 to one entity, or 5% or less of the entities, whichever is less, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | The Balancing Authority did not distribute its data specification, as developed in Requirement R2 to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is less, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | The Balancing Authority did not distribute its data specification, as developed in Requirement R2 to three entities, or more than 10% and less than or equal to 15% of the entities, whichever is less, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring process used in meeting its NERC-mandated reliability requirements . | The Balancing Authority did not distribute its data specification, as developed in Requirement R2 to four or more entities, or more than 15% of the entities, whichever is less,that have data required by the Balancing Authority’s analysis functions and Realtime monitoring process used in meeting its NERC-mandated reliability requirements. | M4. Each Balancing Authority shall make available evidence that it has distributed its data specification, as developed in Requirement R2, to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring process used in meeting its NERC-mandated reliability requirements, in accordance with Requirement R4. Such evidence could include, but is not limited to, web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | 2012-05-09 |  | 2016-12-31 |  |  |  | MRO-SK | [6 empty] | 40000000
TOP-003-2 (Saskatchewan) | 83750000000327 | R5. | 837500000004303 | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Interchange Authority, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications for data. |  | BA, DP, GO, GOP, IA, LSE, TO, TOP | BA | DP |  |  | GO | GOP | IA | LSE | [9 empty] | TO | TOP |  |  | Operations Planning | Medium | N/A | N/A | N/A | The responsible entity receiving a data specification in Requirement R3 or R4 did not satisfy the obligations of the documented specifications for data. | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Interchange Authority, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications for data, in accordance with Requirement R5. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2012-05-09 |  | 2016-12-31 |  |  |  | MRO-SK | [6 empty] | 50000000
TOP-003-3 | 501 | R1. | 6010 | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to:[See standard for additional information.] | See standard for additional information. | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not include one of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include two of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. OR The Transmission Operator did not have a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2017-01-01 |  | 2021-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-003-3 | 501 | R2. | 6011 | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [See standard for additional information.] | See standard for additional information. | BA | BA | [20 empty] | Long-Term Planning, Operations Planning | Low | The Balancing Authority did not include one of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include two of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. OR The Balancing Authority did not have a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2017-01-01 |  | 2021-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-003-3 | 501 | R3. | 6012 | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning, Operations Planning | Low | The Transmission Operator did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | M3. Each Transmission Operator shall make available evidence that it has distributed its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | 2017-01-01 |  | 2021-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-003-3 | 501 | R4. | 6013 | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. |  | BA | BA | [20 empty] | Long-Term Planning, Operations Planning | Low | The Balancing Authority did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | M4. Each Balancing Authority shall make available evidence that it has distributed its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | 2017-01-01 |  | 2021-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-003-3 | 501 | R5. | 6014 | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: [See standard for additional information.] |  | BA, DP, GO, GOP, LSE, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE | [9 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet one of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet two of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet three of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 did not satisfy the obligations of the documented specifications for data. | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2017-04-01 |  | 2021-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-003-3 (British Columbia) | 666700000010283 | R1. | 666700000011751 | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to:[See standard for additional information.] | See standard for additional information. | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not include one of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include two of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. OR The Transmission Operator did not have a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2019-04-01 |  | 2021-12-31 |  |  |  | WECC-BC | [6 empty] | 10000000
TOP-003-3 (British Columbia) | 666700000010283 | R2. | 666700000011752 | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [See standard for additional information.] | See standard for additional information. | BA | BA | [20 empty] | Long-Term Planning, Operations Planning | Low | The Balancing Authority did not include one of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include two of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. OR The Balancing Authority did not have a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2019-04-01 |  | 2021-12-31 |  |  |  | WECC-BC | [6 empty] | 20000000
TOP-003-3 (British Columbia) | 666700000010283 | R3. | 666700000011753 | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning, Operations Planning | Low | The Transmission Operator did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | M3. Each Transmission Operator shall make available evidence that it has distributed its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | 2019-04-01 |  | 2021-12-31 |  |  |  | WECC-BC | [6 empty] | 30000000
TOP-003-3 (British Columbia) | 666700000010283 | R4. | 666700000011754 | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. |  | BA | BA | [20 empty] | Long-Term Planning, Operations Planning | Low | The Balancing Authority did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | M4. Each Balancing Authority shall make available evidence that it has distributed its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | 2019-04-01 |  | 2021-12-31 |  |  |  | WECC-BC | [6 empty] | 40000000
TOP-003-3 (British Columbia) | 666700000010283 | R5. | 666700000011755 | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: [See standard for additional information.] |  | BA, DP, GO, GOP, LSE, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE | [9 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet one of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet two of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet three of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 did not satisfy the obligations of the documented specifications for data. | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2019-04-01 |  | 2021-12-31 |  |  |  | WECC-BC | [6 empty] | 50000000
TOP-003-3 (Manitoba) | 77660000000501 | R1. | 776600000006010 | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to:[See standard for additional information.] | See standard for additional information. | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not include one of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include two of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. OR The Transmission Operator did not have a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2017-07-01 | [5 empty] | MRO-MB | [6 empty] | 10000000
TOP-003-3 (Manitoba) | 77660000000501 | R2. | 776600000006011 | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [See standard for additional information.] | See standard for additional information. | BA | BA | [20 empty] | Long-Term Planning, Operations Planning | Low | The Balancing Authority did not include one of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include two of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. OR The Balancing Authority did not have a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2017-07-01 | [5 empty] | MRO-MB | [6 empty] | 20000000
TOP-003-3 (Manitoba) | 77660000000501 | R3. | 776600000006012 | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning, Operations Planning | Low | The Transmission Operator did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | M3. Each Transmission Operator shall make available evidence that it has distributed its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | 2017-07-01 | [5 empty] | MRO-MB | [6 empty] | 30000000
TOP-003-3 (Manitoba) | 77660000000501 | R4. | 776600000006013 | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. |  | BA | BA | [20 empty] | Long-Term Planning, Operations Planning | Low | The Balancing Authority did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | M4. Each Balancing Authority shall make available evidence that it has distributed its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | 2017-07-01 | [5 empty] | MRO-MB | [6 empty] | 40000000
TOP-003-3 (Manitoba) | 77660000000501 | R5. | 776600000006014 | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: [See standard for additional information.] |  | BA, DP, GO, GOP, LSE, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE | [9 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet one of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet two of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet three of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 did not satisfy the obligations of the documented specifications for data. | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2017-07-01 | [5 empty] | MRO-MB | [6 empty] | 50000000
TOP-003-3 (Nova Scotia) | 78830000000501 | R1. | 788300000006010 | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to:[See standard for additional information.] | See standard for additional information. | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not include one of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include two of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. OR The Transmission Operator did not have a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2017-10-01 |  | 2021-09-30 |  |  |  | NPCC-NS | [6 empty] | 10000000
TOP-003-3 (Nova Scotia) | 78830000000501 | R2. | 788300000006011 | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [See standard for additional information.] | See standard for additional information. | BA | BA | [20 empty] | Long-Term Planning, Operations Planning | Low | The Balancing Authority did not include one of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include two of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. OR The Balancing Authority did not have a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2017-10-01 |  | 2021-09-30 |  |  |  | NPCC-NS | [6 empty] | 20000000
TOP-003-3 (Nova Scotia) | 78830000000501 | R3. | 788300000006012 | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning, Operations Planning | Low | The Transmission Operator did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | M3. Each Transmission Operator shall make available evidence that it has distributed its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | 2017-10-01 |  | 2021-09-30 |  |  |  | NPCC-NS | [6 empty] | 30000000
TOP-003-3 (Nova Scotia) | 78830000000501 | R4. | 788300000006013 | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. |  | BA | BA | [20 empty] | Long-Term Planning, Operations Planning | Low | The Balancing Authority did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | M4. Each Balancing Authority shall make available evidence that it has distributed its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | 2017-10-01 |  | 2021-09-30 |  |  |  | NPCC-NS | [6 empty] | 40000000
TOP-003-3 (Nova Scotia) | 78830000000501 | R5. | 788300000006014 | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: [See standard for additional information.] |  | BA, DP, GO, GOP, LSE, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE | [9 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet one of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet two of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet three of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 did not satisfy the obligations of the documented specifications for data. | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2017-10-01 |  | 2021-09-30 |  |  |  | NPCC-NS | [6 empty] | 50000000
TOP-003-3 (Ontario) | 79780000501 | R1. | 79780006010 | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to:[See standard for additional information.] | See standard for additional information. | TOP | [18 empty] | TOP |  |  | Long-Term Planning, Operations Planning | Low | The Transmission Operator did not include one of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include two of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. OR The Transmission Operator did not have a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2017-01-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-003-3 (Ontario) | 79780000501 | R2. | 79780006011 | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [See standard for additional information.] | See standard for additional information. | BA | BA | [20 empty] | Long-Term Planning, Operations Planning | Low | The Balancing Authority did not include one of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include two of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. OR The Balancing Authority did not have a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2017-01-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-003-3 (Ontario) | 79780000501 | R3. | 79780006012 | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning, Operations Planning | Low | The Transmission Operator did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | M3. Each Transmission Operator shall make available evidence that it has distributed its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | 2017-01-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-003-3 (Ontario) | 79780000501 | R4. | 79780006013 | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. |  | BA | BA | [20 empty] | Long-Term Planning, Operations Planning | Low | The Balancing Authority did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | M4. Each Balancing Authority shall make available evidence that it has distributed its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | 2017-01-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-003-3 (Ontario) | 79780000501 | R5. | 79780006014 | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: [See standard for additional information.] |  | BA, DP, GO, GOP, LSE, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE | [9 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet one of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet two of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet three of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 did not satisfy the obligations of the documented specifications for data. | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2017-04-01 |  | 2021-03-31 |  |  |  | NPCC-ON | [6 empty] | 50000000
TOP-003-3 (Saskatchewan) | 83750000000501 | R1. | 837500000006010 | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to:[See standard for additional information.] | See standard for additional information. | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not include one of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include two of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. OR The Transmission Operator did not have a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | M1. Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2017-01-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 10000000
TOP-003-3 (Saskatchewan) | 83750000000501 | R2. | 837500000006011 | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [See standard for additional information.] | See standard for additional information. | BA | BA | [20 empty] | Long-Term Planning, Operations Planning | Low | The Balancing Authority did not include one of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include two of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. OR The Balancing Authority did not have a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | M2. Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2017-01-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 20000000
TOP-003-3 (Saskatchewan) | 83750000000501 | R3. | 837500000006012 | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning, Operations Planning | Low | The Transmission Operator did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | M3. Each Transmission Operator shall make available evidence that it has distributed its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | 2017-01-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 30000000
TOP-003-3 (Saskatchewan) | 83750000000501 | R4. | 837500000006013 | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. |  | BA | BA | [20 empty] | Long-Term Planning, Operations Planning | Low | The Balancing Authority did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | M4. Each Balancing Authority shall make available evidence that it has distributed its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | 2017-01-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 40000000
TOP-003-3 (Saskatchewan) | 83750000000501 | R5. | 837500000006014 | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: [See standard for additional information.] |  | BA, DP, GO, GOP, LSE, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE | [9 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet one of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet two of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet three of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 did not satisfy the obligations of the documented specifications for data. | M5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2017-01-01 |  | 2021-03-31 |  |  |  | MRO-SK | [6 empty] | 50000000
TOP-003-4 | 620 | R1. | 9204 | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to:[See standard for additional information.] |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not include one of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include two of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. OR The Transmission Operator did not have a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2021-04-01 |  | 2023-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-003-4 | 620 | R2. | 9209 | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [See standard for additional information.] |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not include one of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include two of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. OR The Balancing Authority did not have a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2021-04-01 |  | 2023-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-003-4 | 620 | R3. | 9214 | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Each Transmission Operator shall make available evidence that it has distributed its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | 2021-04-01 |  | 2023-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-003-4 | 620 | R4. | 9215 | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | Each Balancing Authority shall make available evidence that it has distributed its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | 2021-04-01 |  | 2023-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-003-4 | 620 | R5. | 9216 | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet one of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet two of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet three of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 did not satisfy the obligations of the documented specifications for data. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2021-04-01 |  | 2023-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-003-4 (British Columbia) | 666700000010284 | R1. | 666700000011756 | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to:[See standard for additional information.] |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not include one of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include two of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. OR The Transmission Operator did not have a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2022-01-01 | [5 empty] | WECC-BC | [6 empty] | 10000000
TOP-003-4 (British Columbia) | 666700000010284 | R2. | 666700000011757 | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [See standard for additional information.] |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not include one of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include two of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. OR The Balancing Authority did not have a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2022-01-01 | [5 empty] | WECC-BC | [6 empty] | 20000000
TOP-003-4 (British Columbia) | 666700000010284 | R3. | 666700000011758 | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Each Transmission Operator shall make available evidence that it has distributed its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | 2022-01-01 | [5 empty] | WECC-BC | [6 empty] | 30000000
TOP-003-4 (British Columbia) | 666700000010284 | R4. | 666700000011759 | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | Each Balancing Authority shall make available evidence that it has distributed its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | 2022-01-01 | [5 empty] | WECC-BC | [6 empty] | 40000000
TOP-003-4 (British Columbia) | 666700000010284 | R5. | 666700000011760 | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet one of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet two of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet three of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 did not satisfy the obligations of the documented specifications for data. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2022-01-01 | [5 empty] | WECC-BC | [6 empty] | 50000000
TOP-003-4 (Manitoba) | 77660000000620 | R1. | 776600000009204 | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to:[See standard for additional information.] |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not include one of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include two of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. OR The Transmission Operator did not have a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 10000000
TOP-003-4 (Manitoba) | 77660000000620 | R2. | 776600000009209 | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [See standard for additional information.] |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not include one of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include two of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. OR The Balancing Authority did not have a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 20000000
TOP-003-4 (Manitoba) | 77660000000620 | R3. | 776600000009214 | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Each Transmission Operator shall make available evidence that it has distributed its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 30000000
TOP-003-4 (Manitoba) | 77660000000620 | R4. | 776600000009215 | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | Each Balancing Authority shall make available evidence that it has distributed its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 40000000
TOP-003-4 (Manitoba) | 77660000000620 | R5. | 776600000009216 | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet one of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet two of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet three of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 did not satisfy the obligations of the documented specifications for data. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2022-07-01 | [5 empty] | MRO-MB | [6 empty] | 50000000
TOP-003-4 (Nova Scotia) | 78830000000620 | R1. | 788300000009204 | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to:[See standard for additional information.] |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not include one of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include two of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. OR The Transmission Operator did not have a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2021-10-01 |  | 2023-06-30 |  |  |  | NPCC-NS | [6 empty] | 10000000
TOP-003-4 (Nova Scotia) | 78830000000620 | R2. | 788300000009209 | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [See standard for additional information.] |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not include one of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include two of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. OR The Balancing Authority did not have a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2021-10-01 |  | 2023-06-30 |  |  |  | NPCC-NS | [6 empty] | 20000000
TOP-003-4 (Nova Scotia) | 78830000000620 | R3. | 788300000009214 | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Each Transmission Operator shall make available evidence that it has distributed its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | 2021-10-01 |  | 2023-06-30 |  |  |  | NPCC-NS | [6 empty] | 30000000
TOP-003-4 (Nova Scotia) | 78830000000620 | R4. | 788300000009215 | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | Each Balancing Authority shall make available evidence that it has distributed its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | 2021-10-01 |  | 2023-06-30 |  |  |  | NPCC-NS | [6 empty] | 40000000
TOP-003-4 (Nova Scotia) | 78830000000620 | R5. | 788300000009216 | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet one of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet two of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet three of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 did not satisfy the obligations of the documented specifications for data. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2021-10-01 |  | 2023-06-30 |  |  |  | NPCC-NS | [6 empty] | 50000000
TOP-003-4 (Ontario) | 79780000620 | R1. | 79780009204 | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to:[See standard for additional information.] |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not include one of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include two of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. OR The Transmission Operator did not have a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | &lt;p&gt;Each Transmission Operator shall make available its dated, current, in force&lt;br/&gt;documented specification for data.&lt;/p&gt; | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 10000000
TOP-003-4 (Ontario) | 79780000620 | R2. | 79780009209 | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [See standard for additional information.] |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not include one of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include two of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. OR The Balancing Authority did not have a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | &lt;p&gt;&lt;br/&gt;Each Balancing Authority shall make available its dated, current, in force documented&lt;br/&gt;specification for data.&lt;/p&gt; | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 20000000
TOP-003-4 (Ontario) | 79780000620 | R3. | 79780009214 | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | &lt;p&gt;Each Transmission Operator shall make available evidence that it has distributed its&lt;br/&gt;data specification to entities that have data required by the Transmission Operator’s Operational &lt;br/&gt;Planning Analyses, Real-time monitoring, and Real-time Assessments.&lt;br/&gt;Such evidence could include but is not limited to web postings with an electronic notice of the &lt;br/&gt;posting, dated operator logs, voice recordings, postal receipts showing&lt;br/&gt;the recipient, date and contents, or e-mail records.&lt;/p&gt; | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 30000000
TOP-003-4 (Ontario) | 79780000620 | R4. | 79780009215 | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | &lt;p&gt;Each Balancing Authority shall make available evidence that it has distributed its data&lt;br/&gt;specification to entities that have data required by the Balancing Authority’s analysis functions &lt;br/&gt;and Real-time monitoring. Such evidence could include but is not limited to web postings with an &lt;br/&gt;electronic notice of the posting, dated operator logs, voice&lt;br/&gt;recordings, postal receipts showing the recipient, or e-mail records.&lt;/p&gt; | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 40000000
TOP-003-4 (Ontario) | 79780000620 | R5. | 79780009216 | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet one of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet two of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet three of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 did not satisfy the obligations of the documented specifications for data. | &lt;p&gt;Each Transmission Operator, Balancing Authority, Generator Owner, Generator&lt;br/&gt;Operator, Transmission Owner, and Distribution Provider receiving a data specification in &lt;br/&gt;Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the &lt;br/&gt;documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving&lt;br/&gt;entities.&lt;/p&gt; | 2021-04-01 | [5 empty] | NPCC-ON | [6 empty] | 50000000
TOP-003-4 (Saskatchewan) | 83750000000620 | R1. | 837500000009204 | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to:[See standard for additional information.] |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not include one of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include two of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. OR The Transmission Operator did not have a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2021-04-01 |  | 2023-06-30 |  |  |  | MRO-SK | [6 empty] | 10000000
TOP-003-4 (Saskatchewan) | 83750000000620 | R2. | 837500000009209 | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [See standard for additional information.] |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not include one of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include two of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. OR The Balancing Authority did not have a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2021-04-01 |  | 2023-06-30 |  |  |  | MRO-SK | [6 empty] | 20000000
TOP-003-4 (Saskatchewan) | 83750000000620 | R3. | 837500000009214 | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Each Transmission Operator shall make available evidence that it has distributed its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | 2021-04-01 |  | 2023-06-30 |  |  |  | MRO-SK | [6 empty] | 30000000
TOP-003-4 (Saskatchewan) | 83750000000620 | R4. | 837500000009215 | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | Each Balancing Authority shall make available evidence that it has distributed its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | 2021-04-01 |  | 2023-06-30 |  |  |  | MRO-SK | [6 empty] | 40000000
TOP-003-4 (Saskatchewan) | 83750000000620 | R5. | 837500000009216 | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet one of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet two of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet three of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 did not satisfy the obligations of the documented specifications for data. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2021-04-01 |  | 2023-06-30 |  |  |  | MRO-SK | [6 empty] | 50000000
TOP-003-5 | ST-2021-06-24-0000003 | R1. | RQ-2021-06-24-0000012 | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to: |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not include two or fewer of the parts (Part 1.1 through Part 1.5) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.5) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.5) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | The Transmission Operator did not include any of the parts (Part 1.1 through Part 1.5) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. OR, The Transmission Operator did not have a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-003-5 | ST-2021-06-24-0000003 | R2. | RQ-2021-06-24-0000013 | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not include two or fewer of the parts (Part 2.1 through Part 2.5) of the documented specification for the data necessary for it to perform its analysis functions and Real- time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.5) of the documented specification for the data necessary for it to perform its analysis functions and Real- time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.5) of the documented specification for the data necessary for it to perform its analysis functions and Real- time monitoring. | The Balancing Authority did not include any of the parts (Part 2.1 through Part 2.5) of the documented specification for the data necessary for it to perform its analysis functions and Real- time monitoring. OR, The Balancing Authority did not have a documented specification for the data necessary for it to perform its analysis functions and Real- time monitoring. | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-003-5 | ST-2021-06-24-0000003 | R3. | RQ-2021-06-24-0000014 | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real- time monitoring, and Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Each Transmission Operator shall make available evidence that it has distributed its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | 2023-04-01 |  | 2025-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-003-5 | ST-2021-06-24-0000003 | R4. | RQ-2021-06-24-0000015 | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | Each Balancing Authority shall make available evidence that it has distributed its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | 2023-04-01 |  | 2025-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-003-5 | ST-2021-06-24-0000003 | R5. | RQ-2021-06-24-0000016 | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet one of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet two of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet three of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 did not satisfy the obligations of the documented specifications for data. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2023-04-01 |  | 2025-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-003-5 (Nova Scotia) | ST-2021-06-24-0000003-NS | R1. | RQ-2021-06-24-0000012-NS | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to: |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not include two or fewer of the parts (Part 1.1 through Part 1.5) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.5) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.5) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | The Transmission Operator did not include any of the parts (Part 1.1 through Part 1.5) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. OR, The Transmission Operator did not have a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-07-01 | [5 empty] | NPCC-NS | [6 empty] | 10000000
TOP-003-5 (Nova Scotia) | ST-2021-06-24-0000003-NS | R2. | RQ-2021-06-24-0000013-NS | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not include two or fewer of the parts (Part 2.1 through Part 2.5) of the documented specification for the data necessary for it to perform its analysis functions and Real- time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.5) of the documented specification for the data necessary for it to perform its analysis functions and Real- time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.5) of the documented specification for the data necessary for it to perform its analysis functions and Real- time monitoring. | The Balancing Authority did not include any of the parts (Part 2.1 through Part 2.5) of the documented specification for the data necessary for it to perform its analysis functions and Real- time monitoring. OR, The Balancing Authority did not have a documented specification for the data necessary for it to perform its analysis functions and Real- time monitoring. | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-07-01 | [5 empty] | NPCC-NS | [6 empty] | 20000000
TOP-003-5 (Nova Scotia) | ST-2021-06-24-0000003-NS | R3. | RQ-2021-06-24-0000014-NS | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real- time monitoring, and Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Each Transmission Operator shall make available evidence that it has distributed its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | 2023-07-01 | [5 empty] | NPCC-NS | [6 empty] | 30000000
TOP-003-5 (Nova Scotia) | ST-2021-06-24-0000003-NS | R4. | RQ-2021-06-24-0000015-NS | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | Each Balancing Authority shall make available evidence that it has distributed its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | 2023-07-01 | [5 empty] | NPCC-NS | [6 empty] | 40000000
TOP-003-5 (Nova Scotia) | ST-2021-06-24-0000003-NS | R5. | RQ-2021-06-24-0000016-NS | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet one of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet two of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet three of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 did not satisfy the obligations of the documented specifications for data. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2023-07-01 | [5 empty] | NPCC-NS | [6 empty] | 50000000
TOP-003-5 (Saskatchewan) | ST-2023-10-03-0000006 | R1. | RQ-2023-10-03-0000019 | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to: |  | TO | [17 empty] | TO |  |  |  | Operations Planning | Low | The Transmission Operator did not include two or fewer of the parts (Part 1.1 through Part 1.5) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Realtime Assessments. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.5) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Realtime Assessments. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.5) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Realtime Assessments. | The Transmission Operator did not include any of the parts (Part 1.1 through Part 1.5) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Realtime Assessments. OR, The Transmission Operator did not have a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Realtime Assessments. | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-07-01 | [5 empty] | MRO-SK | [6 empty] | 10000000
TOP-003-5 (Saskatchewan) | ST-2023-10-03-0000006 | R2. | RQ-2023-10-03-0000020 | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: | For the Requirement R3 and R4 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size of entity. If a small entity has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not include two or fewer of the parts (Part 2.1 through Part 2.5) of the documented specification for the data necessary for it to perform its analysis functions and Realtime monitoring | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.5) of the documented specification for the data necessary for it to perform its analysis functions and Realtime monitoring | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.5) of the documented specification for the data necessary for it to perform its analysis functions and Realtime monitoring | The Balancing Authority did not include any of the parts (Part 2.1 through Part 2.5) of the documented specification for the data necessary for it to perform its analysis functions and Realtime monitoring. OR, The Balancing Authority did not have a documented specification for the data necessary for it to perform its analysis functions and Realtime monitoring. | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-07-01 | [5 empty] | MRO-SK | [6 empty] | 20000000
TOP-003-5 (Saskatchewan) | ST-2023-10-03-0000006 | R3. | RQ-2023-10-03-0000021 | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Realtime monitoring, and Real-time Assessments. |  | TO | [17 empty] | TO |  |  |  | Operations Planning | Low | The Transmission Operator did not distribute its data specification to one entity, or 5% or less of the entities whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | The Transmission Operator did not distribute its data specification to two entities, or more than 5% and less than or equal to10% of the reliability entities,whichever is greater,that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the reliability entities,whichever is greater,that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | The Transmission Operator did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Each Transmission Operator shall make available evidence that it has distributed its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | 2023-07-01 | [5 empty] | MRO-SK | [6 empty] | 30000000
TOP-003-5 (Saskatchewan) | ST-2023-10-03-0000006 | R4. | RQ-2023-10-03-0000022 | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. The Balancing Authority did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | Each Balancing Authority shall make available evidence that it has distributed its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | 2023-07-01 | [5 empty] | MRO-SK | [6 empty] | 40000000
TOP-003-5 (Saskatchewan) | ST-2023-10-03-0000006 | R5. | RQ-2023-10-03-0000023 | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet one of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet two of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet three of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 did not satisfy the obligations of the documented specifications for data. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2023-07-01 | [5 empty] | MRO-SK | [6 empty] | 50000000
TOP-003-6 | ST-2023-08-22-0000005 | R1. | RQ-2023-08-22-0000004 | Each Transmission Operator shall maintain documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real‐ time monitoring, and Real‐time Assessments. The specification shall include, but not be limited to: |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not include one or two of the parts (Part 1.1 through Part 1.5) of the documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real‐time monitoring, and Real‐ time Assessments. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.5) of the documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real‐ time monitoring, and Real‐ time Assessments. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.5) of the documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real‐time monitoring, and Real‐ time Assessments. | The Transmission Operator did not include any of the parts (Part 1.1 through Part 1.5) of the documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real‐time monitoring, and Real‐ time Assessments. OR, The Transmission Operator did not have a documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real‐ time monitoring, and Real‐ time Assessments. | Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. |  |  | 2023-08-23 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-003-6 | ST-2023-08-22-0000005 | R2. | RQ-2023-08-22-0000005 | Each Balancing Authority shall maintain documented specification(s) for the data and information necessary for it to perform its analysis functions and Real‐time monitoring. The data specification shall include, but not be limited to: |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not include two or fewer of the parts (Part 2.1 through Part 2.5) of the documented specification(s) for the data and information necessary for it to perform its analysis functions and Real‐ time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.5) of the documented specification(s) for the data and information necessary for it to perform its analysis functions and Real‐ time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.5) of the documented specification(s) for the data and information necessary for it to perform its analysis functions and Real‐ time monitoring. | The Balancing Authority did not include any of the parts (Part 2.1 through Part 2.5) of the documented specification(s) for the data and information necessary for it to perform its analysis functions and Real‐ time monitoring. OR, The Balancing Authority did not have a documented specification(s) for the data and information necessary for it to perform its analysis functions and Real‐ time monitoring. | Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. |  |  | 2023-08-23 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-003-6 | ST-2023-08-22-0000005 | R3. | RQ-2023-08-22-0000006 | Each Transmission Operator shall distribute its data and information specification(s) to entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real‐ time monitoring, and Real‐time Assessments. | For the Requirement R3 and R4 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size of entity. If a small entity has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not distribute its Specification(s) to one entity, or 5% or less of the entities, whichever is greater, that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real‐ time monitoring, and Real‐time Assessments. | The Transmission Operator did not distribute its Specification(s) to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is greater, that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real‐ time monitoring, and Real‐time Assessments. | The Transmission Operator did not distribute its Specification(s) to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real‐ time monitoring, and Real‐time Assessments. | The Transmission Operator did not distribute its Specification(s) to four or more entities, or more than 15% of the entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real‐ time monitoring, and Real‐time Assessments. | Each Transmission Operator shall make available evidence that it has distributed its data specification(s) to entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real‐time monitoring, and Real‐time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e‐mail records. |  |  | 2023-08-23 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-003-6 | ST-2023-08-22-0000005 | R4. | RQ-2023-08-22-0000007 | Each Balancing Authority shall distribute its data and information specification(s) to entities that have data and information required by the Balancing Authority’s analysis functions and Real‐time monitoring. | For the Requirement R3 and R4 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size of entity. If a small entity has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  | Operations Planning | Low | The Balancing Authority did not distribute its Specification(s) to one entity, or 5% or less of the entities, whichever is greater, that have data and information required by the Balancing Authority’s analysis functions and Real‐time monitoring. | The Balancing Authority did not distribute its Specification(s) to two entities, or more than 5% and less than or equal to 10% of the entities,whichever is greater, that have data and information required by the Balancing Authority’s analysis functions and Real‐time monitoring. | The Balancing Authority did not distribute its Specification(s) to three entities, or more than10% and less than or equal to 15% of the entities,whichever is greater, that have data and information required by the Balancing Authority’s analysis functions and Real‐time monitoring. | The Balancing Authority did not distribute its Specification(s) to four or more entities, or more than 15% of the entities that have data and information required by the Balancing Authority’s analysis functions and Real‐time monitoring. | Each Balancing Authority shall make available evidence that it has distributed its data specification(s) to entities that have data and information required by the Balancing Authority’s analysis functions and Real‐time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e‐mail records. |  |  | 2023-08-23 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-003-6 | ST-2023-08-22-0000005 | R5. | RQ-2023-08-23-0000001 | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data and information specification(s) in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using. |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity receiving a specification(s) in Requirement R3 or R4 satisfied the obligations in the specification but failed to meet one of the parts in Requirement R1 Part1.5 or Requirement R2 Part 2.5. | The responsible entity receiving a specification(s) in Requirement R3 or R4 satisfied the obligations in the specification but failed to meet two of the parts in Requirement R1 Part 1.5 or Requirement R2 Part 2.5. | The responsible entity receiving a specification(s) in Requirement R3 or R4 satisfied the obligations in the specification but failed to meet three or more of the parts in Requirement R1 Part 1.5 or Requirement R2 Part 2.5. | The responsible entity receiving a specification(s) in Requirement R3 or R4 did not satisfy the obligations of the documented specifications. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a specification(s) in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specification. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. |  |  | 2023-08-23 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-003-6.1 | ST-2023-09-13-0000001 | R1. | RQ-2023-09-13-0000001 | Each Transmission Operator shall maintain documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The specification shall include, but not be limited to: |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not include one or two of the parts (Part 1.1 through Part 1.5) of the documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.5) of the documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.5) of the documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | The Transmission Operator did not include any of the parts (Part 1.1 through Part 1.5) of the documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. OR, The Transmission Operator did not have a documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | Each Transmission Operator shall make available its dated, current, in force documented specification(s) for data and information. | 2025-07-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-003-6.1 | ST-2023-09-13-0000001 | R2. | RQ-2023-09-13-0000002 | Each Balancing Authority shall maintain documented specification(s) for the data and information necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: |  | BA | BA | [20 empty] | Operations Planning | Low | The Balancing Authority did not include two or fewer of the parts (Part 2.1 through Part 2.5) of the documented specification(s) for the data and information necessary for it to perform its analysis functions and Real- time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.5) of the documented specification(s) for the data and information necessary for it to perform its analysis functions and Real- time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.5) of the documented specification(s) for the data and information necessary for it to perform its analysis functions and Real- time monitoring | The Balancing Authority did not include any of the parts (Part 2.1 through Part 2.5) of the documented specification(s) for the data and information necessary for it to perform its analysis functions and Real- time monitoring. OR, The Balancing Authority did not have a documented specification(s) for the data and information necessary for it to perform its analysis functions and Real- time monitoring. | Each Balancing Authority shall make available its dated, current, in force documented specification(s) for data and information. | 2025-07-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-003-6.1 | ST-2023-09-13-0000001 | R3. | RQ-2023-09-13-0000003 | Each Transmission Operator shall distribute its data and information specification(s) to entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real- time monitoring, and Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator did not distribute its Specification(s) to one entity, or 5% or less of the entities, whichever is greater, that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its Specification(s) to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is greater, that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its Specification(s) to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its Specification(s) to four or more entities, or more than 15% of the entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments | Each Transmission Operator shall make available evidence that it has distributed its data specification(s) to entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, date and contents, or e-mail records. | 2025-07-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-003-6.1 | ST-2023-09-13-0000001 | R4. | RQ-2023-09-13-0000004 | Each Balancing Authority shall distribute its data and information specification(s) to entities that have data and information required by the Balancing Authority’s analysis functions and Real-time monitoring. |  | BA | BA | [20 empty] | Long-Term Planning | Low | The Balancing Authority did not distribute its Specification(s) to one entity, or 5% or less of the entities, whichever is greater, that have data and information required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its Specification(s) to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is greater, that have data and information required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its Specification(s) to three entities, or more than10% and less than or equal to 15% of the entities, whichever is greater, that have data and information required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its Specification(s) to four or more entities, or more than 15% of the entities that have data and information required by the Balancing Authority’s analysis functions and Real-time monitoring. | Each Balancing Authority shall make available evidence that it has distributed its data specification(s) to entities that have data and information required by the Balancing Authority’s analysis functions and Real-time monitoring. Such evidence could include but is not limited to web postings with an electronic notice of the posting, dated operator logs, voice recordings, postal receipts showing the recipient, or e-mail records. | 2025-07-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-003-6.1 | ST-2023-09-13-0000001 | R5. | RQ-2023-09-13-0000005 | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data and information specification(s) in Requirement R3 or R4 shall satisfy the obligations of the documented specifications. |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | Medium | The responsible entity receiving a specification(s) in Requirement R3 or R4 satisfied the obligations in the specification but failed to meet one of the parts in Requirement R1 Part1.5 or Requirement R2 Part 2.5. | The responsible entity receiving a specification(s) in Requirement R3 or R4 satisfied the obligations in the specification but failed to meet two of the parts in Requirement R1 Part 1.5 or Requirement R2 Part 2.5. | The responsible entity receiving a specification(s) in Requirement R3 or R4 satisfied the obligations in the specification but failed to meet three or more of the parts in Requirement R1 Part 1.5 or Requirement R2 Part 2.5. | The responsible entity receiving a specification(s) in Requirement R3 or R4 did not satisfy the obligations of the documented specifications. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a specification(s) in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specification. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2025-07-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-004-0 | 420 | R1. | 5200 | Each Transmission Operator shall operate within the Interconnection Reliability Operating Limits (IROLs) and System Operating Limits (SOLs). |  | TOP | [18 empty] | TOP | [11 empty] | 2005-04-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-004-0 | 420 | R2. | 5201 | Each Transmission Operator shall operate so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single contingency. |  | TOP | [18 empty] | TOP | [11 empty] | 2005-04-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-004-0 | 420 | R3. | 5202 | Each Transmission Operator shall, when practical, operate to protect against instability, uncontrolled separation, or cascading outages resulting from multiple outages, as specified by Regional Reliability Organization policy. |  | TOP | [18 empty] | TOP | [11 empty] | 2005-04-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-004-0 | 420 | R4. | 5203 | If a Transmission Operator enters an unknown operating state (i.e. any state for which valid operating limits have not been determined), it will be considered to be in an emergency and shall restore operations to respect proven reliable power system limits within 30 minutes. |  | TOP | [18 empty] | TOP | [11 empty] | 2005-04-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-004-0 | 420 | R5. | 5204 | Each Transmission Operator shall make every effort to remain connected to the Interconnection. If the Transmission Operator determines that by remaining interconnected, it is in imminent danger of violating an IROL or SOL, the Transmission Operator may take such actions, as it deems necessary, to protect its area. |  | TOP | [18 empty] | TOP | [11 empty] | 2005-04-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-004-0 | 420 | R6. | 5205 | Transmission Operators, individually and jointly with other Transmission Operators, shall develop, maintain, and implement formal policies and procedures to provide for transmission reliability. These policies and procedures shall address the execution and coordination of activities that impact inter- and intra-Regional reliability, including: |  | TOP | [18 empty] | TOP | [11 empty] | 2005-04-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TOP-004-0 (Ontario) | 79780000420 | R1. | 79780005200 |  |  | TOP | [18 empty] | TOP | [11 empty] | 2005-04-01 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-004-0 (Ontario) | 79780000420 | R2. | 79780005201 |  |  | TOP | [18 empty] | TOP | [11 empty] | 2005-04-01 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-004-0 (Ontario) | 79780000420 | R3. | 79780005202 |  |  | TOP | [18 empty] | TOP | [11 empty] | 2005-04-01 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-004-0 (Ontario) | 79780000420 | R4. | 79780005203 |  |  | TOP | [18 empty] | TOP | [11 empty] | 2005-04-01 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-004-0 (Ontario) | 79780000420 | R5. | 79780005204 |  |  | TOP | [18 empty] | TOP | [11 empty] | 2005-04-01 |  |  |  | NPCC-ON | [6 empty] | 50000000
TOP-004-0 (Ontario) | 79780000420 | R6. | 79780005205 |  |  | TOP | [18 empty] | TOP | [11 empty] | 2005-04-01 |  |  |  | NPCC-ON | [6 empty] | 60000000
TOP-004-1 | 173 | R1. | 1963 | Each Transmission Operator shall operate within the Interconnection Reliability Operating Limits (IROLs) and System Operating Limits (SOLs). |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2007-06-18 |  | 2009-01-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-004-1 | 173 | R2. | 1964 | Each Transmission Operator shall operate so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single contingency. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2007-06-18 |  | 2009-01-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-004-1 | 173 | R3. | 1965 | Each Transmission Operator shall, when practical, operate to protect against instability, uncontrolled separation, or cascading outages resulting from multiple outages, as specified by Regional Reliability Organization policy. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2007-06-18 |  | 2009-01-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-004-1 | 173 | R4. | 1966 | If a Transmission Operator enters an unknown operating state (i.e., any state for which valid operating limits have not been determined), it will be considered to be in an emergency and shall restore operations to respect proven reliable power system limits within 30 minutes. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2007-06-18 |  | 2009-01-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-004-1 | 173 | R5. | 1967 | Each Transmission Operator shall make every effort to remain connected to the Interconnection. If the Transmission Operator determines that by remaining interconnected, it is in imminent danger of violating an IROL or SOL, the Transmission Operator may take such actions, as it deems necessary, to protect its area. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2007-06-18 |  | 2009-01-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-004-1 | 173 | R6. | 1968 | Transmission Operators, individually and jointly with other Transmission Operators, shall develop, maintain, and implement formal policies and procedures to provide for transmission reliability. These policies and procedures shall address the execution and coordination of activities that impact inter- and intra-Regional reliability, including: |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2009-01-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TOP-004-1 (British Columbia) | 666700000010285 | R1. | 666700000011761 | Each Transmission Operator shall operate within the Interconnection Reliability Operating Limits (IROLs) and System Operating Limits (SOLs). |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 10000000
TOP-004-1 (British Columbia) | 666700000010285 | R2. | 666700000011762 | Each Transmission Operator shall operate so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single contingency. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 20000000
TOP-004-1 (British Columbia) | 666700000010285 | R3. | 666700000011763 | Each Transmission Operator shall, when practical, operate to protect against instability, uncontrolled separation, or cascading outages resulting from multiple outages, as specified by Regional Reliability Organization policy. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 30000000
TOP-004-1 (British Columbia) | 666700000010285 | R4. | 666700000011764 | If a Transmission Operator enters an unknown operating state (i.e., any state for which valid operating limits have not been determined), it will be considered to be in an emergency and shall restore operations to respect proven reliable power system limits within 30 minutes. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 40000000
TOP-004-1 (British Columbia) | 666700000010285 | R5. | 666700000011765 | Each Transmission Operator shall make every effort to remain connected to the Interconnection. If the Transmission Operator determines that by remaining interconnected, it is in imminent danger of violating an IROL or SOL, the Transmission Operator may take such actions, as it deems necessary, to protect its area. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 50000000
TOP-004-1 (British Columbia) | 666700000010285 | R6. | 666700000011766 | Transmission Operators, individually and jointly with other Transmission Operators, shall develop, maintain, and implement formal policies and procedures to provide for transmission reliability. These policies and procedures shall address the execution and coordination of activities that impact inter- and intra-Regional reliability, including: |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 60000000
TOP-004-1 (Ontario) | 79780000173 | R1. | 79780001963 | Each Transmission Operator shall operate within the Interconnection Reliability Operating Limits (IROLs) and System Operating Limits (SOLs). |  | TOP | [18 empty] | TOP |  |  |  | High |  |  | The Transmission Operator operated within the Interconnection Reliability Operating Limits (IROLs), but failed to operate within the System Operating Limits (SOLs). | The Transmission Operator failed to operate within the Interconnection Reliability Operating Limits (IROLs) and System Operating Limits (SOLs). |  | 2007-06-18 |  | 2009-01-21 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-004-1 (Ontario) | 79780000173 | R2. | 79780001964 | Each Transmission Operator shall operate so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single contingency. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  | The Transmission Operator failed to operate so that instability, uncontrolled separation, or cascading outages would not occur as a result of the most severe single contingency. |  | 2007-06-18 |  | 2009-01-21 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-004-1 (Ontario) | 79780000173 | R3. | 79780001965 | Each Transmission Operator shall, when practical, operate to protect against instability, uncontrolled separation, or cascading outages resulting from multiple outages, as specified by Regional Reliability Organization policy. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  | The Transmission Operator failed to operate (when practical) to protect against instability, uncontrolled separation, or cascading outages resulting from multiple outages, as specified by Regional Reliability Organization policy. |  | 2007-06-18 |  | 2009-01-21 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-004-1 (Ontario) | 79780000173 | R4. | 79780001966 | If a Transmission Operator enters an unknown operating state (i.e., any state for which valid operating limits have not been determined), it will be considered to be in an emergency and shall restore operations to respect proven reliable power system limits within 30 minutes. |  | TOP | [18 empty] | TOP |  |  |  | High | The Transmission Operator entering an unknown operating state (i.e., any state for which valid operating limits have not been determined), failed to restore operations to respect proven reliable power system limits for more than 30 minutes but less than o | The Transmission Operator entering an unknown operating state (i.e., any state for which valid operating limits have not been determined), failed to restore operations to respect proven reliable power system limits for more than 35 minutes but less than o | The Transmission Operator entering an unknown operating state (i.e., any state for which valid operating limits have not been determined), failed to restore operations to respect proven reliable power system limits for more than 40 minutes but less than o | The Transmission Operator entering an unknown operating state (i.e., any state for which valid operating limits have not been determined), failed to restore operations to respect proven reliable power system limits for more than 45 minutes. |  | 2007-06-18 |  | 2009-01-21 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-004-1 (Ontario) | 79780000173 | R5. | 79780001967 | Each Transmission Operator shall make every effort to remain connected to the Interconnection. If the Transmission Operator determines that by remaining interconnected, it is in imminent danger of violating an IROL or SOL, the Transmission Operator may take such actions, as it deems necessary, to protect its area. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  | The Transmission Operator does not have evidence that the actions taken to protect its area, resulting in its disconnection from the Interconnection, were necessary to prevent the danger of violating an IROL or SOL. |  | 2007-06-18 |  | 2009-01-21 |  |  |  | NPCC-ON | [6 empty] | 50000000
TOP-004-1 (Ontario) | 79780000173 | R6. | 79780001968 | Transmission Operators, individually and jointly with other Transmission Operators, shall develop, maintain, and implement formal policies and procedures to provide for transmission reliability. These policies and procedures shall address the execution and coordination of activities that impact inter- and intra-Regional reliability, including: |  | TOP | [18 empty] | TOP |  |  |  | Medium | The Transmission Operator developed, maintained, and implemented formal policies and procedures to provide for transmission reliability, addressing the execution and coordination of activities that impact inter- and intra-Regional reliability, including t | The Transmission Operator, individually and jointly with other Transmission Operators, developed, maintained, and implemented formal policies and procedures to provide for transmission reliability, addressing the execution and coordination of activities t | The Transmission Operator, individually and jointly with other Transmission Operators, developed, maintained, and implemented formal policies and procedures to provide for transmission reliability, addressing the execution and coordination of activities t | The Transmission Operator, individually and jointly with other Transmission Operators, developed, maintained, and implemented formal policies and procedures to provide for transmission reliability, addressing the execution and coordination of activities t |  | 2007-06-18 |  | 2009-01-21 |  |  |  | NPCC-ON | [6 empty] | 60000000
TOP-004-2 | 174 | R1. | 1975 | Each Transmission Operator shall operate within the Interconnection Reliability Operating Limits (IROLs) and System Operating Limits (SOLs). |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  |  | M1. Each Transmission Operator that enters an unknown operating state for which valid limits have not been determined, shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, alarm program printouts, or other equivalent evidence that will be used to determine if it restored operations to respect proven reliable power system limits within 30 minutes as specified in Requirement 4. | 2009-01-22 |  | 2017-03-31 |  |  | TOP-004-1 R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-004-2 | 174 | R2. | 1976 | Each Transmission Operator shall operate so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single contingency. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  |  | M2. Each Transmission Operator shall have and provide upon request current policies and procedures that address the execution and coordination of activities that impact inter- and intra-Regional reliability for each of the topics listed in Requirements 6.1 through 6.6. | 2009-01-22 |  | 2017-03-31 |  |  | TOP-004-1 R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-004-2 | 174 | R3. | 1977 | Each Transmission Operator shall operate to protect against instability, uncontrolled separation, or cascading outages resulting from multiple outages, as specified by its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2009-01-22 |  | 2017-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-004-2 | 174 | R4. | 1978 | If a Transmission Operator enters an unknown operating state (i.e. any state for which valid operating limits have not been determined), it will be considered to be in an emergency and shall restore operations to respect proven reliable power system limits within 30 minutes. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  | The Transmission Operator entering an unknown operating state (i.e., any state for which valid operating limits have not been determined), failed to restore operations to respect proven reliable power system limits for more than 45 minutes. |  | 2009-01-22 |  | 2017-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-004-2 | 174 | R5. | 1979 | Each Transmission Operator shall make every effort to remain connected to the Interconnection. If the Transmission Operator determines that by remaining interconnected, it is in imminent danger of violating an IROL or SOL, the Transmission Operator may take such actions, as it deems necessary, to protect its area. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2009-01-22 |  | 2017-03-31 |  |  | TOP-004-1 R5. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-004-2 | 174 | R6. | 1980 | Transmission Operators, individually and jointly with other Transmission Operators, shall develop, maintain, and implement formal policies and procedures to provide for transmission reliability. These policies and procedures shall address the execution and coordination of activities that impact inter- and intra-Regional reliability, including: |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2009-01-22 |  | 2017-03-31 |  |  | TOP-004-1 R6. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TOP-004-2 (British Columbia) | 666700000010286 | R1. | 666700000011767 | Each Transmission Operator shall operate within the Interconnection Reliability Operating Limits (IROLs) and System Operating Limits (SOLs). |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  |  | M1. Each Transmission Operator that enters an unknown operating state for which valid limits have not been determined, shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, alarm program printouts, or other equivalent evidence that will be used to determine if it restored operations to respect proven reliable power system limits within 30 minutes as specified in Requirement 4. | 2011-01-01 | [5 empty] | WECC-BC | [6 empty] | 10000000
TOP-004-2 (British Columbia) | 666700000010286 | R2. | 666700000011768 | Each Transmission Operator shall operate so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single contingency. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  |  | M2. Each Transmission Operator shall have and provide upon request current policies and procedures that address the execution and coordination of activities that impact inter- and intra-Regional reliability for each of the topics listed in Requirements 6.1 through 6.6. | 2011-01-01 | [5 empty] | WECC-BC | [6 empty] | 20000000
TOP-004-2 (British Columbia) | 666700000010286 | R3. | 666700000011769 | Each Transmission Operator shall operate to protect against instability, uncontrolled separation, or cascading outages resulting from multiple outages, as specified by its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2011-01-01 | [5 empty] | WECC-BC | [6 empty] | 30000000
TOP-004-2 (British Columbia) | 666700000010286 | R4. | 666700000011770 | If a Transmission Operator enters an unknown operating state (i.e. any state for which valid operating limits have not been determined), it will be considered to be in an emergency and shall restore operations to respect proven reliable power system limits within 30 minutes. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  | The Transmission Operator entering an unknown operating state (i.e., any state for which valid operating limits have not been determined), failed to restore operations to respect proven reliable power system limits for more than 45 minutes. |  | 2011-01-01 | [5 empty] | WECC-BC | [6 empty] | 40000000
TOP-004-2 (British Columbia) | 666700000010286 | R5. | 666700000011771 | Each Transmission Operator shall make every effort to remain connected to the Interconnection. If the Transmission Operator determines that by remaining interconnected, it is in imminent danger of violating an IROL or SOL, the Transmission Operator may take such actions, as it deems necessary, to protect its area. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2011-01-01 | [5 empty] | WECC-BC | [6 empty] | 50000000
TOP-004-2 (British Columbia) | 666700000010286 | R6. | 666700000011772 | Transmission Operators, individually and jointly with other Transmission Operators, shall develop, maintain, and implement formal policies and procedures to provide for transmission reliability. These policies and procedures shall address the execution and coordination of activities that impact inter- and intra-Regional reliability, including: |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-01-01 | [5 empty] | WECC-BC | [6 empty] | 60000000
TOP-004-2 (Manitoba) | 77660000000174 | R1. | 776600000001975 | Each Transmission Operator shall operate within the Interconnection Reliability Operating Limits (IROLs) and System Operating Limits (SOLs). |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  |  | M1. Each Transmission Operator that enters an unknown operating state for which valid limits have not been determined, shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, alarm program printouts, or other equivalent evidence that will be used to determine if it restored operations to respect proven reliable power system limits within 30 minutes as specified in Requirement 4. | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
TOP-004-2 (Manitoba) | 77660000000174 | R2. | 776600000001976 | Each Transmission Operator shall operate so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single contingency. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  |  | M2. Each Transmission Operator shall have and provide upon request current policies and procedures that address the execution and coordination of activities that impact inter- and intra-Regional reliability for each of the topics listed in Requirements 6.1 through 6.6. | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
TOP-004-2 (Manitoba) | 77660000000174 | R3. | 776600000001977 | Each Transmission Operator shall operate to protect against instability, uncontrolled separation, or cascading outages resulting from multiple outages, as specified by its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
TOP-004-2 (Manitoba) | 77660000000174 | R4. | 776600000001978 | If a Transmission Operator enters an unknown operating state (i.e. any state for which valid operating limits have not been determined), it will be considered to be in an emergency and shall restore operations to respect proven reliable power system limits within 30 minutes. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  | The Transmission Operator entering an unknown operating state (i.e., any state for which valid operating limits have not been determined), failed to restore operations to respect proven reliable power system limits for more than 45 minutes. |  | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 40000000
TOP-004-2 (Manitoba) | 77660000000174 | R5. | 776600000001979 | Each Transmission Operator shall make every effort to remain connected to the Interconnection. If the Transmission Operator determines that by remaining interconnected, it is in imminent danger of violating an IROL or SOL, the Transmission Operator may take such actions, as it deems necessary, to protect its area. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 50000000
TOP-004-2 (Manitoba) | 77660000000174 | R6. | 776600000001980 | Transmission Operators, individually and jointly with other Transmission Operators, shall develop, maintain, and implement formal policies and procedures to provide for transmission reliability. These policies and procedures shall address the execution and coordination of activities that impact inter- and intra-Regional reliability, including: |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 60000000
TOP-004-2 (Ontario) | 79780000174 | R1. | 79780001975 | Each Transmission Operator shall operate within the Interconnection Reliability Operating Limits (IROLs) and System Operating Limits (SOLs). |  | TOP | [18 empty] | TOP |  |  |  | High |  |  | The Transmission Operator operated within the Interconnection Reliability Operating Limits (IROLs), but failed to operate within the System Operating Limits (SOLs). | The Transmission Operator failed to operate within the Interconnection Reliability Operating Limits (IROLs) and System Operating Limits (SOLs). | M1. Each Transmission Operator that enters an unknown operating state for which valid limits&lt;br/&gt;have not been determined, shall have and provide upon request evidence that could include,&lt;br/&gt;but is not limited to, operator logs, voice recordings or transcripts of voice recordings,&lt;br/&gt;electronic communications, alarm program printouts, or other equivalent evidence that will&lt;br/&gt;be used to determine if it restored operations to respect proven reliable power system limits&lt;br/&gt;within 30 minutes as specified in Requirement 4. | 2009-01-22 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-004-2 (Ontario) | 79780000174 | R2. | 79780001976 | Each Transmission Operator shall operate so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single contingency. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  | The Transmission Operator failed to operate so that instability, uncontrolled separation, or cascading outages would not occur as a result of the most severe single contingency. | M2. Each Transmission Operator shall have and provide upon request current policies and&lt;br/&gt;procedures that address the execution and coordination of activities that impact inter- and&lt;br/&gt;intra-Regional reliability for each of the topics listed in Requirements 6.1 through 6.6. | 2009-01-22 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-004-2 (Ontario) | 79780000174 | R3. | 79780001977 | Each Transmission Operator shall operate to protect against instability, uncontrolled separation, or cascading outages resulting from multiple outages, as specified by its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  | The Transmission Operator failed to operate to protect against instability, uncontrolled separation, or cascading outages resulting from multiple outages, as specified by its Reliability Coordinator policy. |  | 2009-01-22 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-004-2 (Ontario) | 79780000174 | R4. | 79780001978 | If a Transmission Operator enters an unknown operating state (i.e. any state for which valid operating limits have not been determined), it will be considered to be in an emergency and shall restore operations to respect proven reliable power system limits within 30 minutes. |  | TOP | [18 empty] | TOP |  |  |  | High | The Transmission Operator entering an unknown operating state (i.e., any state for which valid operating limits have not been determined), failed to restore operations to respect proven reliable power system limits for more than 30 minutes but less than o | The Transmission Operator entering an unknown operating state (i.e., any state for which valid operating limits have not been determined), failed to restore operations to respect proven reliable power system limits for more than 35 minutes but less than o | The Transmission Operator entering an unknown operating state (i.e., any state for which valid operating limits have not been determined), failed to restore operations to respect proven reliable power system limits for more than 40 minutes but less than o | The Transmission Operator entering an unknown operating state (i.e., any state for which valid operating limits have not been determined), failed to restore operations to respect proven reliable power system limits for more than 45 minutes. |  | 2009-01-22 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-004-2 (Ontario) | 79780000174 | R5. | 79780001979 | Each Transmission Operator shall make every effort to remain connected to the Interconnection. If the Transmission Operator determines that by remaining interconnected, it is in imminent danger of violating an IROL or SOL, the Transmission Operator may take such actions, as it deems necessary, to protect its area. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  | The Transmission Operator does not have evidence that the actions taken to protect its area, resulting in its disconnection from the Interconnection, were necessary to prevent the danger of violating an IROL or SOL. |  | 2009-01-22 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 50000000
TOP-004-2 (Ontario) | 79780000174 | R6. | 79780001980 | Transmission Operators, individually and jointly with other Transmission Operators, shall develop, maintain, and implement formal policies and procedures to provide for transmission reliability. These policies and procedures shall address the execution and coordination of activities that impact inter- and intra-Regional reliability, including: |  | TOP | [18 empty] | TOP |  |  |  | Medium | The Transmission Operator developed, maintained, and implemented formal policies and procedures to provide for transmission reliability, addressing the execution and coordination of activities that impact inter- and intra-Regional reliability, including t | The Transmission Operator, individually and jointly with other Transmission Operators, developed, maintained, and implemented formal policies and procedures to provide for transmission reliability, addressing the execution and coordination of activities t | The Transmission Operator, individually and jointly with other Transmission Operators, developed, maintained, and implemented formal policies and procedures to provide for transmission reliability, addressing the execution and coordination of activities t | The Transmission Operator, individually and jointly with other Transmission Operators, developed, maintained, and implemented formal policies and procedures to provide for transmission reliability, addressing the execution and coordination of activities t |  | 2009-01-22 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 60000000
TOP-004-2 (Saskatchewan) | 83750000000174 | R1. | 837500000001975 | Each Transmission Operator shall operate within the Interconnection Reliability Operating Limits (IROLs) and System Operating Limits (SOLs). |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  |  | M1. Each Transmission Operator that enters an unknown operating state for which valid limits have not been determined, shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, alarm program printouts, or other equivalent evidence that will be used to determine if it restored operations to respect proven reliable power system limits within 30 minutes as specified in Requirement 4. | 2015-04-15 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 10000000
TOP-004-2 (Saskatchewan) | 83750000000174 | R2. | 837500000001976 | Each Transmission Operator shall operate so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single contingency. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  |  | M2. Each Transmission Operator shall have and provide upon request current policies and procedures that address the execution and coordination of activities that impact inter- and intra-Regional reliability for each of the topics listed in Requirements 6.1 through 6.6. | 2015-04-15 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 20000000
TOP-004-2 (Saskatchewan) | 83750000000174 | R3. | 837500000001977 | Each Transmission Operator shall operate to protect against instability, uncontrolled separation, or cascading outages resulting from multiple outages, as specified by its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2015-04-15 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 30000000
TOP-004-2 (Saskatchewan) | 83750000000174 | R4. | 837500000001978 | If a Transmission Operator enters an unknown operating state (i.e. any state for which valid operating limits have not been determined), it will be considered to be in an emergency and shall restore operations to respect proven reliable power system limits within 30 minutes. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  | The Transmission Operator entering an unknown operating state (i.e., any state for which valid operating limits have not been determined), failed to restore operations to respect proven reliable power system limits for more than 45 minutes. |  | 2015-04-15 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 40000000
TOP-004-2 (Saskatchewan) | 83750000000174 | R5. | 837500000001979 | Each Transmission Operator shall make every effort to remain connected to the Interconnection. If the Transmission Operator determines that by remaining interconnected, it is in imminent danger of violating an IROL or SOL, the Transmission Operator may take such actions, as it deems necessary, to protect its area. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2015-04-15 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 50000000
TOP-004-2 (Saskatchewan) | 83750000000174 | R6. | 837500000001980 | Transmission Operators, individually and jointly with other Transmission Operators, shall develop, maintain, and implement formal policies and procedures to provide for transmission reliability. These policies and procedures shall address the execution and coordination of activities that impact inter- and intra-Regional reliability, including: |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2015-04-15 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 60000000
TOP-005-0 | 421 | R1. | 5212 | Each Transmission Operator and Balancing Authority shall provide its Reliability Coordinator with the operating data that the Reliability Coordinator requires to perform operational reliability assessments and to coordinate reliable operations within the Reliability Coordinator Area. |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2006-11-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-005-0 | 421 | R2. | 5214 | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” | [32 empty] | 2006-11-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-005-0 | 421 | R3. | 5215 | Upon request, each Reliability Coordinator shall, via the ISN or equivalent system, exchange with other Reliability Coordinators operating data that are necessary to allow the Reliability Coordinators to perform operational reliability assessments and coordinate reliable operations. Reliability Coordinators shall share with each other the types of data listed in Attachment 1- TOP-005-0 “Electric System Reliability Data,” unless otherwise agreed to. |  | RC | [11 empty] | RC | [18 empty] | 2006-11-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-005-0 | 421 | R4. | 5216 | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005-0 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2006-11-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-005-0 | 421 | R5. | 5217 | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | PSE | [10 empty] | PSE | [19 empty] | 2006-11-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-005-0 (Ontario) | 79780000421 | R1. | 79780005212 |  |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2006-11-01 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-005-0 (Ontario) | 79780000421 | R2. | 79780005214 | [33 empty] | 2006-11-01 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-005-0 (Ontario) | 79780000421 | R3. | 79780005215 |  |  | RC | [11 empty] | RC | [18 empty] | 2006-11-01 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-005-0 (Ontario) | 79780000421 | R4. | 79780005216 |  |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2006-11-01 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-005-0 (Ontario) | 79780000421 | R5. | 79780005217 |  |  | PSE | [10 empty] | PSE | [19 empty] | 2006-11-01 |  |  |  | NPCC-ON | [6 empty] | 50000000
TOP-005-1 | 175 | R1. | 1985 | Each Transmission Operator and Balancing Authority shall provide its Reliability Coordinator with the operating data that the Reliability Coordinator requires to perform operational reliability assessments and to coordinate reliable operations within the Reliability Coordinator Area. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-005-1 | 175 | R2. | 1987 | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Low | [5 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-005-1 | 175 | R3. | 1988 | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005-0 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. |  |  | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | 2007-06-18 |  | 2009-05-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-005-1 | 175 | R4. | 1989 | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | PSE | [10 empty] | PSE | [11 empty] | Medium | [5 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-005-1.1 | 176 | R1. | 1990 | Each Transmission Operator and Balancing Authority shall provide its Reliability Coordinator with the operating data that the Reliability Coordinator requires to perform operational reliability assessments and to coordinate reliable operations within the Reliability Coordinator Area. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2009-05-13 |  | 2011-05-25 |  |  | TOP-005-1 R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-005-1.1 | 176 | R2. | 1992 | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Low | [5 empty] | 2009-05-13 |  | 2011-05-25 |  |  | TOP-005-1 R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-005-1.1 | 176 | R3. | 1993 | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005-0 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2009-05-13 |  | 2011-05-25 |  |  | TOP-005-1 R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-005-1.1 | 176 | R4. | 1994 | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | PSE | [10 empty] | PSE | [11 empty] | Medium | [5 empty] | 2009-05-13 |  | 2011-05-25 |  |  | TOP-005-1 R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-005-1.1a | 274 | R1. | 3591 | Each Transmission Operator and Balancing Authority shall provide its Reliability Coordinator with the operating data that the Reliability Coordinator requires to perform operational reliability assessments and to coordinate reliable operations within the Reliability Coordinator Area. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-05-26 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-005-1.1a | 274 | R2. | 3593 | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Low | [5 empty] | 2011-05-26 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-005-1.1a | 274 | R3. | 3594 | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005-0 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-05-26 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-005-1.1a | 274 | R4. | 3595 | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | PSE | [10 empty] | PSE | [11 empty] | Medium | [5 empty] | 2011-05-26 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-005-1.1a (Ontario) | 79780000274 | R1. | 79780003591 | Each Transmission Operator and Balancing Authority shall provide its Reliability Coordinator with the operating data that the Reliability Coordinator requires to perform operational reliability assessments and to coordinate reliable operations within the Reliability Coordinator Area. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | The responsible entity failed to provide all of the data requested by its Reliability Coordinator. | N/A | N/A | The responsible entity failed to provide all of the data requested by its Reliability Coordinator. |  | 2011-05-26 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-005-1.1a (Ontario) | 79780000274 | R2. | 79780003593 | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Low | N/A | N/A | N/A | The ISN data recipient failed to sign the NERC Confidentiality Agreement for “Electric System Reliability Data”. |  | 2011-05-26 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-005-1.1a (Ontario) | 79780000274 | R3. | 79780003594 | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005-0 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. | N/A | N/A | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | 2011-05-26 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-005-1.1a (Ontario) | 79780000274 | R4. | 79780003595 | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | PSE | [10 empty] | PSE | [11 empty] | Medium | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. | N/A | N/A | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | 2011-05-26 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-005-1.1 (British Columbia) | 666700000010288 | R1. | 666700000011777 | Each Transmission Operator and Balancing Authority shall provide its Reliability Coordinator with the operating data that the Reliability Coordinator requires to perform operational reliability assessments and to coordinate reliable operations within the Reliability Coordinator Area. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-01-01 |  | 2013-04-14 |  |  |  | WECC-BC | [6 empty] | 10000000
TOP-005-1.1 (British Columbia) | 666700000010288 | R2. | 666700000011778 | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Low | [5 empty] | 2011-01-01 |  | 2013-04-14 |  |  |  | WECC-BC | [6 empty] | 20000000
TOP-005-1.1 (British Columbia) | 666700000010288 | R3. | 666700000011779 | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005-0 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-01-01 |  | 2013-04-14 |  |  |  | WECC-BC | [6 empty] | 30000000
TOP-005-1.1 (British Columbia) | 666700000010288 | R4. | 666700000011780 | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | PSE | [10 empty] | PSE | [11 empty] | Medium | [5 empty] | 2011-01-01 |  | 2013-04-14 |  |  |  | WECC-BC | [6 empty] | 40000000
TOP-005-1.1 (Ontario) | 79780000176 | R1. | 79780001990 | Each Transmission Operator and Balancing Authority shall provide its Reliability Coordinator with the operating data that the Reliability Coordinator requires to perform operational reliability assessments and to coordinate reliable operations within the Reliability Coordinator Area. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | The responsible entity failed to provide all of the data requested by its Reliability Coordinator. |  |  | The responsible entity failed to provide all of the data requested by its Reliability Coordinator. |  | 2009-05-13 |  | 2011-05-25 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-005-1.1 (Ontario) | 79780000176 | R2. | 79780001992 | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Low |  |  |  | The ISN data recipient failed to sign the NERC Confidentiality Agreement for “Electric System Reliability Data”. |  | 2009-05-13 |  | 2011-05-25 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-005-1.1 (Ontario) | 79780000176 | R3. | 79780001993 | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005-0 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. |  |  | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | 2009-05-13 |  | 2011-05-25 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-005-1.1 (Ontario) | 79780000176 | R4. | 79780001994 | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | PSE | [10 empty] | PSE | [11 empty] | Medium | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. |  |  | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | 2009-05-13 |  | 2011-05-25 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-005-1 (British Columbia) | 666700000010287 | R1. | 666700000011773 | Each Transmission Operator and Balancing Authority shall provide its Reliability Coordinator with the operating data that the Reliability Coordinator requires to perform operational reliability assessments and to coordinate reliable operations within the Reliability Coordinator Area. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 10000000
TOP-005-1 (British Columbia) | 666700000010287 | R2. | 666700000011774 | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Low | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 20000000
TOP-005-1 (British Columbia) | 666700000010287 | R3. | 666700000011775 | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005-0 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. |  |  | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 30000000
TOP-005-1 (British Columbia) | 666700000010287 | R4. | 666700000011776 | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | PSE | [10 empty] | PSE | [11 empty] | Medium | [5 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 40000000
TOP-005-1 (Manitoba) | 77660000000175 | R1. | 776600000001985 | Each Transmission Operator and Balancing Authority shall provide its Reliability Coordinator with the operating data that the Reliability Coordinator requires to perform operational reliability assessments and to coordinate reliable operations within the Reliability Coordinator Area. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 10000000
TOP-005-1 (Manitoba) | 77660000000175 | R2. | 776600000001987 | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Low | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 20000000
TOP-005-1 (Manitoba) | 77660000000175 | R3. | 776600000001988 | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005-0 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. |  |  | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 30000000
TOP-005-1 (Manitoba) | 77660000000175 | R4. | 776600000001989 | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | PSE | [10 empty] | PSE | [11 empty] | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 40000000
TOP-005-1 (Ontario) | 79780000175 | R1. | 79780001985 | Each Transmission Operator and Balancing Authority shall provide its Reliability Coordinator with the operating data that the Reliability Coordinator requires to perform operational reliability assessments and to coordinate reliable operations within the Reliability Coordinator Area. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | The responsible entity failed to provide all of the data requested by its Reliability Coordinator. |  |  | The responsible entity failed to provide all of the data requested by its Reliability Coordinator. |  | 2007-06-18 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-005-1 (Ontario) | 79780000175 | R2. | 79780001987 | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Low |  |  |  | The ISN data recipient failed to sign the NERC Confidentiality Agreement for “Electric System Reliability Data”. |  | 2007-06-18 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-005-1 (Ontario) | 79780000175 | R3. | 79780001988 | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005-0 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. |  |  | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | 2007-06-18 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-005-1 (Ontario) | 79780000175 | R4. | 79780001989 | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | PSE | [10 empty] | PSE | [11 empty] | Medium | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. |  |  | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | 2007-06-18 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-005-2 | 291 | R1. | 3823 | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  | BA, TOP | BA | [17 empty] | TOP |  |  |  |  | N/A | N/A | N/A | The ISN data recipient failed to sign the NERC Confidentiality Agreement for “Electric System Reliability Data”. |  |  |  | 2011-05-25 |  |  | TOP-005-1.1 R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-005-2 | 291 | R2. | 3824 | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  |  | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. | N/A | N/A | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  |  |  | 2011-05-25 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-005-2 | 291 | R3. | 3825 | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | PSE | [10 empty] | PSE | [12 empty] | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. | N/A | N/A | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  |  |  | 2011-05-25 |  |  | TOP-005-1.1 R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-005-2a | 177 | R1. | 1995 | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  | BA, TOP | BA | [17 empty] | TOP |  |  |  |  | N/A | N/A | N/A | The ISN data recipient failed to sign the NERC Confidentiality Agreement for “Electric System Reliability Data”. | M1. Evidence that the Balancing Authority, Transmission Operator, and Purchasing-Selling Entity is providing the information required, within the time intervals specified, and in a format agreed upon by the requesting entities. | 2011-10-01 |  | 2017-03-31 |  |  | TOP-005-2a R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-005-2a | 177 | R2. | 1996 | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  |  | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. | N/A | N/A | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | 2011-10-01 |  | 2017-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-005-2a | 177 | R3. | 1997 | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | PSE | [10 empty] | PSE | [12 empty] | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. | N/A | N/A | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | 2011-10-01 |  | 2017-03-31 |  |  | TOP-005-1.1 R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-005-2a (British Columbia) | 666700000010289 | R1. | 666700000011781 | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  | BA, TOP | BA | [17 empty] | TOP |  |  |  |  | N/A | N/A | N/A | The ISN data recipient failed to sign the NERC Confidentiality Agreement for “Electric System Reliability Data”. | M1. Evidence that the Balancing Authority, Transmission Operator, and Purchasing-Selling Entity is providing the information required, within the time intervals specified, and in a format agreed upon by the requesting entities. | 2013-04-15 | [5 empty] | WECC-BC | [6 empty] | 10000000
TOP-005-2a (British Columbia) | 666700000010289 | R2. | 666700000011782 | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  |  | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. | N/A | N/A | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | 2013-04-15 | [5 empty] | WECC-BC | [6 empty] | 20000000
TOP-005-2a (British Columbia) | 666700000010289 | R3. | 666700000011783 | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | PSE | [10 empty] | PSE | [12 empty] | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. | N/A | N/A | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | 2013-04-15 | [5 empty] | WECC-BC | [6 empty] | 30000000
TOP-005-2a (Manitoba) | 77660000000177 | R1. | 776600000001995 | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  | BA, TOP | BA | [17 empty] | TOP |  |  |  |  | N/A | N/A | N/A | The ISN data recipient failed to sign the NERC Confidentiality Agreement for “Electric System Reliability Data”. | M1. Evidence that the Balancing Authority, Transmission Operator, and Purchasing-Selling Entity is providing the information required, within the time intervals specified, and in a format agreed upon by the requesting entities. | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
TOP-005-2a (Manitoba) | 77660000000177 | R2. | 776600000001996 | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  |  | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. | N/A | N/A | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
TOP-005-2a (Manitoba) | 77660000000177 | R3. | 776600000001997 | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | PSE | [10 empty] | PSE | [12 empty] | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. | N/A | N/A | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
TOP-005-2a (Ontario) | 79780000177 | R1. | 79780001995 | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  | BA, TOP | BA | [17 empty] | TOP | [8 empty] | M1. Evidence that the Balancing Authority, Transmission Operator, and Purchasing-Selling Entity is providing the information required, within the time intervals specified, and in a format agreed upon by the requesting entities. | 2011-10-01 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-005-2a (Ontario) | 79780000177 | R2. | 79780001996 | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | BA, TOP | BA | [17 empty] | TOP | [9 empty] | 2011-10-01 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-005-2a (Ontario) | 79780000177 | R3. | 79780001997 | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | PSE | [10 empty] | PSE | [17 empty] | 2011-10-01 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-005-2a (Saskatchewan) | 83750000000177 | R1. | 837500000001995 | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  | BA, TOP | BA | [17 empty] | TOP |  |  |  |  | N/A | N/A | N/A | The ISN data recipient failed to sign the NERC Confidentiality Agreement for “Electric System Reliability Data”. | M1. Evidence that the Balancing Authority, Transmission Operator, and Purchasing-Selling Entity is providing the information required, within the time intervals specified, and in a format agreed upon by the requesting entities. | 2014-04-01 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 10000000
TOP-005-2a (Saskatchewan) | 83750000000177 | R2. | 837500000001996 | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  |  | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. | N/A | N/A | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | 2014-04-01 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 20000000
TOP-005-2a (Saskatchewan) | 83750000000177 | R3. | 837500000001997 | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | PSE | [10 empty] | PSE | [12 empty] | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. | N/A | N/A | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | 2014-04-01 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 30000000
TOP-005-2 (Ontario) | 79780000291 | R1. | 79780003823 | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2011-05-25 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-005-2 (Ontario) | 79780000291 | R2. | 79780003824 | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2011-05-25 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-005-2 (Ontario) | 79780000291 | R3. | 79780003825 | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | PSE | [10 empty] | PSE | [19 empty] | 2011-05-25 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-005-2 (Saskatchewan) | 83750000000291 | R1. | 837500000003823 | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  | BA, TOP | BA | [17 empty] | TOP |  |  |  |  | N/A | N/A | N/A | The ISN data recipient failed to sign the NERC Confidentiality Agreement for “Electric System Reliability Data”. |  | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 10000000
TOP-005-2 (Saskatchewan) | 83750000000291 | R2. | 837500000003824 | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  |  | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. | N/A | N/A | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 20000000
TOP-005-2 (Saskatchewan) | 83750000000291 | R3. | 837500000003825 | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | PSE | [10 empty] | PSE | [12 empty] | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. | N/A | N/A | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 30000000
TOP-005-3a | 481 | R1. | 5748 | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  | BA, PSE, TOP | BA | [9 empty] | PSE | [7 empty] | TOP |  |  |  |  | N/A | N/A | N/A | The ISN data recipient failed to sign the NERC Confidentiality Agreement for “Electric System Reliability Data”. |  |  |  | 2014-11-13 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-005-3a | 481 | R2. | 5749 | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  |  | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. |  |  | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  |  |  | 2014-11-13 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-005-3a | 481 | R3. | 5750 | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | PSE | [10 empty] | PSE | [12 empty] | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. |  |  | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  |  |  | 2014-11-13 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-005-3a (Ontario) | 79780000481 | R1. | 79780005748 | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  | BA, PSE, TOP | BA | [9 empty] | PSE | [7 empty] | TOP | [7 empty] | The ISN data recipient failed to sign the NERC Confidentiality Agreement for “Electric System Reliability Data”. |  |  |  | 2014-11-13 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-005-3a (Ontario) | 79780000481 | R2. | 79780005749 | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  |  | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. |  |  | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  |  |  | 2014-11-13 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-005-3a (Ontario) | 79780000481 | R3. | 79780005750 | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | PSE | [10 empty] | PSE | [12 empty] | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. |  |  | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  |  |  | 2014-11-13 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-006-0 | 422 | R1. | 5218 | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. |  | BA, TOP | BA | [17 empty] | TOP | [7 empty] | The responsible entity failed to know the status of all generation and transmission resources available for use, even though said information was reported by the Generator Operator, Transmission Operator, or Balancing Authority. |  |  |  | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-006-0 | 422 | R2. | 5221 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  |  | The responsible entity failed to monitor 3% or less of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 3% up to (and including) 6% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 6% up to (and including) 9% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 9% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  |  |  | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-006-0 | 422 | R3. | 5222 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide appropriate technical information concerning protective relays to their operating personnel. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [6 empty] | The responsible entity failed to provide appropriate technical information concerning protective relays to all of its operating personnel. | The responsible entity failed to provide appropriate technical information concerning protective relays to any of its operating personnel. |  |  |  | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-006-0 | 422 | R4. | 5223 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [6 empty] | The responsible entity has either weather forecasts or past load patterns, available to predict the system’s near-term load pattern, but not both. | The responsible entity failed to have both weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  |  |  | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-006-0 | 422 | R5. | 5224 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [6 empty] | The responsible entity used monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions, but does not have indication of the need for corrective action | The responsible entity failed to use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions. |  |  |  | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-006-0 | 422 | R6. | 5225 | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  | BA, TOP | BA | [17 empty] | TOP | [7 empty] | The responsible entity failed to use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  |  |  | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TOP-006-0 | 422 | R7. | 5226 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [7 empty] | The responsible entity failed to monitor system frequency. |  |  |  | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
TOP-006-0 (Ontario) | 79780000422 | R1. | 79780005218 |  |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-006-0 (Ontario) | 79780000422 | R2. | 79780005221 |  |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-006-0 (Ontario) | 79780000422 | R3. | 79780005222 |  |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-006-0 (Ontario) | 79780000422 | R4. | 79780005223 |  |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-006-0 (Ontario) | 79780000422 | R5. | 79780005224 |  |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 50000000
TOP-006-0 (Ontario) | 79780000422 | R6. | 79780005225 |  |  | BA, TOP | BA | [17 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 60000000
TOP-006-0 (Ontario) | 79780000422 | R7. | 79780005226 |  |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 70000000
TOP-006-1 | 179 | R1. | 2003 | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to know the status of all generation and transmission resources available for use, even though said information was reported by the Generator Operator, Transmission Operator, or Balancing Authority. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-006-1 | 179 | R2. | 2006 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | High |  | The responsible entity monitors the applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, but is not aware of the status of rotating and static reactive resources. | The responsible entity fails to monitor all of the applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of all rotating and static reactive resources. | The responsible entity fails to monitor any of the applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-006-1 | 179 | R3. | 2007 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide appropriate technical information concerning protective relays to their operating personnel. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Medium | The responsible entity failed to provide any of the appropriate technical information concerning protective relays to their operating personnel. |  |  | The responsible entity failed to provide all of the appropriate technical information concerning protective relays to their operating personnel. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-006-1 | 179 | R4. | 2008 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Medium |  |  | The responsible entity has either weather forecasts or past load patterns, available to predict the system’s near-term load pattern, but not both. | The responsible entity failed to have both weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-006-1 | 179 | R5. | 2009 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Medium |  |  | The responsible entity used monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions, but does not have indication of the need for corrective action. | The responsible entity failed to use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-006-1 | 179 | R6. | 2010 | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High |  |  |  | The responsible entity failed to use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TOP-006-1 | 179 | R7. | 2011 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | High |  |  |  | The responsible entity failed to monitor system frequency. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
TOP-006-1 (British Columbia) | 666700000010290 | R1. | 666700000011784 | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to know the status of all generation and transmission resources available for use, even though said information was reported by the Generator Operator, Transmission Operator, or Balancing Authority. |  | 2010-11-01 |  | 2013-04-14 |  |  |  | WECC-BC | [6 empty] | 10000000
TOP-006-1 (British Columbia) | 666700000010290 | R2. | 666700000011785 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | High |  | The responsible entity monitors the applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, but is not aware of the status of rotating and static reactive resources. | The responsible entity fails to monitor all of the applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of all rotating and static reactive resources. | The responsible entity fails to monitor any of the applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  | 2010-11-01 |  | 2013-04-14 |  |  |  | WECC-BC | [6 empty] | 20000000
TOP-006-1 (British Columbia) | 666700000010290 | R3. | 666700000011786 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide appropriate technical information concerning protective relays to their operating personnel. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Medium | The responsible entity failed to provide any of the appropriate technical information concerning protective relays to their operating personnel. |  |  | The responsible entity failed to provide all of the appropriate technical information concerning protective relays to their operating personnel. |  | 2010-11-01 |  | 2013-04-14 |  |  |  | WECC-BC | [6 empty] | 30000000
TOP-006-1 (British Columbia) | 666700000010290 | R4. | 666700000011787 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Medium |  |  | The responsible entity has either weather forecasts or past load patterns, available to predict the system’s near-term load pattern, but not both. | The responsible entity failed to have both weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  | 2010-11-01 |  | 2013-04-14 |  |  |  | WECC-BC | [6 empty] | 40000000
TOP-006-1 (British Columbia) | 666700000010290 | R5. | 666700000011788 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Medium |  |  | The responsible entity used monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions, but does not have indication of the need for corrective action. | The responsible entity failed to use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions. |  | 2010-11-01 |  | 2013-04-14 |  |  |  | WECC-BC | [6 empty] | 50000000
TOP-006-1 (British Columbia) | 666700000010290 | R6. | 666700000011789 | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High |  |  |  | The responsible entity failed to use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  | 2010-11-01 |  | 2013-04-14 |  |  |  | WECC-BC | [6 empty] | 60000000
TOP-006-1 (British Columbia) | 666700000010290 | R7. | 666700000011790 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | High |  |  |  | The responsible entity failed to monitor system frequency. |  | 2010-11-01 |  | 2013-04-14 |  |  |  | WECC-BC | [6 empty] | 70000000
TOP-006-1 (Manitoba) | 77660000000179 | R1. | 776600000002003 | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to know the status of all generation and transmission resources available for use, even though said information was reported by the Generator Operator, Transmission Operator, or Balancing Authority. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 10000000
TOP-006-1 (Manitoba) | 77660000000179 | R2. | 776600000002006 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | High |  | The responsible entity monitors the applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, but is not aware of the status of rotating and static reactive resources. | The responsible entity fails to monitor all of the applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of all rotating and static reactive resources. | The responsible entity fails to monitor any of the applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 20000000
TOP-006-1 (Manitoba) | 77660000000179 | R3. | 776600000002007 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide appropriate technical information concerning protective relays to their operating personnel. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Medium | The responsible entity failed to provide any of the appropriate technical information concerning protective relays to their operating personnel. |  |  | The responsible entity failed to provide all of the appropriate technical information concerning protective relays to their operating personnel. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 30000000
TOP-006-1 (Manitoba) | 77660000000179 | R4. | 776600000002008 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Medium |  |  | The responsible entity has either weather forecasts or past load patterns, available to predict the system’s near-term load pattern, but not both. | The responsible entity failed to have both weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 40000000
TOP-006-1 (Manitoba) | 77660000000179 | R5. | 776600000002009 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Medium |  |  | The responsible entity used monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions, but does not have indication of the need for corrective action. | The responsible entity failed to use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 50000000
TOP-006-1 (Manitoba) | 77660000000179 | R6. | 776600000002010 | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High |  |  |  | The responsible entity failed to use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 60000000
TOP-006-1 (Manitoba) | 77660000000179 | R7. | 776600000002011 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | High |  |  |  | The responsible entity failed to monitor system frequency. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 70000000
TOP-006-1 (Ontario) | 79780000179 | R1. | 79780002003 | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  | The responsible entity failed to know the status of all generation and transmission resources available for use, even though said information was reported by the Generator Operator, Transmission Operator, or Balancing Authority. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-006-1 (Ontario) | 79780000179 | R2. | 79780002006 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | High |  | The responsible entity monitors the applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, but is not aware of the status of rotating and static reactive resources. | The responsible entity fails to monitor all of the applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of all rotating and static reactive resources. | The responsible entity fails to monitor any of the applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-006-1 (Ontario) | 79780000179 | R3. | 79780002007 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide appropriate technical information concerning protective relays to their operating personnel. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Medium | The responsible entity failed to provide any of the appropriate technical information concerning protective relays to their operating personnel. |  |  | The responsible entity failed to provide all of the appropriate technical information concerning protective relays to their operating personnel. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-006-1 (Ontario) | 79780000179 | R4. | 79780002008 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Medium |  |  | The responsible entity has either weather forecasts or past load patterns, available to predict the system’s near-term load pattern, but not both. | The responsible entity failed to have both weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-006-1 (Ontario) | 79780000179 | R5. | 79780002009 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Medium |  |  | The responsible entity used monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions, but does not have indication of the need for corrective action. | The responsible entity failed to use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 50000000
TOP-006-1 (Ontario) | 79780000179 | R6. | 79780002010 | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High |  |  |  | The responsible entity failed to use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 60000000
TOP-006-1 (Ontario) | 79780000179 | R7. | 79780002011 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | High |  |  |  | The responsible entity failed to monitor system frequency. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 70000000
TOP-006-2 | 180 | R1. | 2012 | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium | N/A | N/A | N/A | The responsible entity failed to know the status of all generation and transmission resources available for use, even though said information was reported by the Generator Operator, Transmission Operator, or Balancing Authority. | M1. The Generator Operator shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Host Balancing Authority and Transmission Operator of all generation resources available for use. (Requirement 1.1) | 2011-10-01 |  | 2017-03-31 |  |  | TOP-006-1 R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-006-2 | 180 | R2. | 2015 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | High | The responsible entity failed to monitor 3% or less of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 3% up to (and including) 9% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 6% up to (and including) 9% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 9% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | M2. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. (Requirement 1.2) | 2011-10-01 |  | 2017-03-31 |  |  | TOP-006-1 R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-006-2 | 180 | R3. | 2016 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide appropriate technical information concerning protective relays to their operating personnel. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Medium | N/A | N/A | The responsible entity failed to provide appropriate technical information concerning protective relays to all of its operating personnel. | The responsible entity failed to provide appropriate technical information concerning protective relays to any of its operating personnel. | M3. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, computer printouts or other equivalent evidence that will be used to confirm that it monitored each of the applicable items listed in Requirement 2. | 2011-10-01 |  | 2017-03-31 |  |  | TOP-006-1 R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-006-2 | 180 | R4. | 2017 | Each Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | N/A | N/A | The responsible entity has either weather forecasts or past load patterns, available to predict the system’s near-term load pattern, but not both. | The responsible entity failed to have both weather forecasts and past load patterns, available to predict the system’s near-term load pattern. | M4. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, printouts, training documents, description documents or other equivalent evidence that will be used to confirm that it has weather forecasts and past load patterns, available to predict the system’s near-term load pattern. (Requirement 4) | 2011-10-01 |  | 2017-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-006-2 | 180 | R5. | 2018 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Medium | N/A | N/A | The responsible entity used monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions, but does not have indication of the need for corrective action. | The responsible entity failed to use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions. | M5. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, a description of its EMS alarm capability, training documents, or other equivalent evidence that will be used to confirm that important deviations in operating conditions and the need for corrective actions will be brought to the attention of its operators. (Requirement 5) | 2011-10-01 |  | 2017-03-31 |  |  | TOP-006-1 R5. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-006-2 | 180 | R6. | 2019 | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High | N/A | N/A | N/A | The responsible entity failed to use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. | M6. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, a list of the frequency monitoring points available to the shift-operators or other equivalent evidence that will be used to confirm that it monitors system frequency. (Requirement 7) | 2011-10-01 |  | 2017-03-31 |  |  | TOP-006-1 R6. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TOP-006-2 | 180 | R7. | 2020 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | High | N/A | N/A | N/A | The responsible entity failed to monitor system frequency. |  | 2011-10-01 |  | 2017-03-31 |  |  | TOP-006-1 R7. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
TOP-006-2 (British Columbia) | 666700000010291 | R1. | 666700000011791 | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium | N/A | N/A | N/A | The responsible entity failed to know the status of all generation and transmission resources available for use, even though said information was reported by the Generator Operator, Transmission Operator, or Balancing Authority. | M1. The Generator Operator shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Host Balancing Authority and Transmission Operator of all generation resources available for use. (Requirement 1.1) | 2013-04-15 | [5 empty] | WECC-BC | [6 empty] | 10000000
TOP-006-2 (British Columbia) | 666700000010291 | R2. | 666700000011792 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | High | The responsible entity failed to monitor 3% or less of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 3% up to (and including) 9% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 6% up to (and including) 9% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 9% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | M2. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. (Requirement 1.2) | 2013-04-15 | [5 empty] | WECC-BC | [6 empty] | 20000000
TOP-006-2 (British Columbia) | 666700000010291 | R3. | 666700000011793 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide appropriate technical information concerning protective relays to their operating personnel. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Medium | N/A | N/A | The responsible entity failed to provide appropriate technical information concerning protective relays to all of its operating personnel. | The responsible entity failed to provide appropriate technical information concerning protective relays to any of its operating personnel. | M3. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, computer printouts or other equivalent evidence that will be used to confirm that it monitored each of the applicable items listed in Requirement 2. | 2013-04-15 | [5 empty] | WECC-BC | [6 empty] | 30000000
TOP-006-2 (British Columbia) | 666700000010291 | R4. | 666700000011794 | Each Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | N/A | N/A | The responsible entity has either weather forecasts or past load patterns, available to predict the system’s near-term load pattern, but not both. | The responsible entity failed to have both weather forecasts and past load patterns, available to predict the system’s near-term load pattern. | M4. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, printouts, training documents, description documents or other equivalent evidence that will be used to confirm that it has weather forecasts and past load patterns, available to predict the system’s near-term load pattern. (Requirement 4) | 2013-04-15 | [5 empty] | WECC-BC | [6 empty] | 40000000
TOP-006-2 (British Columbia) | 666700000010291 | R5. | 666700000011795 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Medium | N/A | N/A | The responsible entity used monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions, but does not have indication of the need for corrective action. | The responsible entity failed to use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions. | M5. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, a description of its EMS alarm capability, training documents, or other equivalent evidence that will be used to confirm that important deviations in operating conditions and the need for corrective actions will be brought to the attention of its operators. (Requirement 5) | 2013-04-15 | [5 empty] | WECC-BC | [6 empty] | 50000000
TOP-006-2 (British Columbia) | 666700000010291 | R6. | 666700000011796 | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High | N/A | N/A | N/A | The responsible entity failed to use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. | M6. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, a list of the frequency monitoring points available to the shift-operators or other equivalent evidence that will be used to confirm that it monitors system frequency. (Requirement 7) | 2013-04-15 | [5 empty] | WECC-BC | [6 empty] | 60000000
TOP-006-2 (British Columbia) | 666700000010291 | R7. | 666700000011797 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | High | N/A | N/A | N/A | The responsible entity failed to monitor system frequency. |  | 2013-04-15 | [5 empty] | WECC-BC | [6 empty] | 70000000
TOP-006-2 (Manitoba) | 77660000000180 | R1. | 776600000002012 | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium | N/A | N/A | N/A | The responsible entity failed to know the status of all generation and transmission resources available for use, even though said information was reported by the Generator Operator, Transmission Operator, or Balancing Authority. | M1. The Generator Operator shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Host Balancing Authority and Transmission Operator of all generation resources available for use. (Requirement 1.1) | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
TOP-006-2 (Manitoba) | 77660000000180 | R2. | 776600000002015 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | High | The responsible entity failed to monitor 3% or less of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 3% up to (and including) 9% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 6% up to (and including) 9% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 9% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | M2. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. (Requirement 1.2) | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
TOP-006-2 (Manitoba) | 77660000000180 | R3. | 776600000002016 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide appropriate technical information concerning protective relays to their operating personnel. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Medium | N/A | N/A | The responsible entity failed to provide appropriate technical information concerning protective relays to all of its operating personnel. | The responsible entity failed to provide appropriate technical information concerning protective relays to any of its operating personnel. | M3. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, computer printouts or other equivalent evidence that will be used to confirm that it monitored each of the applicable items listed in Requirement 2. | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
TOP-006-2 (Manitoba) | 77660000000180 | R4. | 776600000002017 | Each Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | N/A | N/A | The responsible entity has either weather forecasts or past load patterns, available to predict the system’s near-term load pattern, but not both. | The responsible entity failed to have both weather forecasts and past load patterns, available to predict the system’s near-term load pattern. | M4. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, printouts, training documents, description documents or other equivalent evidence that will be used to confirm that it has weather forecasts and past load patterns, available to predict the system’s near-term load pattern. (Requirement 4) | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 40000000
TOP-006-2 (Manitoba) | 77660000000180 | R5. | 776600000002018 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Medium | N/A | N/A | The responsible entity used monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions, but does not have indication of the need for corrective action. | The responsible entity failed to use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions. | M5. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, a description of its EMS alarm capability, training documents, or other equivalent evidence that will be used to confirm that important deviations in operating conditions and the need for corrective actions will be brought to the attention of its operators. (Requirement 5) | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 50000000
TOP-006-2 (Manitoba) | 77660000000180 | R6. | 776600000002019 | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High | N/A | N/A | N/A | The responsible entity failed to use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. | M6. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, a list of the frequency monitoring points available to the shift-operators or other equivalent evidence that will be used to confirm that it monitors system frequency. (Requirement 7) | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 60000000
TOP-006-2 (Manitoba) | 77660000000180 | R7. | 776600000002020 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | High | N/A | N/A | N/A | The responsible entity failed to monitor system frequency. |  | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 70000000
TOP-006-2 (Ontario) | 79780000180 | R1. | 79780002012 | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium |  |  |  |  | M1. The Generator Operator shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Host Balancing Authority and Transmission Operator of all generation resources available for use. (Requirement 1.1) | 2011-10-01 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-006-2 (Ontario) | 79780000180 | R2. | 79780002015 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | High | The responsible entity failed to monitor 3% or less of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 3% up to (and including) 6% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 6% up to (and including) 9% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 9% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | M2. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. (Requirement 1.2) | 2011-10-01 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-006-2 (Ontario) | 79780000180 | R3. | 79780002016 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide appropriate technical information concerning protective relays to their operating personnel. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Medium | N/A | N/A | The responsible entity failed to provide appropriate technical information concerning protective relays to all of its operating personnel. | The responsible entity failed to provide appropriate technical information concerning protective relays to any of its operating personnel. | M3. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, computer printouts or other equivalent evidence that will be used to confirm that it monitored each of the applicable items listed in Requirement 2. | 2011-10-01 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-006-2 (Ontario) | 79780000180 | R4. | 79780002017 | Each Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium |  |  |  |  | M4. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, printouts, training documents, description documents or other equivalent evidence that will be used to confirm that it has weather forecasts and past load patterns, available to predict the system’s near-term load pattern. (Requirement 4) | 2011-10-01 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-006-2 (Ontario) | 79780000180 | R5. | 79780002018 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Medium |  |  |  |  | M5. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, a description of its EMS alarm capability, training documents, or other equivalent evidence that will be used to confirm that important deviations in operating conditions and the need for corrective actions will be brought to the attention of its operators. (Requirement 5) | 2011-10-01 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 50000000
TOP-006-2 (Ontario) | 79780000180 | R6. | 79780002019 | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High |  |  |  |  | M6. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, a list of the frequency monitoring points available to the shift-operators or other equivalent evidence that will be used to confirm that it monitors system frequency. (Requirement 7) | 2011-10-01 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 60000000
TOP-006-2 (Ontario) | 79780000180 | R7. | 79780002020 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | High | [5 empty] | 2011-10-01 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 70000000
TOP-006-2 (Saskatchewan) | 83750000000180 | R1. | 837500000002012 | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. |  | BA, GOP, TOP | BA |  |  |  |  | GOP | [12 empty] | TOP |  |  |  | Medium | N/A | N/A | N/A | The responsible entity failed to know the status of all generation and transmission resources available for use, even though said information was reported by the Generator Operator, Transmission Operator, or Balancing Authority. | M1. The Generator Operator shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Host Balancing Authority and Transmission Operator of all generation resources available for use. (Requirement 1.1) | 2015-04-15 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 10000000
TOP-006-2 (Saskatchewan) | 83750000000180 | R2. | 837500000002015 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | High | The responsible entity failed to monitor 3% or less of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 3% up to (and including) 9% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 6% up to (and including) 9% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 9% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | M2. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. (Requirement 1.2) | 2015-04-15 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 20000000
TOP-006-2 (Saskatchewan) | 83750000000180 | R3. | 837500000002016 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide appropriate technical information concerning protective relays to their operating personnel. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Medium | N/A | N/A | The responsible entity failed to provide appropriate technical information concerning protective relays to all of its operating personnel. | The responsible entity failed to provide appropriate technical information concerning protective relays to any of its operating personnel. | M3. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, computer printouts or other equivalent evidence that will be used to confirm that it monitored each of the applicable items listed in Requirement 2. | 2015-04-15 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 30000000
TOP-006-2 (Saskatchewan) | 83750000000180 | R4. | 837500000002017 | Each Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | Medium | N/A | N/A | The responsible entity has either weather forecasts or past load patterns, available to predict the system’s near-term load pattern, but not both. | The responsible entity failed to have both weather forecasts and past load patterns, available to predict the system’s near-term load pattern. | M4. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, printouts, training documents, description documents or other equivalent evidence that will be used to confirm that it has weather forecasts and past load patterns, available to predict the system’s near-term load pattern. (Requirement 4) | 2015-04-15 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 40000000
TOP-006-2 (Saskatchewan) | 83750000000180 | R5. | 837500000002018 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | Medium | N/A | N/A | The responsible entity used monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions, but does not have indication of the need for corrective action. | The responsible entity failed to use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions. | M5. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, a description of its EMS alarm capability, training documents, or other equivalent evidence that will be used to confirm that important deviations in operating conditions and the need for corrective actions will be brought to the attention of its operators. (Requirement 5) | 2015-04-15 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 50000000
TOP-006-2 (Saskatchewan) | 83750000000180 | R6. | 837500000002019 | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | High | N/A | N/A | N/A | The responsible entity failed to use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. | M6. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, a list of the frequency monitoring points available to the shift-operators or other equivalent evidence that will be used to confirm that it monitors system frequency. (Requirement 7) | 2015-04-15 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 60000000
TOP-006-2 (Saskatchewan) | 83750000000180 | R7. | 837500000002020 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | High | N/A | N/A | N/A | The responsible entity failed to monitor system frequency. |  | 2015-04-15 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 70000000
TOP-006-3 | 344 | R1. | 4461 | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | N/A | The responsible entity failed to know the status of all generation and transmission resources available for use, even though said information was reported by the Generator Operator, Transmission Operator, or Balancing Authority. OR The Generator Operator failed to inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. OR The responsible entity failed to inform the Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. | M1. The Generator Operator shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Host Balancing Authority and Transmission Operator of all generation resources available for use. (Requirement R1.1) |  |  | 2015-03-18 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-006-3 | 344 | R2. | 4462 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Real-Time Operations | High | The responsible entity failed to monitor 5% or less of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 5% up to (and including) 10% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 10% up to (and including) 15% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 15% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | M2. Each Transmission Operator shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Reliability Coordinator and other affected Transmission Operators of all transmission resources available for use. (Requirement R1.2) |  |  | 2015-03-18 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-006-3 | 344 | R3. | 4466 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide its operating personnel with appropriate technical information concerning protective relays within the Reliability Coordinator Area, the Transmission Operator Area, and the Balancing Authority Area, respectively. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Real-Time Operations | Medium | The responsible entity failed to provide 5% or less of the appropriate technical information concerning protective relays to its operating personnel. | The responsible entity failed to provide more than 5% up to (and including) 10% of the appropriate technical information concerning protective relays to its operating personnel. | The responsible entity failed to provide more than 10% up to (and including) 15% of the appropriate technical information concerning protective relays to its operating personnel. | The responsible entity failed to provide more than 15% of the appropriate technical information concerning protective relays to its operating personnel. | M3. Each Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Reliability Coordinator of all generation resources available for use. (Requirement R1.3) |  |  | 2015-03-18 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-006-3 | 344 | R4. | 4467 | Each Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | The responsible entity has either weather forecasts or past load patterns, available to predict the system’s near-term load pattern, but not both. | The responsible entity failed to have both weather forecasts and past load patterns, available to predict the system’s near-term load pattern. | M4. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, computer printouts or other equivalent evidence that will be used to confirm that it monitored each of the applicable items listed in Requirement R2. |  |  | 2015-03-18 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-006-3 | 344 | R5. | 4468 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | The responsible entity used monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions, but does not have indication of the need for corrective action. | The responsible entity failed to use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions. | M5. Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, operating instructions, training materials, or other equivalent evidence that will be used to confirm that it informed its operating personnel of appropriate technical information concerning protective relays within the Reliability Coordinator Area, the Transmission Operator Area, and the Balancing Authority Area, respectively. (Requirement R3) |  |  | 2015-03-18 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TOP-006-3 | 344 | R6. | 4469 | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The responsible entity failed to use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. | M6. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, printouts, training documents, description documents or other equivalent evidence that will be used to confirm that it has weather forecasts and past load patterns, available to predict the system’s near-term load pattern. (Requirement R4) |  |  | 2015-03-18 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TOP-006-3 | 344 | R7. | 4470 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The responsible entity failed to monitor system frequency. | M7. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, a description of its EMS alarm capability, training documents, or other equivalent evidence that will be used to confirm that important deviations in operating conditions and the need for corrective actions will be brought to the attention of its operators. (Requirement R5) |  |  | 2015-03-18 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
TOP-006-3 (Ontario) | 79780000344 | R1. | 79780004461 | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | N/A | The responsible entity failed to know the status of all generation and transmission resources available for use, even though said information was reported by the Generator Operator, Transmission Operator, or Balancing Authority. | M1. The Generator Operator shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Host Balancing Authority and Transmission Operator of all generation resources available for use. (Requirement R1.1) |  |  | 2015-03-18 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-006-3 (Ontario) | 79780000344 | R2. | 79780004462 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Real-Time Operations | High | N/A | The responsible entity monitors the applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, but is not aware of the status of rotating and static reactive resources. | The responsible entity fails to monitor all of the applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of all rotating and static reactive resources. | The responsible entity fails to monitor any of the applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | M2. Each Transmission Operator shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Reliability Coordinator and other affected Transmission Operators of all transmission resources available for use. (Requirement R1.2) |  |  | 2015-03-18 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-006-3 (Ontario) | 79780000344 | R3. | 79780004466 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide its operating personnel with appropriate technical information concerning protective relays within the Reliability Coordinator Area, the Transmission Operator Area, and the Balancing Authority Area, respectively. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Real-Time Operations | Medium | The Reliability Coordinator, the Transmission Operator, or the Balancing Authority, failed to provide some of the appropriate technical information concerning protective relays within their respective Reliability Coordinator Area, the Transmission Operator Area, and the Balancing Authority to their operating personnel. | N/A | N/A | The Reliability Coordinator, the Transmission Operator, or the Balancing Authority, failed to provide all of the appropriate technical information concerning protective relays within their respective Reliability Coordinator Area, the Transmission Operator Area, and the Balancing Authority to their operating personnel. | M3. Each Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it informed its Reliability Coordinator of all generation resources available for use. (Requirement R1.3) |  |  | 2015-03-18 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-006-3 (Ontario) | 79780000344 | R4. | 79780004467 | Each Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | The responsible entity has either weather forecasts or past load patterns, available to predict the system’s near-term load pattern, but not both. | The responsible entity failed to have both weather forecasts and past load patterns, available to predict the system’s near-term load pattern. | M4. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, computer printouts or other equivalent evidence that will be used to confirm that it monitored each of the applicable items listed in Requirement R2. |  |  | 2015-03-18 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-006-3 (Ontario) | 79780000344 | R5. | 79780004468 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | The responsible entity used monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions, but does not have indication of the need for corrective action. | The responsible entity failed to use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions. | M5. Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, operator logs, voice recordings, electronic communications, operating instructions, training materials, or other equivalent evidence that will be used to confirm that it informed its operating personnel of appropriate technical information concerning protective relays within the Reliability Coordinator Area, the Transmission Operator Area, and the Balancing Authority Area, respectively. (Requirement R3) |  |  | 2015-03-18 |  |  |  | NPCC-ON | [6 empty] | 50000000
TOP-006-3 (Ontario) | 79780000344 | R6. | 79780004469 | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The responsible entity failed to use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. | M6. Each Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, printouts, training documents, description documents or other equivalent evidence that will be used to confirm that it has weather forecasts and past load patterns, available to predict the system’s near-term load pattern. (Requirement R4) |  |  | 2015-03-18 |  |  |  | NPCC-ON | [6 empty] | 60000000
TOP-006-3 (Ontario) | 79780000344 | R7. | 79780004470 | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Real-Time Operations | High | N/A | N/A | N/A | The responsible entity failed to monitor system frequency. | M7. Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have and provide upon request evidence that could include but is not limited to, a description of its EMS alarm capability, training documents, or other equivalent evidence that will be used to confirm that important deviations in operating conditions and the need for corrective actions will be brought to the attention of its operators. (Requirement R5) |  |  | 2015-03-18 |  |  |  | NPCC-ON | [6 empty] | 70000000
TOP-007-0 | 181 | R1. | 2021 | A Transmission Operator shall inform its Reliability Coordinator when an IROL or SOL has been exceeded and the actions being taken to return the system to within limits. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  |  | M1. Evidence that the Transmission Operator informed the Reliability Coordinator when an IROL or SOL was exceeded and the actions taken to return the system to within limits. | 2007-06-18 |  | 2017-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-007-0 | 181 | R2. | 2022 | Following a Contingency or other event that results in an IROL violation, the Transmission Operator shall return its transmission system to within IROL as soon as possible, but not longer than 30 minutes. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  |  | M2. Evidence that the Transmission Operator returned the system to within IROL within 30 minutes for each incident that an IROL, or SOL that became an IROL due to changed system conditions, was exceeded. | 2007-06-18 |  | 2017-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-007-0 | 181 | R3. | 2023 | A Transmission Operator shall take all appropriate actions up to and including shedding firm load, or directing the shedding of firm load, in order to comply with Requirement R2. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  |  | M3. Evidence that the Reliability Coordinator evaluated actions and provided direction required to return the system to within limits. | 2007-06-18 |  | 2017-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-007-0 | 181 | R4. | 2024 | The Reliability Coordinator shall evaluate actions taken to address an IROL or SOL violation and, if the actions taken are not appropriate or sufficient, direct actions required to return the system to within limits. |  | RC | [11 empty] | RC | [10 empty] | High | [5 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-007-0 (British Columbia) | 666700000010292 | R1. | 666700000011798 | A Transmission Operator shall inform its Reliability Coordinator when an IROL or SOL has been exceeded and the actions being taken to return the system to within limits. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  |  | M1. Evidence that the Transmission Operator informed the Reliability Coordinator when an IROL or SOL was exceeded and the actions taken to return the system to within limits. | 2010-11-01 | [5 empty] | WECC-BC | [6 empty] | 10000000
TOP-007-0 (British Columbia) | 666700000010292 | R2. | 666700000011799 | Following a Contingency or other event that results in an IROL violation, the Transmission Operator shall return its transmission system to within IROL as soon as possible, but not longer than 30 minutes. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  |  | M2. Evidence that the Transmission Operator returned the system to within IROL within 30 minutes for each incident that an IROL, or SOL that became an IROL due to changed system conditions, was exceeded. | 2010-11-01 | [5 empty] | WECC-BC | [6 empty] | 20000000
TOP-007-0 (British Columbia) | 666700000010292 | R3. | 666700000011800 | A Transmission Operator shall take all appropriate actions up to and including shedding firm load, or directing the shedding of firm load, in order to comply with Requirement R2. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  |  | M3. Evidence that the Reliability Coordinator evaluated actions and provided direction required to return the system to within limits. | 2010-11-01 | [5 empty] | WECC-BC | [6 empty] | 30000000
TOP-007-0 (British Columbia) | 666700000010292 | R4. | 666700000011801 | The Reliability Coordinator shall evaluate actions taken to address an IROL or SOL violation and, if the actions taken are not appropriate or sufficient, direct actions required to return the system to within limits. |  | RC | [11 empty] | RC | [10 empty] | High | [5 empty] | 2010-11-01 | [5 empty] | WECC-BC | [6 empty] | 40000000
TOP-007-0 (Manitoba) | 77660000000181 | R1. | 776600000002021 | A Transmission Operator shall inform its Reliability Coordinator when an IROL or SOL has been exceeded and the actions being taken to return the system to within limits. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  |  | M1. Evidence that the Transmission Operator informed the Reliability Coordinator when an IROL or SOL was exceeded and the actions taken to return the system to within limits. | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
TOP-007-0 (Manitoba) | 77660000000181 | R2. | 776600000002022 | Following a Contingency or other event that results in an IROL violation, the Transmission Operator shall return its transmission system to within IROL as soon as possible, but not longer than 30 minutes. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  |  | M2. Evidence that the Transmission Operator returned the system to within IROL within 30 minutes for each incident that an IROL, or SOL that became an IROL due to changed system conditions, was exceeded. | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
TOP-007-0 (Manitoba) | 77660000000181 | R3. | 776600000002023 | A Transmission Operator shall take all appropriate actions up to and including shedding firm load, or directing the shedding of firm load, in order to comply with Requirement R2. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  |  | M3. Evidence that the Reliability Coordinator evaluated actions and provided direction required to return the system to within limits. | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
TOP-007-0 (Manitoba) | 77660000000181 | R4. | 776600000002024 | The Reliability Coordinator shall evaluate actions taken to address an IROL or SOL violation and, if the actions taken are not appropriate or sufficient, direct actions required to return the system to within limits. |  | RC | [11 empty] | RC | [10 empty] | High | [5 empty] | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 40000000
TOP-007-0 (Ontario) | 79780000181 | R1. | 79780002021 | A Transmission Operator shall inform its Reliability Coordinator when an IROL or SOL has been exceeded and the actions being taken to return the system to within limits. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  | The Transmission Operator informed its Reliability Coordinator when an IROL or SOL had been exceeded but failed to provide the actions being taken to return the system to within limits. | The Transmission Operator failed to inform its Reliability Coordinator when an IROL or SOL had been exceeded. | M1. Evidence that the Transmission Operator informed the Reliability Coordinator when an IROL&lt;br/&gt;or SOL was exceeded and the actions taken to return the system to within limits. | 2007-06-18 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-007-0 (Ontario) | 79780000181 | R2. | 79780002022 | Following a Contingency or other event that results in an IROL violation, the Transmission Operator shall return its transmission system to within IROL as soon as possible, but not longer than 30 minutes. |  | TOP | [18 empty] | TOP |  |  |  | High | Following a Contingency or other event that resulted in an IROL violation of a magnitude up to and including 5%, the Transmission Operator failed to return its transmission system to within IROL in less than or equal to 35 minutes. | Following a Contingency or other event that resulted in an IROL violation, the Transmission Operator failed to return its transmission system to within IROL in accordance with the following: (a) an IROL with a magnitude up to and including 5% for a period | Following a Contingency or other event that resulted in an IROL violation, the Transmission Operator failed to return its transmission system to within IROL in accordance with the following: (a) an IROL with a magnitude up to and including 5% for a period | Following a Contingency or other event that resulted in an IROL violation, the Transmission Operator failed to return its transmission system to within IROL in accordance with the following: (a) an IROL with a magnitude greater than 10% but less than or e | M2. Evidence that the Transmission Operator returned the system to within IROL within 30&lt;br/&gt;minutes for each incident that an IROL, or SOL that became an IROL due to changed system&lt;br/&gt;conditions, was exceeded. | 2007-06-18 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-007-0 (Ontario) | 79780000181 | R3. | 79780002023 | A Transmission Operator shall take all appropriate actions up to and including shedding firm load, or directing the shedding of firm load, in order to comply with Requirement R2. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  | The Transmission Operator failed to take all appropriate actions up to and including shedding firm load, or directing the shedding of firm load, in order to return the transmission system to IROL within 30 minutes. | M3. Evidence that the Reliability Coordinator evaluated actions and provided direction required to&lt;br/&gt;return the system to within limits. | 2007-06-18 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-007-0 (Ontario) | 79780000181 | R4. | 79780002024 | The Reliability Coordinator shall evaluate actions taken to address an IROL or SOL violation and, if the actions taken are not appropriate or sufficient, direct actions required to return the system to within limits. |  | RC | [11 empty] | RC | [10 empty] | High |  |  |  | The Reliability Coordinator failed to evaluate actions taken to address an IROL or SOL violation and, if the actions taken were not appropriate or sufficient, direct actions required to return the system to within limits. | M4. The Transmission Operator shall have and provide upon request evidence that could | 2007-06-18 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-007-0 (Saskatchewan) | 83750000000181 | R1. | 837500000002021 | A Transmission Operator shall inform its Reliability Coordinator when an IROL or SOL has been exceeded and the actions being taken to return the system to within limits. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  |  | M1. Evidence that the Transmission Operator informed the Reliability Coordinator when an IROL or SOL was exceeded and the actions taken to return the system to within limits. | 2015-04-15 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 10000000
TOP-007-0 (Saskatchewan) | 83750000000181 | R2. | 837500000002022 | Following a Contingency or other event that results in an IROL violation, the Transmission Operator shall return its transmission system to within IROL as soon as possible, but not longer than 30 minutes. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  |  | M2. Evidence that the Transmission Operator returned the system to within IROL within 30 minutes for each incident that an IROL, or SOL that became an IROL due to changed system conditions, was exceeded. | 2015-04-15 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 20000000
TOP-007-0 (Saskatchewan) | 83750000000181 | R3. | 837500000002023 | A Transmission Operator shall take all appropriate actions up to and including shedding firm load, or directing the shedding of firm load, in order to comply with Requirement R2. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  |  | M3. Evidence that the Reliability Coordinator evaluated actions and provided direction required to return the system to within limits. | 2015-04-15 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 30000000
TOP-007-0 (Saskatchewan) | 83750000000181 | R4. | 837500000002024 | The Reliability Coordinator shall evaluate actions taken to address an IROL or SOL violation and, if the actions taken are not appropriate or sufficient, direct actions required to return the system to within limits. |  | RC | [11 empty] | RC | [10 empty] | High | [5 empty] | 2015-04-15 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 40000000
TOP-007-WECC-1 | 182 | R1. | 2025 | When the actual power flow exceeds an SOL for a Transmission path, the Transmission Operators shall take immediate action to reduce the actual power flow across the path such that at no time shall the power flow for the Transmission path exceed the SOL for more than 30 minutes. [Time Horizon: Real-time Operations] |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2011-07-01 |  | 2014-06-17 |  |  |  | WECC-US | [5 empty] | WECC-US | 10000000
TOP-007-WECC-1 | 182 | R2. | 2026 | The Transmission Operator shall not have the Net Scheduled Interchange for power flow over an interconnection or Transmission path above the path’s SOL when the Transmission Operator implements its real-time schedules for the next hour. For paths internal to a Transmission Operator Area that are not scheduled, this requirement does not apply. [Time Horizon: Real-time Operations] |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-07-01 |  | 2014-06-17 |  |  |  | WECC-US | [5 empty] | WECC-US | 20000000
TOP-007-WECC-1a | 444 | R1. | 5437 | When the actual power flow exceeds an SOL for a Transmission path, the Transmission Operators shall take immediate action to reduce the actual power flow across the path such that at no time shall the power flow for the Transmission path exceed the SOL for more than 30 minutes. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High |  |  |  |  | M1. Evidence that actual power flow has not exceeded the SOL for the specified time limit in R1. | 2014-06-18 |  | 2017-03-10 |  |  |  | WECC-US | [5 empty] | WECC-US | 10000000
TOP-007-WECC-1a | 444 | R2. | 5438 | The Transmission Operator shall not have the Net Scheduled Interchange for power flow over an interconnection or Transmission path above the path’s SOL when the Transmission Operator implements its real-time schedules for the next hour. For paths internal to a Transmission Operator Area that are not scheduled, this requirement does not apply. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium |  |  |  |  | M2. Evidence that Net Scheduled Interchange has not exceeded the SOL when the Transmission Operator implements real-time schedules as required by R2. | 2014-06-18 |  | 2017-03-10 |  |  |  | WECC-US | [5 empty] | WECC-US | 20000000
TOP-007-WECC-1a (British Columbia) | 666700000010294 | R1. | 666700000011804 | When the actual power flow exceeds an SOL for a Transmission path, the Transmission Operators shall take immediate action to reduce the actual power flow across the path such that at no time shall the power flow for the Transmission path exceed the SOL for more than 30 minutes. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High |  |  |  |  | M1. Evidence that actual power flow has not exceeded the SOL for the specified time limit in R1. | 2015-10-01 |  | 2018-10-01 |  |  |  | WECC-BC | [6 empty] | 10000000
TOP-007-WECC-1a (British Columbia) | 666700000010294 | R2. | 666700000011805 | The Transmission Operator shall not have the Net Scheduled Interchange for power flow over an interconnection or Transmission path above the path’s SOL when the Transmission Operator implements its real-time schedules for the next hour. For paths internal to a Transmission Operator Area that are not scheduled, this requirement does not apply. |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium |  |  |  |  | M2. Evidence that Net Scheduled Interchange has not exceeded the SOL when the Transmission Operator implements real-time schedules as required by R2. | 2015-10-01 |  | 2018-10-01 |  |  |  | WECC-BC | [6 empty] | 20000000
TOP-007-WECC-1 (British Columbia) | 666700000010293 | R1. | 666700000011802 | When the actual power flow exceeds an SOL for a Transmission path, the Transmission Operators shall take immediate action to reduce the actual power flow across the path such that at no time shall the power flow for the Transmission path exceed the SOL for more than 30 minutes. [Time Horizon: Real-time Operations] |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2013-04-15 |  | 2015-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
TOP-007-WECC-1 (British Columbia) | 666700000010293 | R2. | 666700000011803 | The Transmission Operator shall not have the Net Scheduled Interchange for power flow over an interconnection or Transmission path above the path’s SOL when the Transmission Operator implements its real-time schedules for the next hour. For paths internal to a Transmission Operator Area that are not scheduled, this requirement does not apply. [Time Horizon: Real-time Operations] |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2013-04-15 |  | 2015-09-30 |  |  |  | WECC-BC | [6 empty] | 20000000
TOP-008-0 | 423 | R1. | 5227 | The Transmission Operator experiencing or contributing to an IROL or SOL violation shall take immediate steps to relieve the condition, which may include shedding firm load. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | [8 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-008-0 | 423 | R2. | 5228 | Each Transmission Operator shall operate to prevent the likelihood that a disturbance, action, or inaction will result in an IROL or SOL violation in its area or another area of the Interconnection. In instances where there is a difference in derived operating limits, the Transmission Operator shall always operate the Bulk Electric System to the most limiting parameter. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | [8 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-008-0 | 423 | R3. | 5229 | The Transmission Operator shall disconnect the affected facility if the overload on a transmission facility or abnormal voltage or reactive condition persists and equipment is endangered. In doing so, the transmission Operator shall notify its Reliability Coordinator and all neighboring Transmission Operators impacted by the disconnection prior to switching, if time permits, otherwise, immediately thereafter. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | [8 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-008-0 | 423 | R4. | 5230 | The Transmission Operator shall have sufficient information and analysis tools to determine the cause(s) of SOL violations. This analysis shall be conducted in all operating timeframes. The Transmission operator shall use the results of these analyses to immediately mitigate the SOL violation. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | [8 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-008-0 (Ontario) | 79780000423 | R1. | 79780005227 |  |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | [8 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-008-0 (Ontario) | 79780000423 | R2. | 79780005228 |  |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | [5 empty] | M2. Each Generator Owner and Transmission Owner with applicable Facilities will have evidence of the coordination required by the events listed in Requirement R2. This evidence should include dated documentation that demonstrates the specified intervals in Requirement R2 have been met. |  |  | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-008-0 (Ontario) | 79780000423 | R3. | 79780005229 |  |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | [5 empty] | M1. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence such as spreadsheets or summaries of calculations to show that each of its transmission relays is set according to one of the criteria in Requirement R1, criterion 1 through 13 and shall have evidence such as coordination curves or summaries of calculations that show that relays set per criterion 10 do not expose the transformer to fault levels and durations beyond those indicated in the standard. (R1) |  |  | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-008-0 (Ontario) | 79780000423 | R4. | 79780005230 |  |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | [5 empty] | M2. Each Transmission Owner, Generator Owner, and Distribution Provider shall have evidence such as spreadsheets or summaries of calculations to show that each of its out-of-step blocking elements is set to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. (R2) |  |  | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-008-1 | 183 | R1. | 2028 | The Transmission Operator experiencing or contributing to an IROL or SOL violation shall take immediate steps to relieve the condition, which may include shedding firm load. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | High |  |  |  |  | The Transmission Operator involved in an SOL or IROL violation shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings, electronic communications, alarm program printouts, or other equivalent evidence that will be used to determine if it took immediate steps to relieve the condition. (Requirement 1) | 2007-06-18 |  | 2017-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-008-1 | 183 | R2. | 2029 | Each Transmission Operator shall operate to prevent the likelihood that a disturbance, action, or inaction will result in an IROL or SOL violation in its area or another area of the Interconnection. In instances where there is a difference in derived operating limits, the Transmission Operator shall always operate the Bulk Electric System to the most limiting parameter. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | High |  |  |  | The Transmission Operator failed to operate to prevent the likelihood that a disturbance, action, or inaction would result in an IROL or SOL violation in its area or another area of the Interconnection. | The Transmission Operator that disconnects an overloaded facility shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings, electronic communications, alarm program print outs, or other equivalent evidence that will be used to determine if it disconnected an overloaded facility in accordance with Requirement 3 Part 1 | 2007-06-18 |  | 2017-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-008-1 | 183 | R3. | 2030 | The Transmission Operator shall disconnect the affected facility if the overload on a transmission facility or abnormal voltage or reactive condition persists and equipment is endangered. In doing so, the Transmission Operator shall notify its Reliability Coordinator and all neighboring Transmission Operators impacted by the disconnection prior to switching, if time permits, otherwise, immediately thereafter. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | High |  |  |  |  | The Transmission Operator that disconnects an overloaded facility shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it notified its Reliability Coordinator and all neighboring Transmission Operators impacted by the disconnection prior to switching, if time permitted, otherwise, immediately thereafter. (Requirement 3 Part 2) | 2007-06-18 |  | 2017-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-008-1 | 183 | R4. | 2031 | The Transmission Operator shall have sufficient information and analysis tools to determine the cause(s) of SOL violations. This analysis shall be conducted in all operating timeframes. The Transmission Operator shall use the results of these analyses to immediately mitigate the SOL violation. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | Medium |  |  |  |  | M4. The Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, computer facilities documents, computer printouts, training documents, copies of analysis program results, operator logs or other equivalent evidence that will be used to confirm that it has sufficient information and analysis tools to determine the cause(s) of SOL violations. (Requirement 4 Part 1) M5. The Transmission Operator that violates an SOL shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it used the results of these analyses to immediately mitigate the SOL violation. (Requirement 4 Part 3) | 2007-06-18 |  | 2017-03-31 |  | 4.2.2 Circuits Subject to Requirement R6: 4.2.2.1 Transmission lines operated at 100 kV to 200 kV and transformers with low voltage terminals connected at 100 kV to 200 kV, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. 4.2.2.2 Transmission lines operated below 100 kV and transformers with low voltage terminals connected below 100 kV that are part of the BES, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-008-1 (British Columbia) | 666700000010295 | R1. | 666700000011806 | The Transmission Operator experiencing or contributing to an IROL or SOL violation shall take immediate steps to relieve the condition, which may include shedding firm load. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | High |  |  |  |  | The Transmission Operator involved in an SOL or IROL violation shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings, electronic communications, alarm program printouts, or other equivalent evidence that will be used to determine if it took immediate steps to relieve the condition. (Requirement 1) | 2010-11-01 | [5 empty] | WECC-BC | [6 empty] | 10000000
TOP-008-1 (British Columbia) | 666700000010295 | R2. | 666700000011807 | Each Transmission Operator shall operate to prevent the likelihood that a disturbance, action, or inaction will result in an IROL or SOL violation in its area or another area of the Interconnection. In instances where there is a difference in derived operating limits, the Transmission Operator shall always operate the Bulk Electric System to the most limiting parameter. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | High |  |  |  | The Transmission Operator failed to operate to prevent the likelihood that a disturbance, action, or inaction would result in an IROL or SOL violation in its area or another area of the Interconnection. | The Transmission Operator that disconnects an overloaded facility shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings, electronic communications, alarm program print outs, or other equivalent evidence that will be used to determine if it disconnected an overloaded facility in accordance with Requirement 3 Part 1 | 2010-11-01 | [5 empty] | WECC-BC | [6 empty] | 20000000
TOP-008-1 (British Columbia) | 666700000010295 | R3. | 666700000011808 | The Transmission Operator shall disconnect the affected facility if the overload on a transmission facility or abnormal voltage or reactive condition persists and equipment is endangered. In doing so, the Transmission Operator shall notify its Reliability Coordinator and all neighboring Transmission Operators impacted by the disconnection prior to switching, if time permits, otherwise, immediately thereafter. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | High |  |  |  |  | The Transmission Operator that disconnects an overloaded facility shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it notified its Reliability Coordinator and all neighboring Transmission Operators impacted by the disconnection prior to switching, if time permitted, otherwise, immediately thereafter. (Requirement 3 Part 2) | 2010-11-01 | [5 empty] | WECC-BC | [6 empty] | 30000000
TOP-008-1 (British Columbia) | 666700000010295 | R4. | 666700000011809 | The Transmission Operator shall have sufficient information and analysis tools to determine the cause(s) of SOL violations. This analysis shall be conducted in all operating timeframes. The Transmission Operator shall use the results of these analyses to immediately mitigate the SOL violation. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | Medium |  |  |  |  | M4. The Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, computer facilities documents, computer printouts, training documents, copies of analysis program results, operator logs or other equivalent evidence that will be used to confirm that it has sufficient information and analysis tools to determine the cause(s) of SOL violations. (Requirement 4 Part 1) M5. The Transmission Operator that violates an SOL shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it used the results of these analyses to immediately mitigate the SOL violation. (Requirement 4 Part 3) | 2010-11-01 |  |  |  | 4.2.2 Circuits Subject to Requirement R6: 4.2.2.1 Transmission lines operated at 100 kV to 200 kV and transformers with low voltage terminals connected at 100 kV to 200 kV, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. 4.2.2.2 Transmission lines operated below 100 kV and transformers with low voltage terminals connected below 100 kV that are part of the BES, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. |  | WECC-BC | [6 empty] | 40000000
TOP-008-1 (Manitoba) | 77660000000183 | R1. | 776600000002028 | The Transmission Operator experiencing or contributing to an IROL or SOL violation shall take immediate steps to relieve the condition, which may include shedding firm load. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | High |  |  |  |  | The Transmission Operator involved in an SOL or IROL violation shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings, electronic communications, alarm program printouts, or other equivalent evidence that will be used to determine if it took immediate steps to relieve the condition. (Requirement 1) | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
TOP-008-1 (Manitoba) | 77660000000183 | R2. | 776600000002029 | Each Transmission Operator shall operate to prevent the likelihood that a disturbance, action, or inaction will result in an IROL or SOL violation in its area or another area of the Interconnection. In instances where there is a difference in derived operating limits, the Transmission Operator shall always operate the Bulk Electric System to the most limiting parameter. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | High |  |  |  | The Transmission Operator failed to operate to prevent the likelihood that a disturbance, action, or inaction would result in an IROL or SOL violation in its area or another area of the Interconnection. | The Transmission Operator that disconnects an overloaded facility shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings, electronic communications, alarm program print outs, or other equivalent evidence that will be used to determine if it disconnected an overloaded facility in accordance with Requirement 3 Part 1 | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
TOP-008-1 (Manitoba) | 77660000000183 | R3. | 776600000002030 | The Transmission Operator shall disconnect the affected facility if the overload on a transmission facility or abnormal voltage or reactive condition persists and equipment is endangered. In doing so, the Transmission Operator shall notify its Reliability Coordinator and all neighboring Transmission Operators impacted by the disconnection prior to switching, if time permits, otherwise, immediately thereafter. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | High |  |  |  |  | The Transmission Operator that disconnects an overloaded facility shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it notified its Reliability Coordinator and all neighboring Transmission Operators impacted by the disconnection prior to switching, if time permitted, otherwise, immediately thereafter. (Requirement 3 Part 2) | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
TOP-008-1 (Manitoba) | 77660000000183 | R4. | 776600000002031 | The Transmission Operator shall have sufficient information and analysis tools to determine the cause(s) of SOL violations. This analysis shall be conducted in all operating timeframes. The Transmission Operator shall use the results of these analyses to immediately mitigate the SOL violation. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | Medium |  |  |  |  | M4. The Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, computer facilities documents, computer printouts, training documents, copies of analysis program results, operator logs or other equivalent evidence that will be used to confirm that it has sufficient information and analysis tools to determine the cause(s) of SOL violations. (Requirement 4 Part 1) M5. The Transmission Operator that violates an SOL shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it used the results of these analyses to immediately mitigate the SOL violation. (Requirement 4 Part 3) | 2012-04-01 |  | 2017-06-30 |  | 4.2.2 Circuits Subject to Requirement R6: 4.2.2.1 Transmission lines operated at 100 kV to 200 kV and transformers with low voltage terminals connected at 100 kV to 200 kV, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. 4.2.2.2 Transmission lines operated below 100 kV and transformers with low voltage terminals connected below 100 kV that are part of the BES, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. |  | MRO-MB | [6 empty] | 40000000
TOP-008-1 (Ontario) | 79780000183 | R1. | 79780002028 | The Transmission Operator experiencing or contributing to an IROL or SOL violation shall take immediate steps to relieve the condition, which may include shedding firm load. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | High |  |  |  | The Transmission Operator experiencing or contributing to an IROL or SOL violation failed to take immediate steps to relieve the condition, which may have included shedding firm load. | M3. Each Transmission Owner, Generator Owner, and Distribution Provider with transmission relays set according to Requirement R1, criterion 7, 8, 9, 12, or 13 shall have evidence such as Facility Rating spreadsheets or Facility Rating database to show that it used the calculated circuit capability as the Facility Rating of the circuit and evidence such as dated correspondence that the resulting Facility Rating was agreed to by its associated Planning Coordinator, Transmission Operator, and Reliability Coordinator. (R3) | 2007-06-18 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-008-1 (Ontario) | 79780000183 | R2. | 79780002029 | Each Transmission Operator shall operate to prevent the likelihood that a disturbance, action, or inaction will result in an IROL or SOL violation in its area or another area of the Interconnection. In instances where there is a difference in derived operating limits, the Transmission Operator shall always operate the Bulk Electric System to the most limiting parameter. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | High |  | The Transmission Operator operated to prevent the likelihood that a disturbance, action, or inaction would result in an IROL or SOL violation in its area or another area of the Interconnection but failed to operate the Bulk Electric System to the most lim | The Transmission Operator operated to prevent the likelihood that a disturbance, action, or inaction would result in an IROL or SOL violation in its area but failed to operate to prevent the likelihood that a disturbance, action, or inaction would result | The Transmission Operator failed to operate to prevent the likelihood that a disturbance, action, or inaction would result in an IROL or SOL violation in its area or another area of the Interconnection. | M4. Each Transmission Owner, Generator Owner, or Distribution Provider that sets transmission line relays according to Requirement R1, criterion 2 shall have evidence such as dated correspondence to show that it provided its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays within the required timeframe. The updated list may either be a full list, a list of incremental changes to the previous list, or a statement that there are no changes to the previous list. (R4) | 2007-06-18 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-008-1 (Ontario) | 79780000183 | R3. | 79780002030 | The Transmission Operator shall disconnect the affected facility if the overload on a transmission facility or abnormal voltage or reactive condition persists and equipment is endangered. In doing so, the Transmission Operator shall notify its Reliability Coordinator and all neighboring Transmission Operators impacted by the disconnection prior to switching, if time permits, otherwise, immediately thereafter. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | High |  | The Transmission Operator disconnected the affected facility when the overload on a transmission facility or abnormal voltage or reactive condition persisted and equipment was endangered but failed to notify its Reliability Coordinator and all neighboring |  | The Transmission Operator failed to disconnect the affected facility when the overload on a transmission facility or abnormal voltage or reactive condition persisted and equipment was endangered. | M5. Each Transmission Owner, Generator Owner, or Distribution Provider that sets transmission line relays according to Requirement R1, criterion 12 shall have evidence such as dated correspondence that it provided an updated list of the circuits associated with those relays to its Regional Entity within the required timeframe. The updated list may either be a full list, a list of incremental changes to the previous list, or a statement that there are no changes to the previous list. (R5) | 2007-06-18 |  | 2017-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-008-1 (Ontario) | 79780000183 | R4. | 79780002031 | The Transmission Operator shall have sufficient information and analysis tools to determine the cause(s) of SOL violations. This analysis shall be conducted in all operating timeframes. The Transmission Operator shall use the results of these analyses to immediately mitigate the SOL violation. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | Medium |  |  | The Transmission Operator had sufficient information and analysis tools to determine the cause(s) of SOL violations and used the results of these analyses to immediately mitigate the SOL violation(s), but failed to conduct these analyses in all operating | The Transmission Operator failed to have sufficient information and analysis tools to determine the cause(s) of SOL violations or failed to use the results of analyses to immediately mitigate the SOL violation. | M6. Each Planning Coordinator shall have evidence such as power flow results, calculation summaries, or study reports that it used the criteria established within PRC-023-4, Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard as described in Requirement R6. The Planning Coordinator shall have a dated list of such circuits and shall have evidence such as dated correspondence that it provided the list to the Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within the required timeframe. (R6) | 2007-06-18 |  | 2017-03-31 |  | 4.2.2 Circuits Subject to Requirement R6:&lt;br/&gt;4.2.2.1 Transmission lines operated at 100 kV to 200 kV and transformers with low voltage terminals connected at 100 kV to 200 kV, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads.&lt;br/&gt;4.2.2.2 Transmission lines operated below 100 kV and transformers with low voltage terminals connected below 100 kV that are part of the BES, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. |  | NPCC-ON | [6 empty] | 40000000
TOP-008-1 (Saskatchewan) | 83750000000183 | R1. | 837500000002028 | The Transmission Operator experiencing or contributing to an IROL or SOL violation shall take immediate steps to relieve the condition, which may include shedding firm load. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | High |  |  |  |  | The Transmission Operator involved in an SOL or IROL violation shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings, electronic communications, alarm program printouts, or other equivalent evidence that will be used to determine if it took immediate steps to relieve the condition. (Requirement 1) | 2015-04-15 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 10000000
TOP-008-1 (Saskatchewan) | 83750000000183 | R2. | 837500000002029 | Each Transmission Operator shall operate to prevent the likelihood that a disturbance, action, or inaction will result in an IROL or SOL violation in its area or another area of the Interconnection. In instances where there is a difference in derived operating limits, the Transmission Operator shall always operate the Bulk Electric System to the most limiting parameter. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | High |  |  |  | The Transmission Operator failed to operate to prevent the likelihood that a disturbance, action, or inaction would result in an IROL or SOL violation in its area or another area of the Interconnection. | The Transmission Operator that disconnects an overloaded facility shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings, electronic communications, alarm program print outs, or other equivalent evidence that will be used to determine if it disconnected an overloaded facility in accordance with Requirement 3 Part 1 | 2015-04-15 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 20000000
TOP-008-1 (Saskatchewan) | 83750000000183 | R3. | 837500000002030 | The Transmission Operator shall disconnect the affected facility if the overload on a transmission facility or abnormal voltage or reactive condition persists and equipment is endangered. In doing so, the Transmission Operator shall notify its Reliability Coordinator and all neighboring Transmission Operators impacted by the disconnection prior to switching, if time permits, otherwise, immediately thereafter. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | High |  |  |  |  | The Transmission Operator that disconnects an overloaded facility shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to determine if it notified its Reliability Coordinator and all neighboring Transmission Operators impacted by the disconnection prior to switching, if time permitted, otherwise, immediately thereafter. (Requirement 3 Part 2) | 2015-04-15 |  | 2017-03-31 |  |  |  | MRO-SK | [6 empty] | 30000000
TOP-008-1 (Saskatchewan) | 83750000000183 | R4. | 837500000002031 | The Transmission Operator shall have sufficient information and analysis tools to determine the cause(s) of SOL violations. This analysis shall be conducted in all operating timeframes. The Transmission Operator shall use the results of these analyses to immediately mitigate the SOL violation. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | Medium |  |  |  |  | M4. The Transmission Operator shall have and provide upon request evidence that could include, but is not limited to, computer facilities documents, computer printouts, training documents, copies of analysis program results, operator logs or other equivalent evidence that will be used to confirm that it has sufficient information and analysis tools to determine the cause(s) of SOL violations. (Requirement 4 Part 1) M5. The Transmission Operator that violates an SOL shall have and provide upon request evidence that could include, but is not limited to, operator logs, voice recordings or transcripts of voice recordings, electronic communications, or other equivalent evidence that will be used to confirm that it used the results of these analyses to immediately mitigate the SOL violation. (Requirement 4 Part 3) | 2015-04-15 |  | 2017-03-31 |  | 4.2.2 Circuits Subject to Requirement R6: 4.2.2.1 Transmission lines operated at 100 kV to 200 kV and transformers with low voltage terminals connected at 100 kV to 200 kV, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. 4.2.2.2 Transmission lines operated below 100 kV and transformers with low voltage terminals connected below 100 kV that are part of the BES, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. |  | MRO-SK | [6 empty] | 40000000
TOP-010-1 | 548 | R1. | 7724 | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include one of the elements listed in Part 1.1 through Part 1.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include two of the elements listed in Part 1.1 through Part 1.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include any of the elements listed in Part 1.1 through Part 1.3; OR The Transmission Operator did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. | M1. Each Transmission Operator shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. |  |  | 2018-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-010-1 | 548 | R2. | 7728 | Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: |  | BA | BA | [20 empty] | Real-Time Operations | Medium | N/A | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include one of the elements listed in Part 2.1 through Part 2.3. | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include two of the elements listed in Part 2.1 through Part 2.3. | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include any of the elements listed in Part 2.1 through Part 2.3; OR The Balancing Authority did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. | M2. Each Balancing Authority shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Balancing Authority implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. |  |  | 2018-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-010-1 | 548 | R3. | 7732 | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include one of the elements listed in Part 3.1 through Part 3.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include two of the elements listed in Part 3.1 through Part 3.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include any of the elements listed in Part 3.1 through Part 3.3; OR The Transmission Operator did not implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. | M3. Each Transmission Operator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in requirement R3. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R3; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. |  |  | 2018-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-010-1 | 548 | R4. | 7736 | Each Transmission Operator and Balancing Authority shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | The responsible entity has an alarm process monitor but the alarm process monitor did not provide notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor occurred. | The responsible entity does not have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | M4. Each Transmission Operator and Balancing Authority shall have evidence of an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. This evidence could include, but is not limited to, operator logs, computer printouts, system specifications, or other evidence. |  |  | 2018-03-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-010-1(i) | 556 | R1. | 7860 | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include one of the elements listed in Part 1.1 through Part 1.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include two of the elements listed in Part 1.1 through Part 1.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include any of the elements listed in Part 1.1 through Part 1.3; OR The Transmission Operator did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. | M1. Each Transmission Operator shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2018-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TOP-010-1(i) | 556 | R2. | 7864 | Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: |  | BA | BA | [20 empty] | Real-Time Operations | High | N/A | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include one of the elements listed in Part 2.1 through Part 2.3. | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include two of the elements listed in Part 2.1 through Part 2.3. | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include any of the elements listed in Part 2.1 through Part 2.3; OR The Balancing Authority did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. | M2. Each Balancing Authority shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Balancing Authority implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2018-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TOP-010-1(i) | 556 | R3. | 7868 | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include one of the elements listed in Part 3.1 through Part 3.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include two of the elements listed in Part 3.1 through Part 3.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include any of the elements listed in Part 3.1 through Part 3.3; OR The Transmission Operator did not implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. | M3. Each Transmission Operator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R3. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R3; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2018-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TOP-010-1(i) | 556 | R4. | 7873 | Each Transmission Operator and Balancing Authority shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | The responsible entity has an alarm process monitor but the alarm process monitor did not provide notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor occurred. | The responsible entity does not have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | M4. Each Transmission Operator and Balancing Authority shall have evidence of an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. This evidence could include, but is not limited to, operator logs, computer printouts, system specifications, or other evidence. | 2018-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TOP-010-1i (British Columbia) | 666700000010296 | R1. | 666700000011810 | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include one of the elements listed in Part 1.1 through Part 1.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include two of the elements listed in Part 1.1 through Part 1.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include any of the elements listed in Part 1.1 through Part 1.3; OR The Transmission Operator did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. | M1. Each Transmission Operator shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2021-04-01 | [5 empty] | WECC-BC | [6 empty] | 10000000
TOP-010-1i (British Columbia) | 666700000010296 | R2. | 666700000011811 | Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: |  | BA | BA | [20 empty] | Real-Time Operations | High | N/A | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include one of the elements listed in Part 2.1 through Part 2.3. | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include two of the elements listed in Part 2.1 through Part 2.3. | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include any of the elements listed in Part 2.1 through Part 2.3; OR The Balancing Authority did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. | M2. Each Balancing Authority shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Balancing Authority implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2021-04-01 | [5 empty] | WECC-BC | [6 empty] | 20000000
TOP-010-1i (British Columbia) | 666700000010296 | R3. | 666700000011812 | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include one of the elements listed in Part 3.1 through Part 3.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include two of the elements listed in Part 3.1 through Part 3.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include any of the elements listed in Part 3.1 through Part 3.3; OR The Transmission Operator did not implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. | M3. Each Transmission Operator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R3. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R3; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2021-04-01 | [5 empty] | WECC-BC | [6 empty] | 30000000
TOP-010-1i (British Columbia) | 666700000010296 | R4. | 666700000011813 | Each Transmission Operator and Balancing Authority shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | The responsible entity has an alarm process monitor but the alarm process monitor did not provide notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor occurred. | The responsible entity does not have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | M4. Each Transmission Operator and Balancing Authority shall have evidence of an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. This evidence could include, but is not limited to, operator logs, computer printouts, system specifications, or other evidence. | 2021-04-01 | [5 empty] | WECC-BC | [6 empty] | 40000000
TOP-010-1(i) (Manitoba) | 77660000000556 | R1. | 776600000007860 | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include one of the elements listed in Part 1.1 through Part 1.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include two of the elements listed in Part 1.1 through Part 1.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include any of the elements listed in Part 1.1 through Part 1.3; OR The Transmission Operator did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. | M1. Each Transmission Operator shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2019-07-01 | [5 empty] | MRO-MB | [6 empty] | 10000000
TOP-010-1(i) (Manitoba) | 77660000000556 | R2. | 776600000007864 | Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: |  | BA | BA | [20 empty] | Real-Time Operations | High | N/A | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include one of the elements listed in Part 2.1 through Part 2.3. | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include two of the elements listed in Part 2.1 through Part 2.3. | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include any of the elements listed in Part 2.1 through Part 2.3; OR The Balancing Authority did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. | M2. Each Balancing Authority shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Balancing Authority implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2019-07-01 | [5 empty] | MRO-MB | [6 empty] | 20000000
TOP-010-1(i) (Manitoba) | 77660000000556 | R3. | 776600000007868 | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include one of the elements listed in Part 3.1 through Part 3.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include two of the elements listed in Part 3.1 through Part 3.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include any of the elements listed in Part 3.1 through Part 3.3; OR The Transmission Operator did not implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. | M3. Each Transmission Operator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R3. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R3; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2019-07-01 | [5 empty] | MRO-MB | [6 empty] | 30000000
TOP-010-1(i) (Manitoba) | 77660000000556 | R4. | 776600000007873 | Each Transmission Operator and Balancing Authority shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | The responsible entity has an alarm process monitor but the alarm process monitor did not provide notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor occurred. | The responsible entity does not have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | M4. Each Transmission Operator and Balancing Authority shall have evidence of an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. This evidence could include, but is not limited to, operator logs, computer printouts, system specifications, or other evidence. | 2019-07-01 | [5 empty] | MRO-MB | [6 empty] | 40000000
TOP-010-1(i) (Nova Scotia) | 78830000000556 | R1. | 788300000007860 | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include one of the elements listed in Part 1.1 through Part 1.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include two of the elements listed in Part 1.1 through Part 1.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include any of the elements listed in Part 1.1 through Part 1.3; OR The Transmission Operator did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. | M1. Each Transmission Operator shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2018-04-01 | [5 empty] | NPCC-NS | [6 empty] | 10000000
TOP-010-1(i) (Nova Scotia) | 78830000000556 | R2. | 788300000007864 | Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: |  | BA | BA | [20 empty] | Real-Time Operations | High | N/A | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include one of the elements listed in Part 2.1 through Part 2.3. | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include two of the elements listed in Part 2.1 through Part 2.3. | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include any of the elements listed in Part 2.1 through Part 2.3; OR The Balancing Authority did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. | M2. Each Balancing Authority shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Balancing Authority implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2018-04-01 | [5 empty] | NPCC-NS | [6 empty] | 20000000
TOP-010-1(i) (Nova Scotia) | 78830000000556 | R3. | 788300000007868 | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include one of the elements listed in Part 3.1 through Part 3.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include two of the elements listed in Part 3.1 through Part 3.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include any of the elements listed in Part 3.1 through Part 3.3; OR The Transmission Operator did not implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. | M3. Each Transmission Operator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R3. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R3; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2018-04-01 | [5 empty] | NPCC-NS | [6 empty] | 30000000
TOP-010-1(i) (Nova Scotia) | 78830000000556 | R4. | 788300000007873 | Each Transmission Operator and Balancing Authority shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | The responsible entity has an alarm process monitor but the alarm process monitor did not provide notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor occurred. | The responsible entity does not have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | M4. Each Transmission Operator and Balancing Authority shall have evidence of an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. This evidence could include, but is not limited to, operator logs, computer printouts, system specifications, or other evidence. | 2018-04-01 | [5 empty] | NPCC-NS | [6 empty] | 40000000
TOP-010-1(i) (Ontario) | 79780000556 | R1. | 79780007860 | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning, Real-Time Operations | High | N/A | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include one of the elements listed in Part 1.1 through Part 1.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include two of the elements listed in Part 1.1 through Part 1.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include any of the elements listed in Part 1.1 through Part 1.3; OR The Transmission Operator did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. | M1. Each Transmission Operator shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2018-04-01 | [5 empty] | NPCC-ON | [6 empty] | 10000000
TOP-010-1(i) (Ontario) | 79780000556 | R2. | 79780007864 | Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: |  | BA | BA | [20 empty] | Real-Time Operations | High | N/A | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include one of the elements listed in Part 2.1 through Part 2.3. | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include two of the elements listed in Part 2.1 through Part 2.3. | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include any of the elements listed in Part 2.1 through Part 2.3; OR The Balancing Authority did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. | M2. Each Balancing Authority shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Balancing Authority implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2018-04-01 | [5 empty] | NPCC-ON | [6 empty] | 20000000
TOP-010-1(i) (Ontario) | 79780000556 | R3. | 79780007868 | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;&lt;br/&gt;The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include one of the elements listed in Part 3.1 through Part 3.3.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;The Transmission Operator's&lt;/p&gt; &lt;p&gt;Operating Process or Operating Procedure to address the quality of analysis used in its Real-time &lt;br/&gt;Assessments did not include two of the elements listed in Part 3.1 through Part 3.3.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include any of the elements listed in Part 3.1 through Part 3.3;&lt;/p&gt; &lt;p&gt;OR&lt;/p&gt; &lt;p&gt;The Transmission Operator did not implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments.&lt;/p&gt; &lt;p/&gt; | M3. Each Transmission Operator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R3. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R3; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2018-04-01 | [5 empty] | NPCC-ON | [6 empty] | 30000000
TOP-010-1(i) (Ontario) | 79780000556 | R4. | 79780007873 | Each Transmission Operator and Balancing Authority shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Long-Term Planning, Real-Time Operations | Medium | N/A | N/A | The responsible entity has an alarm process monitor but the alarm process monitor did not provide notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor occurred. | The responsible entity does not have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | M4. Each Transmission Operator and Balancing Authority shall have evidence of an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. This evidence could include, but is not limited to, operator logs, computer printouts, system specifications, or other evidence. | 2018-04-01 | [5 empty] | NPCC-ON | [6 empty] | 40000000
TOP-010-1(i) (Saskatchewan) | 83750000000556 | R1. | 837500000007860 | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | High | N/A | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include one of the elements listed in Part 1.1 through Part 1.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include two of the elements listed in Part 1.1 through Part 1.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include any of the elements listed in Part 1.1 through Part 1.3; OR The Transmission Operator did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. | M1. Each Transmission Operator shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2018-04-01 | [5 empty] | MRO-SK | [6 empty] | 10000000
TOP-010-1(i) (Saskatchewan) | 83750000000556 | R2. | 837500000007864 | Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: |  | BA | BA | [20 empty] | Real-Time Operations | High | N/A | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include one of the elements listed in Part 2.1 through Part 2.3. | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include two of the elements listed in Part 2.1 through Part 2.3. | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include any of the elements listed in Part 2.1 through Part 2.3; OR The Balancing Authority did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. | M2. Each Balancing Authority shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Balancing Authority implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2018-04-01 | [5 empty] | MRO-SK | [6 empty] | 20000000
TOP-010-1(i) (Saskatchewan) | 83750000000556 | R3. | 837500000007868 | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include one of the elements listed in Part 3.1 through Part 3.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include two of the elements listed in Part 3.1 through Part 3.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include any of the elements listed in Part 3.1 through Part 3.3; OR The Transmission Operator did not implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. | M3. Each Transmission Operator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R3. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R3; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2018-04-01 | [5 empty] | MRO-SK | [6 empty] | 30000000
TOP-010-1(i) (Saskatchewan) | 83750000000556 | R4. | 837500000007873 | Each Transmission Operator and Balancing Authority shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | The responsible entity has an alarm process monitor but the alarm process monitor did not provide notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor occurred. | The responsible entity does not have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | M4. Each Transmission Operator and Balancing Authority shall have evidence of an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. This evidence could include, but is not limited to, operator logs, computer printouts, system specifications, or other evidence. | 2018-04-01 | [5 empty] | MRO-SK | [6 empty] | 40000000
TOP-010-1 (Ontario) | 79780000548 | R1. | 79780007724 | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning, Real-Time Operations | High | N/A | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include one of the elements listed in Part 1.1 through Part 1.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include two of the elements listed in Part 1.1 through Part 1.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include any of the elements listed in Part 1.1 through Part 1.3; OR The Transmission Operator did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. | M1. Each Transmission Operator shall have evidence that it implemented its Operating&lt;br/&gt;Process or Operating Procedure to address the quality of the Real-time data necessary&lt;br/&gt;to perform its Real-time monitoring and Real-time Assessments. This evidence could&lt;br/&gt;include, but is not limited to: 1) an Operating Process or Operating Procedure in&lt;br/&gt;electronic or hard copy format meeting all provisions of Requirement R1; and 2)&lt;br/&gt;evidence the Transmission Operator implemented the Operating Process or Operating&lt;br/&gt;Procedure as called for in the Operating Process or Operating Procedure, such as&lt;br/&gt;dated operator logs, dated checklists, voice recordings, voice transcripts, or other&lt;br/&gt;evidence. |  |  | 2018-03-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TOP-010-1 (Ontario) | 79780000548 | R2. | 79780007728 | Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: |  | BA | BA | [20 empty] | Real-Time Operations | High | N/A | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include one of the elements listed in Part 2.1 through Part 2.3. | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include two of the elements listed in Part 2.1 through Part 2.3. | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include any of the elements listed in Part 2.1 through Part 2.3; OR The Balancing Authority did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. | M2. Each Balancing Authority shall have evidence that it implemented its Operating&lt;br/&gt;Process or Operating Procedure to address the quality of the Real-time data necessary&lt;br/&gt;to perform its analysis functions and Real-time monitoring. This evidence could&lt;br/&gt;include, but is not limited to: 1) an Operating Process or Operating Procedure in&lt;br/&gt;electronic or hard copy format meeting all provisions of Requirement R2; and 2)&lt;br/&gt;evidence the Balancing Authority implemented the Operating Process or Operating&lt;br/&gt;Procedure as called for in the Operating Process or Operating Procedure, such as&lt;br/&gt;dated operator logs, dated checklists, voice recordings, voice transcripts, or other&lt;br/&gt;evidence. |  |  | 2018-03-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TOP-010-1 (Ontario) | 79780000548 | R3. | 79780007732 | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include one of the elements listed in Part 3.1 through Part 3.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include two of the elements listed in Part 3.1 through Part 3.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include any of the elements listed in Part 3.1 through Part 3.3; OR The Transmission Operator did not implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. | M3. Each Transmission Operator shall have evidence it implemented its Operating Process&lt;br/&gt;or Operating Procedure to address the quality of analysis used in its Real-time&lt;br/&gt;Assessments as specified in Requirement R3. This evidence could include, but is not&lt;br/&gt;limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy&lt;br/&gt;format meeting all provisions of Requirement R3; and 2) evidence the Transmission&lt;br/&gt;Operator implemented the Operating Process or Operating Procedure as called for in&lt;br/&gt;the Operating Process or Operating Procedure, such as dated operator logs, dated&lt;br/&gt;checklists, voice recordings, voice transcripts, or other evidence. |  |  | 2018-03-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
TOP-010-1 (Ontario) | 79780000548 | R4. | 79780007736 | Each Transmission Operator and Balancing Authority shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | The responsible entity has an alarm process monitor but the alarm process monitor did not provide notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor occurred. | The responsible entity does not have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | M4. Each Transmission Operator and Balancing Authority shall have evidence of an alarm&lt;br/&gt;process monitor that provides notification(s) to its System Operators when a failure of&lt;br/&gt;its Real-time monitoring alarm processor has occurred. This evidence could include,&lt;br/&gt;but is not limited to, operator logs, computer printouts, system specifications, or&lt;br/&gt;other evidence. |  |  | 2018-03-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
TOP-010-1 (Saskatchewan) | 83750000000548 | R1. | 837500000007724 | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include one of the elements listed in Part 1.1 through Part 1.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include two of the elements listed in Part 1.1 through Part 1.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include any of the elements listed in Part 1.1 through Part 1.3; OR The Transmission Operator did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. | M1. Each Transmission Operator shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. |  |  | 2018-03-31 |  |  |  | MRO-SK | [6 empty] | 10000000
TOP-010-1 (Saskatchewan) | 83750000000548 | R2. | 837500000007728 | Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: |  | BA | BA | [20 empty] | Real-Time Operations | Medium | N/A | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include one of the elements listed in Part 2.1 through Part 2.3. | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include two of the elements listed in Part 2.1 through Part 2.3. | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include any of the elements listed in Part 2.1 through Part 2.3; OR The Balancing Authority did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. | M2. Each Balancing Authority shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Balancing Authority implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. |  |  | 2018-03-31 |  |  |  | MRO-SK | [6 empty] | 20000000
TOP-010-1 (Saskatchewan) | 83750000000548 | R3. | 837500000007732 | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: |  | TOP | [18 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include one of the elements listed in Part 3.1 through Part 3.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include two of the elements listed in Part 3.1 through Part 3.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include any of the elements listed in Part 3.1 through Part 3.3; OR The Transmission Operator did not implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. | M3. Each Transmission Operator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in requirement R3. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R3; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. |  |  | 2018-03-31 |  |  |  | MRO-SK | [6 empty] | 30000000
TOP-010-1 (Saskatchewan) | 83750000000548 | R4. | 837500000007736 | Each Transmission Operator and Balancing Authority shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. |  | BA, TOP | BA | [17 empty] | TOP |  |  | Real-Time Operations | Medium | N/A | N/A | The responsible entity has an alarm process monitor but the alarm process monitor did not provide notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor occurred. | The responsible entity does not have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | M4. Each Transmission Operator and Balancing Authority shall have evidence of an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. This evidence could include, but is not limited to, operator logs, computer printouts, system specifications, or other evidence. |  |  | 2018-03-31 |  |  |  | MRO-SK | [6 empty] | 40000000
TOP-STD-007-0 | 184 | WR1. | 2032 | Operating Transfer Capability Limit Criteria Actual power flow and net scheduled power flow over an interconnection or transfer path shall be maintained within Operating Transfer Capability Limits (“OTC”). The OTC is the maximum amount of actual power that can be transferred over direct or parallel transmission elements comprising: • An interconnection from one Transmission Operator area to another Transmission Operator area; or • A transfer path within a Transmission Operator area. The net schedule over an interconnection or transfer path within a Transmission Operator area shall not exceed the OTC, regardless of the prevailing actual power flow on the interconnection or transfer path. a. Operating limits. No elements within the interconnection shall be scheduled above continuous operating limits. An element is defined as any generating unit, transmission line, transformer, bus, or piece of electrical equipment involved in the transfer of power within an interconnection. b. Stability. The interconnected power system shall remain stable upon loss of any one single element without system cascading that could result in the successive loss of additional elements. The system voltages shall be within acceptable limits defined in the WECC Reliability Criteria for Transmission System Planning. If a single event could cause loss of multiple elements, these shall be considered in lieu of a single element outage. This could occur in exceptional cases such as two lines on the same right-of-way next to an airport. In either case, loss of either single or multiple elements should not cause uncontrolled, widespread collapse of the interconnected power system. For purposes of this WECC Standard TOP-STD-007-0 - Operating Transfer Capability Section, stability shall include transient stability, post transient stability or dynamic stability whichever is most limiting to OTC. c. System contingency response. Following the outage and before adjustments can be made: (i) No remaining element shall exceed its short-time emergency rating. (ii) The steady-state system voltages shall be within emergency limits. The limiting event shall be determined by conducting power flow and stability studies while simulating various operating conditions. These studies shall be updated as system configurations introduce significant changes in the interconnection.(Source: WECC Criterion) |  | TOP | [18 empty] | TOP | [9 empty] | 2007-06-18 |  | 2011-06-30 |  |  |  | WECC-US | [5 empty] | WECC-US | 10000000
TOP-STD-007-0 (British Columbia) | 666700000010297 | WR1. | 666700000011814 | Operating Transfer Capability Limit Criteria Actual power flow and net scheduled power flow over an interconnection or transfer path shall be maintained within Operating Transfer Capability Limits (“OTC”). The OTC is the maximum amount of actual power that can be transferred over direct or parallel transmission elements comprising: • An interconnection from one Transmission Operator area to another Transmission Operator area; or • A transfer path within a Transmission Operator area. The net schedule over an interconnection or transfer path within a Transmission Operator area shall not exceed the OTC, regardless of the prevailing actual power flow on the interconnection or transfer path. a. Operating limits. No elements within the interconnection shall be scheduled above continuous operating limits. An element is defined as any generating unit, transmission line, transformer, bus, or piece of electrical equipment involved in the transfer of power within an interconnection. b. Stability. The interconnected power system shall remain stable upon loss of any one single element without system cascading that could result in the successive loss of additional elements. The system voltages shall be within acceptable limits defined in the WECC Reliability Criteria for Transmission System Planning. If a single event could cause loss of multiple elements, these shall be considered in lieu of a single element outage. This could occur in exceptional cases such as two lines on the same right-of-way next to an airport. In either case, loss of either single or multiple elements should not cause uncontrolled, widespread collapse of the interconnected power system. For purposes of this WECC Standard TOP-STD-007-0 - Operating Transfer Capability Section, stability shall include transient stability, post transient stability or dynamic stability whichever is most limiting to OTC. c. System contingency response. Following the outage and before adjustments can be made: (i) No remaining element shall exceed its short-time emergency rating. (ii) The steady-state system voltages shall be within emergency limits. The limiting event shall be determined by conducting power flow and stability studies while simulating various operating conditions. These studies shall be updated as system configurations introduce significant changes in the interconnection.(Source: WECC Criterion) |  | TOP | [18 empty] | TOP | [9 empty] | 2010-11-01 |  | 2013-04-14 |  |  |  | WECC-BC | [6 empty] | 10000000
TPL-001-0 | 185 | R1. | 2033 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2007-06-18 |  | 2009-05-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-001-0 | 185 | R2. | 2047 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2007-06-18 |  | 2009-05-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-001-0 | 185 | R3. | 2053 | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2007-06-18 |  | 2009-05-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-001-0.1 | 186 | R1. | 2054 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High |  |  |  |  | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. | 2009-05-13 |  | 2015-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-001-0.1 | 186 | R2. | 2068 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium |  |  |  |  | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its Reliability Assessments and corrective plans per Reliability Standard TPL-001-0_R3. | 2009-05-13 |  | 2015-12-31 |  |  | TPL-001-0 R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-001-0.1 | 186 | R3. | 2074 | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | [5 empty] | 2009-05-13 |  | 2015-12-31 |  |  | TPL-001-0 R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-001-0.1 (British Columbia) | 666700000010299 | R1. | 666700000011818 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High |  |  |  |  | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. | 2011-01-01 |  | 2019-06-30 |  |  |  | WECC-BC | [6 empty] | 10000000
TPL-001-0.1 (British Columbia) | 666700000010299 | R2. | 666700000011819 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium |  |  |  |  | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its Reliability Assessments and corrective plans per Reliability Standard TPL-001-0_R3. | 2011-01-01 |  | 2019-06-30 |  |  |  | WECC-BC | [6 empty] | 20000000
TPL-001-0.1 (British Columbia) | 666700000010299 | R3. | 666700000011820 | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | [5 empty] | 2011-01-01 |  | 2019-06-30 |  |  |  | WECC-BC | [6 empty] | 30000000
TPL-001-0.1(i) | 483 | R1. | 5811 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High |  |  |  |  | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  |  | 2015-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-001-0.1(i) | 483 | R2. | 5825 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-0.1(i)_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium |  |  |  |  | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its Reliability Assessments and corrective plans per Reliability Standard TPL-001-0_R3. |  |  | 2015-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-001-0.1(i) | 483 | R3. | 5831 | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | [7 empty] | 2015-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-001-0.1(i) (Ontario) | 79780000483 | R1. | 79780005811 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High |  |  |  |  | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. |  |  | 2015-12-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-001-0.1(i) (Ontario) | 79780000483 | R2. | 79780005825 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-0.1(i)_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium |  |  |  |  | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its Reliability Assessments and corrective plans per Reliability Standard TPL-001-0_R3. |  |  | 2015-12-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-001-0.1(i) (Ontario) | 79780000483 | R3. | 79780005831 | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | [7 empty] | 2015-12-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
TPL-001-0.1(i) (Saskatchewan) | 83750000000483 | R1. | 837500000005811 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High |  |  |  |  | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. | [6 empty] | MRO-SK | [6 empty] | 10000000
TPL-001-0.1(i) (Saskatchewan) | 83750000000483 | R2. | 837500000005825 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-0.1(i)_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium |  |  |  |  | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its Reliability Assessments and corrective plans per Reliability Standard TPL-001-0_R3. | [6 empty] | MRO-SK | [6 empty] | 20000000
TPL-001-0.1(i) (Saskatchewan) | 83750000000483 | R3. | 837500000005831 | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | [11 empty] | MRO-SK | [6 empty] | 30000000
TPL-001-0.1 (Manitoba) | 77660000000186 | R1. | 776600000002054 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High |  |  |  |  | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. | 2014-02-14 |  | 2014-07-22 |  |  |  | MRO-MB | [6 empty] | 10000000
TPL-001-0.1 (Manitoba) | 77660000000186 | R2. | 776600000002068 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium |  |  |  |  | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its Reliability Assessments and corrective plans per Reliability Standard TPL-001-0_R3. | 2014-02-14 |  | 2014-07-22 |  |  |  | MRO-MB | [6 empty] | 20000000
TPL-001-0.1 (Manitoba) | 77660000000186 | R3. | 776600000002074 | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | [5 empty] | 2014-02-14 |  | 2014-07-22 |  |  |  | MRO-MB | [6 empty] | 30000000
TPL-001-0.1 (Ontario) | 79780000186 | R1. | 79780002054 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. | 2009-05-13 |  | 2015-12-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-001-0.1 (Ontario) | 79780000186 | R2. | 79780002068 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its Reliability Assessments and corrective plans per Reliability Standard TPL-001-0_R3. | 2009-05-13 |  | 2015-12-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-001-0.1 (Ontario) | 79780000186 | R3. | 79780002074 | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2009-05-13 |  | 2015-12-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
TPL-001-0.1 (Saskatchewan) | 83750000000186 | R1. | 837500000002054 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High |  |  |  |  | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-001-0_R1 and TPL-001-0_R2. | 2015-04-15 |  | 2018-01-20 |  |  |  | MRO-SK | [6 empty] | 10000000
TPL-001-0.1 (Saskatchewan) | 83750000000186 | R2. | 837500000002068 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium |  |  |  |  | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its Reliability Assessments and corrective plans per Reliability Standard TPL-001-0_R3. | 2015-04-15 |  | 2018-01-20 |  |  |  | MRO-SK | [6 empty] | 20000000
TPL-001-0.1 (Saskatchewan) | 83750000000186 | R3. | 837500000002074 | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | [5 empty] | 2015-04-15 |  | 2018-01-20 |  |  |  | MRO-SK | [6 empty] | 30000000
TPL-001-0 (British Columbia) | 666700000010298 | R1. | 666700000011815 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 10000000
TPL-001-0 (British Columbia) | 666700000010298 | R2. | 666700000011816 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 20000000
TPL-001-0 (British Columbia) | 666700000010298 | R3. | 666700000011817 | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 30000000
TPL-001-0 (Manitoba) | 77660000000185 | R1. | 776600000002033 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 10000000
TPL-001-0 (Manitoba) | 77660000000185 | R2. | 776600000002047 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 20000000
TPL-001-0 (Manitoba) | 77660000000185 | R3. | 776600000002053 | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 30000000
TPL-001-0 (Ontario) | 79780000185 | R1. | 79780002033 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2007-06-18 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-001-0 (Ontario) | 79780000185 | R2. | 79780002047 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2007-06-18 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-001-0 (Ontario) | 79780000185 | R3. | 79780002053 | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2007-06-18 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 30000000
TPL-001-1 | 264 | R1. | 3452 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2012-07-06 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-001-1 | 264 | R2. | 3466 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-1_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2012-07-06 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-001-1 | 264 | R3. | 3472 | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  |  |  | 2012-07-06 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-001-1 (Ontario) | 79780000264 | R1. | 79780003452 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2012-07-06 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-001-1 (Ontario) | 79780000264 | R2. | 79780003466 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-1_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2012-07-06 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-001-1 (Ontario) | 79780000264 | R3. | 79780003472 | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  |  |  | 2012-07-06 |  |  |  | NPCC-ON | [6 empty] | 30000000
TPL-001-2 | 298 | R1. | 3882 | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. [See standard for further information regarding R1] |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity’s System model failed to represent one of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent two of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent three of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent four or more of the Requirement R1, Parts 1.1.1 through 1.1.6. OR The responsible entity’s System model did not represent projected System conditions as described in Requirement R1. OR The resp |  |  |  | 2013-12-23 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-001-2 | 298 | R2. | 3883 | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. [See standard for further information regarding R2] |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity failed to comply with Requirement R2, Part 2.6. | The responsible entity failed to comply with Requirement R2, Part 2.3 or Part 2.8. | The responsible entity failed to comply with one of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, Part 2.5, or Part 2.7. | The responsible entity failed to comply with two or more of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, or Part 2.7. OR The responsible entity does not have a completed annual Planning Assessment. |  |  |  | 2013-12-23 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-001-2 | 298 | R3. | 3884 | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. [See standard for further information regarding R3] |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity did not identify planning events as described in Requirement R3, Part 3.4 or extreme events as described in Requirement R3, Part 3.5. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for one of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for two of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform Continge | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for three or more of the categories (P2 through P7) in Table 1. OR The responsible entity did not perfor |  |  |  | 2013-12-23 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-001-2 | 298 | R4. | 3885 | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. [See standard for further information regarding R4] |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity did not identify planning events as described in Requirement R4, Part 4.4 or extreme events as described in Requirement R4, Part 4.5. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for one of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform studies | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for two of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform Continge | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for three or more of the categories (P1 through P7) in Table 1. OR The responsible entity did not base i |  |  |  | 2013-12-23 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TPL-001-2 | 298 | R5. | 3886 | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | N/A | N/A | N/A | The responsible entity does not have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, or the transient voltage response for its System. |  |  |  | 2013-12-23 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TPL-001-2 | 298 | R6. | 3887 | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | N/A | N/A | The responsible entity failed to define and document the criteria or methodology for System instability used within its analysis as described in Requirement R6. |  |  |  | 2013-12-23 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TPL-001-2 | 298 | R7. | 3888 | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with each of its Transmission Planners, failed to determine and identify individual or joint responsibilities for performing required studies. |  |  |  | 2013-12-23 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
TPL-001-2 | 298 | R8. | 3889 | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. [See standard for further information regarding R8] |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 90 days but less than or equal to 120 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 30 days but less than or equal to 40 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 120 days but less than or equal to 130 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 40 days but less than or equal to 50 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 130 days but less than or equal to 140 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 50 days but less than or equal to 60 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 140 days following its completion. OR The responsible entity did not distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 60 days following the request. OR The responsible entity did not distribute its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing. | M3. Each Generator Owner shall have evidence that it has documented and communicated any known regulatory or equipment limitations (excluding limitations noted in footnote 3) that resulted in an exception to Requirements R1 or R2 in accordance with Requirement R3 such as a dated email or letter that contains such documentation as study results, experience from an actual event, or manufacturer’s advice. |  |  | 2013-12-23 | In those jurisdictions where regulatory approval is required: o By the first day of the first calendar quarter, two calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to R3, and R4. In those jurisdictions where regulatory approval is not required: o By the first day of the first calendar quarter, two calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 60 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, four calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 80 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, five calendar years following Board of Trustees approval, each Generator Owner shall have verified 100 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
TPL-001-2 (Ontario) | 79780000298 | R1. | 79780003882 | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. [See standard for further information regarding R1] |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity’s System model failed to represent one of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent two of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent three of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent four or more of the Requirement R1, Parts 1.1.1 through 1.1.6. OR The responsible entity’s System model did not represent projected System conditions as described in Requirement R1. OR The resp |  |  |  | 2013-12-23 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-001-2 (Ontario) | 79780000298 | R2. | 79780003883 | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. [See standard for further information regarding R2] |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity failed to comply with Requirement R2, Part 2.6. | The responsible entity failed to comply with Requirement R2, Part 2.3 or Part 2.8. | The responsible entity failed to comply with one of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, Part 2.5, or Part 2.7. | The responsible entity failed to comply with two or more of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, or Part 2.7. OR The responsible entity does not have a completed annual Planning Assessment. |  |  |  | 2013-12-23 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-001-2 (Ontario) | 79780000298 | R3. | 79780003884 | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. [See standard for further information regarding R3] |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity did not identify planning events as described in Requirement R3, Part 3.4 or extreme events as described in Requirement R3, Part 3.5. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for one of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for two of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform Continge | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for three or more of the categories (P2 through P7) in Table 1. OR The responsible entity did not perfor |  |  |  | 2013-12-23 |  |  |  | NPCC-ON | [6 empty] | 30000000
TPL-001-2 (Ontario) | 79780000298 | R4. | 79780003885 | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. [See standard for further information regarding R4] |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity did not identify planning events as described in Requirement R4, Part 4.4 or extreme events as described in Requirement R4, Part 4.5. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for one of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform studies | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for two of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform Continge | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for three or more of the categories (P1 through P7) in Table 1. OR The responsible entity did not base i |  |  |  | 2013-12-23 |  |  |  | NPCC-ON | [6 empty] | 40000000
TPL-001-2 (Ontario) | 79780000298 | R5. | 79780003886 | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | N/A | N/A | N/A | The responsible entity does not have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, or the transient voltage response for its System. |  |  |  | 2013-12-23 |  |  |  | NPCC-ON | [6 empty] | 50000000
TPL-001-2 (Ontario) | 79780000298 | R6. | 79780003887 | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | N/A | N/A | The responsible entity failed to define and document the criteria or methodology for System instability used within its analysis as described in Requirement R6. |  |  |  | 2013-12-23 |  |  |  | NPCC-ON | [6 empty] | 60000000
TPL-001-2 (Ontario) | 79780000298 | R7. | 79780003888 | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with each of its Transmission Planners, failed to determine and identify individual or joint responsibilities for performing required studies. |  |  |  | 2013-12-23 |  |  |  | NPCC-ON | [6 empty] | 70000000
TPL-001-2 (Ontario) | 79780000298 | R8. | 79780003889 | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. [See standard for further information regarding R8] |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 90 days but less than or equal to 120 days following its completion. OR, The responsible entity | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 120 days but less than or equal to 130 days following its completion. OR, The responsible entity | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 130 days but less than or equal to 140 days following its completion. OR, The responsible entity | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 140 days following its completion. OR The responsible entity did not distribute its Planning Ass | M3. Each Generator Owner shall have evidence that it has documented and communicated any known regulatory or equipment limitations (excluding limitations noted in footnote 3) that resulted in an exception to Requirements R1 or R2 in accordance with Requirement R3 such as a dated email or letter that contains such documentation as study results, experience from an actual event, or manufacturer’s advice. |  |  | 2013-12-23 | In those jurisdictions where regulatory approval is required:&lt;br/&gt;o By the first day of the first calendar quarter, two calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4.&lt;br/&gt;o By the first day of the first calendar quarter, three calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to R3, and R4.&lt;br/&gt;In those jurisdictions where regulatory approval is not required:&lt;br/&gt;o By the first day of the first calendar quarter, two calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4.&lt;br/&gt;o By the first day of the first calendar quarter, three calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 60 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4.&lt;br/&gt;o By the first day of the first calendar quarter, four calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 80 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4.&lt;br/&gt;o By the first day of the first calendar quarter, five calendar years following Board of Trustees approval, each Generator Owner shall have verified 100 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. |  |  | NPCC-ON | [6 empty] | 80000000
TPL-001-2 (Saskatchewan) | 83750000000298 | R1. | 837500000003882 | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. [See standard for further information regarding R1] |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity’s System model failed to represent one of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent two of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent three of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent four or more of the Requirement R1, Parts 1.1.1 through 1.1.6. OR The responsible entity’s System model did not represent projected System conditions as described in Requirement R1. OR The resp |  | 2011-08-04 |  | 2016-01-19 |  |  |  | MRO-SK | [6 empty] | 10000000
TPL-001-2 (Saskatchewan) | 83750000000298 | R2. | 837500000003883 | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. [See standard for further information regarding R2] |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity failed to comply with Requirement R2, Part 2.6. | The responsible entity failed to comply with Requirement R2, Part 2.3 or Part 2.8. | The responsible entity failed to comply with one of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, Part 2.5, or Part 2.7. | The responsible entity failed to comply with two or more of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, or Part 2.7. OR The responsible entity does not have a completed annual Planning Assessment. |  | 2011-08-04 |  | 2016-01-19 |  |  |  | MRO-SK | [6 empty] | 20000000
TPL-001-2 (Saskatchewan) | 83750000000298 | R3. | 837500000003884 | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. [See standard for further information regarding R3] |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity did not identify planning events as described in Requirement R3, Part 3.4 or extreme events as described in Requirement R3, Part 3.5. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for one of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for two of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform Continge | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for three or more of the categories (P2 through P7) in Table 1. OR The responsible entity did not perfor |  | 2011-08-04 |  | 2016-01-19 |  |  |  | MRO-SK | [6 empty] | 30000000
TPL-001-2 (Saskatchewan) | 83750000000298 | R4. | 837500000003885 | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. [See standard for further information regarding R4] |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity did not identify planning events as described in Requirement R4, Part 4.4 or extreme events as described in Requirement R4, Part 4.5. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for one of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform studies | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for two of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform Continge | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for three or more of the categories (P1 through P7) in Table 1. OR The responsible entity did not base i |  | 2011-08-04 |  | 2016-01-19 |  |  |  | MRO-SK | [6 empty] | 40000000
TPL-001-2 (Saskatchewan) | 83750000000298 | R5. | 837500000003886 | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | N/A | N/A | N/A | The responsible entity does not have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, or the transient voltage response for its System. |  | 2011-08-04 |  | 2016-01-19 |  |  |  | MRO-SK | [6 empty] | 50000000
TPL-001-2 (Saskatchewan) | 83750000000298 | R6. | 837500000003887 | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | N/A | N/A | The responsible entity failed to define and document the criteria or methodology for System instability used within its analysis as described in Requirement R6. |  | 2011-08-04 |  | 2016-01-19 |  |  |  | MRO-SK | [6 empty] | 60000000
TPL-001-2 (Saskatchewan) | 83750000000298 | R7. | 837500000003888 | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with each of its Transmission Planners, failed to determine and identify individual or joint responsibilities for performing required studies. |  | 2011-08-04 |  | 2016-01-19 |  |  |  | MRO-SK | [6 empty] | 70000000
TPL-001-2 (Saskatchewan) | 83750000000298 | R8. | 837500000003889 | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. [See standard for further information regarding R8] |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 90 days but less than or equal to 120 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 30 days but less than or equal to 40 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 120 days but less than or equal to 130 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 40 days but less than or equal to 50 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 130 days but less than or equal to 140 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 50 days but less than or equal to 60 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 140 days following its completion. OR The responsible entity did not distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 60 days following the request. OR The responsible entity did not distribute its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing. | M3. Each Generator Owner shall have evidence that it has documented and communicated any known regulatory or equipment limitations (excluding limitations noted in footnote 3) that resulted in an exception to Requirements R1 or R2 in accordance with Requirement R3 such as a dated email or letter that contains such documentation as study results, experience from an actual event, or manufacturer’s advice. | 2011-08-04 |  | 2016-01-19 | In those jurisdictions where regulatory approval is required: o By the first day of the first calendar quarter, two calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to R3, and R4. In those jurisdictions where regulatory approval is not required: o By the first day of the first calendar quarter, two calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 40 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, three calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 60 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, four calendar years following Board of Trustees approval, each Generator Owner shall have verified at least 80 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. o By the first day of the first calendar quarter, five calendar years following Board of Trustees approval, each Generator Owner shall have verified 100 percent of its applicable Facilities are fully compliant with Requirements R1, R2, R3, and R4. |  |  | MRO-SK | [6 empty] | 80000000
TPL-001-3 | 367 | R1. | 4580 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2014-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-001-3 | 367 | R2. | 4581 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-1_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Real-Time Operations | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2014-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-001-3 | 367 | R3. | 4582 | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Real-Time Operations | Low | N/A | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat | M11. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. |  |  | 2014-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-001-3 (Ontario) | 79780000367 | R1. | 79780004580 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2014-12-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-001-3 (Ontario) | 79780000367 | R2. | 79780004581 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-1_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Real-Time Operations | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2014-12-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-001-3 (Ontario) | 79780000367 | R3. | 79780004582 | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Real-Time Operations | Low | N/A | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat | M11. Each Balancing Authority shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitors its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. |  |  | 2014-12-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
TPL-001-4 | 366 | R1. | 4572 | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. System models shall represent: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity’s System model failed to represent one of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent two of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent three of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent four or more of the Requirement R1, Parts 1.1.1 through 1.1.6. OR The responsible entity’s System model did not represent projected System conditions as described in Requirement R1. OR The responsible entity’s System model did not use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards and other sources, including items represented in the Corrective Action Plan. | Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within their respective area, using data consistent with MOD-010 and MOD-012, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | 2015-01-01 |  | 2023-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-001-4 | 366 | R2. | 4573 | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity failed to comply with Requirement R2, Part 2.6. | The responsible entity failed to comply with Requirement R2, Part 2.3 or Part 2.8. | The responsible entity failed to comply with one of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, Part 2.5, or Part 2.7. | The responsible entity failed to comply with two or more of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, or Part 2.7. OR The responsible entity does not have a completed annual Planning Assessment. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  | 2023-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-001-4 | 366 | R3. | 4574 | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity did not identify planning events as described in Requirement R3, Part 3.4 or extreme events as described in Requirement R3, Part 3.5. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for one of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R3, Part 3.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for two of the categories (P2 through P7) in Table 1 OR The responsible entity did not perform Contingency analysis as described in Requirement R3, Part 3.3. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for three or more of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies to determine that the BES meets the performance requirements for the P0 or P1 categories in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2016-01-01 |  | 2023-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-001-4 | 366 | R4. | 4575 | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity did not identify planning events as described in Requirement R4, Part 4.4 or extreme events as described in Requirement R4, Part 4.5. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for one of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R4, Part 4.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for two of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform Contingency analysis as described in Requirement R4, Part 4.3. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for three or more of the categories (P1 through P7) in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2016-01-01 |  | 2023-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TPL-001-4 | 366 | R5. | 4576 | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity does not have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, or the transient voltage response for its System. | M5. Each Transmission Planner and Planning Coordinator shall provide dated evidence such as electronic or hard copies of the documentation specifying the criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System in accordance with Requirement R5. | 2016-01-01 |  | 2023-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TPL-001-4 | 366 | R6. | 4577 | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity failed to define and document the criteria or methodology for System instability used within its analysis as described in Requirement R6. | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of documentation specifying the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding that was utilized in preparing the Planning Assessment in accordance with Requirement R6. | 2016-01-01 |  | 2023-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TPL-001-4 | 366 | R7. | 4578 | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with each of its Transmission Planners, failed to determine and identify individual or joint responsibilities for performing required studies. | M7. Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall provide dated documentation on roles and responsibilities, such as meeting minutes, agreements, and e-mail correspondence that identifies that agreement has been reached on individual and joint responsibilities for performing the required studies and Assessments in accordance with Requirement R7. | 2015-01-01 |  | 2023-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
TPL-001-4 | 366 | R8. | 4579 | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 90 days but less than or equal to 120 days following its completion. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 30 days but less than or equal to 40 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 120 days but less than or equal to 130 days following its completion. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 40 days but less than or equal to 50 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 130 days but less than or equal to 140 days following its completion. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 50 days but less than or equal to 60 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 140 days following its completion. OR The responsible entity did not distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 60 days following the request. OR The responsible entity did not distribute its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing. | M8. Each Planning Coordinator and Transmission Planner shall provide evidence, such as email notices, documentation of updated web pages, postal receipts showing recipient and date; or a demonstration of a public posting, that it has distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 days of having completed its Planning Assessment, and to any functional entity who has indicated a reliability need within 30 days of a written request and that the Planning Coordinator or Transmission Planner has provided a documented response to comments received on Planning Assessment results within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2016-01-01 |  | 2023-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
TPL-001-4 (British Columbia) | 666700000010300 | R1. | 666700000011821 | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. System models shall represent: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity’s System model failed to represent one of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent two of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent three of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent four or more of the Requirement R1, Parts 1.1.1 through 1.1.6. OR The responsible entity’s System model did not represent projected System conditions as described in Requirement R1. OR The responsible entity’s System model did not use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards and other sources, including items represented in the Corrective Action Plan. | Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within their respective area, using data consistent with MOD-010 and MOD-012, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | 2019-07-01 | [5 empty] | WECC-BC | [6 empty] | 10000000
TPL-001-4 (British Columbia) | 666700000010300 | R2. | 666700000011822 | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity failed to comply with Requirement R2, Part 2.6. | The responsible entity failed to comply with Requirement R2, Part 2.3 or Part 2.8. | The responsible entity failed to comply with one of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, Part 2.5, or Part 2.7. | The responsible entity failed to comply with two or more of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, or Part 2.7. OR The responsible entity does not have a completed annual Planning Assessment. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2019-07-01 | [5 empty] | WECC-BC | [6 empty] | 20000000
TPL-001-4 (British Columbia) | 666700000010300 | R3. | 666700000011823 | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity did not identify planning events as described in Requirement R3, Part 3.4 or extreme events as described in Requirement R3, Part 3.5. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for one of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R3, Part 3.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for two of the categories (P2 through P7) in Table 1 OR The responsible entity did not perform Contingency analysis as described in Requirement R3, Part 3.3. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for three or more of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies to determine that the BES meets the performance requirements for the P0 or P1 categories in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2019-07-01 | [5 empty] | WECC-BC | [6 empty] | 30000000
TPL-001-4 (British Columbia) | 666700000010300 | R4. | 666700000011824 | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity did not identify planning events as described in Requirement R4, Part 4.4 or extreme events as described in Requirement R4, Part 4.5. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for one of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R4, Part 4.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for two of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform Contingency analysis as described in Requirement R4, Part 4.3. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for three or more of the categories (P1 through P7) in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2019-07-01 | [5 empty] | WECC-BC | [6 empty] | 40000000
TPL-001-4 (British Columbia) | 666700000010300 | R5. | 666700000011825 | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity does not have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, or the transient voltage response for its System. | M5. Each Transmission Planner and Planning Coordinator shall provide dated evidence such as electronic or hard copies of the documentation specifying the criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System in accordance with Requirement R5. | 2019-07-01 | [5 empty] | WECC-BC | [6 empty] | 50000000
TPL-001-4 (British Columbia) | 666700000010300 | R6. | 666700000011826 | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity failed to define and document the criteria or methodology for System instability used within its analysis as described in Requirement R6. | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of documentation specifying the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding that was utilized in preparing the Planning Assessment in accordance with Requirement R6. | 2019-07-01 | [5 empty] | WECC-BC | [6 empty] | 60000000
TPL-001-4 (British Columbia) | 666700000010300 | R7. | 666700000011827 | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with each of its Transmission Planners, failed to determine and identify individual or joint responsibilities for performing required studies. | M7. Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall provide dated documentation on roles and responsibilities, such as meeting minutes, agreements, and e-mail correspondence that identifies that agreement has been reached on individual and joint responsibilities for performing the required studies and Assessments in accordance with Requirement R7. | 2019-07-01 | [5 empty] | WECC-BC | [6 empty] | 70000000
TPL-001-4 (British Columbia) | 666700000010300 | R8. | 666700000011828 | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 90 days but less than or equal to 120 days following its completion. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 30 days but less than or equal to 40 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 120 days but less than or equal to 130 days following its completion. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 40 days but less than or equal to 50 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 130 days but less than or equal to 140 days following its completion. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 50 days but less than or equal to 60 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 140 days following its completion. OR The responsible entity did not distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 60 days following the request. OR The responsible entity did not distribute its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing. | M8. Each Planning Coordinator and Transmission Planner shall provide evidence, such as email notices, documentation of updated web pages, postal receipts showing recipient and date; or a demonstration of a public posting, that it has distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 days of having completed its Planning Assessment, and to any functional entity who has indicated a reliability need within 30 days of a written request and that the Planning Coordinator or Transmission Planner has provided a documented response to comments received on Planning Assessment results within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2019-07-01 | [5 empty] | WECC-BC | [6 empty] | 80000000
TPL-001-4 (Manitoba) | 77660000000366 | R1. | 776600000004572 | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. System models shall represent: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity’s System model failed to represent one of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent two of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent three of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent four or more of the Requirement R1, Parts 1.1.1 through 1.1.6. OR The responsible entity’s System model did not represent projected System conditions as described in Requirement R1. OR The responsible entity’s System model did not use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards and other sources, including items represented in the Corrective Action Plan. | Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within their respective area, using data consistent with MOD-010 and MOD-012, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | 2017-07-01 |  | 2023-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
TPL-001-4 (Manitoba) | 77660000000366 | R2. | 776600000004573 | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity failed to comply with Requirement R2, Part 2.6. | The responsible entity failed to comply with Requirement R2, Part 2.3 or Part 2.8. | The responsible entity failed to comply with one of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, Part 2.5, or Part 2.7. | The responsible entity failed to comply with two or more of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, or Part 2.7. OR The responsible entity does not have a completed annual Planning Assessment. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2017-07-01 |  | 2023-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
TPL-001-4 (Manitoba) | 77660000000366 | R3. | 776600000004574 | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity did not identify planning events as described in Requirement R3, Part 3.4 or extreme events as described in Requirement R3, Part 3.5. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for one of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R3, Part 3.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for two of the categories (P2 through P7) in Table 1 OR The responsible entity did not perform Contingency analysis as described in Requirement R3, Part 3.3. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for three or more of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies to determine that the BES meets the performance requirements for the P0 or P1 categories in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2017-07-01 |  | 2023-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
TPL-001-4 (Manitoba) | 77660000000366 | R4. | 776600000004575 | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity did not identify planning events as described in Requirement R4, Part 4.4 or extreme events as described in Requirement R4, Part 4.5. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for one of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R4, Part 4.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for two of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform Contingency analysis as described in Requirement R4, Part 4.3. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for three or more of the categories (P1 through P7) in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2017-07-01 |  | 2023-06-30 |  |  |  | MRO-MB | [6 empty] | 40000000
TPL-001-4 (Manitoba) | 77660000000366 | R5. | 776600000004576 | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity does not have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, or the transient voltage response for its System. | M5. Each Transmission Planner and Planning Coordinator shall provide dated evidence such as electronic or hard copies of the documentation specifying the criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System in accordance with Requirement R5. | 2017-07-01 |  | 2023-06-30 |  |  |  | MRO-MB | [6 empty] | 50000000
TPL-001-4 (Manitoba) | 77660000000366 | R6. | 776600000004577 | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity failed to define and document the criteria or methodology for System instability used within its analysis as described in Requirement R6. | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of documentation specifying the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding that was utilized in preparing the Planning Assessment in accordance with Requirement R6. | 2017-07-01 |  | 2023-06-30 |  |  |  | MRO-MB | [6 empty] | 60000000
TPL-001-4 (Manitoba) | 77660000000366 | R7. | 776600000004578 | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with each of its Transmission Planners, failed to determine and identify individual or joint responsibilities for performing required studies. | M7. Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall provide dated documentation on roles and responsibilities, such as meeting minutes, agreements, and e-mail correspondence that identifies that agreement has been reached on individual and joint responsibilities for performing the required studies and Assessments in accordance with Requirement R7. | 2017-07-01 |  | 2023-06-30 |  |  |  | MRO-MB | [6 empty] | 70000000
TPL-001-4 (Manitoba) | 77660000000366 | R8. | 776600000004579 | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 90 days but less than or equal to 120 days following its completion. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 30 days but less than or equal to 40 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 120 days but less than or equal to 130 days following its completion. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 40 days but less than or equal to 50 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 130 days but less than or equal to 140 days following its completion. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 50 days but less than or equal to 60 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 140 days following its completion. OR The responsible entity did not distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 60 days following the request. OR The responsible entity did not distribute its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing. | M8. Each Planning Coordinator and Transmission Planner shall provide evidence, such as email notices, documentation of updated web pages, postal receipts showing recipient and date; or a demonstration of a public posting, that it has distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 days of having completed its Planning Assessment, and to any functional entity who has indicated a reliability need within 30 days of a written request and that the Planning Coordinator or Transmission Planner has provided a documented response to comments received on Planning Assessment results within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2017-07-01 |  | 2023-06-30 |  |  |  | MRO-MB | [6 empty] | 80000000
TPL-001-4 (Nova Scotia) | 78830000000366 | R1. | 788300000004572 | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. System models shall represent: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity’s System model failed to represent one of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent two of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent three of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent four or more of the Requirement R1, Parts 1.1.1 through 1.1.6. OR The responsible entity’s System model did not represent projected System conditions as described in Requirement R1. OR The responsible entity’s System model did not use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards and other sources, including items represented in the Corrective Action Plan. | Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within their respective area, using data consistent with MOD-010 and MOD-012, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | 2015-10-01 |  | 2023-09-30 |  |  |  | NPCC-NS | [6 empty] | 10000000
TPL-001-4 (Nova Scotia) | 78830000000366 | R2. | 788300000004573 | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity failed to comply with Requirement R2, Part 2.6. | The responsible entity failed to comply with Requirement R2, Part 2.3 or Part 2.8. | The responsible entity failed to comply with one of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, Part 2.5, or Part 2.7. | The responsible entity failed to comply with two or more of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, or Part 2.7. OR The responsible entity does not have a completed annual Planning Assessment. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2015-10-01 |  | 2023-09-30 |  |  |  | NPCC-NS | [6 empty] | 20000000
TPL-001-4 (Nova Scotia) | 78830000000366 | R3. | 788300000004574 | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity did not identify planning events as described in Requirement R3, Part 3.4 or extreme events as described in Requirement R3, Part 3.5. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for one of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R3, Part 3.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for two of the categories (P2 through P7) in Table 1 OR The responsible entity did not perform Contingency analysis as described in Requirement R3, Part 3.3. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for three or more of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies to determine that the BES meets the performance requirements for the P0 or P1 categories in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2015-10-01 |  | 2023-09-30 |  |  |  | NPCC-NS | [6 empty] | 30000000
TPL-001-4 (Nova Scotia) | 78830000000366 | R4. | 788300000004575 | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity did not identify planning events as described in Requirement R4, Part 4.4 or extreme events as described in Requirement R4, Part 4.5. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for one of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R4, Part 4.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for two of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform Contingency analysis as described in Requirement R4, Part 4.3. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for three or more of the categories (P1 through P7) in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2015-10-01 |  | 2023-09-30 |  |  |  | NPCC-NS | [6 empty] | 40000000
TPL-001-4 (Nova Scotia) | 78830000000366 | R5. | 788300000004576 | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity does not have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, or the transient voltage response for its System. | M5. Each Transmission Planner and Planning Coordinator shall provide dated evidence such as electronic or hard copies of the documentation specifying the criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System in accordance with Requirement R5. | 2015-10-01 |  | 2023-09-30 |  |  |  | NPCC-NS | [6 empty] | 50000000
TPL-001-4 (Nova Scotia) | 78830000000366 | R6. | 788300000004577 | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity failed to define and document the criteria or methodology for System instability used within its analysis as described in Requirement R6. | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of documentation specifying the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding that was utilized in preparing the Planning Assessment in accordance with Requirement R6. | 2015-10-01 |  | 2023-09-30 |  |  |  | NPCC-NS | [6 empty] | 60000000
TPL-001-4 (Nova Scotia) | 78830000000366 | R7. | 788300000004578 | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with each of its Transmission Planners, failed to determine and identify individual or joint responsibilities for performing required studies. | M7. Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall provide dated documentation on roles and responsibilities, such as meeting minutes, agreements, and e-mail correspondence that identifies that agreement has been reached on individual and joint responsibilities for performing the required studies and Assessments in accordance with Requirement R7. | 2015-10-01 |  | 2023-09-30 |  |  |  | NPCC-NS | [6 empty] | 70000000
TPL-001-4 (Nova Scotia) | 78830000000366 | R8. | 788300000004579 | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 90 days but less than or equal to 120 days following its completion. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 30 days but less than or equal to 40 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 120 days but less than or equal to 130 days following its completion. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 40 days but less than or equal to 50 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 130 days but less than or equal to 140 days following its completion. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 50 days but less than or equal to 60 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 140 days following its completion. OR The responsible entity did not distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 60 days following the request. OR The responsible entity did not distribute its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing. | M8. Each Planning Coordinator and Transmission Planner shall provide evidence, such as email notices, documentation of updated web pages, postal receipts showing recipient and date; or a demonstration of a public posting, that it has distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 days of having completed its Planning Assessment, and to any functional entity who has indicated a reliability need within 30 days of a written request and that the Planning Coordinator or Transmission Planner has provided a documented response to comments received on Planning Assessment results within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2015-10-01 |  | 2023-09-30 |  |  |  | NPCC-NS | [6 empty] | 80000000
TPL-001-4 (Ontario) | 79780000366 | R1. | 79780004572 | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1.&lt;br/&gt;System models shall represent: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity’s System model failed to represent one of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent two of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent three of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent four or more of the Requirement R1, Parts 1.1.1 through 1.1.6. OR The responsible entity’s System model did not represent projected System conditions as described in Requirement R1. OR The responsible entity’s System model did not use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards and other sources, including items represented in the Corrective Action Plan. | &lt;p&gt;Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within their respective area, using data consistent with MOD-010 and MOD-012, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1.&lt;/p&gt; &lt;p/&gt; | 2015-01-01 |  | 2023-06-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-001-4 (Ontario) | 79780000366 | R2. | 79780004573 | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity failed to comply with Requirement R2, Part 2.6. | The responsible entity failed to comply with Requirement R2, Part 2.3 or Part 2.8. | The responsible entity failed to comply with one of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, Part 2.5, or Part 2.7. | The responsible entity failed to comply with two or more of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, or Part 2.7. OR The responsible entity does not have a completed annual Planning Assessment. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  | 2023-06-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-001-4 (Ontario) | 79780000366 | R3. | 79780004574 | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity did not identify planning events as described in Requirement R3, Part 3.4 or extreme events as described in Requirement R3, Part 3.5. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for one of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R3, Part 3.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for two of the categories (P2 through P7) in Table 1 OR The responsible entity did not perform Contingency analysis as described in Requirement R3, Part 3.3. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for three or more of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies to determine that the BES meets the performance requirements for the P0 or P1 categories in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2016-01-01 |  | 2023-06-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
TPL-001-4 (Ontario) | 79780000366 | R4. | 79780004575 | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity did not identify planning events as described in Requirement R4, Part 4.4 or extreme events as described in Requirement R4, Part 4.5. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for one of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R4, Part 4.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for two of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform Contingency analysis as described in Requirement R4, Part 4.3. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for three or more of the categories (P1 through P7) in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2016-01-01 |  | 2023-06-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
TPL-001-4 (Ontario) | 79780000366 | R5. | 79780004576 | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity does not have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, or the transient voltage response for its System. | M5. Each Transmission Planner and Planning Coordinator shall provide dated evidence such as electronic or hard copies of the documentation specifying the criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System in accordance with Requirement R5. | 2016-01-01 |  | 2023-06-30 |  |  |  | NPCC-ON | [6 empty] | 50000000
TPL-001-4 (Ontario) | 79780000366 | R6. | 79780004577 | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity failed to define and document the criteria or methodology for System instability used within its analysis as described in Requirement R6. | &lt;p&gt;Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of documentation specifying the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding that was utilized in preparing the Planning Assessment in accordance with Requirement R6.&lt;/p&gt; &lt;p/&gt; | 2016-01-01 |  | 2023-06-30 |  |  |  | NPCC-ON | [6 empty] | 60000000
TPL-001-4 (Ontario) | 79780000366 | R7. | 79780004578 | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with each of its Transmission Planners, failed to determine and identify individual or joint responsibilities for performing required studies. | M7. Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall provide dated documentation on roles and responsibilities, such as meeting minutes, agreements, and e-mail correspondence that identifies that agreement has been reached on individual and joint responsibilities for performing the required studies and Assessments in accordance with Requirement R7. | 2015-01-01 |  | 2023-06-30 |  |  |  | NPCC-ON | [6 empty] | 70000000
TPL-001-4 (Ontario) | 79780000366 | R8. | 79780004579 | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 90 days but less than or equal to 120 days following its completion. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 30 days but less than or equal to 40 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 120 days but less than or equal to 130 days following its completion. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 40 days but less than or equal to 50 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 130 days but less than or equal to 140 days following its completion. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 50 days but less than or equal to 60 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 140 days following its completion. OR The responsible entity did not distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 60 days following the request. OR The responsible entity did not distribute its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing. | M8. Each Planning Coordinator and Transmission Planner shall provide evidence, such as email notices, documentation of updated web pages, postal receipts showing recipient and date; or a demonstration of a public posting, that it has distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 days of having completed its Planning Assessment, and to any functional entity who has indicated a reliability need within 30 days of a written request and that the Planning Coordinator or Transmission Planner has provided a documented response to comments received on Planning Assessment results within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2016-01-01 |  | 2023-06-30 |  |  |  | NPCC-ON | [6 empty] | 80000000
TPL-001-4 (Saskatchewan) | 83750000000366 | R1. | 837500000004572 | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. System models shall represent: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity’s System model failed to represent one of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent two of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent three of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent four or more of the Requirement R1, Parts 1.1.1 through 1.1.6. OR The responsible entity’s System model did not represent projected System conditions as described in Requirement R1. OR The responsible entity’s System model did not use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards and other sources, including items represented in the Corrective Action Plan. | Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within their respective area, using data consistent with MOD-010 and MOD-012, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | 2016-01-20 |  | 2023-06-30 |  |  |  | MRO-SK | [6 empty] | 10000000
TPL-001-4 (Saskatchewan) | 83750000000366 | R2. | 837500000004573 | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity failed to comply with Requirement R2, Part 2.6. | The responsible entity failed to comply with Requirement R2, Part 2.3 or Part 2.8. | The responsible entity failed to comply with one of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, Part 2.5, or Part 2.7. | The responsible entity failed to comply with two or more of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, or Part 2.7. OR The responsible entity does not have a completed annual Planning Assessment. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-20 |  | 2023-06-30 |  |  |  | MRO-SK | [6 empty] | 20000000
TPL-001-4 (Saskatchewan) | 83750000000366 | R3. | 837500000004574 | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity did not identify planning events as described in Requirement R3, Part 3.4 or extreme events as described in Requirement R3, Part 3.5. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for one of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R3, Part 3.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for two of the categories (P2 through P7) in Table 1 OR The responsible entity did not perform Contingency analysis as described in Requirement R3, Part 3.3. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for three or more of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies to determine that the BES meets the performance requirements for the P0 or P1 categories in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2016-01-20 |  | 2023-06-30 |  |  |  | MRO-SK | [6 empty] | 30000000
TPL-001-4 (Saskatchewan) | 83750000000366 | R4. | 837500000004575 | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity did not identify planning events as described in Requirement R4, Part 4.4 or extreme events as described in Requirement R4, Part 4.5. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for one of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R4, Part 4.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for two of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform Contingency analysis as described in Requirement R4, Part 4.3. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for three or more of the categories (P1 through P7) in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2016-01-20 |  | 2023-06-30 |  |  |  | MRO-SK | [6 empty] | 40000000
TPL-001-4 (Saskatchewan) | 83750000000366 | R5. | 837500000004576 | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity does not have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, or the transient voltage response for its System. | M5. Each Transmission Planner and Planning Coordinator shall provide dated evidence such as electronic or hard copies of the documentation specifying the criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System in accordance with Requirement R5. | 2016-01-20 |  | 2023-06-30 |  |  |  | MRO-SK | [6 empty] | 50000000
TPL-001-4 (Saskatchewan) | 83750000000366 | R6. | 837500000004577 | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity failed to define and document the criteria or methodology for System instability used within its analysis as described in Requirement R6. | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of documentation specifying the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding that was utilized in preparing the Planning Assessment in accordance with Requirement R6. | 2016-01-20 |  | 2023-06-30 |  |  |  | MRO-SK | [6 empty] | 60000000
TPL-001-4 (Saskatchewan) | 83750000000366 | R7. | 837500000004578 | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with each of its Transmission Planners, failed to determine and identify individual or joint responsibilities for performing required studies. | M7. Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall provide dated documentation on roles and responsibilities, such as meeting minutes, agreements, and e-mail correspondence that identifies that agreement has been reached on individual and joint responsibilities for performing the required studies and Assessments in accordance with Requirement R7. | 2016-01-20 |  | 2023-06-30 |  |  |  | MRO-SK | [6 empty] | 70000000
TPL-001-4 (Saskatchewan) | 83750000000366 | R8. | 837500000004579 | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 90 days but less than or equal to 120 days following its completion. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 30 days but less than or equal to 40 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 120 days but less than or equal to 130 days following its completion. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 40 days but less than or equal to 50 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 130 days but less than or equal to 140 days following its completion. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 50 days but less than or equal to 60 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 140 days following its completion. OR The responsible entity did not distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 60 days following the request. OR The responsible entity did not distribute its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing. | M8. Each Planning Coordinator and Transmission Planner shall provide evidence, such as email notices, documentation of updated web pages, postal receipts showing recipient and date; or a demonstration of a public posting, that it has distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 days of having completed its Planning Assessment, and to any functional entity who has indicated a reliability need within 30 days of a written request and that the Planning Coordinator or Transmission Planner has provided a documented response to comments received on Planning Assessment results within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2016-01-20 |  | 2023-06-30 |  |  |  | MRO-SK | [6 empty] | 80000000
TPL-001-5 | 589 | R1. | 8451 | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-032 standard, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity’s System model failed to represent one of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent two of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent three of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent four or more of the Requirement R1, Parts 1.1.1 through 1.1.5. OR The responsible entity’s System model did not represent projected System conditions as described in Requirement R1. OR The responsible entity’s System model did not use data consistent with that provided in accordance with the MOD-032 standard and other sources, including items represented in the Corrective Action Plan. |  |  |  | 2020-06-10 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-001-5 | 589 | R2. | 8458 | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity failed to comply with Requirement R2, Part 2.6. | The responsible entity failed to comply with Requirement R2, Part 2.3 or Part 2.8. | The responsible entity failed to comply with one of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, Part 2.5, or Part 2.7. | The responsible entity failed to comply with two or more of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, or Part 2.7. OR The responsible entity does not have a completed annual Planning Assessment. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. |  |  | 2020-06-10 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-001-5 | 589 | R3. | 8484 | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity did not identify planning events as described in Requirement R3, Part 3.4 or extreme events as described in Requirement R3, Part 3.5. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for one of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R3, Part 3.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for two of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform Contingency analysis as described in Requirement R3, Part 3.3. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for three or more of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies to determine that the BES meets the performance requirements for the P0 or P1 categories in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. |  |  | 2020-06-10 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-001-5 | 589 | R4. | 8501 | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity did not identify planning events as described in Requirement R4, Part 4.4 or extreme events as described in Requirement R4, Part 4.5. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for one of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R4, Part 4.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for two of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform Contingency analysis as described in Requirement R4, Part 4.3. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for three or more of the categories (P1 through P7) in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. |  |  | 2020-06-10 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TPL-001-5 | 589 | R5. | 8502 | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity does not have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, or the transient voltage response for its System. | M5. Each Transmission Planner and Planning Coordinator shall provide dated evidence such as electronic or hard copies of the documentation specifying the criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System in accordance with Requirement R5. |  |  | 2020-06-10 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TPL-001-5 | 589 | R6. | 8503 | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity failed to define and document the criteria or methodology for System instability used within its analysis as described in Requirement R6. | M6. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of documentation specifying the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding that was utilized in preparing the Planning Assessment in accordance with Requirement R6. |  |  | 2020-06-10 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TPL-001-5 | 589 | R7. | 8504 | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with each of its Transmission Planners, failed to determine and identify individual or joint responsibilities for performing required studies. | M7. Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall provide dated documentation on roles and responsibilities, such as meeting minutes, agreements, and e-mail correspondence that identifies that agreement has been reached on individual and joint responsibilities for performing the required studies and Assessments in accordance with Requirement R7. |  |  | 2020-06-10 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
TPL-001-5 | 589 | R8. | 8505 | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 90 days but less than or equal to 120 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 30 days but less than or equal to 40 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 120 days but less than or equal to 130 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 40 days but less than or equal to 50 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 130 days but less than or equal to 140 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 50 days but less than or equal to 60 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 140 days following its completion. OR The responsible entity did not distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 60 days following the request. OR The responsible entity did not distribute its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing. | M8. Each Planning Coordinator and Transmission Planner shall provide evidence, such as email notices, documentation of updated web pages, postal receipts showing recipient and date; or a demonstration of a public posting, that it has distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 days of having completed its Planning Assessment, and to any functional entity who has indicated a reliability need within 30 days of a written request and that the Planning Coordinator or Transmission Planner has provided a documented response to comments received on Planning Assessment results within 90 calendar days of receipt of those comments in accordance with Requirement R8. |  |  | 2020-06-10 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
TPL-001-5.1 | 627 | R1. | 9295 | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-032 standard, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity’s System model failed to represent one of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent two of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent three of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent four or more of the Requirement R1, Parts 1.1.1 through 1.1.5. OR The responsible entity’s System model did not represent projected System conditions as described in Requirement R1. OR The responsible entity’s System model did not use data consistent with that provided in accordance with the MOD-032 standard and other sources, including items represented in the Corrective Action Plan. | M1. Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within its respective area, using data consistent with MOD-032, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | 2023-07-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-001-5.1 | 627 | R2. | 9302 | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity failed to comply with Requirement R2, Part 2.6. | The responsible entity failed to comply with Requirement R2, Part 2.3 or Part 2.8. | The responsible entity failed to comply with one of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, Part 2.5, or Part 2.7. | The responsible entity failed to comply with two or more of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, or Part 2.7. OR The responsible entity does not have a completed annual Planning Assessment. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-001-5.1 | 627 | R3. | 9328 | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity did not identify planning events as described in Requirement R3, Part 3.4 or extreme events as described in Requirement R3, Part 3.5. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for one of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R3, Part 3.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for two of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform Contingency analysis as described in Requirement R3, Part 3.3. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for three or more of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies to determine that the BES meets the performance requirements for the P0 or P1 categories in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2023-07-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-001-5.1 | 627 | R4. | 9339 | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. 4.1. Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R4, Part 4.4. 4.1.1. For planning event P1: No generating unit shall pull out of synchronism. A generator being disconnected from the System by fault clearing action or by a Remedial Action Scheme is not considered pulling out of synchronism. 4.1.2. For planning events P2 through P7: When a generator pulls out of synchronism in the simulations, the resulting apparent impedance swings shall not result in the tripping of any Transmission system elements other than the generating unit and its directly connected Facilities. 4.1.3. For planning events P1 through P7: Power oscillations shall exhibit acceptable damping as established by the Planning Coordinator and Transmission Planner. 4.2. Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R4, Part 4.5. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences of the event (s) shall be conducted. 4.3. Contingency analyses for Requirement R4, Parts 4.1 and 4.2 shall : 4.3.1. Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: 4.3.1.1. Successful high speed (less than one second) reclosing and unsuccessful high speed reclosing into a Fault where high speed reclosing is utilized. 4.3.1.2. Tripping of generators where simulations show generator bus voltages or high side of the GSU voltages are less than known or assumed generator low voltage ride through capability. Include in the assessment any assumptions made. 4.3.1.3. Tripping of Transmission lines and transformers where transient swings cause Protection System operation based on generic or actual relay models. 4.3.2. Simulate the expected automatic operation of existing and planned devices designed to provide dynamic control of electrical system quantities when such devices impact the study area. These devices may include equipment such as generation exciter control and power system stabilizers, static var compensators, power flow controllers, and DC Transmission controllers. 4.4. Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES, shall be identified, and a list created of those Contingencies to be evaluated in Requirement R4, Part 4.1. The rationale for those Contingencies selected for evaluation shall be available as supporting information. 4.4.1. Each Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. 4.5. Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R4, Part 4.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity did not identify planning events as described in Requirement R4, Part 4.4 or extreme events as described in Requirement R4, Part 4.5. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for one of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R4, Part 4.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for two of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform Contingency analysis as described in Requirement R4, Part 4.3. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for three or more of the categories (P1 through P7) in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2023-07-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TPL-001-5.1 | 627 | R5. | 9340 | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity does not have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, or the transient voltage response for its System. | Each Transmission Planner and Planning Coordinator shall provide dated evidence such as electronic or hard copies of the documentation specifying the criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System in accordance with Requirement R5. | 2023-07-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TPL-001-5.1 | 627 | R6. | 9341 | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity failed to define and document the criteria or methodology for System instability used within its analysis as described in Requirement R6. | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of documentation specifying the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding that was utilized in preparing the Planning Assessment in accordance with Requirement R6. | 2023-07-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TPL-001-5.1 | 627 | R7. | 9342 | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with each of its Transmission Planners, failed to determine and identify individual or joint responsibilities for performing required studies. | M7. Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall provide dated documentation on roles and responsibilities, such as meeting minutes, agreements, and e-mail correspondence that identifies that agreement has been reached on individual and joint responsibilities for performing the required studies and Assessments in accordance with Requirement R7. | 2023-07-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
TPL-001-5.1 | 627 | R8. | 9343 | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. 8.1. If a recipient of the Planning Assessment results provides documented comments on the results, the respective Planning Coordinator or Transmission Planner shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 90 days but less than or equal to 120 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 30 days but less than or equal to 40 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 120 days but less than or equal to 130 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 40 days but less than or equal to 50 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 130 days but less than or equal to 140 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 50 days but less than or equal to 60 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 140 days following its completion. OR The responsible entity did not distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 60 days following the request. OR The responsible entity did not distribute its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing. | M8. Each Planning Coordinator and Transmission Planner shall provide evidence, such as email notices, documentation of updated web pages, postal receipts showing recipient and date; or a demonstration of a public posting, that it has distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 days of having completed its Planning Assessment, and to any functional entity who has indicated a reliability need within 30 days of a written request and that the Planning Coordinator or Transmission Planner has provided a documented response to comments received on Planning Assessment results within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2023-07-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
TPL-001-5.1 (Nova Scotia) | 78830000000627 | R1. | 788300000009295 | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-032 standard, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity’s System model failed to represent one of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent two of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent three of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent four or more of the Requirement R1, Parts 1.1.1 through 1.1.5. OR The responsible entity’s System model did not represent projected System conditions as described in Requirement R1. OR The responsible entity’s System model did not use data consistent with that provided in accordance with the MOD-032 standard and other sources, including items represented in the Corrective Action Plan. | M1. Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within its respective area, using data consistent with MOD-032, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | 2023-10-01 | [5 empty] | NPCC-NS | [6 empty] | 10000000
TPL-001-5.1 (Nova Scotia) | 78830000000627 | R2. | 788300000009302 | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity failed to comply with Requirement R2, Part 2.6. | The responsible entity failed to comply with Requirement R2, Part 2.3 or Part 2.8. | The responsible entity failed to comply with one of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, Part 2.5, or Part 2.7. | The responsible entity failed to comply with two or more of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, or Part 2.7. OR The responsible entity does not have a completed annual Planning Assessment. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-10-01 | [5 empty] | NPCC-NS | [6 empty] | 20000000
TPL-001-5.1 (Nova Scotia) | 78830000000627 | R3. | 788300000009328 | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity did not identify planning events as described in Requirement R3, Part 3.4 or extreme events as described in Requirement R3, Part 3.5. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for one of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R3, Part 3.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for two of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform Contingency analysis as described in Requirement R3, Part 3.3. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for three or more of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies to determine that the BES meets the performance requirements for the P0 or P1 categories in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2023-10-01 | [5 empty] | NPCC-NS | [6 empty] | 30000000
TPL-001-5.1 (Nova Scotia) | 78830000000627 | R4. | 788300000009339 | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. 4.1. Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R4, Part 4.4. 4.1.1. For planning event P1: No generating unit shall pull out of synchronism. A generator being disconnected from the System by fault clearing action or by a Remedial Action Scheme is not considered pulling out of synchronism. 4.1.2. For planning events P2 through P7: When a generator pulls out of synchronism in the simulations, the resulting apparent impedance swings shall not result in the tripping of any Transmission system elements other than the generating unit and its directly connected Facilities. 4.1.3. For planning events P1 through P7: Power oscillations shall exhibit acceptable damping as established by the Planning Coordinator and Transmission Planner. 4.2. Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R4, Part 4.5. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences of the event (s) shall be conducted. 4.3. Contingency analyses for Requirement R4, Parts 4.1 and 4.2 shall : 4.3.1. Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: 4.3.1.1. Successful high speed (less than one second) reclosing and unsuccessful high speed reclosing into a Fault where high speed reclosing is utilized. 4.3.1.2. Tripping of generators where simulations show generator bus voltages or high side of the GSU voltages are less than known or assumed generator low voltage ride through capability. Include in the assessment any assumptions made. 4.3.1.3. Tripping of Transmission lines and transformers where transient swings cause Protection System operation based on generic or actual relay models. 4.3.2. Simulate the expected automatic operation of existing and planned devices designed to provide dynamic control of electrical system quantities when such devices impact the study area. These devices may include equipment such as generation exciter control and power system stabilizers, static var compensators, power flow controllers, and DC Transmission controllers. 4.4. Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES, shall be identified, and a list created of those Contingencies to be evaluated in Requirement R4, Part 4.1. The rationale for those Contingencies selected for evaluation shall be available as supporting information. 4.4.1. Each Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. 4.5. Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R4, Part 4.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity did not identify planning events as described in Requirement R4, Part 4.4 or extreme events as described in Requirement R4, Part 4.5. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for one of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R4, Part 4.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for two of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform Contingency analysis as described in Requirement R4, Part 4.3. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for three or more of the categories (P1 through P7) in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2023-10-01 | [5 empty] | NPCC-NS | [6 empty] | 40000000
TPL-001-5.1 (Nova Scotia) | 78830000000627 | R5. | 788300000009340 | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity does not have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, or the transient voltage response for its System. | Each Transmission Planner and Planning Coordinator shall provide dated evidence such as electronic or hard copies of the documentation specifying the criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System in accordance with Requirement R5. | 2023-10-01 | [5 empty] | NPCC-NS | [6 empty] | 50000000
TPL-001-5.1 (Nova Scotia) | 78830000000627 | R6. | 788300000009341 | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity failed to define and document the criteria or methodology for System instability used within its analysis as described in Requirement R6. | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of documentation specifying the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding that was utilized in preparing the Planning Assessment in accordance with Requirement R6. | 2023-10-01 | [5 empty] | NPCC-NS | [6 empty] | 60000000
TPL-001-5.1 (Nova Scotia) | 78830000000627 | R7. | 788300000009342 | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with each of its Transmission Planners, failed to determine and identify individual or joint responsibilities for performing required studies. | M7. Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall provide dated documentation on roles and responsibilities, such as meeting minutes, agreements, and e-mail correspondence that identifies that agreement has been reached on individual and joint responsibilities for performing the required studies and Assessments in accordance with Requirement R7. | 2023-10-01 | [5 empty] | NPCC-NS | [6 empty] | 70000000
TPL-001-5.1 (Nova Scotia) | 78830000000627 | R8. | 788300000009343 | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. 8.1. If a recipient of the Planning Assessment results provides documented comments on the results, the respective Planning Coordinator or Transmission Planner shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 90 days but less than or equal to 120 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 30 days but less than or equal to 40 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 120 days but less than or equal to 130 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 40 days but less than or equal to 50 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 130 days but less than or equal to 140 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 50 days but less than or equal to 60 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 140 days following its completion. OR The responsible entity did not distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 60 days following the request. OR The responsible entity did not distribute its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing. | M8. Each Planning Coordinator and Transmission Planner shall provide evidence, such as email notices, documentation of updated web pages, postal receipts showing recipient and date; or a demonstration of a public posting, that it has distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 days of having completed its Planning Assessment, and to any functional entity who has indicated a reliability need within 30 days of a written request and that the Planning Coordinator or Transmission Planner has provided a documented response to comments received on Planning Assessment results within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2023-10-01 | [5 empty] | NPCC-NS | [6 empty] | 80000000
TPL-001-5.1 (Ontario) | 79780000627 | R1. | 79780009295 | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-032 standard, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity’s System model failed to represent one of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent two of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent three of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent four or more of the Requirement R1, Parts 1.1.1 through 1.1.5. OR The responsible entity’s System model did not represent projected System conditions as described in Requirement R1. OR The responsible entity’s System model did not use data consistent with that provided in accordance with the MOD-032 standard and other sources, including items represented in the Corrective Action Plan. |  | 2020-06-10 | [5 empty] | NPCC-ON | [6 empty] | 10000000
TPL-001-5.1 (Ontario) | 79780000627 | R2. | 79780009302 | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity failed to comply with Requirement R2, Part 2.6. | The responsible entity failed to comply with Requirement R2, Part 2.3 or Part 2.8. | The responsible entity failed to comply with one of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, Part 2.5, or Part 2.7. | The responsible entity failed to comply with two or more of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, or Part 2.7. OR The responsible entity does not have a completed annual Planning Assessment. |  | 2020-06-10 | [5 empty] | NPCC-ON | [6 empty] | 20000000
TPL-001-5.1 (Ontario) | 79780000627 | R3. | 79780009328 | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity did not identify planning events as described in Requirement R3, Part 3.4 or extreme events as described in Requirement R3, Part 3.5. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for one of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R3, Part 3.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for two of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform Contingency analysis as described in Requirement R3, Part 3.3. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for three or more of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies to determine that the BES meets the performance requirements for the P0 or P1 categories in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. |  | 2020-06-10 | [5 empty] | NPCC-ON | [6 empty] | 30000000
TPL-001-5.1 (Ontario) | 79780000627 | R4. | 79780009339 | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1.&lt;br/&gt;4.1. Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R4, Part 4.4. &lt;br/&gt;4.1.1. For planning event P1: No generating unit shall pull out of synchronism. A generator being disconnected from the System by fault clearing action or by a Remedial Action Scheme is not considered pulling out of synchronism. &lt;br/&gt;4.1.2. For planning events P2 through P7: When a generator pulls out of synchronism in the simulations, the resulting apparent impedance swings shall not result in the tripping of any Transmission system elements other than the generating unit and its directly connected Facilities.&lt;br/&gt;4.1.3. For planning events P1 through P7: Power oscillations shall exhibit acceptable damping as established by the Planning Coordinator and Transmission Planner.&lt;br/&gt;4.2. Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R4, Part 4.5. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences of the event (s) shall be conducted.&lt;br/&gt;4.3. Contingency analyses for Requirement R4, Parts 4.1 and 4.2 shall : &lt;br/&gt;4.3.1. Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: &lt;br/&gt;4.3.1.1. Successful high speed (less than one second) reclosing and unsuccessful high speed reclosing into a Fault where high speed reclosing is utilized. &lt;br/&gt;4.3.1.2. Tripping of generators where simulations show generator bus voltages or high side of the GSU voltages are less than known or assumed generator low voltage ride through capability. Include in the assessment any assumptions made. &lt;br/&gt;4.3.1.3. Tripping of Transmission lines and transformers where transient swings cause Protection System operation based on generic or actual relay models. &lt;br/&gt;4.3.2. Simulate the expected automatic operation of existing and planned devices designed to provide dynamic control of electrical system quantities when such devices impact the study area. These devices may include equipment such as generation exciter control and power system stabilizers, static var compensators, power flow controllers, and DC Transmission controllers.&lt;br/&gt;4.4. Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES, shall be identified, and a list created of those Contingencies to be evaluated in Requirement R4, Part 4.1. The rationale for those Contingencies selected for evaluation shall be available as supporting information. &lt;br/&gt;4.4.1. Each Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. &lt;br/&gt;4.5. Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R4, Part 4.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity did not identify planning events as described in Requirement R4, Part 4.4 or extreme events as described in Requirement R4, Part 4.5. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for one of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R4, Part 4.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for two of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform Contingency analysis as described in Requirement R4, Part 4.3. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for three or more of the categories (P1 through P7) in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. |  | 2020-06-10 | [5 empty] | NPCC-ON | [6 empty] | 40000000
TPL-001-5.1 (Ontario) | 79780000627 | R5. | 79780009340 | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | N/A | N/A | N/A | The responsible entity does not have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, or the transient voltage response for its System. |  | 2020-06-10 | [5 empty] | NPCC-ON | [6 empty] | 50000000
TPL-001-5.1 (Ontario) | 79780000627 | R6. | 79780009341 | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | N/A | N/A | N/A | The responsible entity failed to define and document the criteria or methodology for System instability used within its analysis as described in Requirement R6. |  | 2020-06-10 | [5 empty] | NPCC-ON | [6 empty] | 60000000
TPL-001-5.1 (Ontario) | 79780000627 | R7. | 79780009342 | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with each of its Transmission Planners, failed to determine and identify individual or joint responsibilities for performing required studies. |  | 2020-06-10 | [5 empty] | NPCC-ON | [6 empty] | 70000000
TPL-001-5.1 (Ontario) | 79780000627 | R8. | 79780009343 | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request.&lt;br/&gt;8.1. If a recipient of the Planning Assessment results provides documented comments on the results, the respective Planning Coordinator or Transmission Planner shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 90 days but less than or equal to 120 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 30 days but less than or equal to 40 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 120 days but less than or equal to 130 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 40 days but less than or equal to 50 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 130 days but less than or equal to 140 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 50 days but less than or equal to 60 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 140 days following its completion. OR The responsible entity did not distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 60 days following the request. OR The responsible entity did not distribute its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing. |  | 2020-06-10 | [5 empty] | NPCC-ON | [6 empty] | 80000000
TPL-001-5.1 (Saskatchewan) | 83750000000627 | R1. | 837500000009295 | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-032 standard, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity’s System model failed to represent one of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent two of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent three of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent four or more of the Requirement R1, Parts 1.1.1 through 1.1.5. OR The responsible entity’s System model did not represent projected System conditions as described in Requirement R1. OR The responsible entity’s System model did not use data consistent with that provided in accordance with the MOD-032 standard and other sources, including items represented in the Corrective Action Plan. | M1. Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within its respective area, using data consistent with MOD-032, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | 2023-07-01 | [5 empty] | MRO-SK | [6 empty] | 10000000
TPL-001-5.1 (Saskatchewan) | 83750000000627 | R2. | 837500000009302 | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity failed to comply with Requirement R2, Part 2.6. | The responsible entity failed to comply with Requirement R2, Part 2.3 or Part 2.8. | The responsible entity failed to comply with one of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, Part 2.5, or Part 2.7. | The responsible entity failed to comply with two or more of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, or Part 2.7. OR The responsible entity does not have a completed annual Planning Assessment. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 | [5 empty] | MRO-SK | [6 empty] | 20000000
TPL-001-5.1 (Saskatchewan) | 83750000000627 | R3. | 837500000009328 | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity did not identify planning events as described in Requirement R3, Part 3.4 or extreme events as described in Requirement R3, Part 3.5. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for one of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R3, Part 3.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for two of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform Contingency analysis as described in Requirement R3, Part 3.3. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for three or more of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies to determine that the BES meets the performance requirements for the P0 or P1 categories in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2023-07-01 | [5 empty] | MRO-SK | [6 empty] | 30000000
TPL-001-5.1 (Saskatchewan) | 83750000000627 | R4. | 837500000009339 | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. 4.1. Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R4, Part 4.4. 4.1.1. For planning event P1: No generating unit shall pull out of synchronism. A generator being disconnected from the System by fault clearing action or by a Remedial Action Scheme is not considered pulling out of synchronism. 4.1.2. For planning events P2 through P7: When a generator pulls out of synchronism in the simulations, the resulting apparent impedance swings shall not result in the tripping of any Transmission system elements other than the generating unit and its directly connected Facilities. 4.1.3. For planning events P1 through P7: Power oscillations shall exhibit acceptable damping as established by the Planning Coordinator and Transmission Planner. 4.2. Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R4, Part 4.5. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences of the event (s) shall be conducted. 4.3. Contingency analyses for Requirement R4, Parts 4.1 and 4.2 shall : 4.3.1. Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: 4.3.1.1. Successful high speed (less than one second) reclosing and unsuccessful high speed reclosing into a Fault where high speed reclosing is utilized. 4.3.1.2. Tripping of generators where simulations show generator bus voltages or high side of the GSU voltages are less than known or assumed generator low voltage ride through capability. Include in the assessment any assumptions made. 4.3.1.3. Tripping of Transmission lines and transformers where transient swings cause Protection System operation based on generic or actual relay models. 4.3.2. Simulate the expected automatic operation of existing and planned devices designed to provide dynamic control of electrical system quantities when such devices impact the study area. These devices may include equipment such as generation exciter control and power system stabilizers, static var compensators, power flow controllers, and DC Transmission controllers. 4.4. Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES, shall be identified, and a list created of those Contingencies to be evaluated in Requirement R4, Part 4.1. The rationale for those Contingencies selected for evaluation shall be available as supporting information. 4.4.1. Each Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. 4.5. Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R4, Part 4.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity did not identify planning events as described in Requirement R4, Part 4.4 or extreme events as described in Requirement R4, Part 4.5. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for one of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R4, Part 4.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for two of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform Contingency analysis as described in Requirement R4, Part 4.3. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for three or more of the categories (P1 through P7) in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2023-07-01 | [5 empty] | MRO-SK | [6 empty] | 40000000
TPL-001-5.1 (Saskatchewan) | 83750000000627 | R5. | 837500000009340 | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity does not have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, or the transient voltage response for its System. | Each Transmission Planner and Planning Coordinator shall provide dated evidence such as electronic or hard copies of the documentation specifying the criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System in accordance with Requirement R5. | 2023-07-01 | [5 empty] | MRO-SK | [6 empty] | 50000000
TPL-001-5.1 (Saskatchewan) | 83750000000627 | R6. | 837500000009341 | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity failed to define and document the criteria or methodology for System instability used within its analysis as described in Requirement R6. | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of documentation specifying the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding that was utilized in preparing the Planning Assessment in accordance with Requirement R6. | 2023-07-01 | [5 empty] | MRO-SK | [6 empty] | 60000000
TPL-001-5.1 (Saskatchewan) | 83750000000627 | R7. | 837500000009342 | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with each of its Transmission Planners, failed to determine and identify individual or joint responsibilities for performing required studies. | M7. Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall provide dated documentation on roles and responsibilities, such as meeting minutes, agreements, and e-mail correspondence that identifies that agreement has been reached on individual and joint responsibilities for performing the required studies and Assessments in accordance with Requirement R7. | 2023-07-01 | [5 empty] | MRO-SK | [6 empty] | 70000000
TPL-001-5.1 (Saskatchewan) | 83750000000627 | R8. | 837500000009343 | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. 8.1. If a recipient of the Planning Assessment results provides documented comments on the results, the respective Planning Coordinator or Transmission Planner shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 90 days but less than or equal to 120 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 30 days but less than or equal to 40 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 120 days but less than or equal to 130 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 40 days but less than or equal to 50 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 130 days but less than or equal to 140 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 50 days but less than or equal to 60 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 140 days following its completion. OR The responsible entity did not distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 60 days following the request. OR The responsible entity did not distribute its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing. | M8. Each Planning Coordinator and Transmission Planner shall provide evidence, such as email notices, documentation of updated web pages, postal receipts showing recipient and date; or a demonstration of a public posting, that it has distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 days of having completed its Planning Assessment, and to any functional entity who has indicated a reliability need within 30 days of a written request and that the Planning Coordinator or Transmission Planner has provided a documented response to comments received on Planning Assessment results within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2023-07-01 | [5 empty] | MRO-SK | [6 empty] | 80000000
TPL-001-5 (Ontario) | 79780000589 | R1. | 79780008451 | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-032 standard, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity’s System model failed to represent one of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent two of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent three of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent four or more of the Requirement R1, Parts 1.1.1 through 1.1.5. OR The responsible entity’s System model did not represent projected System conditions as described in Requirement R1. OR The responsible entity’s System model did not use data consistent with that provided in accordance with the MOD-032 standard and other sources, including items represented in the Corrective Action Plan. |  | 2020-04-13 |  | 2020-06-10 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-001-5 (Ontario) | 79780000589 | R2. | 79780008458 | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity failed to comply with Requirement R2, Part 2.6. | The responsible entity failed to comply with Requirement R2, Part 2.3 or Part 2.8. | The responsible entity failed to comply with one of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, Part 2.5, or Part 2.7. | The responsible entity failed to comply with two or more of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, or Part 2.7. OR The responsible entity does not have a completed annual Planning Assessment. | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 | [5 empty] | NPCC-ON | [6 empty] | 20000000
TPL-001-5 (Ontario) | 79780000589 | R3. | 79780008484 | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | &lt;p&gt;The responsible entity did&lt;br/&gt;not identify planning events as described in Requirement R3, Part 3.4 or extreme events as &lt;br/&gt;described in&lt;br/&gt;Requirement R3, Part 3.5.&lt;/p&gt; | &lt;p&gt;The responsible entity did&lt;br/&gt;not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the &lt;br/&gt;performance requirements for one of the categories (P2 through P7) in Table 1.&lt;br/&gt;OR&lt;br/&gt;The responsible entity did not perform studies as specified in Requirement R3, Part 3.2 to assess &lt;br/&gt;the impact&lt;br/&gt;of extreme events.&lt;/p&gt; | &lt;p&gt;The responsible entity did&lt;br/&gt;not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the &lt;br/&gt;performance requirements for two of the categories (P2 through P7) in Table 1.&lt;br/&gt;OR&lt;br/&gt;The responsible entity did not perform Contingency analysis as described in Requirement R3, Part &lt;br/&gt;3.3.&lt;/p&gt; | &lt;p&gt;The responsible entity did&lt;br/&gt;not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the &lt;br/&gt;performance requirements for three or more of the categories (P2 through P7) in Table 1.&lt;br/&gt;OR&lt;br/&gt;The responsible entity did not perform studies to determine that the BES meets the performance &lt;br/&gt;requirements for the P0 or P1 categories in Table 1.&lt;br/&gt;OR The responsible entity did&lt;br/&gt;not base its studies on computer simulation models using data provided in&lt;br/&gt;Requirement R1.&lt;/p&gt; | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2023-07-01 | [5 empty] | NPCC-ON | [6 empty] | 30000000
TPL-001-5 (Ontario) | 79780000589 | R4. | 79780008501 | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity did not identify planning events as described in Requirement R4, Part 4.4 or extreme events as described in Requirement R4, Part 4.5. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for one of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R4, Part 4.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for two of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform Contingency analysis as described in Requirement R4, Part 4.3. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for three or more of the categories (P1 through P7) in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2023-07-01 | [5 empty] | NPCC-ON | [6 empty] | 40000000
TPL-001-5 (Ontario) | 79780000589 | R5. | 79780008502 | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity does not have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, or the transient voltage response for its System. | M5. Each Transmission Planner and Planning Coordinator shall provide dated evidence such as electronic or hard copies of the documentation specifying the criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System in accordance with Requirement R5. | 2023-07-01 | [5 empty] | NPCC-ON | [6 empty] | 50000000
TPL-001-5 (Ontario) | 79780000589 | R6. | 79780008503 | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity failed to define and document the criteria or methodology for System instability used within its analysis as described in Requirement R6. | M6. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of documentation specifying the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding that was utilized in preparing the Planning Assessment in accordance with Requirement R6. | 2023-07-01 | [5 empty] | NPCC-ON | [6 empty] | 60000000
TPL-001-5 (Ontario) | 79780000589 | R7. | 79780008504 | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with each of its Transmission Planners, failed to determine and identify individual or joint responsibilities for performing required studies. | M7. Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall provide dated documentation on roles and responsibilities, such as meeting minutes, agreements, and e-mail correspondence that identifies that agreement has been reached on individual and joint responsibilities for performing the required studies and Assessments in accordance with Requirement R7. | 2023-07-01 | [5 empty] | NPCC-ON | [6 empty] | 70000000
TPL-001-5 (Ontario) | 79780000589 | R8. | 79780008505 | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 90 days but less than or equal to 120 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 30 days but less than or equal to 40 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 120 days but less than or equal to 130 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 40 days but less than or equal to 50 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 130 days but less than or equal to 140 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 50 days but less than or equal to 60 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 140 days following its completion. OR The responsible entity did not distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 60 days following the request. OR The responsible entity did not distribute its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing. | M8. Each Planning Coordinator and Transmission Planner shall provide evidence, such as email notices, documentation of updated web pages, postal receipts showing recipient and date; or a demonstration of a public posting, that it has distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 days of having completed its Planning Assessment, and to any functional entity who has indicated a reliability need within 30 days of a written request and that the Planning Coordinator or Transmission Planner has provided a documented response to comments received on Planning Assessment results within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2023-07-01 | [5 empty] | NPCC-ON | [6 empty] | 80000000
TPL-001-AB-0 (Alberta) | 656600000009057 | R1. | 656600000009289 | The ISO must demonstrate through a planning assessment that a transmission system is planned such that, with all transmission facilities in service and with precontingency operating procedures in effect, the transmission system can be operated to accommodate forecasted customer demands, supply and forecasted firm (nonrecallable reserved) transmission services at all demand levels over the range of forecast system demands, under the conditions defined in Category A of Appendix 1. The ISO planning assessment must: |  | ISO | [28 empty] | 2010-09-24 | [5 empty] | WECC-AB | [6 empty] | 10000000
TPL-001-AB-0 (Alberta) | 656600000009057 | R2. | 656600000009290 | When system simulations indicate an inability of the systems to respond as set out in R1.3.7 in this reliability standard, the ISO must: |  | ISO | [28 empty] | 2010-09-24 | [5 empty] | WECC-AB | [6 empty] | 20000000
TPL-001-AB-0 (Alberta) | 656600000009057 | R3. | 656600000009291 | The ISO must provide the planning assessment to WECC on an annual basis. |  | ISO | [28 empty] | 2010-09-24 | [5 empty] | WECC-AB | [6 empty] | 30000000
TPL-002-0 | 187 | R1. | 2075 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2007-06-18 |  | 2010-04-22 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-002-0 | 187 | R2. | 2093 | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2007-06-18 |  | 2010-04-22 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-002-0 | 187 | R3. | 2099 | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2007-06-18 |  | 2010-04-22 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-002-0a | 188 | R1. | 2100 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2010-04-23 |  | 2011-10-23 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-002-0a | 188 | R2. | 2118 | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2010-04-23 |  | 2011-10-23 |  |  | TPL-002-0 R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-002-0a | 188 | R3. | 2124 | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2010-04-23 |  | 2011-10-23 |  |  | TPL-002-0 R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-002-0a (British Columbia) | 666700000010302 | R1. | 666700000011832 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2011-10-30 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 10000000
TPL-002-0a (British Columbia) | 666700000010302 | R2. | 666700000011833 | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2011-10-30 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 20000000
TPL-002-0a (British Columbia) | 666700000010302 | R3. | 666700000011834 | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2011-10-30 |  | 2013-01-14 |  |  |  | WECC-BC | [6 empty] | 30000000
TPL-002-0a (Ontario) | 79780000188 | R1. | 79780002100 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2010-04-23 |  | 2011-10-23 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-002-0a (Ontario) | 79780000188 | R2. | 79780002118 | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2010-04-23 |  | 2011-10-23 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-002-0a (Ontario) | 79780000188 | R3. | 79780002124 | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2010-04-23 |  | 2011-10-23 |  |  |  | NPCC-ON | [6 empty] | 30000000
TPL-002-0b | 265 | R1. | 3473 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High |  |  |  |  | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. | 2011-10-24 |  | 2015-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-002-0b | 265 | R2. | 3491 | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium |  |  |  |  | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-002-1_R3. | 2011-10-24 |  | 2015-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-002-0b | 265 | R3. | 3497 | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | [5 empty] | 2011-10-24 |  | 2015-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-002-0b (British Columbia) | 666700000010303 | R1. | 666700000011835 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High |  |  |  |  | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. | 2013-01-15 | [5 empty] | WECC-BC | [6 empty] | 10000000
TPL-002-0b (British Columbia) | 666700000010303 | R2. | 666700000011836 | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium |  |  |  |  | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-002-1_R3. | 2013-01-15 | [5 empty] | WECC-BC | [6 empty] | 20000000
TPL-002-0b (British Columbia) | 666700000010303 | R3. | 666700000011837 | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | [5 empty] | 2013-01-15 | [5 empty] | WECC-BC | [6 empty] | 30000000
TPL-002-0b (Manitoba) | 77660000000265 | R1. | 776600000003473 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High |  |  |  |  | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
TPL-002-0b (Manitoba) | 77660000000265 | R2. | 776600000003491 | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium |  |  |  |  | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-002-1_R3. | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
TPL-002-0b (Manitoba) | 77660000000265 | R3. | 776600000003497 | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
TPL-002-0b (Ontario) | 79780000265 | R1. | 79780003473 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective&lt;br/&gt;plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. | 2011-10-24 |  | 2015-12-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-002-0b (Ontario) | 79780000265 | R2. | 79780003491 | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | M2. The Planning Authority and Transmission Planner shall have evidence it reported&lt;br/&gt;documentation of results of its reliability assessments and corrective plans per Reliability&lt;br/&gt;Standard TPL-002-1_R3. | 2011-10-24 |  | 2015-12-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-002-0b (Ontario) | 79780000265 | R3. | 79780003497 | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2011-10-24 |  | 2015-12-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
TPL-002-0 (British Columbia) | 666700000010301 | R1. | 666700000011829 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 10000000
TPL-002-0 (British Columbia) | 666700000010301 | R2. | 666700000011830 | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 20000000
TPL-002-0 (British Columbia) | 666700000010301 | R3. | 666700000011831 | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 30000000
TPL-002-0(i)b | 484 | R1. | 5832 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP | [7 empty] | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-0(i)b_R1 and TPL-002-0(i)b_R2. |  |  | 2015-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-002-0(i)b | 484 | R2. | 5850 | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0(i)b_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP | [7 empty] | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-002-0(i)b_R3. |  |  | 2015-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-002-0(i)b | 484 | R3. | 5856 | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP | [10 empty] | 2015-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-002-0(i)b (Ontario) | 79780000484 | R1. | 79780005832 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP | [7 empty] | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-0(i)b_R1 and TPL-002-0(i)b_R2. |  |  | 2015-12-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-002-0(i)b (Ontario) | 79780000484 | R2. | 79780005850 | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0(i)b_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP | [7 empty] | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-002-0(i)b_R3. |  |  | 2015-12-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-002-0(i)b (Ontario) | 79780000484 | R3. | 79780005856 | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP | [10 empty] | 2015-12-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
TPL-002-0(i)b (Saskatchewan) | 83750000000484 | R1. | 837500000005832 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP | [7 empty] | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-0(i)b_R1 and TPL-002-0(i)b_R2. | [6 empty] | MRO-SK | [6 empty] | 10000000
TPL-002-0(i)b (Saskatchewan) | 83750000000484 | R2. | 837500000005850 | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0(i)b_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP | [7 empty] | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-002-0(i)b_R3. | [6 empty] | MRO-SK | [6 empty] | 20000000
TPL-002-0(i)b (Saskatchewan) | 83750000000484 | R3. | 837500000005856 | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP | [14 empty] | MRO-SK | [6 empty] | 30000000
TPL-002-0 (Manitoba) | 77660000000187 | R1. | 776600000002075 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 10000000
TPL-002-0 (Manitoba) | 77660000000187 | R2. | 776600000002093 | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 20000000
TPL-002-0 (Manitoba) | 77660000000187 | R3. | 776600000002099 | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 30000000
TPL-002-0 (Ontario) | 79780000187 | R1. | 79780002075 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2007-06-18 |  | 2010-04-22 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-002-0 (Ontario) | 79780000187 | R2. | 79780002093 | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2007-06-18 |  | 2010-04-22 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-002-0 (Ontario) | 79780000187 | R3. | 79780002099 | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2007-06-18 |  | 2010-04-22 |  |  |  | NPCC-ON | [6 empty] | 30000000
TPL-002-0 (Saskatchewan) | 83750000000187 | R1. | 837500000002075 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2015-04-15 |  | 2018-01-20 |  |  |  | MRO-SK | [6 empty] | 10000000
TPL-002-0 (Saskatchewan) | 83750000000187 | R2. | 837500000002093 | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2015-04-15 |  | 2018-01-20 |  |  |  | MRO-SK | [6 empty] | 20000000
TPL-002-0 (Saskatchewan) | 83750000000187 | R3. | 837500000002099 | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2015-04-15 |  | 2018-01-20 |  |  |  | MRO-SK | [6 empty] | 30000000
TPL-002-1b | 266 | R1. | 3498 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2012-07-06 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-002-1b | 266 | R2. | 3516 | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-1_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2012-07-06 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-002-1b | 266 | R3. | 3522 | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  |  |  | 2012-07-06 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-002-1b (Ontario) | 79780000266 | R1. | 79780003498 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2012-07-06 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-002-1b (Ontario) | 79780000266 | R2. | 79780003516 | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-1_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2012-07-06 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-002-1b (Ontario) | 79780000266 | R3. | 79780003522 | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  |  |  | 2012-07-06 |  |  |  | NPCC-ON | [6 empty] | 30000000
TPL-002-1b (Saskatchewan) | 83750000000266 | R1. | 837500000003498 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2011-02-17 |  | 2014-07-22 |  |  |  | MRO-SK | [6 empty] | 10000000
TPL-002-1b (Saskatchewan) | 83750000000266 | R2. | 837500000003516 | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-1_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2011-02-17 |  | 2014-07-22 |  |  |  | MRO-SK | [6 empty] | 20000000
TPL-002-1b (Saskatchewan) | 83750000000266 | R3. | 837500000003522 | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2011-02-17 |  | 2014-07-22 |  |  |  | MRO-SK | [6 empty] | 30000000
TPL-002-2b | 369 | R1. | 4622 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2014-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-002-2b | 369 | R2. | 4623 | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2014-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-002-2b | 369 | R3. | 4624 | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  |  |  | 2014-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-002-2b (Ontario) | 79780000369 | R1. | 79780004622 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2014-12-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-002-2b (Ontario) | 79780000369 | R2. | 79780004623 | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2014-12-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-002-2b (Ontario) | 79780000369 | R3. | 79780004624 | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  |  |  | 2014-12-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
TPL-002-AB1-0 (Alberta) | 656600000009058 | R1. | 656600000009292 | The ISO must demonstrate for transmission facilities rated 69 kV and above, through a planning assessment, that a transmission system is planned such that the transmission system can be operated to accommodate forecasted customer demands and forecasted firm (non-recallable reserved) transmission services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Appendix 1. The ISO planning assessments must: |  | ISO | [28 empty] | 2017-10-30 | [5 empty] | WECC-AB | [6 empty] | 10000000
TPL-002-AB1-0 (Alberta) | 656600000009058 | R2. | 656600000009293 | When system simulations indicate an inability of the systems to respond as set out in R1.3.7 of this reliability standard the ISO must: |  | ISO | [28 empty] | 2017-10-30 | [5 empty] | WECC-AB | [6 empty] | 20000000
TPL-002-AB1-0 (Alberta) | 656600000009058 | R3. | 656600000009294 | The ISO must provide the planning assessment to WECC on an annual basis. |  | ISO | [28 empty] | 2017-10-30 | [5 empty] | WECC-AB | [6 empty] | 30000000
TPL-003-0 | 189 | R1. | 2125 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I. The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: See standard for table. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2007-06-18 |  | 2010-04-22 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-003-0 | 189 | R2. | 2143 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2007-06-18 |  | 2010-04-22 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-003-0 | 189 | R3. | 2149 | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2007-06-18 |  | 2010-04-22 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-003-0a | 190 | R1. | 2150 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2010-04-23 |  | 2013-06-19 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-003-0a | 190 | R2. | 2168 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2010-04-23 |  | 2013-06-19 |  |  | TPL-003-0 R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-003-0a | 190 | R3. | 2174 | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2010-04-23 |  | 2013-06-19 |  |  | TPL-003-0 R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-003-0a (British Columbia) | 666700000010305 | R1. | 666700000011841 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2011-10-30 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 10000000
TPL-003-0a (British Columbia) | 666700000010305 | R2. | 666700000011842 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2011-10-30 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 20000000
TPL-003-0a (British Columbia) | 666700000010305 | R3. | 666700000011843 | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2011-10-30 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 30000000
TPL-003-0a (Manitoba) | 77660000000190 | R1. | 776600000002150 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
TPL-003-0a (Manitoba) | 77660000000190 | R2. | 776600000002168 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
TPL-003-0a (Manitoba) | 77660000000190 | R3. | 776600000002174 | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
TPL-003-0a (Ontario) | 79780000190 | R1. | 79780002150 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2010-04-23 |  | 2013-06-19 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-003-0a (Ontario) | 79780000190 | R2. | 79780002168 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2010-04-23 |  | 2013-06-19 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-003-0a (Ontario) | 79780000190 | R3. | 79780002174 | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2010-04-23 |  | 2013-06-19 |  |  |  | NPCC-ON | [6 empty] | 30000000
TPL-003-0b | 372 | R1. | 4687 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High |  |  |  |  | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0_R1 and TPL-003-0_R2. | 2013-06-20 |  | 2015-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-003-0b | 372 | R2. | 4688 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium |  |  |  |  | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-003-0_R3. | 2013-06-20 |  | 2015-12-31 |  |  | TPL-003-0 R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-003-0b | 372 | R3. | 4689 | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | [5 empty] | 2013-06-20 |  | 2015-12-31 |  |  | TPL-003-0 R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-003-0b (British Columbia) | 666700000010306 | R1. | 666700000011844 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High |  |  |  |  | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0_R1 and TPL-003-0_R2. | 2014-08-01 | [5 empty] | WECC-BC | [6 empty] | 10000000
TPL-003-0b (British Columbia) | 666700000010306 | R2. | 666700000011845 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium |  |  |  |  | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-003-0_R3. | 2014-08-01 | [5 empty] | WECC-BC | [6 empty] | 20000000
TPL-003-0b (British Columbia) | 666700000010306 | R3. | 666700000011846 | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | [5 empty] | 2014-08-01 | [5 empty] | WECC-BC | [6 empty] | 30000000
TPL-003-0b (Manitoba) | 77660000000372 | R1. | 776600000004687 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High |  |  |  |  | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0_R1 and TPL-003-0_R2. | 2016-07-01 |  | 2016-04-19 |  |  |  | MRO-MB | [6 empty] | 10000000
TPL-003-0b (Manitoba) | 77660000000372 | R2. | 776600000004688 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium |  |  |  |  | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-003-0_R3. | 2016-07-01 |  | 2016-04-19 |  |  |  | MRO-MB | [6 empty] | 20000000
TPL-003-0b (Manitoba) | 77660000000372 | R3. | 776600000004689 | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | [5 empty] | 2016-07-01 |  | 2016-04-19 |  |  |  | MRO-MB | [6 empty] | 30000000
TPL-003-0b (Ontario) | 79780000372 | R1. | 79780004687 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0_R1 and TPL-003-0_R2. | 2013-06-20 |  | 2015-12-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-003-0b (Ontario) | 79780000372 | R2. | 79780004688 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-003-0_R3. | 2013-06-20 |  | 2015-12-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-003-0b (Ontario) | 79780000372 | R3. | 79780004689 | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2013-06-20 |  | 2015-12-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
TPL-003-0 (British Columbia) | 666700000010304 | R1. | 666700000011838 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I. The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: See standard for table. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 10000000
TPL-003-0 (British Columbia) | 666700000010304 | R2. | 666700000011839 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 20000000
TPL-003-0 (British Columbia) | 666700000010304 | R3. | 666700000011840 | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2010-11-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 30000000
TPL-003-0(i)b | 485 | R1. | 5857 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High |  |  |  |  | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0(i)b_R1 and TPL-003-0(i)b_R2. |  |  | 2015-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-003-0(i)b | 485 | R2. | 5875 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0(i)b_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium |  |  |  |  | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-003-0(i)b_R3. |  |  | 2015-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-003-0(i)b | 485 | R3. | 5881 | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | [7 empty] | 2015-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-003-0(i)b (Ontario) | 79780000485 | R1. | 79780005857 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High |  |  |  |  | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-003-0(i)b_R1 and TPL-003-0(i)b_R2. |  |  | 2015-12-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-003-0(i)b (Ontario) | 79780000485 | R2. | 79780005875 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0(i)b_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium |  |  |  |  | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-003-0(i)b_R3. |  |  | 2015-12-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-003-0(i)b (Ontario) | 79780000485 | R3. | 79780005881 | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | [7 empty] | 2015-12-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
TPL-003-0 (Manitoba) | 77660000000189 | R1. | 776600000002125 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I. The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: See standard for table. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 10000000
TPL-003-0 (Manitoba) | 77660000000189 | R2. | 776600000002143 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 20000000
TPL-003-0 (Manitoba) | 77660000000189 | R3. | 776600000002149 | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 30000000
TPL-003-0 (Ontario) | 79780000189 | R1. | 79780002125 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I. The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: See standard for table. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2007-06-18 |  | 2010-04-22 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-003-0 (Ontario) | 79780000189 | R2. | 79780002143 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2007-06-18 |  | 2010-04-22 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-003-0 (Ontario) | 79780000189 | R3. | 79780002149 | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2007-06-18 |  | 2010-04-22 |  |  |  | NPCC-ON | [6 empty] | 30000000
TPL-003-1a | 267 | R1. | 3523 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2012-07-06 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-003-1a | 267 | R2. | 3541 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-1_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2012-07-06 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-003-1a | 267 | R3. | 3547 | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  |  |  | 2012-07-06 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-003-1a (Ontario) | 79780000267 | R1. | 79780003523 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2012-07-06 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-003-1a (Ontario) | 79780000267 | R2. | 79780003541 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-1_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2012-07-06 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-003-1a (Ontario) | 79780000267 | R3. | 79780003547 | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  |  |  | 2012-07-06 |  |  |  | NPCC-ON | [6 empty] | 30000000
TPL-003-1a (Saskatchewan) | 83750000000267 | R1. | 837500000003523 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2011-02-17 |  | 2014-07-22 |  |  |  | MRO-SK | [6 empty] | 10000000
TPL-003-1a (Saskatchewan) | 83750000000267 | R2. | 837500000003541 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-1_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2011-02-17 |  | 2014-07-22 |  |  |  | MRO-SK | [6 empty] | 20000000
TPL-003-1a (Saskatchewan) | 83750000000267 | R3. | 837500000003547 | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  | 2011-02-17 |  | 2014-07-22 |  |  |  | MRO-SK | [6 empty] | 30000000
TPL-003-2a | 370 | R1. | 4647 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2014-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-003-2a | 370 | R2. | 4648 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2014-12-31 |  |  | TPL-003-0 R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-003-2a | 370 | R3. | 4649 | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  |  |  | 2014-12-31 |  |  | TPL-003-0 R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-003-2a (Ontario) | 79780000370 | R1. | 79780004647 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2014-12-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-003-2a (Ontario) | 79780000370 | R2. | 79780004648 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2014-12-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-003-2a (Ontario) | 79780000370 | R3. | 79780004649 | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  |  |  | 2014-12-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
TPL-003-2b | 373 | R1. | 4714 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2013-12-23 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-003-2b | 373 | R2. | 4713 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2013-12-23 |  |  | TPL-003-0 R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-003-2b | 373 | R3. | 4712 | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  |  |  | 2013-12-23 |  |  | TPL-003-0 R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-003-2b (Ontario) | 79780000373 | R1. | 79780004714 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2013-12-23 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-003-2b (Ontario) | 79780000373 | R2. | 79780004713 | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2013-12-23 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-003-2b (Ontario) | 79780000373 | R3. | 79780004712 | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat |  |  |  | 2013-12-23 |  |  |  | NPCC-ON | [6 empty] | 30000000
TPL-003-AB-0 (Alberta) | 656600000009059 | R1. | 656600000009295 | The ISO must demonstrate for transmission facilities rated 100 kV and above, through a planning assessment that the AIES is planned such that the AIES can be operated to accommodate forecasted customer demands, supply and forecasted firm (nonrecallable reserved) transmission services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Appendix 1. The controlled interruption of demand to demand customers, the planned removal of generating units, or the curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this reliability standard. The ISO planning assessments must: |  | ISO | [28 empty] | 2010-09-24 | [5 empty] | WECC-AB | [6 empty] | 10000000
TPL-003-AB-0 (Alberta) | 656600000009059 | R2. | 656600000009296 | When system simulations indicate an inability of the systems to respond as set out in R1.3.7 of this reliability standard, the ISO must: |  | ISO | [28 empty] | 2010-09-24 | [5 empty] | WECC-AB | [6 empty] | 20000000
TPL-003-AB-0 (Alberta) | 656600000009059 | R3. | 656600000009297 | The ISO must provide the planning assessment to WECC on an annual basis. |  | ISO | [28 empty] | 2010-09-24 | [5 empty] | WECC-AB | [6 empty] | 30000000
TPL-004-0 | 191 | R1. | 2175 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2007-06-18 |  | 2013-06-19 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-004-0 | 191 | R2. | 2189 | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | 2007-06-18 |  | 2013-06-19 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-004-0a | 374 | R1. | 4737 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium |  |  |  |  | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0_R1. | 2013-06-20 |  | 2015-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-004-0a | 374 | R2. | 4738 | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  |  |  |  | M2. The Planning Authority and Transmission Planner shall provide evidence to its Compliance Monitor that it reported documentation of results of its reliability assessments per Reliability Standard TPL-004-0_R1. | 2013-06-20 |  | 2015-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-004-0a (British Columbia) | 666700000010308 | R1. | 666700000011849 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium |  |  |  |  | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0_R1. | 2014-08-01 | [5 empty] | WECC-BC | [6 empty] | 10000000
TPL-004-0a (British Columbia) | 666700000010308 | R2. | 666700000011850 | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  |  |  |  | M2. The Planning Authority and Transmission Planner shall provide evidence to its Compliance Monitor that it reported documentation of results of its reliability assessments per Reliability Standard TPL-004-0_R1. | 2014-08-01 | [5 empty] | WECC-BC | [6 empty] | 20000000
TPL-004-0a (Manitoba) | 77660000000374 | R1. | 776600000004737 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium |  |  |  |  | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0_R1. | 2016-07-01 |  | 2014-04-19 |  |  |  | MRO-MB | [6 empty] | 10000000
TPL-004-0a (Manitoba) | 77660000000374 | R2. | 776600000004738 | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  |  |  |  | M2. The Planning Authority and Transmission Planner shall provide evidence to its Compliance Monitor that it reported documentation of results of its reliability assessments per Reliability Standard TPL-004-0_R1. | 2016-07-01 |  | 2014-04-19 |  |  |  | MRO-MB | [6 empty] | 20000000
TPL-004-0a (Ontario) | 79780000374 | R1. | 79780004737 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0_R1. | 2013-06-20 |  | 2015-12-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-004-0a (Ontario) | 79780000374 | R2. | 79780004738 | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | M2. The Planning Authority and Transmission Planner shall provide evidence to its Compliance Monitor that it reported documentation of results of its reliability assessments per Reliability Standard TPL-004-0_R1. | 2013-06-20 |  | 2015-12-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-004-0 (British Columbia) | 666700000010307 | R1. | 666700000011847 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2010-11-01 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 10000000
TPL-004-0 (British Columbia) | 666700000010307 | R2. | 666700000011848 | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | 2010-11-01 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 20000000
TPL-004-0(i)a | 486 | R1. | 5882 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium |  |  |  |  | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0(i)a_R1. |  |  | 2015-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-004-0(i)a | 486 | R2. | 5896 | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  |  |  |  | M2. The Planning Authority and Transmission Planner shall provide evidence to its Compliance Monitor that it reported documentation of results of its reliability assessments per Reliability Standard TPL-004-0(i)a_R1. |  |  | 2015-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-004-0(i)a (Ontario) | 79780000486 | R1. | 79780005882 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non- compliant with 25% or less of the sub- components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non- compliant with 50% or more but less than 75% of the sub- components. | The responsible entity is non-compliant with 75% or more of the sub-components. | M1. The Planning Authority and Transmission Planner shall have a valid assessment for its system responses as specified in Reliability Standard TPL-004-0(i)a_R1. |  |  | 2015-12-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-004-0(i)a (Ontario) | 79780000486 | R2. | 79780005896 | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  |  |  |  | M2. The Planning Authority and Transmission Planner shall provide evidence to its Compliance Monitor that it reported documentation of results of its reliability assessments per Reliability Standard TPL-004-0(i)a_R1. |  |  | 2015-12-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-004-0 (Manitoba) | 77660000000191 | R1. | 776600000002175 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
TPL-004-0 (Manitoba) | 77660000000191 | R2. | 776600000002189 | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | 2012-04-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
TPL-004-0 (Ontario) | 79780000191 | R1. | 79780002175 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2007-06-18 |  | 2013-06-19 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-004-0 (Ontario) | 79780000191 | R2. | 79780002189 | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low |  | The responsible entity documented the results of its reliability assessments but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | 2007-06-18 |  | 2013-06-19 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-004-1 | 268 | R1. | 3548 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2012-07-06 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-004-1 | 268 | R2. | 3562 | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | The responsible entity documented the results of its reliability assessments but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  |  |  | 2012-07-06 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-004-1 (Ontario) | 79780000268 | R1. | 79780003548 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2012-07-06 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-004-1 (Ontario) | 79780000268 | R2. | 79780003562 | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | The responsible entity documented the results of its reliability assessments but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  |  |  | 2012-07-06 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-004-1 (Saskatchewan) | 83750000000268 | R1. | 837500000003548 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  | 2011-02-17 |  | 2014-07-22 |  |  |  | MRO-SK | [6 empty] | 10000000
TPL-004-1 (Saskatchewan) | 83750000000268 | R2. | 837500000003562 | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | The responsible entity documented the results of its reliability assessments but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | 2011-02-17 |  | 2014-07-22 |  |  |  | MRO-SK | [6 empty] | 20000000
TPL-004-2 | 371 | R1. | 4672 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2014-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-004-2 | 371 | R2. | 4673 | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | The responsible entity documented the results of its reliability assessments but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  |  |  | 2014-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-004-2a | 375 | R1. | 4753 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2013-12-23 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-004-2a | 375 | R2. | 4752 | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | The responsible entity documented the results of its reliability assessments but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  |  |  | 2013-12-23 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-004-2a (Ontario) | 79780000375 | R1. | 79780004753 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2013-12-23 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-004-2a (Ontario) | 79780000375 | R2. | 79780004752 | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | The responsible entity documented the results of its reliability assessments but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  |  |  | 2013-12-23 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-004-2 (Ontario) | 79780000371 | R1. | 79780004672 | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. |  |  |  | 2014-12-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-004-2 (Ontario) | 79780000371 | R2. | 79780004673 | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | Low | N/A | The responsible entity documented the results of its reliability assessments but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  |  |  | 2014-12-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-004-AB-0 (Alberta) | 656600000009060 | R1. | 656600000009298 | The ISO must demonstrate for transmission facilities rated 100 kV and above, through a planning assessment that a transmission system is planned such that it has been evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Appendix 1. The ISO planning assessments must: |  | ISO | [28 empty] | 2010-09-24 | [5 empty] | WECC-AB | [6 empty] | 10000000
TPL-004-AB-0 (Alberta) | 656600000009060 | R2. | 656600000009299 | The ISO must provide the planning assessment to WECC on an annual basis. |  | ISO | [28 empty] | 2010-09-24 | [5 empty] | WECC-AB | [6 empty] | 20000000
TPL-005-0 | 192 | R1. | 2190 | Each Regional Reliability Organization shall annually conduct reliability assessments of its respective existing and planned Regional Bulk Electric System (generation and transmission facilities) for: |  | RRO | [14 empty] | RRO | [7 empty] | Medium | [7 empty] | 2014-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-005-0 | 192 | R2. | 2198 | The Regional Reliability Organization shall provide its Regional and Inter-Regional seasonal, near-term, and longer-term reliability assessments to NERC on an annual basis. |  | RRO | [14 empty] | RRO | [7 empty] | Low | [7 empty] | 2014-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-005-0 | 192 | R3. | 2199 | The Regional Reliability Organization shall perform special reliability assessments as requested by NERC or the NERC Board of Trustees under their specific directions and criteria. Such assessments may include, but are not limited to: |  | RRO | [14 empty] | RRO | [7 empty] | Medium | [7 empty] | 2014-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-005-0 (Ontario) | 79780000192 | R1. | 79780002190 | Each Regional Reliability Organization shall annually conduct reliability assessments of its respective existing and planned Regional Bulk Electric System (generation and transmission facilities) for: |  | RRO | [14 empty] | RRO | [7 empty] | Medium | [7 empty] | 2014-12-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-005-0 (Ontario) | 79780000192 | R2. | 79780002198 | The Regional Reliability Organization shall provide its Regional and Inter-Regional seasonal, near-term, and longer-term reliability assessments to NERC on an annual basis. |  | RRO | [14 empty] | RRO | [7 empty] | Low | [7 empty] | 2014-12-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-005-0 (Ontario) | 79780000192 | R3. | 79780002199 | The Regional Reliability Organization shall perform special reliability assessments as requested by NERC or the NERC Board of Trustees under their specific directions and criteria. Such assessments may include, but are not limited to: |  | RRO | [14 empty] | RRO | [7 empty] | Medium | [7 empty] | 2014-12-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
TPL-005-0 (Saskatchewan) | 83750000000192 | R1. | 837500000002190 | Each Regional Reliability Organization shall annually conduct reliability assessments of its respective existing and planned Regional Bulk Electric System (generation and transmission facilities) for: |  | RRO | [14 empty] | RRO | [7 empty] | Medium | [5 empty] | 2005-02-08 |  | 2014-07-22 |  |  |  | MRO-SK | [6 empty] | 10000000
TPL-005-0 (Saskatchewan) | 83750000000192 | R2. | 837500000002198 | The Regional Reliability Organization shall provide its Regional and Inter-Regional seasonal, near-term, and longer-term reliability assessments to NERC on an annual basis. |  | RRO | [14 empty] | RRO | [7 empty] | Low | [5 empty] | 2005-02-08 |  | 2014-07-22 |  |  |  | MRO-SK | [6 empty] | 20000000
TPL-005-0 (Saskatchewan) | 83750000000192 | R3. | 837500000002199 | The Regional Reliability Organization shall perform special reliability assessments as requested by NERC or the NERC Board of Trustees under their specific directions and criteria. Such assessments may include, but are not limited to: |  | RRO | [14 empty] | RRO | [7 empty] | Medium | [5 empty] | 2005-02-08 |  | 2014-07-22 |  |  |  | MRO-SK | [6 empty] | 30000000
TPL-006-0 | 193 | R1. | 2206 | Each Regional Reliability Organization shall provide, as requested (seasonally, annually, or as otherwise specified) by NERC, system data, including past, existing, and future facility and Bulk Electric System data, reports, and system performance information, necessary to assess reliability and compliance with the NERC Reliability Standards and the respective Regional planning criteria. The facility and Bulk Electric System data, reports, and system performance information shall include, but not be limited to, one or more of the following types of information as outlined below: |  | RRO | [14 empty] | RRO | [6 empty] | Long-Term Planning | Medium | [7 empty] | 2009-04-15 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-006-0.1 | 207 | R1. | 2346 | Each Regional Reliability Organization shall provide, as requested (seasonally, annually, or as otherwise specified) by NERC, system data, including past, existing, and future facility and Bulk Electric System data, reports, and system performance information, necessary to assess reliability and compliance with the NERC Reliability Standards and the respective Regional planning criteria. The facility and Bulk Electric System data, reports, and system performance information shall include, but not be limited to, one or more of the following types of information as outlined below: |  | RRO | [14 empty] | RRO | [6 empty] | Long-Term Planning | Medium | [7 empty] | 2014-12-31 |  |  | TPL-006-0 R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-006-0.1 (Ontario) | 79780000207 | R1. | 79780002346 | Each Regional Reliability Organization shall provide, as requested (seasonally, annually, or as otherwise specified) by NERC, system data, including past, existing, and future facility and Bulk Electric System data, reports, and system performance information, necessary to assess reliability and compliance with the NERC Reliability Standards and the respective Regional planning criteria. The facility and Bulk Electric System data, reports, and system performance information shall include, but not be limited to, one or more of the following types of information as outlined below: |  | RRO | [14 empty] | RRO | [6 empty] | Long-Term Planning | Medium | [7 empty] | 2014-12-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-006-0.1 (Saskatchewan) | 83750000000207 | R1. | 837500000002346 | Each Regional Reliability Organization shall provide, as requested (seasonally, annually, or as otherwise specified) by NERC, system data, including past, existing, and future facility and Bulk Electric System data, reports, and system performance information, necessary to assess reliability and compliance with the NERC Reliability Standards and the respective Regional planning criteria. The facility and Bulk Electric System data, reports, and system performance information shall include, but not be limited to, one or more of the following types of information as outlined below: |  | RRO | [14 empty] | RRO | [6 empty] | Long-Term Planning | Medium | [5 empty] | 2009-04-15 |  | 2014-07-22 |  |  |  | MRO-SK | [6 empty] | 10000000
TPL-006-0 (Ontario) | 79780000193 | R1. | 79780002206 | Each Regional Reliability Organization shall provide, as requested (seasonally, annually, or as otherwise specified) by NERC, system data, including past, existing, and future facility and Bulk Electric System data, reports, and system performance information, necessary to assess reliability and compliance with the NERC Reliability Standards and the respective Regional planning criteria. The facility and Bulk Electric System data, reports, and system performance information shall include, but not be limited to, one or more of the following types of information as outlined below: |  | RRO | [14 empty] | RRO | [6 empty] | Long-Term Planning | Medium | [7 empty] | 2009-04-15 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-007-1 | 468 | R1. | 5549 | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models and performing the study or studies needed to complete GMD Vulnerability Assessment(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with its Transmission Planner(s), failed to determine and identify individual or joint responsibilities of the Planning Coordinator and Transmission Planners in the Planning Coordinator’s planning area for maintaining models and performing the study or studies needed to complete GMD Vulnerability Assessment(s). | M1. Each Planning Coordinator, in conjunction with its Transmission Planners, shall provide documentation on roles and responsibilities, such as meeting minutes, agreements, copies of procedures or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for maintaining models and performing the study or studies needed to complete GMD Vulnerability Assessment(s), in accordance with Requirement R1. | 2017-07-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-007-1 | 468 | R2. | 5550 | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete GMD Vulnerability Assessment(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | N/A | N/A | The responsible entity did not maintain either System models or GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete GMD Vulnerability Assessment(s). | The responsible entity did not maintain both System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete GMD Vulnerability Assessment(s). | M2. Each responsible entity, as determined in Requirement R1, shall have evidence in either electronic or hard copy format that it is maintaining System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete GMD Vulnerability Assessment(s). | 2018-07-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-007-1 | 468 | R3. | 5551 | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the benchmark GMD event described in Attachment 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity did not have criteria for acceptable System steady state voltage performance for its System during the benchmark GMD event described in Attachment 1 as required. | M3. Each responsible entity, as determined in Requirement R1, shall have evidence, such as electronic or hard copies of the criteria for acceptable System steady state voltage performance for its System in accordance with Requirement R3. | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-007-1 | 468 | R4. | 5552 | Each responsible entity, as determined in Requirement R1, shall complete a GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon once every 60 calendar months. This GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity completed a GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last GMD Vulnerability Assessment. | The responsible entity's completed GMD Vulnerability Assessment failed to satisfy one of elements listed in Requirement R4 Parts 4.1 through 4.3; OR The responsible entity completed a GMD Vulnerability Assessment, but it was more than 64 calendar months and less than or equal to 68 calendar months since the last GMD Vulnerability Assessment. | The responsible entity's completed GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R4 Parts 4.1 through 4.3; OR The responsible entity completed a GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last GMD Vulnerability Assessment. | The responsible entity's completed GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R4 Parts 4.1 through 4.3; OR The responsible entity completed a GMD Vulnerability Assessment, but it was more than 72 calendar months since the last GMD Vulnerability Assessment; OR The responsible entity does not have a completed GMD Vulnerability Assessment. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its GMD Vulnerability Assessment within 90 calendar days of completion to its Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and to any functional entity who has submitted a written request and has a reliability-related need as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TPL-007-1 | 468 | R5. | 5553 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the transformer thermal impact assessment specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | M5. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2019-01-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TPL-007-1 | 468 | R6. | 5554 | Each Transmission Owner and Generator Owner shall conduct a thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A per phase or greater. The thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase; OR The responsible entity conducted a thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R5. | The responsible entity conducted a thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R5. OR The responsible entity conducted a thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R5; OR The responsible entity failed to include one of the required elements as listed in Requirement R6 Parts 6.1 through 6.3. | The responsible entity failed to conduct a thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase; OR The responsible entity conducted a thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R5; OR The responsible entity failed to include two of the required elements as listed in Requirement R6 Parts 6.1 through 6.3. | The responsible entity failed to conduct a thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase; OR The responsible entity conducted a thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R5; OR The responsible entity failed to include three of the required elements as listed in Requirement R6 Parts 6.1 through 6.3. | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | 2021-01-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TPL-007-1 | 468 | R7. | 5555 | Each responsible entity, as determined in Requirement R1, that concludes, through the GMD Vulnerability Assessment conducted in Requirement R4, that their System does not meet the performance requirements of Table 1 shall develop a Corrective Action Plan addressing how the performance requirements will be met. The Corrective Action Plan shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | N/A | The responsible entity's Corrective Action Plan failed to comply with one of the elements in Requirement R7 Parts 7.1 through 7.3. | The responsible entity's Corrective Action Plan failed to comply with two of the elements in Requirement R7 Parts 7.1 through 7.3. | The responsible entity's Corrective Action Plan failed to comply with all three of the elements in Requirement R7 Parts 7.1 through 7.3; OR The responsible entity did not have a Corrective Action Plan as required by Requirement R7. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements of Table 1 shall have evidence such as electronic or hard copies of its Corrective Action Plan, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its Corrective Action Plan or relevant information, if any, within 90 calendar days of its completion to its Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), a functional entity referenced in the Corrective Action Plan, and any functional entity that submits a written request and has a reliability-related need, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its Corrective Action Plan within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
TPL-007-1 (Ontario) | 79780000468 | R1. | 79780005549 | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models and performing the study or studies needed to complete GMD Vulnerability Assessment(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with its Transmission Planner(s), failed to determine and identify individual or joint responsibilities of the Planning Coordinator and Transmission Planners in the Planning Coordinator’s planning area for maintaining models and performing the study or studies needed to complete GMD Vulnerability Assessment(s). | M1. Each Planning Coordinator, in conjunction with its Transmission Planners, shall provide documentation on roles and responsibilities, such as meeting minutes, agreements, copies of procedures or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for maintaining models and performing the study or studies needed to complete GMD Vulnerability Assessment(s), in accordance with Requirement R1. | 2017-07-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 10000000
TPL-007-1 (Ontario) | 79780000468 | R2. | 79780005550 | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete GMD Vulnerability Assessment(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | N/A | N/A | The responsible entity did not maintain either System models or GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete GMD Vulnerability Assessment(s). | The responsible entity did not maintain both System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete GMD Vulnerability Assessment(s). | M2. Each responsible entity, as determined in Requirement R1, shall have evidence in either electronic or hard copy format that it is maintaining System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete GMD Vulnerability Assessment(s). | 2018-07-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 20000000
TPL-007-1 (Ontario) | 79780000468 | R3. | 79780005551 | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the benchmark GMD event described in Attachment 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;The responsible entity did not have criteria for acceptable System steady state voltage performance for its System during &lt;br/&gt;the benchmark GMD event described in Attachment 1 as required.&lt;/p&gt; &lt;p/&gt; | M3. Each responsible entity, as determined in Requirement R1, shall have evidence, such as electronic or hard copies of the criteria for acceptable System steady state voltage performance for its System in accordance with Requirement R3. | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 30000000
TPL-007-1 (Ontario) | 79780000468 | R4. | 79780005552 | Each responsible entity, as determined in Requirement R1, shall complete a GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon once every 60 calendar months. This GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity completed a GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last GMD Vulnerability Assessment. | The responsible entity's completed GMD Vulnerability Assessment failed to satisfy one of elements listed in Requirement R4 Parts 4.1 through 4.3; OR The responsible entity completed a GMD Vulnerability Assessment, but it was more than 64 calendar months and less than or equal to 68 calendar months since the last GMD Vulnerability Assessment. | The responsible entity's completed GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R4 Parts 4.1 through 4.3; OR The responsible entity completed a GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last GMD Vulnerability Assessment. | The responsible entity's completed GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R4 Parts 4.1 through 4.3; OR The responsible entity completed a GMD Vulnerability Assessment, but it was more than 72 calendar months since the last GMD Vulnerability Assessment; OR The responsible entity does not have a completed GMD Vulnerability Assessment. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its GMD Vulnerability Assessment within 90 calendar days of completion to its Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and to any functional entity who has submitted a written request and has a reliability-related need as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 40000000
TPL-007-1 (Ontario) | 79780000468 | R5. | 79780005553 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the transformer thermal impact assessment specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | M5. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2019-01-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 50000000
TPL-007-1 (Ontario) | 79780000468 | R6. | 79780005554 | Each Transmission Owner and Generator Owner shall conduct a thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A per phase or greater. The thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase; OR The responsible entity conducted a thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R5. | The responsible entity conducted a thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R5. OR The responsible entity conducted a thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R5; OR The responsible entity failed to include one of the required elements as listed in Requirement R6 Parts 6.1 through 6.3. | The responsible entity failed to conduct a thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase; OR The responsible entity conducted a thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R5; OR The responsible entity failed to include two of the required elements as listed in Requirement R6 Parts 6.1 through 6.3. | The responsible entity failed to conduct a thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase; OR The responsible entity conducted a thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R5; OR The responsible entity failed to include three of the required elements as listed in Requirement R6 Parts 6.1 through 6.3. | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | 2021-01-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 60000000
TPL-007-1 (Ontario) | 79780000468 | R7. | 79780005555 | Each responsible entity, as determined in Requirement R1, that concludes, through the GMD Vulnerability Assessment conducted in Requirement R4, that their System does not meet the performance requirements of Table 1 shall develop a Corrective Action Plan addressing how the performance requirements will be met. The Corrective Action Plan shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | N/A | The responsible entity's Corrective Action Plan failed to comply with one of the elements in Requirement R7 Parts 7.1 through 7.3. | The responsible entity's Corrective Action Plan failed to comply with two of the elements in Requirement R7 Parts 7.1 through 7.3. | The responsible entity's Corrective Action Plan failed to comply with all three of the elements in Requirement R7 Parts 7.1 through 7.3; OR The responsible entity did not have a Corrective Action Plan as required by Requirement R7. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements of Table 1 shall have evidence such as electronic or hard copies of its Corrective Action Plan, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its Corrective Action Plan or relevant information, if any, within 90 calendar days of its completion to its Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), a functional entity referenced in the Corrective Action Plan, and any functional entity that submits a written request and has a reliability-related need, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its Corrective Action Plan within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 70000000
TPL-007-1 (Saskatchewan) | 83750000000468 | R1. | 837500000005549 | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models and performing the study or studies needed to complete GMD Vulnerability Assessment(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with its Transmission Planner(s), failed to determine and identify individual or joint responsibilities of the Planning Coordinator and Transmission Planners in the Planning Coordinator’s planning area for maintaining models and performing the study or studies needed to complete GMD Vulnerability Assessment(s). | M1. Each Planning Coordinator, in conjunction with its Transmission Planners, shall provide documentation on roles and responsibilities, such as meeting minutes, agreements, copies of procedures or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for maintaining models and performing the study or studies needed to complete GMD Vulnerability Assessment(s), in accordance with Requirement R1. | 2017-04-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 10000000
TPL-007-1 (Saskatchewan) | 83750000000468 | R2. | 837500000005550 | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete GMD Vulnerability Assessment(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | N/A | N/A | The responsible entity did not maintain either System models or GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete GMD Vulnerability Assessment(s). | The responsible entity did not maintain both System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete GMD Vulnerability Assessment(s). | M2. Each responsible entity, as determined in Requirement R1, shall have evidence in either electronic or hard copy format that it is maintaining System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete GMD Vulnerability Assessment(s). | 2017-04-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 20000000
TPL-007-1 (Saskatchewan) | 83750000000468 | R3. | 837500000005551 | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the benchmark GMD event described in Attachment 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity did not have criteria for acceptable System steady state voltage performance for its System during the benchmark GMD event described in Attachment 1 as required. | M3. Each responsible entity, as determined in Requirement R1, shall have evidence, such as electronic or hard copies of the criteria for acceptable System steady state voltage performance for its System in accordance with Requirement R3. | 2017-04-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 30000000
TPL-007-1 (Saskatchewan) | 83750000000468 | R4. | 837500000005552 | Each responsible entity, as determined in Requirement R1, shall complete a GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon once every 60 calendar months. This GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity completed a GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last GMD Vulnerability Assessment. | The responsible entity's completed GMD Vulnerability Assessment failed to satisfy one of elements listed in Requirement R4 Parts 4.1 through 4.3; OR The responsible entity completed a GMD Vulnerability Assessment, but it was more than 64 calendar months and less than or equal to 68 calendar months since the last GMD Vulnerability Assessment. | The responsible entity's completed GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R4 Parts 4.1 through 4.3; OR The responsible entity completed a GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last GMD Vulnerability Assessment. | The responsible entity's completed GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R4 Parts 4.1 through 4.3; OR The responsible entity completed a GMD Vulnerability Assessment, but it was more than 72 calendar months since the last GMD Vulnerability Assessment; OR The responsible entity does not have a completed GMD Vulnerability Assessment. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its GMD Vulnerability Assessment within 90 calendar days of completion to its Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and to any functional entity who has submitted a written request and has a reliability-related need as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2017-04-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 40000000
TPL-007-1 (Saskatchewan) | 83750000000468 | R5. | 837500000005553 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the transformer thermal impact assessment specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | M5. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2017-04-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 50000000
TPL-007-1 (Saskatchewan) | 83750000000468 | R6. | 837500000005554 | Each Transmission Owner and Generator Owner shall conduct a thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A per phase or greater. The thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase; OR The responsible entity conducted a thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R5. | The responsible entity conducted a thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R5. OR The responsible entity conducted a thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R5; OR The responsible entity failed to include one of the required elements as listed in Requirement R6 Parts 6.1 through 6.3. | The responsible entity failed to conduct a thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase; OR The responsible entity conducted a thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R5; OR The responsible entity failed to include two of the required elements as listed in Requirement R6 Parts 6.1 through 6.3. | The responsible entity failed to conduct a thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase; OR The responsible entity conducted a thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R5; OR The responsible entity failed to include three of the required elements as listed in Requirement R6 Parts 6.1 through 6.3. | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | 2017-04-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 60000000
TPL-007-1 (Saskatchewan) | 83750000000468 | R7. | 837500000005555 | Each responsible entity, as determined in Requirement R1, that concludes, through the GMD Vulnerability Assessment conducted in Requirement R4, that their System does not meet the performance requirements of Table 1 shall develop a Corrective Action Plan addressing how the performance requirements will be met. The Corrective Action Plan shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | N/A | The responsible entity's Corrective Action Plan failed to comply with one of the elements in Requirement R7 Parts 7.1 through 7.3. | The responsible entity's Corrective Action Plan failed to comply with two of the elements in Requirement R7 Parts 7.1 through 7.3. | The responsible entity's Corrective Action Plan failed to comply with all three of the elements in Requirement R7 Parts 7.1 through 7.3; OR The responsible entity did not have a Corrective Action Plan as required by Requirement R7. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements of Table 1 shall have evidence such as electronic or hard copies of its Corrective Action Plan, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its Corrective Action Plan or relevant information, if any, within 90 calendar days of its completion to its Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), a functional entity referenced in the Corrective Action Plan, and any functional entity that submits a written request and has a reliability-related need, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its Corrective Action Plan within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2017-04-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 70000000
TPL-007-2 | 579 | R1. | 8326 | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with its Transmission Planner(s), failed to determine and identify individual or joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. | M1. Each Planning Coordinator, in conjunction with its Transmission Planners, shall provide documentation on roles and responsibilities, such as meeting minutes, agreements, copies of procedures or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data in accordance with Requirement R1. | 2019-07-01 |  | 2019-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-007-2 | 579 | R10. | 8367 | Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a supplemental thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1 OR The responsible entity failed to include one of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | M10. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | 2022-01-01 |  | 2019-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 100000000
TPL-007-2 | 579 | R11. | 8372 | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator's planning area or other part of the system included in the Planning Coordinator's GIC System model. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator’s planning area or other part of the system included in the Planning Coordinator’s GIC System Model. | M11. Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its GIC monitor location(s) and documentation of its process to obtain GIC monitor data in accordance with Requirement R11. | 2021-07-01 |  | 2019-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 110000000
TPL-007-2 | 579 | R12. | 8373 | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its process to obtain geomagnetic field data for its Planning Coordinator’s planning area in accordance with Requirement R12. | 2021-07-01 |  | 2019-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 120000000
TPL-007-2 | 579 | R2. | 8327 | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | N/A | N/A | The responsible entity did not maintain either System models or GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | The responsible entity did not maintain both System models and GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | M2. Each responsible entity, as determined in Requirement R1, shall have evidence in either electronic or hard copy format that it is maintaining System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | 2019-07-01 |  | 2019-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-007-2 | 579 | R3. | 8328 | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity did not have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 as required. | M3. Each responsible entity, as determined in Requirement R1, shall have evidence, such as electronic or hard copies of the criteria for acceptable System steady state voltage performance for its System in accordance with Requirement R3. | 2023-01-01 |  | 2019-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-007-2 | 579 | R4. | 8329 | Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy one of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 64 calendar months and less than or equal to 68 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 72 calendar months since the last benchmark GMD Vulnerability Assessment; OR The responsible entity does not have a completed benchmark GMD Vulnerability Assessment. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2023-01-01 |  | 2019-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TPL-007-2 | 579 | R5. | 8336 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; Or The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | M5. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2020-01-01 |  | 2019-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TPL-007-2 | 579 | R6. | 8339 | Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a benchmark thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include one of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | 2022-01-01 |  | 2019-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TPL-007-2 | 579 | R7. | 8344 | Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity's Corrective Action Plan failed to comply with one of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with two of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with three of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with four or more of the elements in Requirement R7, Parts 7.1 through 7.5; OR The responsible entity did not have a Corrective Action Plan as required by Requirement R7. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2024-01-01 |  | 2019-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
TPL-007-2 | 579 | R8. | 8356 | Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy one of elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy two of elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 64 calendar months and less than or equal to 68 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy four of the elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 72 calendar months since the last supplemental GMD Vulnerability Assessment; OR The responsible entity does not have a completed supplemental GMD Vulnerability Assessment. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2023-01-01 |  | 2019-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
TPL-007-2 | 579 | R9. | 8364 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | M9. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2020-01-01 |  | 2019-06-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
TPL-007-2 (Manitoba) | 77660000000579 | R1. | 776600000008326 | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with its Transmission Planner(s), failed to determine and identify individual or joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. | M1. Each Planning Coordinator, in conjunction with its Transmission Planners, shall provide documentation on roles and responsibilities, such as meeting minutes, agreements, copies of procedures or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data in accordance with Requirement R1. | 2018-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
TPL-007-2 (Manitoba) | 77660000000579 | R10. | 776600000008367 | Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a supplemental thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1 OR The responsible entity failed to include one of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | M10. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | 2018-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 100000000
TPL-007-2 (Manitoba) | 77660000000579 | R11. | 776600000008372 | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator's planning area or other part of the system included in the Planning Coordinator's GIC System model. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator’s planning area or other part of the system included in the Planning Coordinator’s GIC System Model. | M11. Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its GIC monitor location(s) and documentation of its process to obtain GIC monitor data in accordance with Requirement R11. | 2018-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 110000000
TPL-007-2 (Manitoba) | 77660000000579 | R12. | 776600000008373 | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its process to obtain geomagnetic field data for its Planning Coordinator’s planning area in accordance with Requirement R12. | 2018-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 120000000
TPL-007-2 (Manitoba) | 77660000000579 | R2. | 776600000008327 | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | N/A | N/A | The responsible entity did not maintain either System models or GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | The responsible entity did not maintain both System models and GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | M2. Each responsible entity, as determined in Requirement R1, shall have evidence in either electronic or hard copy format that it is maintaining System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | 2018-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
TPL-007-2 (Manitoba) | 77660000000579 | R3. | 776600000008328 | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity did not have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 as required. | M3. Each responsible entity, as determined in Requirement R1, shall have evidence, such as electronic or hard copies of the criteria for acceptable System steady state voltage performance for its System in accordance with Requirement R3. | 2018-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
TPL-007-2 (Manitoba) | 77660000000579 | R4. | 776600000008329 | Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy one of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 64 calendar months and less than or equal to 68 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 72 calendar months since the last benchmark GMD Vulnerability Assessment; OR The responsible entity does not have a completed benchmark GMD Vulnerability Assessment. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2018-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 40000000
TPL-007-2 (Manitoba) | 77660000000579 | R5. | 776600000008336 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; Or The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | M5. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2018-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 50000000
TPL-007-2 (Manitoba) | 77660000000579 | R6. | 776600000008339 | Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a benchmark thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include one of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | 2018-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 60000000
TPL-007-2 (Manitoba) | 77660000000579 | R7. | 776600000008344 | Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity's Corrective Action Plan failed to comply with one of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with two of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with three of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with four or more of the elements in Requirement R7, Parts 7.1 through 7.5; OR The responsible entity did not have a Corrective Action Plan as required by Requirement R7. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2018-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 70000000
TPL-007-2 (Manitoba) | 77660000000579 | R8. | 776600000008356 | Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy one of elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy two of elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 64 calendar months and less than or equal to 68 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy four of the elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 72 calendar months since the last supplemental GMD Vulnerability Assessment; OR The responsible entity does not have a completed supplemental GMD Vulnerability Assessment. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2018-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 80000000
TPL-007-2 (Manitoba) | 77660000000579 | R9. | 776600000008364 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | M9. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2018-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 90000000
TPL-007-2 (Ontario) | 79780000579 | R1. | 79780008326 | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with its Transmission Planner(s), failed to determine and identify individual or joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. | M1. Each Planning Coordinator, in conjunction with its Transmission Planners, shall provide documentation on roles and responsibilities, such as meeting minutes, agreements, copies of procedures or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data in accordance with Requirement R1. | 2019-07-01 |  | 2019-06-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
TPL-007-2 (Ontario) | 79780000579 | R10. | 79780008367 | Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a supplemental thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1 OR The responsible entity failed to include one of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | M10. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | 2022-01-01 |  | 2019-06-30 |  |  |  | NPCC-ON | [6 empty] | 100000000
TPL-007-2 (Ontario) | 79780000579 | R11. | 79780008372 | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator's planning area or other part of the system included in the Planning Coordinator's GIC System model. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator’s planning area or other part of the system included in the Planning Coordinator’s GIC System Model. | M11. Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its GIC monitor location(s) and documentation of its process to obtain GIC monitor data in accordance with Requirement R11. | 2021-07-01 |  | 2019-06-30 |  |  |  | NPCC-ON | [6 empty] | 110000000
TPL-007-2 (Ontario) | 79780000579 | R12. | 79780008373 | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2021-07-01 |  | 2019-06-30 |  |  |  | NPCC-ON | [6 empty] | 120000000
TPL-007-2 (Ontario) | 79780000579 | R2. | 79780008327 | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | N/A | N/A | The responsible entity did not maintain either System models or GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | The responsible entity did not maintain both System models and GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | M2. Each responsible entity, as determined in Requirement R1, shall have evidence in either electronic or hard copy format that it is maintaining System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | 2019-07-01 |  | 2019-06-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
TPL-007-2 (Ontario) | 79780000579 | R3. | 79780008328 | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity did not have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 as required. | M3. Each responsible entity, as determined in Requirement R1, shall have evidence, such as electronic or hard copies of the criteria for acceptable System steady state voltage performance for its System in accordance with Requirement R3. | 2023-01-01 |  | 2019-06-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
TPL-007-2 (Ontario) | 79780000579 | R4. | 79780008329 | Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy one of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 64 calendar months and less than or equal to 68 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 72 calendar months since the last benchmark GMD Vulnerability Assessment; OR The responsible entity does not have a completed benchmark GMD Vulnerability Assessment. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2023-01-01 |  | 2019-06-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
TPL-007-2 (Ontario) | 79780000579 | R5. | 79780008336 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; Or The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | M5. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2020-01-01 |  | 2019-06-30 |  |  |  | NPCC-ON | [6 empty] | 50000000
TPL-007-2 (Ontario) | 79780000579 | R6. | 79780008339 | Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a benchmark thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include one of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | 2022-01-01 |  | 2019-06-30 |  |  |  | NPCC-ON | [6 empty] | 60000000
TPL-007-2 (Ontario) | 79780000579 | R7. | 79780008344 | Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity's Corrective Action Plan failed to comply with one of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with two of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with three of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with four or more of the elements in Requirement R7, Parts 7.1 through 7.5; OR The responsible entity did not have a Corrective Action Plan as required by Requirement R7. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2024-01-01 |  | 2019-06-30 |  |  |  | NPCC-ON | [6 empty] | 70000000
TPL-007-2 (Ontario) | 79780000579 | R8. | 79780008356 | Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning, Real-Time Operations | High | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy one of elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy two of elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 64 calendar months and less than or equal to 68 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy four of the elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 72 calendar months since the last supplemental GMD Vulnerability Assessment; OR The responsible entity does not have a completed supplemental GMD Vulnerability Assessment. | M4. Each Transmission Operator and Balancing Authority shall have evidence of an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. This evidence could include, but is not limited to, operator logs, computer printouts, system specifications, or other evidence. | 2023-01-01 |  | 2019-06-30 |  |  |  | NPCC-ON | [6 empty] | 80000000
TPL-007-2 (Ontario) | 79780000579 | R9. | 79780008364 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | M9. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2020-01-01 |  | 2019-06-30 |  |  |  | NPCC-ON | [6 empty] | 90000000
TPL-007-3 | 593 | D.A.7.3. | 8978 | Include a timetable, subject to revision by the responsible entity in Part D.A.7.4, for implementing the selected actions from Part 7.1. The timetable shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP | [10 empty] | 2020-09-30 |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 687300000
TPL-007-3 | 593 | R1. | 8548 | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with its Transmission Planner(s), failed to determine and identify individual or joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. | M1. Each Planning Coordinator, in conjunction with its Transmission Planners, shall provide documentation on roles and responsibilities, such as meeting minutes, agreements, copies of procedures or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data in accordance with Requirement R1. | 2019-07-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-007-3 | 593 | R10. | 8592 | Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a supplemental thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase;The responsible entity failed to conduct a supplemental thermal impact asseThe responsible entity failed to conduct a supplemental thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1 OR The responsible entity failed to include one of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | M10. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | 2022-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 100000000
TPL-007-3 | 593 | R11. | 8602 | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator's planning area or other part of the system included in the Planning Coordinator's GIC System model. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator’s planning area or other part of the system included in the Planning Coordinator’s GIC System Model. | M11. Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its GIC monitor location(s) and documentation of its process to obtain GIC monitor data in accordance with Requirement R11. | 2021-07-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 110000000
TPL-007-3 | 593 | R12. | 8603 | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | M12. Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its process to obtain geomagnetic field data for its Planning Coordinator’s planning area in accordance with Requirement R12. | 2021-07-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 120000000
TPL-007-3 | 593 | R2. | 8549 | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | N/A | N/A | The responsible entity did not maintain either System models or GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | The responsible entity did not maintain both System models and GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | M2. Each responsible entity, as determined in Requirement R1, shall have evidence in either electronic or hard copy format that it is maintaining System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | 2019-07-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-007-3 | 593 | R3. | 8550 | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity did not have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 as required. | M3. Each responsible entity, as determined in Requirement R1, shall have evidence, such as electronic or hard copies of the criteria for acceptable System steady state voltage performance for its System in accordance with Requirement R3. | 2023-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-007-3 | 593 | R4. | 8551 | Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy one of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR onths since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 72 calendar months since the last benchmark GMD Vulnerability Assessment; OR The responsible entity does not have a completed benchmark GMD Vulnerability Assessment. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2023-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TPL-007-3 | 593 | R5. | 8558 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | M5. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2020-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TPL-007-3 | 593 | R6. | 8561 | Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a benchmark thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include one of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | 2022-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TPL-007-3 | 593 | R7. | 8569 | Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity's Corrective Action Plan failed to comply with one of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with two of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with three of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with four or more of the elements in Requirement R7, Parts 7.1 through 7.5; OR The responsible entity did not have a Corrective Action Plan as required by Requirement R7. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2024-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
TPL-007-3 | 593 | R8. | 8581 | Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy one of elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy two of elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 64 calendar months and less than or equal to 68 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy four of the elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 72 calendar months since the last supplemental GMD Vulnerability Assessment; OR The responsible entity does not have a completed supplemental GMD Vulnerability Assessment. | M8. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2023-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
TPL-007-3 | 593 | R9. | 8589 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | M9. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2020-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
TPL-007-3 (Nova Scotia) | 78830000000593 | R1. | 788300000008548 | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with its Transmission Planner(s), failed to determine and identify individual or joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. | M1. Each Planning Coordinator, in conjunction with its Transmission Planners, shall provide documentation on roles and responsibilities, such as meeting minutes, agreements, copies of procedures or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data in accordance with Requirement R1. | 2019-10-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 10000000
TPL-007-3 (Nova Scotia) | 78830000000593 | R10. | 788300000008592 | Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a supplemental thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase;The responsible entity failed to conduct a supplemental thermal impact asseThe responsible entity failed to conduct a supplemental thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1 OR The responsible entity failed to include one of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | M10. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | 2022-04-01 |  | 2022-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 100000000
TPL-007-3 (Nova Scotia) | 78830000000593 | R11. | 788300000008602 | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator's planning area or other part of the system included in the Planning Coordinator's GIC System model. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator’s planning area or other part of the system included in the Planning Coordinator’s GIC System Model. | M11. Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its GIC monitor location(s) and documentation of its process to obtain GIC monitor data in accordance with Requirement R11. | 2021-11-01 |  | 2021-10-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 110000000
TPL-007-3 (Nova Scotia) | 78830000000593 | R12. | 788300000008603 | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | M12. Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its process to obtain geomagnetic field data for its Planning Coordinator’s planning area in accordance with Requirement R12. | 2021-11-01 |  | 2021-10-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 120000000
TPL-007-3 (Nova Scotia) | 78830000000593 | R2. | 788300000008549 | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | N/A | N/A | The responsible entity did not maintain either System models or GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | The responsible entity did not maintain both System models and GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | M2. Each responsible entity, as determined in Requirement R1, shall have evidence in either electronic or hard copy format that it is maintaining System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | 2019-10-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 20000000
TPL-007-3 (Nova Scotia) | 78830000000593 | R3. | 788300000008550 | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity did not have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 as required. | M3. Each responsible entity, as determined in Requirement R1, shall have evidence, such as electronic or hard copies of the criteria for acceptable System steady state voltage performance for its System in accordance with Requirement R3. | 2023-04-01 |  |  |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 30000000
TPL-007-3 (Nova Scotia) | 78830000000593 | R4. | 788300000008551 | Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy one of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR onths since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 72 calendar months since the last benchmark GMD Vulnerability Assessment; OR The responsible entity does not have a completed benchmark GMD Vulnerability Assessment. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2023-04-01 |  |  |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 40000000
TPL-007-3 (Nova Scotia) | 78830000000593 | R5. | 788300000008558 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | M5. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2020-04-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 50000000
TPL-007-3 (Nova Scotia) | 78830000000593 | R6. | 788300000008561 | Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a benchmark thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include one of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | 2022-04-01 |  | 2022-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 60000000
TPL-007-3 (Nova Scotia) | 78830000000593 | R7. | 788300000008569 | Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity's Corrective Action Plan failed to comply with one of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with two of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with three of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with four or more of the elements in Requirement R7, Parts 7.1 through 7.5; OR The responsible entity did not have a Corrective Action Plan as required by Requirement R7. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2024-04-01 |  |  |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 70000000
TPL-007-3 (Nova Scotia) | 78830000000593 | R8. | 788300000008581 | Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy one of elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy two of elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 64 calendar months and less than or equal to 68 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy four of the elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 72 calendar months since the last supplemental GMD Vulnerability Assessment; OR The responsible entity does not have a completed supplemental GMD Vulnerability Assessment. | M8. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2023-04-01 |  |  |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 80000000
TPL-007-3 (Nova Scotia) | 78830000000593 | R9. | 788300000008589 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | M9. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2020-04-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 90000000
TPL-007-3 (Ontario) | 79780000593 | R1. | 79780008548 | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with its Transmission Planner(s), failed to determine and identify individual or joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. | M1. Each Planning Coordinator, in conjunction with its Transmission Planners, shall provide documentation on roles and responsibilities, such as meeting minutes, agreements, copies of procedures or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data in accordance with Requirement R1. | 2019-07-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 10000000
TPL-007-3 (Ontario) | 79780000593 | R10. | 79780008592 | Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a supplemental thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase;The responsible entity failed to conduct a supplemental thermal impact asseThe responsible entity failed to conduct a supplemental thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1 OR The responsible entity failed to include one of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | M10. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | 2022-01-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 100000000
TPL-007-3 (Ontario) | 79780000593 | R11. | 79780008602 | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator's planning area or other part of the system included in the Planning Coordinator's GIC System model. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator’s planning area or other part of the system included in the Planning Coordinator’s GIC System Model. | M11. Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its GIC monitor location(s) and documentation of its process to obtain GIC monitor data in accordance with Requirement R11. | 2021-07-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 110000000
TPL-007-3 (Ontario) | 79780000593 | R12. | 79780008603 | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | M12. Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its process to obtain geomagnetic field data for its Planning Coordinator’s planning area in accordance with Requirement R12. | 2021-07-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 120000000
TPL-007-3 (Ontario) | 79780000593 | R2. | 79780008549 | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | N/A | N/A | The responsible entity did not maintain either System models or GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | The responsible entity did not maintain both System models and GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | M2. Each responsible entity, as determined in Requirement R1, shall have evidence in either electronic or hard copy format that it is maintaining System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | 2019-07-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 20000000
TPL-007-3 (Ontario) | 79780000593 | R3. | 79780008550 | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity did not have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 as required. | M3. Each responsible entity, as determined in Requirement R1, shall have evidence, such as electronic or hard copies of the criteria for acceptable System steady state voltage performance for its System in accordance with Requirement R3. | 2023-01-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 30000000
TPL-007-3 (Ontario) | 79780000593 | R4. | 79780008551 | Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy one of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR onths since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 72 calendar months since the last benchmark GMD Vulnerability Assessment; OR The responsible entity does not have a completed benchmark GMD Vulnerability Assessment. | &lt;p&gt;M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4.&lt;/p&gt; | 2023-01-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 40000000
TPL-007-3 (Ontario) | 79780000593 | R5. | 79780008558 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | M5. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2020-01-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 50000000
TPL-007-3 (Ontario) | 79780000593 | R6. | 79780008561 | Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a benchmark thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include one of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | 2022-01-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 60000000
TPL-007-3 (Ontario) | 79780000593 | R7. | 79780008569 | Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity's Corrective Action Plan failed to comply with one of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with two of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with three of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with four or more of the elements in Requirement R7, Parts 7.1 through 7.5; OR The responsible entity did not have a Corrective Action Plan as required by Requirement R7. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2024-01-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 70000000
TPL-007-3 (Ontario) | 79780000593 | R8. | 79780008581 | Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy one of elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy two of elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 64 calendar months and less than or equal to 68 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy four of the elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 72 calendar months since the last supplemental GMD Vulnerability Assessment; OR The responsible entity does not have a completed supplemental GMD Vulnerability Assessment. | M8. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2023-01-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 80000000
TPL-007-3 (Ontario) | 79780000593 | R9. | 79780008589 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | M9. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2020-01-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 90000000
TPL-007-3 (Saskatchewan) | 83750000000593 | D.A.7.3. | 837500000008978 | Include a timetable, subject to revision by the responsible entity in Part D.A.7.4, for implementing the selected actions from Part 7.1. The timetable shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP | [8 empty] | 2020-01-01 |  | 2021-03-31 |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 687300000
TPL-007-3 (Saskatchewan) | 83750000000593 | R1. | 837500000008548 | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with its Transmission Planner(s), failed to determine and identify individual or joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. | M1. Each Planning Coordinator, in conjunction with its Transmission Planners, shall provide documentation on roles and responsibilities, such as meeting minutes, agreements, copies of procedures or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data in accordance with Requirement R1. | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 10000000
TPL-007-3 (Saskatchewan) | 83750000000593 | R10. | 837500000008592 | Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a supplemental thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase;The responsible entity failed to conduct a supplemental thermal impact asseThe responsible entity failed to conduct a supplemental thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1 OR The responsible entity failed to include one of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | M10. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 100000000
TPL-007-3 (Saskatchewan) | 83750000000593 | R11. | 837500000008602 | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator's planning area or other part of the system included in the Planning Coordinator's GIC System model. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator’s planning area or other part of the system included in the Planning Coordinator’s GIC System Model. | M11. Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its GIC monitor location(s) and documentation of its process to obtain GIC monitor data in accordance with Requirement R11. | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 110000000
TPL-007-3 (Saskatchewan) | 83750000000593 | R12. | 837500000008603 | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | M12. Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its process to obtain geomagnetic field data for its Planning Coordinator’s planning area in accordance with Requirement R12. | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 120000000
TPL-007-3 (Saskatchewan) | 83750000000593 | R2. | 837500000008549 | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | N/A | N/A | The responsible entity did not maintain either System models or GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | The responsible entity did not maintain both System models and GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | M2. Each responsible entity, as determined in Requirement R1, shall have evidence in either electronic or hard copy format that it is maintaining System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 20000000
TPL-007-3 (Saskatchewan) | 83750000000593 | R3. | 837500000008550 | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity did not have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 as required. | M3. Each responsible entity, as determined in Requirement R1, shall have evidence, such as electronic or hard copies of the criteria for acceptable System steady state voltage performance for its System in accordance with Requirement R3. | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 30000000
TPL-007-3 (Saskatchewan) | 83750000000593 | R4. | 837500000008551 | Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy one of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR onths since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 72 calendar months since the last benchmark GMD Vulnerability Assessment; OR The responsible entity does not have a completed benchmark GMD Vulnerability Assessment. | M4. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 40000000
TPL-007-3 (Saskatchewan) | 83750000000593 | R5. | 837500000008558 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | M5. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 50000000
TPL-007-3 (Saskatchewan) | 83750000000593 | R6. | 837500000008561 | Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a benchmark thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include one of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | M6. Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 60000000
TPL-007-3 (Saskatchewan) | 83750000000593 | R7. | 837500000008569 | Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity's Corrective Action Plan failed to comply with one of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with two of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with three of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with four or more of the elements in Requirement R7, Parts 7.1 through 7.5; OR The responsible entity did not have a Corrective Action Plan as required by Requirement R7. | M7. Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 70000000
TPL-007-3 (Saskatchewan) | 83750000000593 | R8. | 837500000008581 | Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy one of elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy two of elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 64 calendar months and less than or equal to 68 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy four of the elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 72 calendar months since the last supplemental GMD Vulnerability Assessment; OR The responsible entity does not have a completed supplemental GMD Vulnerability Assessment. | M8. Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 80000000
TPL-007-3 (Saskatchewan) | 83750000000593 | R9. | 837500000008589 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | M9. Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 90000000
TPL-007-4 | 612 | D.A.11.3. | 9048 | Include a timetable, subject to revision by the responsible entity in Part D.A.11.4, for implementing the selected actions from Part 11.1. The timetable shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP | [8 empty] | 2020-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 691300000
TPL-007-4 | 612 | D.A.11.4. | 9051 | Be revised if the responsible entity is unable to implement the CAP within the timetable for implementation provided in Part D.A.11.3. The revised CAP shall document the following: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP | [8 empty] | 2020-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 691400000
TPL-007-4 | 612 | D.A.11.5. | 9055 | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later, and (iii) to the Compliance Enforcement Authority or Applicable Governmental Authority when revised under D.A.11.4 within 90 calendar days of revision. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP | [8 empty] | 2020-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 691500000
TPL-007-4 | 612 | D.A.7.3. | RQ-2021-07-12-0000001 | Include a timetable, subject to revision by the responsible entity in Part D.A.7.4, for implementing the selected actions from Part 7.1. The timetable shall: |  | GO, PCPA, TO, TP |  |  |  |  | GO |  |  |  |  | PCPA | [7 empty] | TO |  | TP | [8 empty] | 2020-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 687300000
TPL-007-4 | 612 | D.A.7.4. | 9042 | Be revised if the responsible entity is unable to implement the CAP within the timetable for implementation provided in Part D.A.7.3. The revised CAP shall document the following: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP | [8 empty] | 2020-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 687400000
TPL-007-4 | 612 | D.A.7.5. | 9046 | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later, and (iii) to the Compliance Enforcement Authority or Applicable Governmental Authority when revised under D.A.7.4 within 90 calendar days of revision. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP | [8 empty] | 2020-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 687500000
TPL-007-4 | 612 | R1. | 8981 | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with its Transmission Planner(s), failed to determine and identify individual or joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard | Each Planning Coordinator, in conjunction with its Transmission Planners, shall provide documentation on roles and responsibilities, such as meeting minutes, agreements, copies of procedures or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data in accordance with Requirement R1. | 2020-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
TPL-007-4 | 612 | R10. | 9021 | Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a supplemental thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase;The responsible entity failed to conduct a supplemental thermal impact asseThe responsible entity failed to conduct a supplemental thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1 OR The responsible entity failed to include one of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 100000000
TPL-007-4 | 612 | R11. | 9029 | Each responsible entity, as determined in Requirement R1, that concludes through the supplemental GMD Vulnerability Assessment conducted in Requirement R8 that their System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity’s Corrective Action Plan failed to comply with one of the elements in Requirement R11, Parts 11.1 through 11.5. | The responsible entity’s Corrective Action Plan failed to comply with two of the elements in Requirement R11, Parts 11.1 through 11.5. | The responsible entity’s Corrective Action Plan failed to comply with three of the elements in Requirement R11, Parts 11.1 through 11.5. | The responsible entity’s Corrective Action Plan failed to comply with four or more of the elements in Requirement R11, Parts 11.1 through 11.5; OR The responsible entity did not develop a Corrective Action Plan as required by Requirement R11. | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 110000000
TPL-007-4 | 612 | R12. | 9026 | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator's planning area or other part of the system included in the Planning Coordinator's GIC System model. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator’s planning area or other part of the system included in the Planning Coordinator’s GIC System Model. | Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its GIC monitor location(s) and documentation of its process to obtain GIC monitor data in accordance with Requirement R12. | 2021-07-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 120000000
TPL-007-4 | 612 | R13. | 9027 | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | M13. Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its process to obtain geomagnetic field data for its Planning Coordinator’s planning area in accordance with Requirement R13. | 2021-07-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 130000000
TPL-007-4 | 612 | R2. | 8982 | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | N/A | N/A | The responsible entity did not maintain either System models or GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | The responsible entity did not maintain both System models and GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | Each responsible entity, as determined in Requirement R1, shall have evidence in either electronic or hard copy format that it is maintaining System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | 2020-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
TPL-007-4 | 612 | R3. | 8983 | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity did not have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 as required. | Each responsible entity, as determined in Requirement R1, shall have evidence, such as electronic or hard copies of the criteria for acceptable System steady state voltage performance for its System in accordance with Requirement R3. | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
TPL-007-4 | 612 | R4. | 8984 | Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy one of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR onths since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 72 calendar months since the last benchmark GMD Vulnerability Assessment; OR The responsible entity does not have a completed benchmark GMD Vulnerability Assessment. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
TPL-007-4 | 612 | R5. | 8991 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area | 2020-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
TPL-007-4 | 612 | R6. | 8994 | Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a benchmark thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include one of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
TPL-007-4 | 612 | R7. | 8999 | Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity's Corrective Action Plan failed to comply with one of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with two of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with three of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity’s Corrective Action Plan failed to comply with four or more of the elements in Requirement R7, Parts 7.1 through 7.5; OR The responsible entity did not develop a Corrective Action Plan as required by Requirement R7. | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
TPL-007-4 | 612 | R8. | 9010 | Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity’s completed supplemental GMD Vulnerability Assessment failed to satisfy one of the elements listed in Requirement R8, Parts 8.1 through 8.3; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 64 calendar months and less than or equal to 68 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity’s completed supplemental GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R8, Parts 8.1 through 8.3; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity’s completed supplemental GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R8, Parts 8.1 through 8.3; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 72 calendar months since the last supplemental GMD Vulnerability Assessment; OR The responsible entity does not have a completed supplemental GMD Vulnerability Assessment. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
TPL-007-4 | 612 | R9. | 9018 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2020-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
TPL-007-4 (Nova Scotia) | 78830000000612 | R1. | 788300000008981 | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with its Transmission Planner(s), failed to determine and identify individual or joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard | Each Planning Coordinator, in conjunction with its Transmission Planners, shall provide documentation on roles and responsibilities, such as meeting minutes, agreements, copies of procedures or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data in accordance with Requirement R1. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 10000000
TPL-007-4 (Nova Scotia) | 78830000000612 | R11. | 788300000009029 | Each responsible entity, as determined in Requirement R1, that concludes through the supplemental GMD Vulnerability Assessment conducted in Requirement R8 that their System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity’s Corrective Action Plan failed to comply with one of the elements in Requirement R11, Parts 11.1 through 11.5. | The responsible entity’s Corrective Action Plan failed to comply with two of the elements in Requirement R11, Parts 11.1 through 11.5. | The responsible entity’s Corrective Action Plan failed to comply with three of the elements in Requirement R11, Parts 11.1 through 11.5. | The responsible entity’s Corrective Action Plan failed to comply with four or more of the elements in Requirement R11, Parts 11.1 through 11.5; OR The responsible entity did not develop a Corrective Action Plan as required by Requirement R11. | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2024-04-01 |  | 2024-03-31 | MRO-US ¦ NPCC-US ¦ RF-US ¦ SERC-US ¦ TXRE-US ¦ WECC-US | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 110000000
TPL-007-4 (Nova Scotia) | 78830000000612 | R12. | 788300000009026 | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator's planning area or other part of the system included in the Planning Coordinator's GIC System model. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator’s planning area or other part of the system included in the Planning Coordinator’s GIC System Model. | Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its GIC monitor location(s) and documentation of its process to obtain GIC monitor data in accordance with Requirement R12. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 120000000
TPL-007-4 (Nova Scotia) | 78830000000612 | R13. | 788300000009027 | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | M13. Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its process to obtain geomagnetic field data for its Planning Coordinator’s planning area in accordance with Requirement R13. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 130000000
TPL-007-4 (Nova Scotia) | 78830000000612 | R2. | 788300000008982 | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | N/A | N/A | The responsible entity did not maintain either System models or GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | The responsible entity did not maintain both System models and GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | Each responsible entity, as determined in Requirement R1, shall have evidence in either electronic or hard copy format that it is maintaining System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | 2021-04-01 |  | 2024-04-01 |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 20000000
TPL-007-4 (Nova Scotia) | 78830000000612 | R3. | 788300000008983 | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity did not have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 as required. | Each responsible entity, as determined in Requirement R1, shall have evidence, such as electronic or hard copies of the criteria for acceptable System steady state voltage performance for its System in accordance with Requirement R3. | 2023-04-01 |  | 2023-03-31 | MRO-US ¦ NPCC-US ¦ RF-US ¦ SERC-US ¦ TXRE-US ¦ WECC-US | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 30000000
TPL-007-4 (Nova Scotia) | 78830000000612 | R4. | 788300000008984 | Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy one of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR onths since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 72 calendar months since the last benchmark GMD Vulnerability Assessment; OR The responsible entity does not have a completed benchmark GMD Vulnerability Assessment. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2023-04-01 |  | 2023-03-31 | MRO-US ¦ NPCC-US ¦ RF-US ¦ SERC-US ¦ TXRE-US ¦ WECC-US | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 40000000
TPL-007-4 (Nova Scotia) | 78830000000612 | R5. | 788300000008991 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 50000000
TPL-007-4 (Nova Scotia) | 78830000000612 | R7. | 788300000008999 | Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity's Corrective Action Plan failed to comply with one of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with two of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with three of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity’s Corrective Action Plan failed to comply with four or more of the elements in Requirement R7, Parts 7.1 through 7.5; OR The responsible entity did not develop a Corrective Action Plan as required by Requirement R7. | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2024-04-01 |  | 2024-03-31 | MRO-US ¦ NPCC-US ¦ RF-US ¦ SERC-US ¦ TXRE-US ¦ WECC-US | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 70000000
TPL-007-4 (Nova Scotia) | 78830000000612 | R8. | 788300000009010 | Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity’s completed supplemental GMD Vulnerability Assessment failed to satisfy one of the elements listed in Requirement R8, Parts 8.1 through 8.3; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 64 calendar months and less than or equal to 68 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity’s completed supplemental GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R8, Parts 8.1 through 8.3; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity’s completed supplemental GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R8, Parts 8.1 through 8.3; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 72 calendar months since the last supplemental GMD Vulnerability Assessment; OR The responsible entity does not have a completed supplemental GMD Vulnerability Assessment. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2023-04-01 |  | 2023-03-31 | MRO-US ¦ NPCC-US ¦ RF-US ¦ SERC-US ¦ TXRE-US ¦ WECC-US | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 80000000
TPL-007-4 (Nova Scotia) | 78830000000612 | R9. | 788300000009018 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-NS | [6 empty] | 90000000
TPL-007-4 (Ontario) | 79780000612 | R1. | 79780008981 | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;The Planning Coordinator, in conjunction with its Transmission Planner(s), failed to determine and identify individual or joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard&lt;/p&gt; | &lt;p&gt;Each Planning Coordinator, in conjunction with its Transmission Planners, shall provide documentation on roles and responsibilities, such as meeting minutes, agreements, copies of procedures or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data in accordance with Requirement R1.&lt;/p&gt; | 2020-03-19 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 10000000
TPL-007-4 (Ontario) | 79780000612 | R10. | 79780009021 | Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a supplemental thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase;The responsible entity failed to conduct a supplemental thermal impact asseThe responsible entity failed to conduct a supplemental thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1 OR The responsible entity failed to include one of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | &lt;p&gt;Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10.&lt;/p&gt; | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 100000000
TPL-007-4 (Ontario) | 79780000612 | R11. | 79780009029 | Each responsible entity, as determined in Requirement R1, that concludes through the supplemental GMD Vulnerability Assessment conducted in Requirement R8 that their System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity’s Corrective Action Plan failed to comply with one of the elements in Requirement R11, Parts 11.1 through 11.5. | The responsible entity’s Corrective Action Plan failed to comply with two of the elements in Requirement R11, Parts 11.1 through 11.5. | The responsible entity’s Corrective Action Plan failed to comply with three of the elements in Requirement R11, Parts 11.1 through 11.5. | The responsible entity’s Corrective Action Plan failed to comply with four or more of the elements in Requirement R11, Parts 11.1 through 11.5; OR The responsible entity did not develop a Corrective Action Plan as required by Requirement R11. | &lt;p&gt;Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11.&lt;/p&gt; | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 110000000
TPL-007-4 (Ontario) | 79780000612 | R12. | 79780009026 | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator's planning area or other part of the system included in the Planning Coordinator's GIC System model. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator’s planning area or other part of the system included in the Planning Coordinator’s GIC System Model. | &lt;p&gt;Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its GIC monitor location(s) and documentation of its process to obtain GIC monitor data in accordance with Requirement R12.&lt;/p&gt; | 2021-07-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 120000000
TPL-007-4 (Ontario) | 79780000612 | R13. | 79780009027 | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | M13. Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its process to obtain geomagnetic field data for its Planning Coordinator’s planning area in accordance with Requirement R13. | 2021-07-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 130000000
TPL-007-4 (Ontario) | 79780000612 | R2. | 79780008982 | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | N/A | N/A | The responsible entity did not maintain either System models or GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | The responsible entity did not maintain both System models and GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | &lt;p&gt;Each responsible entity, as determined in Requirement R1, shall have evidence in either electronic or hard copy format that it is maintaining System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments.&lt;/p&gt; | 2020-03-19 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 20000000
TPL-007-4 (Ontario) | 79780000612 | R3. | 79780008983 | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity did not have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 as required. | &lt;p&gt;Each responsible entity, as determined in Requirement R1, shall have evidence, such as electronic or hard copies of the criteria for acceptable System steady state voltage performance for its System in accordance with Requirement R3.&lt;/p&gt; | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 30000000
TPL-007-4 (Ontario) | 79780000612 | R4. | 79780008984 | Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy one of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR onths since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 72 calendar months since the last benchmark GMD Vulnerability Assessment; OR The responsible entity does not have a completed benchmark GMD Vulnerability Assessment. | &lt;p&gt; Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4.&lt;/p&gt; | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 40000000
TPL-007-4 (Ontario) | 79780000612 | R5. | 79780008991 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | &lt;p&gt; Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area&lt;/p&gt; | 2020-03-19 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 50000000
TPL-007-4 (Ontario) | 79780000612 | R6. | 79780008994 | Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a benchmark thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include one of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | &lt;p&gt;Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6.&lt;/p&gt; | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 60000000
TPL-007-4 (Ontario) | 79780000612 | R7. | 79780008999 | Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity's Corrective Action Plan failed to comply with one of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with two of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with three of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity’s Corrective Action Plan failed to comply with four or more of the elements in Requirement R7, Parts 7.1 through 7.5; OR The responsible entity did not develop a Corrective Action Plan as required by Requirement R7. | &lt;p&gt;Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7.&lt;/p&gt; | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 70000000
TPL-007-4 (Ontario) | 79780000612 | R8. | 79780009010 | Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity’s completed supplemental GMD Vulnerability Assessment failed to satisfy one of the elements listed in Requirement R8, Parts 8.1 through 8.3; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 64 calendar months and less than or equal to 68 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity’s completed supplemental GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R8, Parts 8.1 through 8.3; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity’s completed supplemental GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R8, Parts 8.1 through 8.3; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 72 calendar months since the last supplemental GMD Vulnerability Assessment; OR The responsible entity does not have a completed supplemental GMD Vulnerability Assessment. | &lt;p&gt;Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8.&lt;/p&gt; | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 80000000
TPL-007-4 (Ontario) | 79780000612 | R9. | 79780009018 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | &lt;p&gt;Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area.&lt;/p&gt; | 2020-03-19 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | NPCC-ON | [6 empty] | 90000000
TPL-007-4 (Saskatchewan) | 83750000000612 | D.A.11.3. | 837500000009048 | Include a timetable, subject to revision by the responsible entity in Part D.A.11.4, for implementing the selected actions from Part 11.1. The timetable shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP | [8 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 691300000
TPL-007-4 (Saskatchewan) | 83750000000612 | D.A.11.4. | 837500000009051 | Be revised if the responsible entity is unable to implement the CAP within the timetable for implementation provided in Part D.A.11.3. The revised CAP shall document the following: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP | [8 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 691400000
TPL-007-4 (Saskatchewan) | 83750000000612 | D.A.11.5. | 837500000009055 | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later, and (iii) to the Compliance Enforcement Authority or Applicable Governmental Authority when revised under D.A.11.4 within 90 calendar days of revision. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP | [8 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 691500000
TPL-007-4 (Saskatchewan) | 83750000000612 | D.A.7.3. | RQ-2021-07-12-0000001-SK | Include a timetable, subject to revision by the responsible entity in Part D.A.7.4, for implementing the selected actions from Part 7.1. The timetable shall: |  | GO, PCPA, TO, TP |  |  |  |  | GO |  |  |  |  | PCPA | [7 empty] | TO |  | TP | [8 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 687300000
TPL-007-4 (Saskatchewan) | 83750000000612 | D.A.7.4. | 837500000009042 | Be revised if the responsible entity is unable to implement the CAP within the timetable for implementation provided in Part D.A.7.3. The revised CAP shall document the following: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP | [8 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 687400000
TPL-007-4 (Saskatchewan) | 83750000000612 | D.A.7.5. | 837500000009046 | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later, and (iii) to the Compliance Enforcement Authority or Applicable Governmental Authority when revised under D.A.7.4 within 90 calendar days of revision. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP | [8 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 687500000
TPL-007-4 (Saskatchewan) | 83750000000612 | R1. | 837500000008981 | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with its Transmission Planner(s), failed to determine and identify individual or joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard | Each Planning Coordinator, in conjunction with its Transmission Planners, shall provide documentation on roles and responsibilities, such as meeting minutes, agreements, copies of procedures or protocols in effect between entities or between departments of a vertically integrated system, or email correspondence that identifies an agreement has been reached on individual and joint responsibilities for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data in accordance with Requirement R1. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 10000000
TPL-007-4 (Saskatchewan) | 83750000000612 | R10. | 837500000009021 | Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a supplemental thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase;The responsible entity failed to conduct a supplemental thermal impact asseThe responsible entity failed to conduct a supplemental thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1 OR The responsible entity failed to include one of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 100000000
TPL-007-4 (Saskatchewan) | 83750000000612 | R11. | 837500000009029 | Each responsible entity, as determined in Requirement R1, that concludes through the supplemental GMD Vulnerability Assessment conducted in Requirement R8 that their System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity’s Corrective Action Plan failed to comply with one of the elements in Requirement R11, Parts 11.1 through 11.5. | The responsible entity’s Corrective Action Plan failed to comply with two of the elements in Requirement R11, Parts 11.1 through 11.5. | The responsible entity’s Corrective Action Plan failed to comply with three of the elements in Requirement R11, Parts 11.1 through 11.5. | The responsible entity’s Corrective Action Plan failed to comply with four or more of the elements in Requirement R11, Parts 11.1 through 11.5; OR The responsible entity did not develop a Corrective Action Plan as required by Requirement R11. | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 110000000
TPL-007-4 (Saskatchewan) | 83750000000612 | R12. | 837500000009026 | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator's planning area or other part of the system included in the Planning Coordinator's GIC System model. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator’s planning area or other part of the system included in the Planning Coordinator’s GIC System Model. | Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its GIC monitor location(s) and documentation of its process to obtain GIC monitor data in accordance with Requirement R12. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 120000000
TPL-007-4 (Saskatchewan) | 83750000000612 | R13. | 837500000009027 | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | M13. Each responsible entity, as determined in Requirement R1, shall have evidence such as electronic or hard copies of its process to obtain geomagnetic field data for its Planning Coordinator’s planning area in accordance with Requirement R13. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 130000000
TPL-007-4 (Saskatchewan) | 83750000000612 | R2. | 837500000008982 | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | N/A | N/A | The responsible entity did not maintain either System models or GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | The responsible entity did not maintain both System models and GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | Each responsible entity, as determined in Requirement R1, shall have evidence in either electronic or hard copy format that it is maintaining System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 20000000
TPL-007-4 (Saskatchewan) | 83750000000612 | R3. | 837500000008983 | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | N/A | N/A | N/A | The responsible entity did not have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 as required. | Each responsible entity, as determined in Requirement R1, shall have evidence, such as electronic or hard copies of the criteria for acceptable System steady state voltage performance for its System in accordance with Requirement R3. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 30000000
TPL-007-4 (Saskatchewan) | 83750000000612 | R4. | 837500000008984 | Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy one of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR onths since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 72 calendar months since the last benchmark GMD Vulnerability Assessment; OR The responsible entity does not have a completed benchmark GMD Vulnerability Assessment. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 40000000
TPL-007-4 (Saskatchewan) | 83750000000612 | R5. | 837500000008991 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 50000000
TPL-007-4 (Saskatchewan) | 83750000000612 | R6. | 837500000008994 | Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Long-Term Planning | Medium | The responsible entity failed to conduct a benchmark thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include one of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 60000000
TPL-007-4 (Saskatchewan) | 83750000000612 | R7. | 837500000008999 | Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity's Corrective Action Plan failed to comply with one of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with two of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with three of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity’s Corrective Action Plan failed to comply with four or more of the elements in Requirement R7, Parts 7.1 through 7.5; OR The responsible entity did not develop a Corrective Action Plan as required by Requirement R7. | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 70000000
TPL-007-4 (Saskatchewan) | 83750000000612 | R8. | 837500000009010 | Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | High | The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity’s completed supplemental GMD Vulnerability Assessment failed to satisfy one of the elements listed in Requirement R8, Parts 8.1 through 8.3; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 64 calendar months and less than or equal to 68 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity’s completed supplemental GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R8, Parts 8.1 through 8.3; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity’s completed supplemental GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R8, Parts 8.1 through 8.3; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 72 calendar months since the last supplemental GMD Vulnerability Assessment; OR The responsible entity does not have a completed supplemental GMD Vulnerability Assessment. | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 80000000
TPL-007-4 (Saskatchewan) | 83750000000612 | R9. | 837500000009018 | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Long-Term Planning | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | MRO-SK | [6 empty] | 90000000
VAR-001-0 | 424 | R1. | 5231 | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and MVAR flows within their individual areas and with the areas of neighboring Transmission Operators. |  | TOP | [18 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
VAR-001-0 | 424 | R10. | 5242 | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  | TOP | [18 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 100000000
VAR-001-0 | 424 | R2. | 5232 | Each Transmission Operator shall acquire sufficient reactive resources within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  | TOP | [18 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
VAR-001-0 | 424 | R3. | 5233 | Each Purchasing-Selling Entity shall arrange for (self-provide or purchase) reactive resources to satisfy its reactive requirements identified by its Transmission Service Provider |  | PSE | [10 empty] | PSE | [19 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
VAR-001-0 | 424 | R4. | 5234 | The Transmission Operator shall know the status of all transmission reactive power resources, including the status of voltage regulators and power system stabilizers. |  | TOP | [18 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
VAR-001-0 | 424 | R5. | 5235 | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  | TOP | [18 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
VAR-001-0 | 424 | R6. | 5236 | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area – including reactive generation scheduling; transmission line and reactive resource switching; and, if necessary, load shedding – to maintain system and Interconnection voltages within established limits. |  | TOP | [18 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
VAR-001-0 | 424 | R7. | 5237 | Each Transmission Operator shall maintain reactive resources to support its voltage under first Contingency conditions. |  | TOP | [18 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
VAR-001-0 | 424 | R8. | 5239 | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. |  | TOP | [18 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
VAR-001-0 | 424 | R9. | 5240 | Each Generator Operator shall provide information to its Transmission Operator on the status of all generation reactive power resources, including the status of voltage regulators and power system stabilizers. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
VAR-001-0 (Ontario) | 79780000424 | R1. | 79780005231 |  |  | TOP | [18 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 10000000
VAR-001-0 (Ontario) | 79780000424 | R10. | 79780005242 |  |  | TOP | [18 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 100000000
VAR-001-0 (Ontario) | 79780000424 | R2. | 79780005232 |  |  | TOP | [18 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 20000000
VAR-001-0 (Ontario) | 79780000424 | R3. | 79780005233 |  |  | PSE | [10 empty] | PSE | [19 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 30000000
VAR-001-0 (Ontario) | 79780000424 | R4. | 79780005234 |  |  | TOP | [18 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 40000000
VAR-001-0 (Ontario) | 79780000424 | R5. | 79780005235 |  |  | TOP | [18 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 50000000
VAR-001-0 (Ontario) | 79780000424 | R6. | 79780005236 |  |  | TOP | [18 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 60000000
VAR-001-0 (Ontario) | 79780000424 | R7. | 79780005237 |  |  | TOP | [18 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 70000000
VAR-001-0 (Ontario) | 79780000424 | R8. | 79780005239 |  |  | TOP | [18 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 80000000
VAR-001-0 (Ontario) | 79780000424 | R9. | 79780005240 |  |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP | [11 empty] | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 90000000
VAR-001-1 | 194 | R1. | 2214 | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2007-06-18 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
VAR-001-1 | 194 | R10. | 2215 | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2007-06-18 |  | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 100000000
VAR-001-1 | 194 | R11. | 2216 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  |  | Low | [5 empty] | 2007-06-18 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 110000000
VAR-001-1 | 194 | R12. | 2217 | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2007-06-18 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 120000000
VAR-001-1 | 194 | R2. | 2218 | Each Transmission Operator shall acquire sufficient reactive resources within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2007-06-18 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
VAR-001-1 | 194 | R3. | 2219 | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. |  | TOP | [18 empty] | TOP |  |  |  | Low | [5 empty] | 2007-06-18 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
VAR-001-1 | 194 | R4. | 2222 | Each Transmission Operator shall specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | Medium |  |  |  | The Transmission Operator provide No evidence that voltage or Reactive Power schedules were provided to Generator Operators as required in R4. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
VAR-001-1 | 194 | R5. | 2223 | Each Purchasing-Selling Entity shall arrange for (self-provide or purchase) reactive resources to satisfy its reactive requirements identified by its Transmission Service Provider. |  | PSE | [10 empty] | PSE | [11 empty] | High | [5 empty] | 2007-06-18 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
VAR-001-1 | 194 | R6. | 2224 | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2007-06-18 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
VAR-001-1 | 194 | R7. | 2226 | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2007-06-18 |  | 2011-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
VAR-001-1 | 194 | R8. | 2227 | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area - including reactive generation scheduling; transmission line and reactive resource switching; and, if necessary, load shedding - to maintain system and Interconnection voltages within established limits. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2007-06-18 |  | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
VAR-001-1 | 194 | R9. | 2228 | Each Transmission Operator shall maintain reactive resources to support its voltage under first Contingency conditions. |  | TOP | [18 empty] | TOP |  |  |  | High | The Transmission Operator maintains 95% or more of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains 85% or more but less than 95% of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains 75% or more but less then 85% of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains less than 75% of the reactive resources needed to support its voltage under first Contingency conditions. |  | 2007-06-18 |  | 2007-01-01 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
VAR-001-1a | 195 | R1. | 2230 | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. |  | TOP | [18 empty] | TOP | [11 empty] | 2009-05-21 |  |  | VAR-001-1 R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
VAR-001-1a | 195 | R10. | 2231 | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. |  | TOP | [18 empty] | TOP | [9 empty] | 2007-06-18 |  | 2011-09-30 |  |  | VAR-001-1 R10. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 100000000
VAR-001-1a | 195 | R11. | 2232 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP | [9 empty] | 2007-06-18 |  | 2011-09-30 |  |  | VAR-001-1 R11. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 110000000
VAR-001-1a | 195 | R12. | 2233 | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  | TOP | [18 empty] | TOP | [9 empty] | 2007-06-18 |  | 2011-09-30 |  |  | VAR-001-1 R12. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 120000000
VAR-001-1a | 195 | R2. | 2234 | Each Transmission Operator shall acquire sufficient reactive resources within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  | TOP | [18 empty] | TOP | [11 empty] | 2009-05-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
VAR-001-1a | 195 | R3. | 2235 | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. |  | TOP | [18 empty] | TOP | [11 empty] | 2009-05-21 |  |  | VAR-001-1 R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
VAR-001-1a | 195 | R4. | 2238 | Each Transmission Operator shall specify a voltage or Reactive Power schedule 1 at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). |  | TOP | [18 empty] | TOP | [11 empty] | 2009-05-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
VAR-001-1a | 195 | R5. | 2239 | Each Purchasing-Selling Entity shall arrange for (self-provide or purchase) reactive resources to satisfy its reactive requirements identified by its Transmission Service Provider. |  | PSE | [10 empty] | PSE | [19 empty] | 2009-05-21 |  |  | VAR-001-1 R5. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
VAR-001-1a | 195 | R6. | 2240 | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. |  | TOP | [18 empty] | TOP | [11 empty] | 2009-05-21 |  |  | VAR-001-1 R6. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
VAR-001-1a | 195 | R7. | 2242 | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  | TOP | [18 empty] | TOP | [11 empty] | 2009-05-21 |  |  | VAR-001-1 R7. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
VAR-001-1a | 195 | R8. | 2243 | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area - including reactive generation scheduling; transmission line and reactive resource switching; and, if necessary, load shedding - to maintain system and Interconnection voltages within established limits. |  | TOP | [18 empty] | TOP | [11 empty] | 2009-05-21 |  |  | VAR-001-1 R8. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
VAR-001-1a | 195 | R9. | 2244 | Each Transmission Operator shall maintain reactive resources to support its voltage under first Contingency conditions. |  | TOP | [18 empty] | TOP | [11 empty] | 2009-05-21 |  |  | VAR-001-1 R9. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
VAR-001-1a (Ontario) | 79780000195 | R1. | 79780002230 | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. |  | TOP | [18 empty] | TOP | [5 empty] | The Transmission Operator has formal policies and procedures for monitoring and controlling voltage and MVAR flows, but they are not current. | The Transmission Operator has formal policies and procedures for monitoring and controlling voltage and MVAR flows that are current, but they have not been coordinated with one or more neighboring Transmission Operators | The Transmission Operator has formal policies and procedures for monitoring and controlling voltage and MVAR flows, but has not implemented them; or, the Transmission Operator does not have formal policies and procedures for monitoring and controlling vol |  |  |  | 2009-05-21 |  |  |  | NPCC-ON | [6 empty] | 10000000
VAR-001-1a (Ontario) | 79780000195 | R10. | 79780002231 | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. |  | TOP | [18 empty] | TOP |  |  |  |  | The applicable entity did not correct the IROL or SOL violations and/or complete the required IROL or SOL violation reporting, as directed by the requirement, affecting 5% or less of the violations. | The applicable entity did not correct the IROL or SOL violations and/or complete the required IROL or SOL violation reporting, as directed by the requirement, affecting between 5-10% of the violations. | The applicable entity did not correct the IROL or SOL violations and/or complete the required IROL or SOL violation reporting, as directed by the requirement, affecting 10-15%, inclusive, of the violations. | The applicable entity did not correct the IROL or SOL violations and/or complete the required IROL or SOL violation reporting, as directed by the requirement, affecting greater than 15% of the violations. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 100000000
VAR-001-1a (Ontario) | 79780000195 | R11. | 79780002232 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  |  |  | The Transmission Operator provided documentation to the Generator Owner specifying required step-up transformer tap changes and a timeframe for making these changes, but failed to provide technical justification for these changes. | The Transmission Operator provided documentation to the Generator Owner specifying required step-up transformer tap changes, but failed to provide a timeframe for making these changes and technical justification for these changes. | The Transmission Operator failed to provide documentation to the Generator Owner specifying required step-up transformer tap changes, a timeframe for making these changes, and technical justification for these changes. |  |  | 2007-06-18 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 110000000
VAR-001-1a (Ontario) | 79780000195 | R12. | 79780002233 | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  | TOP | [18 empty] | TOP | [7 empty] | The Transmission Operator has failed to direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 120000000
VAR-001-1a (Ontario) | 79780000195 | R2. | 79780002234 | Each Transmission Operator shall acquire sufficient reactive resources within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  | TOP | [18 empty] | TOP |  |  |  |  | The Transmission Operator acquired 95% but less than 100% of the reactive resources within its area needed to protect the voltage levels under normal and Contingency conditions including the Transmission Operator’s share of the reactive requirements of in | The Transmission Operator acquired 90% but less than 95% of the reactive resources within its area needed to protect the voltage levels under normal and Contingency conditions including the Transmission Operator’s share of the reactive requirements of int | The Transmission Operator acquired 85% but less than 90% of the reactive resources within its area needed to protect the voltage levels under normal and Contingency conditions including the Transmission Operator’s share of the reactive requirements of int | The Transmission Operator acquired less than 85% of the reactive resources within its area needed to protect the voltage levels under normal and Contingency conditions including the Transmission Operator’s share of the reactive requirements of interconnec |  |  |  | 2009-05-21 |  |  |  | NPCC-ON | [6 empty] | 20000000
VAR-001-1a (Ontario) | 79780000195 | R3. | 79780002235 | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. |  | TOP | [18 empty] | TOP | [7 empty] | The Transmission Operator did not specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. to all of the parties involved. |  |  |  | 2009-05-21 |  |  |  | NPCC-ON | [6 empty] | 30000000
VAR-001-1a (Ontario) | 79780000195 | R4. | 79780002238 | Each Transmission Operator shall specify a voltage or Reactive Power schedule 1 at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). |  | TOP | [18 empty] | TOP | [6 empty] | The Transmission Operator provide Voltage or Reactive Power schedules were for some but not all generating units as required in R4. | The Transmission Operator provide No evidence that voltage or Reactive Power schedules were provided to Generator Operators as required in R4. |  |  |  | 2009-05-21 |  |  |  | NPCC-ON | [6 empty] | 40000000
VAR-001-1a (Ontario) | 79780000195 | R5. | 79780002239 | Each Purchasing-Selling Entity shall arrange for (self-provide or purchase) reactive resources to satisfy its reactive requirements identified by its Transmission Service Provider. |  | PSE | [10 empty] | PSE | [12 empty] | The applicable entity did not arrange for reactive resources, as directed by the requirement, affecting 5% or less of its reactive requirements. | The applicable entity did not arrange for reactive resources, as directed by the requirement, affecting between 5-10% of its reactive requirements. | The applicable entity did not arrange for reactive resources, as directed by the requirement, affecting 10-15%, inclusive, of its reactive requirements. | The applicable entity did not arrange for reactive resources, as directed by the requirement, affecting greater than 15% of its reactive requirements. |  |  |  | 2009-05-21 |  |  |  | NPCC-ON | [6 empty] | 50000000
VAR-001-1a (Ontario) | 79780000195 | R6. | 79780002240 | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. |  | TOP | [18 empty] | TOP |  |  |  |  | The applicable entity did not know the status of all transmission reactive power resources, including the status of voltage regulators and power system stabilizers, as directed by the requirement, affecting 5% or less of the required resources. | The applicable entity did not know the status of all transmission reactive power resources, including the status of voltage regulators and power system stabilizers, as directed by the requirement, affecting between 5-10% of the required resources. | The applicable entity did not know the status of all transmission reactive power resources, including the status of voltage regulators and power system stabilizers, as directed by the requirement, affecting 10-15%, inclusive, of the required resources. | The applicable entity did not know the status of all transmission reactive power resources, including the status of voltage regulators and power system stabilizers, as directed by the requirement, affecting 15% or greater of required resources. |  |  |  | 2009-05-21 |  |  |  | NPCC-ON | [6 empty] | 60000000
VAR-001-1a (Ontario) | 79780000195 | R7. | 79780002242 | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  | TOP | [18 empty] | TOP |  |  |  |  | The applicable entity was not able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow, affecting 5% or less of the required devices. | The applicable entity was not able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow, affecting between 5-10% of the required devices. | The applicable entity was not able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow, affecting 10-15%, inclusive, of the required devices. | The applicable entity was not able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow, affecting greater than 15% of the required devices. |  |  |  | 2009-05-21 |  |  |  | NPCC-ON | [6 empty] | 70000000
VAR-001-1a (Ontario) | 79780000195 | R8. | 79780002243 | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area - including reactive generation scheduling; transmission line and reactive resource switching; and, if necessary, load shedding - to maintain system and Interconnection voltages within established limits. |  | TOP | [18 empty] | TOP |  |  |  |  | The applicable entity did not operate or direct the operation of capacitive and inductive reactive resources or load shedding within its area, as directed by the requirement, affecting 5% or less of the required resources. | The applicable entity did not operate or direct the operation of capacitive and inductive reactive resources or load shedding within its area, as directed by the requirement, affecting between 5-10% of the required resources. | The applicable entity did not operate or direct the operation of capacitive and inductive reactive resources or load shedding within its area, as directed by the requirement, affecting 10-15%, inclusive, of the required resources. | The applicable entity did not operate or direct the operation of capacitive and inductive reactive resources or load shedding within its area, as directed by the requirement, affecting greater than 15% of the required resources. |  |  |  | 2009-05-21 |  |  |  | NPCC-ON | [6 empty] | 80000000
VAR-001-1a (Ontario) | 79780000195 | R9. | 79780002244 | Each Transmission Operator shall maintain reactive resources to support its voltage under first Contingency conditions. |  | TOP | [18 empty] | TOP |  |  |  |  | The Transmission Operator maintains 95% or more of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains 85% or more but less than 95% of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains 75% or more but less then 85% of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains less than 75% of the reactive resources needed to support its voltage under first Contingency conditions. |  |  |  | 2009-05-21 |  |  |  | NPCC-ON | [6 empty] | 90000000
VAR-001-1 (British Columbia) | 666700000010309 | R1. | 666700000011851 | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2010-11-01 |  | 2013-07-14 |  |  |  | WECC-BC | [6 empty] | 10000000
VAR-001-1 (British Columbia) | 666700000010309 | R10. | 666700000011852 | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2010-11-01 |  | 2013-07-14 |  |  |  | WECC-BC | [6 empty] | 100000000
VAR-001-1 (British Columbia) | 666700000010309 | R11. | 666700000011853 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  |  | Low | [5 empty] | 2010-11-01 |  | 2013-07-14 |  |  |  | WECC-BC | [6 empty] | 110000000
VAR-001-1 (British Columbia) | 666700000010309 | R12. | 666700000011854 | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2010-11-01 |  | 2013-07-14 |  |  |  | WECC-BC | [6 empty] | 120000000
VAR-001-1 (British Columbia) | 666700000010309 | R2. | 666700000011855 | Each Transmission Operator shall acquire sufficient reactive resources within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2010-11-01 |  | 2013-07-14 |  |  |  | WECC-BC | [6 empty] | 20000000
VAR-001-1 (British Columbia) | 666700000010309 | R3. | 666700000011856 | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. |  | TOP | [18 empty] | TOP |  |  |  | Low | [5 empty] | 2010-11-01 |  | 2013-07-14 |  |  |  | WECC-BC | [6 empty] | 30000000
VAR-001-1 (British Columbia) | 666700000010309 | R4. | 666700000011857 | Each Transmission Operator shall specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | Medium |  |  |  | The Transmission Operator provide No evidence that voltage or Reactive Power schedules were provided to Generator Operators as required in R4. |  | 2010-11-01 |  | 2013-07-14 |  |  |  | WECC-BC | [6 empty] | 40000000
VAR-001-1 (British Columbia) | 666700000010309 | R5. | 666700000011858 | Each Purchasing-Selling Entity shall arrange for (self-provide or purchase) reactive resources to satisfy its reactive requirements identified by its Transmission Service Provider. |  | PSE | [10 empty] | PSE | [11 empty] | High | [5 empty] | 2010-11-01 |  | 2013-07-14 |  |  |  | WECC-BC | [6 empty] | 50000000
VAR-001-1 (British Columbia) | 666700000010309 | R6. | 666700000011859 | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-11-01 |  | 2013-07-14 |  |  |  | WECC-BC | [6 empty] | 60000000
VAR-001-1 (British Columbia) | 666700000010309 | R7. | 666700000011860 | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2010-11-01 |  | 2013-07-14 |  |  |  | WECC-BC | [6 empty] | 70000000
VAR-001-1 (British Columbia) | 666700000010309 | R8. | 666700000011861 | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area - including reactive generation scheduling; transmission line and reactive resource switching; and, if necessary, load shedding - to maintain system and Interconnection voltages within established limits. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2010-11-01 |  | 2013-07-14 |  |  |  | WECC-BC | [6 empty] | 80000000
VAR-001-1 (British Columbia) | 666700000010309 | R9. | 666700000011862 | Each Transmission Operator shall maintain reactive resources to support its voltage under first Contingency conditions. |  | TOP | [18 empty] | TOP |  |  |  | High | The Transmission Operator maintains 95% or more of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains 85% or more but less than 95% of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains 75% or more but less then 85% of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains less than 75% of the reactive resources needed to support its voltage under first Contingency conditions. |  | 2010-11-01 |  | 2013-07-14 |  |  |  | WECC-BC | [6 empty] | 90000000
VAR-001-1 (Manitoba) | 77660000000194 | R1. | 776600000002214 | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 10000000
VAR-001-1 (Manitoba) | 77660000000194 | R10. | 776600000002215 | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 100000000
VAR-001-1 (Manitoba) | 77660000000194 | R11. | 776600000002216 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  |  | Low | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 110000000
VAR-001-1 (Manitoba) | 77660000000194 | R12. | 776600000002217 | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 120000000
VAR-001-1 (Manitoba) | 77660000000194 | R2. | 776600000002218 | Each Transmission Operator shall acquire sufficient reactive resources within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 20000000
VAR-001-1 (Manitoba) | 77660000000194 | R3. | 776600000002219 | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. |  | TOP | [18 empty] | TOP |  |  |  | Low | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 30000000
VAR-001-1 (Manitoba) | 77660000000194 | R4. | 776600000002222 | Each Transmission Operator shall specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | Medium |  |  |  | The Transmission Operator provide No evidence that voltage or Reactive Power schedules were provided to Generator Operators as required in R4. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 40000000
VAR-001-1 (Manitoba) | 77660000000194 | R5. | 776600000002223 | Each Purchasing-Selling Entity shall arrange for (self-provide or purchase) reactive resources to satisfy its reactive requirements identified by its Transmission Service Provider. |  | PSE | [10 empty] | PSE | [11 empty] | High | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 50000000
VAR-001-1 (Manitoba) | 77660000000194 | R6. | 776600000002224 | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 60000000
VAR-001-1 (Manitoba) | 77660000000194 | R7. | 776600000002226 | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 70000000
VAR-001-1 (Manitoba) | 77660000000194 | R8. | 776600000002227 | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area - including reactive generation scheduling; transmission line and reactive resource switching; and, if necessary, load shedding - to maintain system and Interconnection voltages within established limits. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 80000000
VAR-001-1 (Manitoba) | 77660000000194 | R9. | 776600000002228 | Each Transmission Operator shall maintain reactive resources to support its voltage under first Contingency conditions. |  | TOP | [18 empty] | TOP |  |  |  | High | The Transmission Operator maintains 95% or more of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains 85% or more but less than 95% of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains 75% or more but less then 85% of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains less than 75% of the reactive resources needed to support its voltage under first Contingency conditions. |  | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 90000000
VAR-001-1 (Ontario) | 79780000194 | R1. | 79780002214 | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. |  | TOP | [18 empty] | TOP |  |  |  | High |  | The Transmission Operator has formal policies and procedures for monitoring and controlling voltage and MVAR flows, but they are not current. | The Transmission Operator has formal policies and procedures for monitoring and controlling voltage and MVAR flows that are current, but they have not been coordinated with one or more neighboring Transmission Operators | The Transmission Operator has formal policies and procedures for monitoring and controlling voltage and MVAR flows, but has not implemented them; or, the Transmission Operator does not have formal policies and procedures for monitoring and controlling vol |  | 2007-06-18 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
VAR-001-1 (Ontario) | 79780000194 | R10. | 79780002215 | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. |  | TOP | [18 empty] | TOP |  |  |  | High | The applicable entity did not correct the IROL or SOL violations and/or complete the required IROL or SOL violation reporting, as directed by the requirement, affecting 5% or less of the violations. | The applicable entity did not correct the IROL or SOL violations and/or complete the required IROL or SOL violation reporting, as directed by the requirement, affecting between 5-10% of the violations. | The applicable entity did not correct the IROL or SOL violations and/or complete the required IROL or SOL violation reporting, as directed by the requirement, affecting 10-15%, inclusive, of the violations. | The applicable entity did not correct the IROL or SOL violations and/or complete the required IROL or SOL violation reporting, as directed by the requirement, affecting greater than 15% of the violations. |  | 2007-06-18 |  | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 100000000
VAR-001-1 (Ontario) | 79780000194 | R11. | 79780002216 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  |  | Low | The Transmission Operator provided documentation to the Generator Owner specifying required step-up transformer tap changes and a timeframe for making these changes, but failed to provide technical justification for these changes. | The Transmission Operator provided documentation to the Generator Owner specifying required step-up transformer tap changes, but failed to provide a timeframe for making these changes and technical justification for these changes. | The Transmission Operator failed to provide documentation to the Generator Owner specifying required step-up transformer tap changes, a timeframe for making these changes, and technical justification for these changes. |  |  | 2007-06-18 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 110000000
VAR-001-1 (Ontario) | 79780000194 | R12. | 79780002217 | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  | TOP | [18 empty] | TOP |  |  |  | High |  |  |  | The Transmission Operator has failed to direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 120000000
VAR-001-1 (Ontario) | 79780000194 | R2. | 79780002218 | Each Transmission Operator shall acquire sufficient reactive resources within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  | TOP | [18 empty] | TOP |  |  |  | High | The Transmission Operator acquired 95% but less than 100% of the reactive resources within its area needed to protect the voltage levels under normal and Contingency conditions including the Transmission Operator’s share of the reactive requirements of in | The Transmission Operator acquired 90% but less than 95% of the reactive resources within its area needed to protect the voltage levels under normal and Contingency conditions including the Transmission Operator’s share of the reactive requirements of int | The Transmission Operator acquired 85% but less than 90% of the reactive resources within its area needed to protect the voltage levels under normal and Contingency conditions including the Transmission Operator’s share of the reactive requirements of int | The Transmission Operator acquired less than 85% of the reactive resources within its area needed to protect the voltage levels under normal and Contingency conditions including the Transmission Operator’s share of the reactive requirements of interconnec |  | 2007-06-18 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
VAR-001-1 (Ontario) | 79780000194 | R3. | 79780002219 | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. |  | TOP | [18 empty] | TOP |  |  |  | Low |  |  |  | The Transmission Operator did not specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. to all of the parties involved. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
VAR-001-1 (Ontario) | 79780000194 | R4. | 79780002222 | Each Transmission Operator shall specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | Medium |  |  | The Transmission Operator provide Voltage or Reactive Power schedules were for some but not all generating units as required in R4. | The Transmission Operator provide No evidence that voltage or Reactive Power schedules were provided to Generator Operators as required in R4. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
VAR-001-1 (Ontario) | 79780000194 | R5. | 79780002223 | Each Purchasing-Selling Entity shall arrange for (self-provide or purchase) reactive resources to satisfy its reactive requirements identified by its Transmission Service Provider. |  | PSE | [10 empty] | PSE | [11 empty] | High | The applicable entity did not arrange for reactive resources, as directed by the requirement, affecting 5% or less of its reactive requirements. | The applicable entity did not arrange for reactive resources, as directed by the requirement, affecting between 5-10% of its reactive requirements. | The applicable entity did not arrange for reactive resources, as directed by the requirement, affecting 10-15%, inclusive, of its reactive requirements. | The applicable entity did not arrange for reactive resources, as directed by the requirement, affecting greater than 15% of its reactive requirements. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 50000000
VAR-001-1 (Ontario) | 79780000194 | R6. | 79780002224 | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. |  | TOP | [18 empty] | TOP |  |  |  | Medium | The applicable entity did not know the status of all transmission reactive power resources, including the status of voltage regulators and power system stabilizers, as directed by the requirement, affecting 5% or less of the required resources. | The applicable entity did not know the status of all transmission reactive power resources, including the status of voltage regulators and power system stabilizers, as directed by the requirement, affecting between 5-10% of the required resources. | The applicable entity did not know the status of all transmission reactive power resources, including the status of voltage regulators and power system stabilizers, as directed by the requirement, affecting 10-15%, inclusive, of the required resources. | The applicable entity did not know the status of all transmission reactive power resources, including the status of voltage regulators and power system stabilizers, as directed by the requirement, affecting 15% or greater of required resources. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 60000000
VAR-001-1 (Ontario) | 79780000194 | R7. | 79780002226 | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  | TOP | [18 empty] | TOP |  |  |  | High | The applicable entity was not able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow, affecting 5% or less of the required devices. | The applicable entity was not able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow, affecting between 5-10% of the required devices. | The applicable entity was not able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow, affecting 10-15%, inclusive, of the required devices. | The applicable entity was not able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow, affecting greater than 15% of the required devices. |  | 2007-06-18 |  | 2011-09-30 |  |  |  | NPCC-ON | [6 empty] | 70000000
VAR-001-1 (Ontario) | 79780000194 | R8. | 79780002227 | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area - including reactive generation scheduling; transmission line and reactive resource switching; and, if necessary, load shedding - to maintain system and Interconnection voltages within established limits. |  | TOP | [18 empty] | TOP |  |  |  | High | The applicable entity did not operate or direct the operation of capacitive and inductive reactive resources or load shedding within its area, as directed by the requirement, affecting 5% or less of the required resources. | The applicable entity did not operate or direct the operation of capacitive and inductive reactive resources or load shedding within its area, as directed by the requirement, affecting between 5-10% of the required resources. | The applicable entity did not operate or direct the operation of capacitive and inductive reactive resources or load shedding within its area, as directed by the requirement, affecting 10-15%, inclusive, of the required resources. | The applicable entity did not operate or direct the operation of capacitive and inductive reactive resources or load shedding within its area, as directed by the requirement, affecting greater than 15% of the required resources. |  | 2007-06-18 |  | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 80000000
VAR-001-1 (Ontario) | 79780000194 | R9. | 79780002228 | Each Transmission Operator shall maintain reactive resources to support its voltage under first Contingency conditions. |  | TOP | [18 empty] | TOP |  |  |  | High | The Transmission Operator maintains 95% or more of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains 85% or more but less than 95% of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains 75% or more but less then 85% of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains less than 75% of the reactive resources needed to support its voltage under first Contingency conditions. |  | 2007-06-18 |  | 2007-01-01 |  |  |  | NPCC-ON | [6 empty] | 90000000
VAR-001-1 (Saskatchewan) | 83750000000194 | R1. | 837500000002214 | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 10000000
VAR-001-1 (Saskatchewan) | 83750000000194 | R10. | 837500000002215 | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 100000000
VAR-001-1 (Saskatchewan) | 83750000000194 | R11. | 837500000002216 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  |  | Low | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 110000000
VAR-001-1 (Saskatchewan) | 83750000000194 | R12. | 837500000002217 | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 120000000
VAR-001-1 (Saskatchewan) | 83750000000194 | R2. | 837500000002218 | Each Transmission Operator shall acquire sufficient reactive resources within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 20000000
VAR-001-1 (Saskatchewan) | 83750000000194 | R3. | 837500000002219 | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. |  | TOP | [18 empty] | TOP |  |  |  | Low | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 30000000
VAR-001-1 (Saskatchewan) | 83750000000194 | R4. | 837500000002222 | Each Transmission Operator shall specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | Medium |  |  |  | The Transmission Operator provide No evidence that voltage or Reactive Power schedules were provided to Generator Operators as required in R4. |  | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 40000000
VAR-001-1 (Saskatchewan) | 83750000000194 | R5. | 837500000002223 | Each Purchasing-Selling Entity shall arrange for (self-provide or purchase) reactive resources to satisfy its reactive requirements identified by its Transmission Service Provider. |  | PSE | [10 empty] | PSE | [11 empty] | High | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 50000000
VAR-001-1 (Saskatchewan) | 83750000000194 | R6. | 837500000002224 | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 60000000
VAR-001-1 (Saskatchewan) | 83750000000194 | R7. | 837500000002226 | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 70000000
VAR-001-1 (Saskatchewan) | 83750000000194 | R8. | 837500000002227 | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area - including reactive generation scheduling; transmission line and reactive resource switching; and, if necessary, load shedding - to maintain system and Interconnection voltages within established limits. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 80000000
VAR-001-1 (Saskatchewan) | 83750000000194 | R9. | 837500000002228 | Each Transmission Operator shall maintain reactive resources to support its voltage under first Contingency conditions. |  | TOP | [18 empty] | TOP |  |  |  | High | The Transmission Operator maintains 95% or more of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains 85% or more but less than 95% of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains 75% or more but less then 85% of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains less than 75% of the reactive resources needed to support its voltage under first Contingency conditions. |  | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 90000000
VAR-001-2 | 275 | R1. | 3596 | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2011-10-01 |  | 2013-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
VAR-001-2 | 275 | R10. | 3597 | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2011-10-01 |  | 2009-05-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 100000000
VAR-001-2 | 275 | R11. | 3598 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  |  | Low | [5 empty] | 2011-10-01 |  | 2009-05-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 110000000
VAR-001-2 | 275 | R12. | 3599 | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2011-10-01 |  | 2009-05-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 120000000
VAR-001-2 | 275 | R2. | 3600 | Each Transmission Operator shall acquire sufficient reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load – within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2011-10-01 |  | 2013-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
VAR-001-2 | 275 | R3. | 3601 | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. |  | TOP | [18 empty] | TOP |  |  |  | Low | [5 empty] | 2011-10-01 |  | 2013-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
VAR-001-2 | 275 | R4. | 3604 | Each Transmission Operator shall specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-01 |  | 2013-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
VAR-001-2 | 275 | R5. | 3605 | Each Purchasing-Selling Entity and Load Serving Entity shall arrange for (self-provide or purchase) reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load– to satisfy its reactive requirements identified by its Transmission Service Provider. |  | LSE, PSE | [7 empty] | LSE |  |  | PSE | [11 empty] | High | [5 empty] | 2011-10-01 |  | 2014-01-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
VAR-001-2 | 275 | R6. | 3606 | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-10-01 |  | 2013-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
VAR-001-2 | 275 | R7. | 3608 | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2011-10-01 |  | 2013-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
VAR-001-2 | 275 | R8. | 3609 | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching; controllable load; and, if necessary, load shedding – to maintain system and Interconnection voltages within established limits. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2011-10-01 |  | 2013-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
VAR-001-2 | 275 | R9. | 3610 | Each Transmission Operator shall maintain reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load– to support its voltage under first Contingency conditions. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2011-10-01 |  | 2013-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
VAR-001-2 (British Columbia) | 666700000010310 | R1. | 666700000011863 | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2013-07-15 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 10000000
VAR-001-2 (British Columbia) | 666700000010310 | R10. | 666700000011864 | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2013-07-15 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 100000000
VAR-001-2 (British Columbia) | 666700000010310 | R11. | 666700000011865 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  |  | Low | [5 empty] | 2013-07-15 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 110000000
VAR-001-2 (British Columbia) | 666700000010310 | R12. | 666700000011866 | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2013-07-15 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 120000000
VAR-001-2 (British Columbia) | 666700000010310 | R2. | 666700000011867 | Each Transmission Operator shall acquire sufficient reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load – within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2013-07-15 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 20000000
VAR-001-2 (British Columbia) | 666700000010310 | R3. | 666700000011868 | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. |  | TOP | [18 empty] | TOP |  |  |  | Low | [5 empty] | 2013-07-15 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 30000000
VAR-001-2 (British Columbia) | 666700000010310 | R4. | 666700000011869 | Each Transmission Operator shall specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2013-07-15 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 40000000
VAR-001-2 (British Columbia) | 666700000010310 | R5. | 666700000011870 | Each Purchasing-Selling Entity and Load Serving Entity shall arrange for (self-provide or purchase) reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load– to satisfy its reactive requirements identified by its Transmission Service Provider. |  | LSE, PSE | [7 empty] | LSE |  |  | PSE | [11 empty] | High | [5 empty] | 2013-07-15 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 50000000
VAR-001-2 (British Columbia) | 666700000010310 | R6. | 666700000011871 | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2013-07-15 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 60000000
VAR-001-2 (British Columbia) | 666700000010310 | R7. | 666700000011872 | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2013-07-15 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 70000000
VAR-001-2 (British Columbia) | 666700000010310 | R8. | 666700000011873 | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching; controllable load; and, if necessary, load shedding – to maintain system and Interconnection voltages within established limits. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2013-07-15 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 80000000
VAR-001-2 (British Columbia) | 666700000010310 | R9. | 666700000011874 | Each Transmission Operator shall maintain reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load– to support its voltage under first Contingency conditions. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2013-07-15 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 90000000
VAR-001-2 (Manitoba) | 77660000000275 | R1. | 776600000003596 | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
VAR-001-2 (Manitoba) | 77660000000275 | R10. | 776600000003597 | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 100000000
VAR-001-2 (Manitoba) | 77660000000275 | R11. | 776600000003598 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  |  | Low | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 110000000
VAR-001-2 (Manitoba) | 77660000000275 | R12. | 776600000003599 | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 120000000
VAR-001-2 (Manitoba) | 77660000000275 | R2. | 776600000003600 | Each Transmission Operator shall acquire sufficient reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load – within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
VAR-001-2 (Manitoba) | 77660000000275 | R3. | 776600000003601 | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. |  | TOP | [18 empty] | TOP |  |  |  | Low | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
VAR-001-2 (Manitoba) | 77660000000275 | R4. | 776600000003604 | Each Transmission Operator shall specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 40000000
VAR-001-2 (Manitoba) | 77660000000275 | R5. | 776600000003605 | Each Purchasing-Selling Entity and Load Serving Entity shall arrange for (self-provide or purchase) reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load– to satisfy its reactive requirements identified by its Transmission Service Provider. |  | LSE, PSE | [7 empty] | LSE |  |  | PSE | [11 empty] | High | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 50000000
VAR-001-2 (Manitoba) | 77660000000275 | R6. | 776600000003606 | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 60000000
VAR-001-2 (Manitoba) | 77660000000275 | R7. | 776600000003608 | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 70000000
VAR-001-2 (Manitoba) | 77660000000275 | R8. | 776600000003609 | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching; controllable load; and, if necessary, load shedding – to maintain system and Interconnection voltages within established limits. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 80000000
VAR-001-2 (Manitoba) | 77660000000275 | R9. | 776600000003610 | Each Transmission Operator shall maintain reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load– to support its voltage under first Contingency conditions. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 90000000
VAR-001-2 (Ontario) | 79780000275 | R1. | 79780003596 | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. |  | TOP | [18 empty] | TOP |  |  |  | High | The applicable entity did not ensure the development and/or maintenance and/or implementation of formal policies and procedures, as directed by the requirement, affecting 5% or less of their individual and neighboring areas voltage levels and Mvar flows. | The applicable entity did not ensure the development and/or maintenance and/or implementation of formal policies and procedures, as directed by the requirement, affecting between 5-10% of their individual and neighboring areas voltage levels and Mvar flow | The applicable entity did not ensure the development and/or maintenance and/or implementation of formal policies and procedures, as directed by the requirement, affecting 10-15%, inclusive, of their individual and neighboring areas voltage levels and Mvar | The applicable entity did not ensure the development and/or maintenance and/or implementation of formal policies and procedures, as directed by the requirement, affecting greater than 15% of their individual and neighboring areas voltage levels and Mvar f |  | 2011-10-01 |  | 2013-12-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
VAR-001-2 (Ontario) | 79780000275 | R10. | 79780003597 | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. |  | TOP | [18 empty] | TOP |  |  |  | High | The applicable entity did not correct the IROL or SOL violations and/or complete the required IROL or SOL violation reporting, as directed by the requirement, affecting 5% or less of the violations. | The applicable entity did not correct the IROL or SOL violations and/or complete the required IROL or SOL violation reporting, as directed by the requirement, affecting between 5-10% of the violations. | The applicable entity did not correct the IROL or SOL violations and/or complete the required IROL or SOL violation reporting, as directed by the requirement, affecting 10-15%, inclusive, of the violations. | The applicable entity did not correct the IROL or SOL violations and/or complete the required IROL or SOL violation reporting, as directed by the requirement, affecting greater than 15% of the violations. |  | 2011-10-01 |  | 2009-05-21 |  |  |  | NPCC-ON | [6 empty] | 100000000
VAR-001-2 (Ontario) | 79780000275 | R11. | 79780003598 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  |  | Low | The Transmission Operator provided documentation to the Generator Owner specifying required step-up transformer tap changes and a timeframe for making these changes, but failed to provide technical justification for these changes. | The Transmission Operator provided documentation to the Generator Owner specifying required step-up transformer tap changes, but failed to provide a timeframe for making these changes and technical justification for these changes. | The Transmission Operator failed to provide documentation to the Generator Owner specifying required step-up transformer tap changes, a timeframe for making these changes, and technical justification for these changes. | N/A |  | 2011-10-01 |  | 2009-05-21 |  |  |  | NPCC-ON | [6 empty] | 110000000
VAR-001-2 (Ontario) | 79780000275 | R12. | 79780003599 | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  | TOP | [18 empty] | TOP |  |  |  | High | N/A | N/A | N/A | The Transmission Operator has failed to direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  | 2011-10-01 |  | 2009-05-21 |  |  |  | NPCC-ON | [6 empty] | 120000000
VAR-001-2 (Ontario) | 79780000275 | R2. | 79780003600 | Each Transmission Operator shall acquire sufficient reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load – within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  | TOP | [18 empty] | TOP |  |  |  | High | The Transmission Operator acquired 95% but less than 100% of the reactive resources within its area needed to protect the voltage levels under normal and Contingency conditions including the Transmission Operator’s share of the reactive requirements of in | The Transmission Operator acquired 90% but less than 95% of the reactive resources within its area needed to protect the voltage levels under normal and Contingency conditions including the Transmission Operator’s share of the reactive requirements of int | The Transmission Operator acquired 85% but less than 90% of the reactive resources within its area needed to protect the voltage levels under normal and Contingency conditions including the Transmission Operator’s share of the reactive requirements of int | The Transmission Operator acquired less than 85% of the reactive resources within its area needed to protect the voltage levels under normal and Contingency conditions including the Transmission Operator’s share of the reactive requirements of interconnec |  | 2011-10-01 |  | 2013-12-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
VAR-001-2 (Ontario) | 79780000275 | R3. | 79780003601 | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. |  | TOP | [18 empty] | TOP |  |  |  | Low | N/A | N/A | N/A | The Transmission Operator did not specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. to all of the parties involved. |  | 2011-10-01 |  | 2013-12-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
VAR-001-2 (Ontario) | 79780000275 | R4. | 79780003604 | Each Transmission Operator shall specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | Medium | N/A | N/A | The Transmission Operator provide Voltage or Reactive Power schedules were for some but not all generating units as required in R4. | The Transmission Operator provide No evidence that voltage or Reactive Power schedules were provided to Generator Operators as required in R4. |  | 2011-10-01 |  | 2013-12-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
VAR-001-2 (Ontario) | 79780000275 | R5. | 79780003605 | Each Purchasing-Selling Entity and Load Serving Entity shall arrange for (self-provide or purchase) reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load– to satisfy its reactive requirements identified by its Transmission Service Provider. |  | LSE, PSE | [7 empty] | LSE |  |  | PSE | [11 empty] | High | The applicable entity did not arrange for reactive resources, as directed by the requirement, affecting 5% or less of its reactive requirements. | The applicable entity did not arrange for reactive resources, as directed by the requirement, affecting between 5-10% of its reactive requirements. | The applicable entity did not arrange for reactive resources, as directed by the requirement, affecting 10-15%, inclusive, of its reactive requirements. | The applicable entity did not arrange for reactive resources, as directed by the requirement, affecting greater than 15% of its reactive requirements. |  | 2011-10-01 |  | 2014-01-21 |  |  |  | NPCC-ON | [6 empty] | 50000000
VAR-001-2 (Ontario) | 79780000275 | R6. | 79780003606 | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. |  | TOP | [18 empty] | TOP |  |  |  | Medium | The applicable entity did not know the status of all transmission reactive power resources, including the status of voltage regulators and power system stabilizers, as directed by the requirement, affecting 5% or less of the required resources. | The applicable entity did not know the status of all transmission reactive power resources, including the status of voltage regulators and power system stabilizers, as directed by the requirement, affecting between 5-10% of the required resources. | The applicable entity did not know the status of all transmission reactive power resources, including the status of voltage regulators and power system stabilizers, as directed by the requirement, affecting 10-15%, inclusive, of the required resources. | The applicable entity did not know the status of all transmission reactive power resources, including the status of voltage regulators and power system stabilizers, as directed by the requirement, affecting 15% or greater of required resources. |  | 2011-10-01 |  | 2013-12-31 |  |  |  | NPCC-ON | [6 empty] | 60000000
VAR-001-2 (Ontario) | 79780000275 | R7. | 79780003608 | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  | TOP | [18 empty] | TOP |  |  |  | High | The applicable entity was not able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow, affecting 5% or less of the required devices. | The applicable entity was not able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow, affecting between 5-10% of the required devices. | The applicable entity was not able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow, affecting 10-15%, inclusive, of the required devices. | The applicable entity was not able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow, affecting greater than 15% of the required devices. |  | 2011-10-01 |  | 2013-12-31 |  |  |  | NPCC-ON | [6 empty] | 70000000
VAR-001-2 (Ontario) | 79780000275 | R8. | 79780003609 | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching; controllable load; and, if necessary, load shedding – to maintain system and Interconnection voltages within established limits. |  | TOP | [18 empty] | TOP |  |  |  | High | The applicable entity did operate or direct the operation of capacitive and inductive reactive resources or load shedding within its area, as directed by the requirement, affecting 5% or less of the required resources. | The applicable entity did operate or direct the operation of capacitive and inductive reactive resources or load shedding within its area, as directed by the requirement, affecting between 5-10% of the required resources. | The applicable entity did operate or direct the operation of capacitive and inductive reactive resources or load shedding within its area, as directed by the requirement, affecting 10-15%, inclusive, of the required resources. | The applicable entity did operate or direct the operation of capacitive and inductive reactive resources or load shedding within its area, as directed by the requirement, affecting greater than 15% of the required resources. |  | 2011-10-01 |  | 2013-12-31 |  |  |  | NPCC-ON | [6 empty] | 80000000
VAR-001-2 (Ontario) | 79780000275 | R9. | 79780003610 | Each Transmission Operator shall maintain reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load– to support its voltage under first Contingency conditions. |  | TOP | [18 empty] | TOP |  |  |  | High | The Transmission Operator maintains 95% or more of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains 85% or more but less than 95% of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains 75% or more but less then 85% of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains less than 75% of the reactive resources needed to support its voltage under first Contingency conditions. |  | 2011-10-01 |  | 2013-12-31 |  |  |  | NPCC-ON | [6 empty] | 90000000
VAR-001-3 | 328 | E.A.13 | 4775 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. |  | 2014-01-01 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2200000
VAR-001-3 | 328 | E.A.14 | 4776 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. |  | 2014-01-01 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2300000
VAR-001-3 | 328 | E.A.15 | 4777 | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. |  | GOP | [5 empty] | GOP | [15 empty] | Long-Term Planning | Medium | The Generator Operator failed to convert at least one voltage schedule in Requirement E.A.13 into the voltage set point for the AVR for less than 25% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 25% or more but less than 50% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 50% or more but less than 75% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 75% or more of the voltage schedules. |  | 2014-01-01 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2400000
VAR-001-3 | 328 | E.A.16 | 4778 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Long-Term Planning | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. |  | 2014-01-01 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2500000
VAR-001-3 | 328 | E.A.17 | 4779 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | TOP | [18 empty] | TOP |  |  |  | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. |  | 2013-06-20 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2600000
VAR-001-3 | 328 | E.A.18 | 4780 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the Automatic Voltage Regulators (AVR) to manage MVar loading: E.A.18.1. Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. E.A.18.2. Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | N/A | The Generator Operator did not meet the control loop specifications in EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 through EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. |  | 2013-06-20 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2700000
VAR-001-3 | 328 | R1. | 4316 | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-01-01 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
VAR-001-3 | 328 | R10. | 4329 | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2011-10-01 |  | 2013-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 100000000
VAR-001-3 | 328 | R11. | 4330 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP | [9 empty] | 2013-06-20 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 110000000
VAR-001-3 | 328 | R12. | 4331 | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2013-06-20 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 120000000
VAR-001-3 | 328 | R2. | 4317 | Each Transmission Operator shall acquire sufficient reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load – within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-01-01 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
VAR-001-3 | 328 | R3. | 4318 | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. |  | TOP | [18 empty] | TOP |  |  |  | Low | [5 empty] | 2014-01-01 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
VAR-001-3 | 328 | R4. | 4321 | Each Transmission Operator shall specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2014-01-01 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
VAR-001-3 | 328 | R5. | 4322 | Each Purchasing-Selling Entity and Load Serving Entity shall arrange for (self-provide or purchase) reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load– to satisfy its reactive requirements identified by its Transmission Service Provider. |  | LSE, PSE | [7 empty] | LSE |  |  | PSE | [11 empty] | High | [5 empty] | 2014-01-01 |  | 2014-01-21 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
VAR-001-3 | 328 | R6. | 4323 | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2014-01-01 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
VAR-001-3 | 328 | R7. | 4325 | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-01-01 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 70000000
VAR-001-3 | 328 | R8. | 4326 | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching; controllable load; and, if necessary, load shedding – to maintain system and Interconnection voltages within established limits. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-01-01 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 80000000
VAR-001-3 | 328 | R9. | 4327 | Each Transmission Operator shall maintain reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching; and controllable load– to support its voltage under first Contingency conditions. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-01-01 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 90000000
VAR-001-3 (British Columbia) | 666700000010311 | E.A.13 | 666700000011875 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. |  | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 2200000
VAR-001-3 (British Columbia) | 666700000010311 | E.A.14 | 666700000011876 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. |  | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 2300000
VAR-001-3 (British Columbia) | 666700000010311 | E.A.15 | 666700000011877 | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. |  | GOP | [5 empty] | GOP | [15 empty] | Long-Term Planning | Medium | The Generator Operator failed to convert at least one voltage schedule in Requirement E.A.13 into the voltage set point for the AVR for less than 25% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 25% or more but less than 50% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 50% or more but less than 75% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 75% or more of the voltage schedules. |  | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 2400000
VAR-001-3 (British Columbia) | 666700000010311 | E.A.16 | 666700000011878 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Long-Term Planning | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. |  | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 2500000
VAR-001-3 (British Columbia) | 666700000010311 | E.A.17 | 666700000011879 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | TOP | [18 empty] | TOP |  |  |  | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. |  | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 2600000
VAR-001-3 (British Columbia) | 666700000010311 | E.A.18 | 666700000011880 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the Automatic Voltage Regulators (AVR) to manage MVar loading: E.A.18.1. Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. E.A.18.2. Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | N/A | The Generator Operator did not meet the control loop specifications in EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 through EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. |  | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 2700000
VAR-001-3 (British Columbia) | 666700000010311 | R1. | 666700000011881 | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
VAR-001-3 (British Columbia) | 666700000010311 | R10. | 666700000011882 | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 100000000
VAR-001-3 (British Columbia) | 666700000010311 | R11. | 666700000011883 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP | [9 empty] | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 110000000
VAR-001-3 (British Columbia) | 666700000010311 | R12. | 666700000011884 | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 120000000
VAR-001-3 (British Columbia) | 666700000010311 | R2. | 666700000011885 | Each Transmission Operator shall acquire sufficient reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load – within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 20000000
VAR-001-3 (British Columbia) | 666700000010311 | R3. | 666700000011886 | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. |  | TOP | [18 empty] | TOP |  |  |  | Low | [5 empty] | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 30000000
VAR-001-3 (British Columbia) | 666700000010311 | R4. | 666700000011887 | Each Transmission Operator shall specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 40000000
VAR-001-3 (British Columbia) | 666700000010311 | R5. | 666700000011888 | Each Purchasing-Selling Entity and Load Serving Entity shall arrange for (self-provide or purchase) reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load– to satisfy its reactive requirements identified by its Transmission Service Provider. |  | LSE, PSE | [7 empty] | LSE |  |  | PSE | [11 empty] | High | [5 empty] | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 50000000
VAR-001-3 (British Columbia) | 666700000010311 | R6. | 666700000011889 | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 60000000
VAR-001-3 (British Columbia) | 666700000010311 | R7. | 666700000011890 | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 70000000
VAR-001-3 (British Columbia) | 666700000010311 | R8. | 666700000011891 | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching; controllable load; and, if necessary, load shedding – to maintain system and Interconnection voltages within established limits. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 80000000
VAR-001-3 (British Columbia) | 666700000010311 | R9. | 666700000011892 | Each Transmission Operator shall maintain reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching; and controllable load– to support its voltage under first Contingency conditions. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 90000000
VAR-001-3 (Ontario) | 79780000328 | E.A.13 | 79780004775 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area:&lt;br/&gt;• A voltage set point with a voltage tolerance band and a specified period.&lt;br/&gt;• An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point.&lt;br/&gt;• A voltage band for a specified period. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | M6. Each Planning Coordinator shall have dated evidence such as a UFLS database, data requests, data input forms, or other dated documentation to show that it maintained a UFLS database for use in event analyses and assessments of the UFLS program per Requirement R6 at least once each calendar year, with no more than 15 months between maintenance activities. | 2014-01-01 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 2200000
VAR-001-3 (Ontario) | 79780000328 | E.A.14 | 79780004776 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator.&lt;br/&gt;• The generator terminals.&lt;br/&gt;• The high side of the generator step-up transformer.&lt;br/&gt;• The point of interconnection.&lt;br/&gt;• A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | M7. Each Planning Coordinator shall have dated evidence such as letters, memorandums, e-mails or other dated documentation that it provided their UFLS database to other Planning Coordinators within their Interconnection within 30 calendar days of a request per Requirement R7. | 2014-01-01 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 2300000
VAR-001-3 (Ontario) | 79780000328 | E.A.15 | 79780004777 | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. |  | GOP | [5 empty] | GOP | [15 empty] | Long-Term Planning | Medium | The Generator Operator failed to convert at least one voltage schedule in Requirement E.A.13 into the voltage set point for the AVR for less than 25% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 25% or more but less than 50% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 50% or more but less than 75% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 75% or more of the voltage schedules. | M8. Each UFLS Entity shall have dated evidence such as responses to data requests, spreadsheets, letters or other dated documentation that it provided data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of the UFLS database per Requirement R8. | 2014-01-01 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 2400000
VAR-001-3 (Ontario) | 79780000328 | E.A.16 | 79780004778 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Long-Term Planning | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | M9. Each UFLS Entity shall have dated evidence such as spreadsheets summarizing feeder load armed with UFLS relays, spreadsheets with UFLS relay settings, or other dated documentation that it provided automatic tripping of load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, per Requirement R9. | 2014-01-01 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 2500000
VAR-001-3 (Ontario) | 79780000328 | E.A.17 | 79780004779 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | TOP | [18 empty] | TOP |  |  |  | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. |  | 2013-06-20 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 2600000
VAR-001-3 (Ontario) | 79780000328 | E.A.18 | 79780004780 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the Automatic Voltage Regulators (AVR) to manage MVar loading:&lt;br/&gt;E.A.18.1. Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances.&lt;br/&gt;E.A.18.2. Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | N/A | The Generator Operator did not meet the control loop specifications in EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 through EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. |  | 2013-06-20 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 2700000
VAR-001-3 (Ontario) | 79780000328 | R1. | 79780004316 | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-01-01 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
VAR-001-3 (Ontario) | 79780000328 | R10. | 79780004329 | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2011-10-01 |  | 2013-12-31 |  |  |  | NPCC-ON | [6 empty] | 100000000
VAR-001-3 (Ontario) | 79780000328 | R11. | 79780004330 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP | [9 empty] | 2013-06-20 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 110000000
VAR-001-3 (Ontario) | 79780000328 | R12. | 79780004331 | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2013-06-20 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 120000000
VAR-001-3 (Ontario) | 79780000328 | R2. | 79780004317 | Each Transmission Operator shall acquire sufficient reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load – within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-01-01 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
VAR-001-3 (Ontario) | 79780000328 | R3. | 79780004318 | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. |  | TOP | [18 empty] | TOP |  |  |  | Low | [5 empty] | 2014-01-01 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
VAR-001-3 (Ontario) | 79780000328 | R4. | 79780004321 | Each Transmission Operator shall specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2014-01-01 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
VAR-001-3 (Ontario) | 79780000328 | R5. | 79780004322 | Each Purchasing-Selling Entity and Load Serving Entity shall arrange for (self-provide or purchase) reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load– to satisfy its reactive requirements identified by its Transmission Service Provider. |  | LSE, PSE | [7 empty] | LSE |  |  | PSE | [11 empty] | High | [5 empty] | 2014-01-01 |  | 2014-01-21 |  |  |  | NPCC-ON | [6 empty] | 50000000
VAR-001-3 (Ontario) | 79780000328 | R6. | 79780004323 | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2014-01-01 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 60000000
VAR-001-3 (Ontario) | 79780000328 | R7. | 79780004325 | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-01-01 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 70000000
VAR-001-3 (Ontario) | 79780000328 | R8. | 79780004326 | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching; controllable load; and, if necessary, load shedding – to maintain system and Interconnection voltages within established limits. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-01-01 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 80000000
VAR-001-3 (Ontario) | 79780000328 | R9. | 79780004327 | Each Transmission Operator shall maintain reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching; and controllable load– to support its voltage under first Contingency conditions. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-01-01 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 90000000
VAR-001-3 (Saskatchewan) | 83750000000328 | E.A.13 | 837500000004775 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. |  | 2014-04-01 |  | 2015-06-30 |  |  |  | MRO-SK | [6 empty] | 2200000
VAR-001-3 (Saskatchewan) | 83750000000328 | E.A.14 | 837500000004776 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | TOP | [18 empty] | TOP |  |  | Long-Term Planning | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. |  | 2014-04-01 |  | 2015-06-30 |  |  |  | MRO-SK | [6 empty] | 2300000
VAR-001-3 (Saskatchewan) | 83750000000328 | E.A.15 | 837500000004777 | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. |  | GOP | [5 empty] | GOP | [15 empty] | Long-Term Planning | Medium | The Generator Operator failed to convert at least one voltage schedule in Requirement E.A.13 into the voltage set point for the AVR for less than 25% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 25% or more but less than 50% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 50% or more but less than 75% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 75% or more of the voltage schedules. |  | 2014-04-01 |  | 2015-06-30 |  |  |  | MRO-SK | [6 empty] | 2400000
VAR-001-3 (Saskatchewan) | 83750000000328 | E.A.16 | 837500000004778 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Long-Term Planning | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. |  | 2014-04-01 |  | 2015-06-30 |  |  |  | MRO-SK | [6 empty] | 2500000
VAR-001-3 (Saskatchewan) | 83750000000328 | E.A.17 | 837500000004779 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | TOP | [18 empty] | TOP |  |  |  | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. |  | 2014-04-01 |  | 2015-06-30 |  |  |  | MRO-SK | [6 empty] | 2600000
VAR-001-3 (Saskatchewan) | 83750000000328 | E.A.18 | 837500000004780 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the Automatic Voltage Regulators (AVR) to manage MVar loading: E.A.18.1. Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. E.A.18.2. Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | N/A | The Generator Operator did not meet the control loop specifications in EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 through EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. |  | 2014-04-01 |  | 2015-06-30 |  |  |  | MRO-SK | [6 empty] | 2700000
VAR-001-3 (Saskatchewan) | 83750000000328 | R1. | 837500000004316 | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-04-01 |  | 2015-06-30 |  |  |  | MRO-SK | [6 empty] | 10000000
VAR-001-3 (Saskatchewan) | 83750000000328 | R10. | 837500000004329 | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-04-01 |  | 2015-06-30 |  |  |  | MRO-SK | [6 empty] | 100000000
VAR-001-3 (Saskatchewan) | 83750000000328 | R11. | 837500000004330 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP | [9 empty] | 2014-04-01 |  | 2015-06-30 |  |  |  | MRO-SK | [6 empty] | 110000000
VAR-001-3 (Saskatchewan) | 83750000000328 | R12. | 837500000004331 | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-04-01 |  | 2015-06-30 |  |  |  | MRO-SK | [6 empty] | 120000000
VAR-001-3 (Saskatchewan) | 83750000000328 | R2. | 837500000004317 | Each Transmission Operator shall acquire sufficient reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load – within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-04-01 |  | 2015-06-30 |  |  |  | MRO-SK | [6 empty] | 20000000
VAR-001-3 (Saskatchewan) | 83750000000328 | R3. | 837500000004318 | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. |  | TOP | [18 empty] | TOP |  |  |  | Low | [5 empty] | 2014-04-01 |  | 2015-06-30 |  |  |  | MRO-SK | [6 empty] | 30000000
VAR-001-3 (Saskatchewan) | 83750000000328 | R4. | 837500000004321 | Each Transmission Operator shall specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2014-04-01 |  | 2015-06-30 |  |  |  | MRO-SK | [6 empty] | 40000000
VAR-001-3 (Saskatchewan) | 83750000000328 | R5. | 837500000004322 | Each Purchasing-Selling Entity and Load Serving Entity shall arrange for (self-provide or purchase) reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load– to satisfy its reactive requirements identified by its Transmission Service Provider. |  | LSE, PSE | [7 empty] | LSE |  |  | PSE | [11 empty] | High | [5 empty] | 2014-04-01 |  | 2015-06-30 |  |  |  | MRO-SK | [6 empty] | 50000000
VAR-001-3 (Saskatchewan) | 83750000000328 | R6. | 837500000004323 | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. |  | TOP | [18 empty] | TOP |  |  |  | Medium | [5 empty] | 2014-04-01 |  | 2015-06-30 |  |  |  | MRO-SK | [6 empty] | 60000000
VAR-001-3 (Saskatchewan) | 83750000000328 | R7. | 837500000004325 | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-04-01 |  | 2015-06-30 |  |  |  | MRO-SK | [6 empty] | 70000000
VAR-001-3 (Saskatchewan) | 83750000000328 | R8. | 837500000004326 | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching; controllable load; and, if necessary, load shedding – to maintain system and Interconnection voltages within established limits. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-04-01 |  | 2015-06-30 |  |  |  | MRO-SK | [6 empty] | 80000000
VAR-001-3 (Saskatchewan) | 83750000000328 | R9. | 837500000004327 | Each Transmission Operator shall maintain reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching; and controllable load– to support its voltage under first Contingency conditions. |  | TOP | [18 empty] | TOP |  |  |  | High | [5 empty] | 2014-04-01 |  | 2015-06-30 |  |  |  | MRO-SK | [6 empty] | 90000000
VAR-001-4 | 443 | E.A.13 | 5440 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: •A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are online and part of the BES in the Transmission Operator Area. | M.E.A.13 Each Transmission Operator shall have and provide upon request, evidence that it provided the voltage schedules to the Generator Operator. Dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13 are acceptable as evidence. | 2014-08-01 |  | 2015-11-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2200000
VAR-001-4 | 443 | E.A.14 | 5441 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. •The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | M.E.A.14 The Transmission Operator shall have and provide upon request, evidence that it provided one of the voltage schedule reference points in Requirement E.A.14 for each generation resource in its Area to the Generator Operator. Dated letters, e-mail, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource are acceptable as evidence. | 2014-08-01 |  | 2015-11-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2300000
VAR-001-4 | 443 | E.A.15 | 5442 | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning, Same-Day Operations | Medium | The Generator Operator failed to convert at least one voltage schedule in Requirement E.A.13 into the voltage set point for the AVR for less than 25% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 25% or more but less than 50% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 50% or more but less than 75% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 75% or more of the voltage schedules. | M.E.A.15 Each Generator Operator shall have and provide upon request, evidence that it converted a voltage schedule as described in Requirement E.A.13 into a voltage set point for the AVR. Dated spreadsheets, logs, reports, or other documentation are acceptable as evidence. | 2014-08-01 |  | 2015-11-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2400000
VAR-001-4 | 443 | E.A.16 | 5443 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | M.E.A.16 The Generator Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2014-08-01 |  | 2015-11-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2500000
VAR-001-4 | 443 | E.A.17 | 5444 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator. Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator. Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. | M.E.A.17 The Transmission Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2014-01-01 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2600000
VAR-001-4 | 443 | E.A.18 | 5445 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the Automatic Voltage Regulators (AVR) to manage MVar loading: E.A.18.1. Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. E.A.18.2. Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | The Generator Operator did not meet the control loop specifications in EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 through EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | M.E.A.18 If the Generator Operator uses outside control loops to manage MVar loading, the Generator Operator shall have and provide upon request, evidence that it met the control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design specifications with identified agreed-upon control loops, system reports, or other dated documentation are acceptable as evidence. | 2014-01-01 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2700000
VAR-001-4 | 443 | R1. | 5431 | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | 2014-10-01 |  | 2015-11-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
VAR-001-4 | 443 | R2. | 5432 | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | M2. Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operational planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | 2014-10-01 |  | 2015-11-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
VAR-001-4 | 443 | R3. | 5433 | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | 2014-10-01 |  | 2015-11-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
VAR-001-4 | 443 | R4. | 5434 | The Transmission Operator shall specify the criteria that will exempt generators from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | M4. Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | 2014-10-01 |  | 2015-11-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
VAR-001-4 | 443 | R5. | 5435 | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. Or The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power Schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | 2014-10-01 |  | 2015-11-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
VAR-001-4 | 443 | R6. | 5436 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | 2014-08-01 |  | 2015-11-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
VAR-001-4.1 | 535 | E.A.13. | 7706 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are on- line and part of the BES in the Transmission Operator Area. | Each Transmission Operator shall have and provide upon request, evidence that it provided the voltage schedules to the Generator Operator. Dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13 are acceptable as evidence. | 2017-09-26 |  | 2018-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2200000
VAR-001-4.1 | 535 | E.A.14. | 7707 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | M.E.A.14 The Transmission Operator shall have and provide upon request, evidence that it provided one of the voltage schedule reference points in Requirement E.A.14 for each generation resource in its Area to the Generator Operator. Dated letters, email, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource are acceptable as evidence. | 2017-09-26 |  | 2018-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2300000
VAR-001-4.1 | 535 | E.A.15. | 7708 | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning, Same-Day Operations | Medium | The Generator Operator failed to convert at least one voltage schedule in Requirement E.A.13 into the voltage set point for the AVR for less than 25% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 25% or more but less than 50% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 50% or more but less than 75% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 75% or more of the voltage schedules. | M.E.A.15 Each Generator Operator shall have and provide upon request, evidence that it converted a voltage schedule as described in Requirement E.A.13 into a voltage set point for the AVR. Dated spreadsheets, logs, reports, or other documentation are acceptable as evidence. | 2017-09-26 |  | 2018-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2400000
VAR-001-4.1 | 535 | E.A.16. | 7709 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | M.E.A.16 The Generator Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2017-09-26 |  | 2018-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2500000
VAR-001-4.1 | 535 | E.A.17. | 7710 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. | M.E.A.17 The Transmission Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2015-11-13 |  | 2017-09-25 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2600000
VAR-001-4.1 | 535 | E.A.18. | 7711 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the Automatic Voltage Regulators (AVR) to manage MVar loading: |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | The Generator Operator did not meet the control loop specifications in EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 through EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | M.E.A.18 If the Generator Operator uses outside control loops to manage MVar loading, the Generator Operator shall have and provide upon request, evidence that it met the control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design specifications with identified agreed-upon control loops, system reports, or other dated documentation are acceptable as evidence. | 2015-11-13 |  | 2017-09-25 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2700000
VAR-001-4.1 | 535 | R1. | 7505 | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | 2015-11-13 |  | 2017-09-25 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
VAR-001-4.1 | 535 | R2. | 7506 | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | M2. Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operational planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | 2015-11-13 |  | 2017-09-25 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
VAR-001-4.1 | 535 | R3. | 7508 | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | 2015-11-13 |  | 2017-09-25 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
VAR-001-4.1 | 535 | R4. | 7509 | The Transmission Operator shall specify the criteria that will exempt generators from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | M4. Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | 2015-11-13 |  | 2017-09-25 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
VAR-001-4.1 | 535 | R5. | 7511 | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. OR The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power Schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | 2015-11-13 |  | 2017-09-25 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
VAR-001-4.1 | 535 | R6. | 7515 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | 2014-10-01 |  | 2015-11-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
VAR-001-4.1 (British Columbia) | 666700000010312 | E.A.13. | 666700000011893 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are on- line and part of the BES in the Transmission Operator Area. | Each Transmission Operator shall have and provide upon request, evidence that it provided the voltage schedules to the Generator Operator. Dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13 are acceptable as evidence. | 2016-10-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 2200000
VAR-001-4.1 (British Columbia) | 666700000010312 | E.A.14. | 666700000011894 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | M.E.A.14 The Transmission Operator shall have and provide upon request, evidence that it provided one of the voltage schedule reference points in Requirement E.A.14 for each generation resource in its Area to the Generator Operator. Dated letters, email, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource are acceptable as evidence. | 2016-10-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 2300000
VAR-001-4.1 (British Columbia) | 666700000010312 | E.A.15. | 666700000011895 | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning, Same-Day Operations | Medium | The Generator Operator failed to convert at least one voltage schedule in Requirement E.A.13 into the voltage set point for the AVR for less than 25% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 25% or more but less than 50% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 50% or more but less than 75% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 75% or more of the voltage schedules. | M.E.A.15 Each Generator Operator shall have and provide upon request, evidence that it converted a voltage schedule as described in Requirement E.A.13 into a voltage set point for the AVR. Dated spreadsheets, logs, reports, or other documentation are acceptable as evidence. | 2016-10-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 2400000
VAR-001-4.1 (British Columbia) | 666700000010312 | E.A.16. | 666700000011896 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | M.E.A.16 The Generator Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2016-10-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 2500000
VAR-001-4.1 (British Columbia) | 666700000010312 | E.A.17. | 666700000011897 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. | M.E.A.17 The Transmission Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2016-10-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 2600000
VAR-001-4.1 (British Columbia) | 666700000010312 | E.A.18. | 666700000011898 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the Automatic Voltage Regulators (AVR) to manage MVar loading: |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | The Generator Operator did not meet the control loop specifications in EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 through EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | M.E.A.18 If the Generator Operator uses outside control loops to manage MVar loading, the Generator Operator shall have and provide upon request, evidence that it met the control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design specifications with identified agreed-upon control loops, system reports, or other dated documentation are acceptable as evidence. | 2016-10-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 2700000
VAR-001-4.1 (British Columbia) | 666700000010312 | R1. | 666700000011899 | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | 2016-10-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
VAR-001-4.1 (British Columbia) | 666700000010312 | R2. | 666700000011900 | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | M2. Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operational planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | 2016-10-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 20000000
VAR-001-4.1 (British Columbia) | 666700000010312 | R3. | 666700000011901 | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | 2016-10-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 30000000
VAR-001-4.1 (British Columbia) | 666700000010312 | R4. | 666700000011902 | The Transmission Operator shall specify the criteria that will exempt generators from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | M4. Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | 2016-10-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 40000000
VAR-001-4.1 (British Columbia) | 666700000010312 | R5. | 666700000011903 | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. OR The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power Schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | 2016-10-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 50000000
VAR-001-4.1 (British Columbia) | 666700000010312 | R6. | 666700000011904 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | 2016-10-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 60000000
VAR-001-4.1 (Manitoba) | 77660000000535 | E.A.13. | 776600000007706 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are on- line and part of the BES in the Transmission Operator Area. | Each Transmission Operator shall have and provide upon request, evidence that it provided the voltage schedules to the Generator Operator. Dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13 are acceptable as evidence. | 2017-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 2200000
VAR-001-4.1 (Manitoba) | 77660000000535 | E.A.14. | 776600000007707 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | M.E.A.14 The Transmission Operator shall have and provide upon request, evidence that it provided one of the voltage schedule reference points in Requirement E.A.14 for each generation resource in its Area to the Generator Operator. Dated letters, email, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource are acceptable as evidence. | 2017-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 2300000
VAR-001-4.1 (Manitoba) | 77660000000535 | E.A.15. | 776600000007708 | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning, Same-Day Operations | Medium | The Generator Operator failed to convert at least one voltage schedule in Requirement E.A.13 into the voltage set point for the AVR for less than 25% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 25% or more but less than 50% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 50% or more but less than 75% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 75% or more of the voltage schedules. | M.E.A.15 Each Generator Operator shall have and provide upon request, evidence that it converted a voltage schedule as described in Requirement E.A.13 into a voltage set point for the AVR. Dated spreadsheets, logs, reports, or other documentation are acceptable as evidence. | 2017-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 2400000
VAR-001-4.1 (Manitoba) | 77660000000535 | E.A.16. | 776600000007709 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | M.E.A.16 The Generator Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2017-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 2500000
VAR-001-4.1 (Manitoba) | 77660000000535 | E.A.17. | 776600000007710 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. | M.E.A.17 The Transmission Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2017-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 2600000
VAR-001-4.1 (Manitoba) | 77660000000535 | E.A.18. | 776600000007711 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the Automatic Voltage Regulators (AVR) to manage MVar loading: |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | The Generator Operator did not meet the control loop specifications in EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 through EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | M.E.A.18 If the Generator Operator uses outside control loops to manage MVar loading, the Generator Operator shall have and provide upon request, evidence that it met the control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design specifications with identified agreed-upon control loops, system reports, or other dated documentation are acceptable as evidence. | 2017-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 2700000
VAR-001-4.1 (Manitoba) | 77660000000535 | R1. | 776600000007505 | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | 2017-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
VAR-001-4.1 (Manitoba) | 77660000000535 | R2. | 776600000007506 | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | M2. Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operational planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | 2017-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
VAR-001-4.1 (Manitoba) | 77660000000535 | R3. | 776600000007508 | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | 2017-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
VAR-001-4.1 (Manitoba) | 77660000000535 | R4. | 776600000007509 | The Transmission Operator shall specify the criteria that will exempt generators from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | M4. Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | 2017-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 40000000
VAR-001-4.1 (Manitoba) | 77660000000535 | R5. | 776600000007511 | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. OR The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power Schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | 2017-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 50000000
VAR-001-4.1 (Manitoba) | 77660000000535 | R6. | 776600000007515 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | 2017-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 60000000
VAR-001-4.1 (Ontario) | 79780000535 | E.A.13. | 79780007706 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area:&lt;br/&gt;• A voltage set point with a voltage tolerance band and a specified period. &lt;br/&gt;• An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. &lt;br/&gt;• A voltage band for a specified period. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | &lt;p&gt;For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at &lt;br/&gt;least one generation resource but less than or equal to 5% of the generation resources that are &lt;br/&gt;on-line and part of the BES in the Transmission Operator Area.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to &lt;br/&gt;more than 5% but less than or equal to 10% of the generation resources that are on-line and part of &lt;br/&gt;the BES in the Transmission Operator Area.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to &lt;br/&gt;more than 10% but less than or equal to 15% of the generation resources that are on-line and part &lt;br/&gt;of the BES in the Transmission Operator Area.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to &lt;br/&gt;more than 15% of the generation resources that are on- line and part of the BES in the Transmission Operator Area.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;Each Transmission Operator shall have and provide upon request, evidence that it provided the voltage schedules to the Generator Operator. Dated spreadsheets, reports, voice &lt;br/&gt;recordings, or other documentation containing the voltage schedule including set points, tolerance &lt;br/&gt;bands, and specified periods as required in Requirement E.A.13 are acceptable as evidence.&lt;/p&gt; &lt;p/&gt; | 2017-09-26 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 2200000
VAR-001-4.1 (Ontario) | 79780000535 | E.A.14. | 79780007707 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator.&lt;br/&gt;• The generator terminals.&lt;br/&gt;• The high side of the generator step-up transformer. &lt;br/&gt;• The point of interconnection.&lt;br/&gt;• A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | &lt;p&gt;The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal &lt;br/&gt;to 5% of the generation resources in the Transmission Operator area.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal &lt;br/&gt;to 10% of the generation resources in the Transmission Operator Area.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% &lt;br/&gt;of the generation resources in the Transmission Operator Area.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation &lt;br/&gt;resources in the Transmission Operator Area.&lt;/p&gt; &lt;p/&gt; | M.E.A.14 The Transmission Operator shall have and provide upon request, evidence that it&lt;br/&gt;provided one of the voltage schedule reference points in Requirement E.A.14 for&lt;br/&gt;each generation resource in its Area to the Generator Operator. Dated letters, email,&lt;br/&gt;or other documentation that contains notification to the Generator Operator&lt;br/&gt;of the voltage schedule reference point for each generation resource are acceptable&lt;br/&gt;as evidence. | 2017-09-26 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 2300000
VAR-001-4.1 (Ontario) | 79780000535 | E.A.15. | 79780007708 | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning, Same-Day Operations | Medium | &lt;p&gt;The Generator Operator failed to convert at least one voltage schedule in Requirement E.A.13 into the voltage set point for the AVR for less than 25% of the voltage schedules.&lt;/p&gt; &lt;p/&gt; &lt;p/&gt; | &lt;p&gt;&lt;br/&gt;The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point &lt;br/&gt;for the AVR for 25% or more but less than 50% of the voltage schedules.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 50% or more but less than 75% of the voltage schedules.&lt;/p&gt; &lt;p/&gt; &lt;p/&gt; | &lt;p&gt;&lt;br/&gt;The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point &lt;br/&gt;for the AVR for 75% or more of the voltage schedules.&lt;/p&gt; &lt;p/&gt; | M.E.A.15 Each Generator Operator shall have and provide upon request, evidence that it&lt;br/&gt;converted a voltage schedule as described in Requirement E.A.13 into a voltage set&lt;br/&gt;point for the AVR. Dated spreadsheets, logs, reports, or other documentation are&lt;br/&gt;acceptable as evidence. | 2017-09-26 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 2400000
VAR-001-4.1 (Ontario) | 79780000535 | E.A.16. | 79780007709 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning | Low | &lt;p&gt;&lt;br/&gt;The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator.&lt;/p&gt; &lt;p/&gt; | M.E.A.16 The Generator Operator shall have and provide upon request, evidence that within&lt;br/&gt;30 calendar days of request by its Transmission Operator it provided its voltage set&lt;br/&gt;point conversion methodology from the point in Requirement E.A.14 to the&lt;br/&gt;generator terminals. Dated reports, spreadsheets, or other documentation are&lt;br/&gt;acceptable as evidence. | 2017-09-26 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 2500000
VAR-001-4.1 (Ontario) | 79780000535 | E.A.17. | 79780007710 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | &lt;p&gt;The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator Operator.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator Operator.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator.&lt;/p&gt; &lt;p/&gt; | M.E.A.17 The Transmission Operator shall have and provide upon request, evidence that&lt;br/&gt;within 30 calendar days of request by its Generator Operator it provided data to&lt;br/&gt;support development of the voltage set point conversion methodology. Dated&lt;br/&gt;reports, spreadsheets, or other documentation are acceptable as evidence. | 2015-11-13 |  | 2017-09-25 |  |  |  | NPCC-ON | [6 empty] | 2600000
VAR-001-4.1 (Ontario) | 79780000535 | E.A.18. | 79780007711 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the Automatic Voltage Regulators (AVR) to manage MVar loading: |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;&lt;br/&gt;The Generator Operator did not meet the control loop specifications in EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;The Generator Operator did not meet the control loop specifications in EA18.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;The Generator Operator did not meet the control loop specifications in EA18.1 through EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading.&lt;/p&gt; &lt;p/&gt; | M.E.A.18 If the Generator Operator uses outside control loops to manage MVar loading, the&lt;br/&gt;Generator Operator shall have and provide upon request, evidence that it met the&lt;br/&gt;control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design&lt;br/&gt;specifications with identified agreed-upon control loops, system reports, or other&lt;br/&gt;dated documentation are acceptable as evidence. | 2015-11-13 |  | 2017-09-25 |  |  |  | NPCC-ON | [6 empty] | 2700000
VAR-001-4.1 (Ontario) | 79780000535 | R1. | 79780007505 | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using&lt;br/&gt;either a range or a target value with an associated tolerance band.&lt;br/&gt;For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is&lt;br/&gt;either a range or a target value with an associated tolerance band) were provided to its Reliability&lt;br/&gt;Coordinator and adjacent Transmission Operators within 30 days of a request. Evidence may include,&lt;br/&gt;but is not limited to, emails, website postings, and meeting minutes. | 2015-11-13 |  | 2017-09-25 |  |  |  | NPCC-ON | [6 empty] | 10000000
VAR-001-4.1 (Ontario) | 79780000535 | R2. | 79780007506 | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | M2. Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on&lt;br/&gt;their assessments of the system. For the operational planning time horizon, Transmission Operators&lt;br/&gt;shall have evidence of assessments used as the basis for how resources were scheduled. | 2015-11-13 |  | 2017-09-25 |  |  |  | NPCC-ON | [6 empty] | 20000000
VAR-001-4.1 (Ontario) | 79780000535 | R3. | 79780007508 | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and&lt;br/&gt;inductive resources as necessary in Real-time. This may include instructions to Generator Operators&lt;br/&gt;to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | 2015-11-13 |  | 2017-09-25 |  |  |  | NPCC-ON | [6 empty] | 30000000
VAR-001-4.1 (Ontario) | 79780000535 | R4. | 79780007509 | The Transmission Operator shall specify the criteria that will exempt generators from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | M4. Each Transmission Operator shall have evidence of the documented criteria for generator&lt;br/&gt;exemptions.&lt;br/&gt;For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in&lt;br/&gt;its area that is exempt from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having&lt;br/&gt;to make any notifications, the associated Generator Operator was notified of this exemption. | 2015-11-13 |  | 2017-09-25 |  |  |  | NPCC-ON | [6 empty] | 40000000
VAR-001-4.1 (Ontario) | 79780000535 | R5. | 79780007511 | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. OR The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power Schedule&lt;br/&gt;(which is either a range or a target value with an associated tolerance band).&lt;br/&gt;For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power&lt;br/&gt;schedule (which is either a range or a target value with an associated tolerance band) to the&lt;br/&gt;applicable Generator Operators, and that the Generator Operator was directed to comply with the&lt;br/&gt;schedule in automatic voltage control mode, unless exempted.&lt;br/&gt;For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for&lt;br/&gt;deviations from the voltage or Reactive Power schedule (which is either a range or a target value&lt;br/&gt;with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it&lt;br/&gt;provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a&lt;br/&gt;range or a target value with an associated tolerance band) within 30 days of receiving a request by a&lt;br/&gt;Generator Operator. | 2015-11-13 |  | 2017-09-25 |  |  |  | NPCC-ON | [6 empty] | 50000000
VAR-001-4.1 (Ontario) | 79780000535 | R6. | 79780007515 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator&lt;br/&gt;Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with&lt;br/&gt;the requirement and that it consulted with the Generator Owner. | 2014-10-01 |  | 2015-11-12 |  |  |  | NPCC-ON | [6 empty] | 60000000
VAR-001-4.1 (Saskatchewan) | 83750000000535 | E.A.13. | 837500000007706 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are on- line and part of the BES in the Transmission Operator Area. | Each Transmission Operator shall have and provide upon request, evidence that it provided the voltage schedules to the Generator Operator. Dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13 are acceptable as evidence. | 2016-04-01 |  | 2018-03-31 |  |  |  | MRO-SK | [6 empty] | 2200000
VAR-001-4.1 (Saskatchewan) | 83750000000535 | E.A.14. | 837500000007707 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | M.E.A.14 The Transmission Operator shall have and provide upon request, evidence that it provided one of the voltage schedule reference points in Requirement E.A.14 for each generation resource in its Area to the Generator Operator. Dated letters, email, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource are acceptable as evidence. | 2016-04-01 |  | 2018-03-31 |  |  |  | MRO-SK | [6 empty] | 2300000
VAR-001-4.1 (Saskatchewan) | 83750000000535 | E.A.15. | 837500000007708 | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning, Same-Day Operations | Medium | The Generator Operator failed to convert at least one voltage schedule in Requirement E.A.13 into the voltage set point for the AVR for less than 25% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 25% or more but less than 50% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 50% or more but less than 75% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 75% or more of the voltage schedules. | M.E.A.15 Each Generator Operator shall have and provide upon request, evidence that it converted a voltage schedule as described in Requirement E.A.13 into a voltage set point for the AVR. Dated spreadsheets, logs, reports, or other documentation are acceptable as evidence. | 2016-04-01 |  | 2018-03-31 |  |  |  | MRO-SK | [6 empty] | 2400000
VAR-001-4.1 (Saskatchewan) | 83750000000535 | E.A.16. | 837500000007709 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | M.E.A.16 The Generator Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2016-04-01 |  | 2018-03-31 |  |  |  | MRO-SK | [6 empty] | 2500000
VAR-001-4.1 (Saskatchewan) | 83750000000535 | E.A.17. | 837500000007710 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. | M.E.A.17 The Transmission Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2016-04-01 |  | 2018-03-31 |  |  |  | MRO-SK | [6 empty] | 2600000
VAR-001-4.1 (Saskatchewan) | 83750000000535 | E.A.18. | 837500000007711 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the Automatic Voltage Regulators (AVR) to manage MVar loading: |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | The Generator Operator did not meet the control loop specifications in EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 through EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | M.E.A.18 If the Generator Operator uses outside control loops to manage MVar loading, the Generator Operator shall have and provide upon request, evidence that it met the control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design specifications with identified agreed-upon control loops, system reports, or other dated documentation are acceptable as evidence. | 2016-04-01 |  | 2018-03-31 |  |  |  | MRO-SK | [6 empty] | 2700000
VAR-001-4.1 (Saskatchewan) | 83750000000535 | R1. | 837500000007505 | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | 2016-04-01 |  | 2018-03-31 |  |  |  | MRO-SK | [6 empty] | 10000000
VAR-001-4.1 (Saskatchewan) | 83750000000535 | R2. | 837500000007506 | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | M2. Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operational planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | 2016-04-01 |  | 2018-03-31 |  |  |  | MRO-SK | [6 empty] | 20000000
VAR-001-4.1 (Saskatchewan) | 83750000000535 | R3. | 837500000007508 | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | 2016-04-01 |  | 2018-03-31 |  |  |  | MRO-SK | [6 empty] | 30000000
VAR-001-4.1 (Saskatchewan) | 83750000000535 | R4. | 837500000007509 | The Transmission Operator shall specify the criteria that will exempt generators from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | M4. Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | 2016-04-01 |  | 2018-03-31 |  |  |  | MRO-SK | [6 empty] | 40000000
VAR-001-4.1 (Saskatchewan) | 83750000000535 | R5. | 837500000007511 | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. OR The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power Schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | 2016-04-01 |  | 2018-03-31 |  |  |  | MRO-SK | [6 empty] | 50000000
VAR-001-4.1 (Saskatchewan) | 83750000000535 | R6. | 837500000007515 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | 2016-04-01 |  | 2018-03-31 |  |  |  | MRO-SK | [6 empty] | 60000000
VAR-001-4.2 | 567 | E.A.13. | 8062 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | Each Transmission Operator shall have and provide upon request, evidence that it provided the voltage schedules to the Generator Operator. Dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13 are acceptable as evidence. | 2019-01-01 |  | 2018-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2200000
VAR-001-4.2 | 567 | E.A.14. | 8063 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator shall have and provide upon request, evidence that it provided one of the voltage schedule reference points in Requirement E.A.14 for each generation resource in its Area to the Generator Operator. Dated letters, e-mail, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource are acceptable as evidence. | 2019-01-01 |  | 2018-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2300000
VAR-001-4.2 | 567 | E.A.15. | 8064 | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning, Same-Day Operations | Medium | The Generator Operator failed to convert at least one voltage schedule in Requirement E.A.13 into the voltage set point for the AVR for less than 25% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 25% or more but less than 50% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 50% or more but less than 75% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 75% or more of the voltage schedules. | Each Generator Operator shall have and provide upon request, evidence that it converted a voltage schedule as described in Requirement E.A.13 into a voltage set point for the AVR. Dated spreadsheets, logs, reports, or other documentation are acceptable as evidence. | 2019-01-01 |  | 2018-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2400000
VAR-001-4.2 | 567 | E.A.16. | 8065 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | The Generator Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2019-01-01 |  | 2018-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2500000
VAR-001-4.2 | 567 | E.A.17. | 8066 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator. Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator. Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. | The Transmission Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2015-11-13 |  | 2017-09-25 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2600000
VAR-001-4.2 | 567 | E.A.18. | 8067 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the automatic voltage regulators (AVR) to manage Mvar loading: |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | The Generator Operator did not meet the control loop specifications in EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 through EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | If the Generator Operator uses outside control loops to manage Mvar loading, the Generator Operator shall have and provide upon request, evidence that it met the control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design specifications with identified agreed-upon control loops, system reports, or other dated documentation are acceptable as evidence. | 2015-11-13 |  | 2017-09-25 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2700000
VAR-001-4.2 | 567 | R1. | 8050 | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | 2017-09-26 |  | 2018-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
VAR-001-4.2 | 567 | R2. | 8053 | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operations planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | 2017-09-26 |  | 2018-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
VAR-001-4.2 | 567 | R3. | 8054 | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include, but is not limited to, instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | 2017-09-26 |  | 2018-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
VAR-001-4.2 | 567 | R4. | 8055 | Each Transmission Operator shall specify the criteria that will exempt generators: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | 2017-09-26 |  | 2018-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
VAR-001-4.2 | 567 | R5. | 8057 | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. OR The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | 2017-09-26 |  | 2018-12-31 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
VAR-001-4.2 | 567 | R6. | 8061 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | 2015-11-13 |  | 2017-09-25 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
VAR-001-4.2 (British Columbia) | 666700000010313 | E.A.13. | 666700000011905 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | Each Transmission Operator shall have and provide upon request, evidence that it provided the voltage schedules to the Generator Operator. Dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13 are acceptable as evidence. | 2018-10-01 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 2200000
VAR-001-4.2 (British Columbia) | 666700000010313 | E.A.14. | 666700000011906 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator shall have and provide upon request, evidence that it provided one of the voltage schedule reference points in Requirement E.A.14 for each generation resource in its Area to the Generator Operator. Dated letters, e-mail, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource are acceptable as evidence. | 2018-10-01 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 2300000
VAR-001-4.2 (British Columbia) | 666700000010313 | E.A.15. | 666700000011907 | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning, Same-Day Operations | Medium | The Generator Operator failed to convert at least one voltage schedule in Requirement E.A.13 into the voltage set point for the AVR for less than 25% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 25% or more but less than 50% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 50% or more but less than 75% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 75% or more of the voltage schedules. | Each Generator Operator shall have and provide upon request, evidence that it converted a voltage schedule as described in Requirement E.A.13 into a voltage set point for the AVR. Dated spreadsheets, logs, reports, or other documentation are acceptable as evidence. | 2018-10-01 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 2400000
VAR-001-4.2 (British Columbia) | 666700000010313 | E.A.16. | 666700000011908 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | The Generator Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2018-10-01 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 2500000
VAR-001-4.2 (British Columbia) | 666700000010313 | E.A.17. | 666700000011909 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator. Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator. Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. | The Transmission Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2018-10-01 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 2600000
VAR-001-4.2 (British Columbia) | 666700000010313 | E.A.18. | 666700000011910 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the automatic voltage regulators (AVR) to manage Mvar loading: |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | The Generator Operator did not meet the control loop specifications in EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 through EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | If the Generator Operator uses outside control loops to manage Mvar loading, the Generator Operator shall have and provide upon request, evidence that it met the control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design specifications with identified agreed-upon control loops, system reports, or other dated documentation are acceptable as evidence. | 2018-10-01 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 2700000
VAR-001-4.2 (British Columbia) | 666700000010313 | R1. | 666700000011911 | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | 2018-10-01 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
VAR-001-4.2 (British Columbia) | 666700000010313 | R2. | 666700000011912 | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operations planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | 2018-10-01 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 20000000
VAR-001-4.2 (British Columbia) | 666700000010313 | R3. | 666700000011913 | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include, but is not limited to, instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | 2018-10-01 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 30000000
VAR-001-4.2 (British Columbia) | 666700000010313 | R4. | 666700000011914 | Each Transmission Operator shall specify the criteria that will exempt generators: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | 2018-10-01 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 40000000
VAR-001-4.2 (British Columbia) | 666700000010313 | R5. | 666700000011915 | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. OR The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | 2018-10-01 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 50000000
VAR-001-4.2 (British Columbia) | 666700000010313 | R6. | 666700000011916 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | 2018-10-01 |  | 2019-09-30 |  |  |  | WECC-BC | [6 empty] | 60000000
VAR-001-4.2 (Manitoba) | 77660000000567 | E.A.13. | 776600000008062 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | Each Transmission Operator shall have and provide upon request, evidence that it provided the voltage schedules to the Generator Operator. Dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13 are acceptable as evidence. | 2019-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 2200000
VAR-001-4.2 (Manitoba) | 77660000000567 | E.A.14. | 776600000008063 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator shall have and provide upon request, evidence that it provided one of the voltage schedule reference points in Requirement E.A.14 for each generation resource in its Area to the Generator Operator. Dated letters, e-mail, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource are acceptable as evidence. | 2019-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 2300000
VAR-001-4.2 (Manitoba) | 77660000000567 | E.A.15. | 776600000008064 | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning, Same-Day Operations | Medium | The Generator Operator failed to convert at least one voltage schedule in Requirement E.A.13 into the voltage set point for the AVR for less than 25% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 25% or more but less than 50% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 50% or more but less than 75% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 75% or more of the voltage schedules. | Each Generator Operator shall have and provide upon request, evidence that it converted a voltage schedule as described in Requirement E.A.13 into a voltage set point for the AVR. Dated spreadsheets, logs, reports, or other documentation are acceptable as evidence. | 2019-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 2400000
VAR-001-4.2 (Manitoba) | 77660000000567 | E.A.16. | 776600000008065 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | The Generator Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2019-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 2500000
VAR-001-4.2 (Manitoba) | 77660000000567 | E.A.17. | 776600000008066 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator. Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator. Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. | The Transmission Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2019-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 2600000
VAR-001-4.2 (Manitoba) | 77660000000567 | E.A.18. | 776600000008067 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the automatic voltage regulators (AVR) to manage Mvar loading: |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | The Generator Operator did not meet the control loop specifications in EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 through EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | If the Generator Operator uses outside control loops to manage Mvar loading, the Generator Operator shall have and provide upon request, evidence that it met the control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design specifications with identified agreed-upon control loops, system reports, or other dated documentation are acceptable as evidence. | 2019-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 2700000
VAR-001-4.2 (Manitoba) | 77660000000567 | R1. | 776600000008050 | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | 2019-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 10000000
VAR-001-4.2 (Manitoba) | 77660000000567 | R2. | 776600000008053 | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operations planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | 2019-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 20000000
VAR-001-4.2 (Manitoba) | 77660000000567 | R3. | 776600000008054 | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include, but is not limited to, instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | 2019-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 30000000
VAR-001-4.2 (Manitoba) | 77660000000567 | R4. | 776600000008055 | Each Transmission Operator shall specify the criteria that will exempt generators: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | 2019-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 40000000
VAR-001-4.2 (Manitoba) | 77660000000567 | R5. | 776600000008057 | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. OR The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | 2019-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 50000000
VAR-001-4.2 (Manitoba) | 77660000000567 | R6. | 776600000008061 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | 2019-07-01 |  | 2020-07-31 |  |  |  | MRO-MB | [6 empty] | 60000000
VAR-001-4.2 (Ontario) | 79780000567 | E.A.13. | 79780008062 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area:&lt;br/&gt;• A voltage set point with a voltage tolerance band and a specified period. &lt;br/&gt;• An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. &lt;br/&gt;• A voltage band for a specified period. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | &lt;p&gt;&lt;br/&gt;Each Transmission Operator shall have and provide upon request, evidence that it provided the voltage schedules to the Generator Operator. Dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and &lt;br/&gt;specified periods as required in Requirement E.A.13 are acceptable as evidence.&lt;/p&gt; &lt;p/&gt; | 2019-01-01 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 2200000
VAR-001-4.2 (Ontario) | 79780000567 | E.A.14. | 79780008063 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. &lt;br/&gt;• The generator terminals.&lt;br/&gt;• The high side of the generator step-up transformer.&lt;br/&gt;• The point of interconnection.&lt;br/&gt;• A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | &lt;p&gt;The Transmission Operator shall have and provide upon request, evidence that it provided one of the voltage schedule reference points in Requirement E.A.14 for each generation resource in its Area to the Generator Operator. Dated letters, e-mail, or other documentation that contains &lt;br/&gt;notification to the Generator Operator of the voltage schedule reference point for each generation resource are acceptable as evidence.&lt;/p&gt; &lt;p/&gt; | 2019-01-01 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 2300000
VAR-001-4.2 (Ontario) | 79780000567 | E.A.15. | 79780008064 | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning, Same-Day Operations | Medium | The Generator Operator failed to convert at least one voltage schedule in Requirement E.A.13 into the voltage set point for the AVR for less than 25% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 25% or more but less than 50% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 50% or more but less than 75% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 75% or more of the voltage schedules. | &lt;p&gt;Each Generator Operator shall have and provide upon request, evidence that it converted a&lt;/p&gt; &lt;p&gt;voltage schedule as described in Requirement E.A.13 into a voltage set point for the AVR.&lt;/p&gt; &lt;p&gt;Dated spreadsheets, logs, reports, or other documentation are acceptable as evidence.&lt;/p&gt; &lt;p/&gt; | 2019-01-01 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 2400000
VAR-001-4.2 (Ontario) | 79780000567 | E.A.16. | 79780008065 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | &lt;p&gt;The Generator Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals. Dated reports, spreadsheets, or other documentation are acceptable as evidence.&lt;/p&gt; &lt;p/&gt; | 2019-01-01 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 2500000
VAR-001-4.2 (Ontario) | 79780000567 | E.A.17. | 79780008066 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator. Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator. Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. | &lt;p&gt;The Transmission Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology. Dated reports, spreadsheets, or other documentation are acceptable as evidence.&lt;/p&gt; &lt;p/&gt; | 2015-11-13 |  | 2017-09-25 |  |  |  | NPCC-ON | [6 empty] | 2600000
VAR-001-4.2 (Ontario) | 79780000567 | E.A.18. | 79780008067 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the automatic voltage regulators (AVR) to manage Mvar loading: |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | The Generator Operator did not meet the control loop specifications in EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 through EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | &lt;p&gt;If the Generator Operator uses outside control loops to manage Mvar loading, the Generator Operator shall have and provide upon request, evidence that it met the control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design specifications with identified agreed-upon control loops, system reports, or other dated documentation are acceptable as evidence.&lt;/p&gt; &lt;p/&gt; | 2015-11-13 |  | 2017-09-25 |  |  |  | NPCC-ON | [6 empty] | 2700000
VAR-001-4.2 (Ontario) | 79780000567 | R1. | 79780008050 | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | &lt;p&gt;&lt;br/&gt;The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band.&lt;/p&gt; &lt;p&gt;For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is &lt;br/&gt;either a range or a target value with an associated tolerance band) were provided to its &lt;br/&gt;Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. &lt;br/&gt;Evidence may include, but is not limited to, emails, website postings, and meeting minutes.&lt;/p&gt; &lt;p/&gt; | 2017-09-26 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 10000000
VAR-001-4.2 (Ontario) | 79780000567 | R2. | 79780008053 | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | &lt;p&gt;Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based&lt;/p&gt; &lt;p&gt;on their assessments of the system. For the operations planning time horizon, Transmission&lt;/p&gt; &lt;p&gt;Operators shall have evidence of assessments used as the basis for how resources were scheduled.&lt;/p&gt; &lt;p/&gt; | 2017-09-26 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 20000000
VAR-001-4.2 (Ontario) | 79780000567 | R3. | 79780008054 | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | &lt;p&gt;Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include, but is not limited to, instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources &lt;br/&gt;on-line; or 3) make manual adjustments.&lt;/p&gt; &lt;p/&gt; | 2017-09-26 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 30000000
VAR-001-4.2 (Ontario) | 79780000567 | R4. | 79780008055 | Each Transmission Operator shall specify the criteria that will exempt generators: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | &lt;p&gt;Each Transmission Operator shall have evidence of the documented criteria for generator exemptions.&lt;/p&gt; &lt;p&gt;For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption.&lt;/p&gt; &lt;p/&gt; | 2017-09-26 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 40000000
VAR-001-4.2 (Ontario) | 79780000567 | R5. | 79780008057 | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | &lt;p&gt;N/A&lt;/p&gt; | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. OR The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | &lt;p&gt;The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band).&lt;/p&gt; &lt;p&gt;For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power &lt;br/&gt;schedule (which is either a range or a target value with an associated tolerance band) to the &lt;br/&gt;applicable Generator Operators, and that the Generator Operator was directed to comply with the &lt;br/&gt;schedule in automatic voltage control mode, unless exempted.&lt;/p&gt; &lt;p&gt;For part 5.2, the Transmission Operator shall have evidence it provided notification requirements &lt;br/&gt;for deviations from the voltage or Reactive Power schedule (which is either a range or a target &lt;br/&gt;value with an associated tolerance band). For part 5.3, the Transmission Operator shall have &lt;br/&gt;evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule &lt;br/&gt;(which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator.&lt;/p&gt; &lt;p/&gt; | 2017-09-26 |  | 2018-12-31 |  |  |  | NPCC-ON | [6 empty] | 50000000
VAR-001-4.2 (Ontario) | 79780000567 | R6. | 79780008061 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | &lt;p&gt;The Transmission Operator shall have evidence that it provided documentation to the Generator&lt;/p&gt; &lt;p&gt;Owner when a change was needed to a generating unit’s step-up transformer tap in accordance&lt;/p&gt; &lt;p&gt;with the requirement and that it consulted with the Generator Owner.&lt;/p&gt; &lt;p/&gt; | 2015-11-13 |  | 2017-09-25 |  |  |  | NPCC-ON | [6 empty] | 60000000
VAR-001-4.2 (Saskatchewan) | 83750000000567 | E.A.13. | 837500000008062 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | Each Transmission Operator shall have and provide upon request, evidence that it provided the voltage schedules to the Generator Operator. Dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13 are acceptable as evidence. | 2018-04-01 | [5 empty] | MRO-SK | [6 empty] | 2200000
VAR-001-4.2 (Saskatchewan) | 83750000000567 | E.A.14. | 837500000008063 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator shall have and provide upon request, evidence that it provided one of the voltage schedule reference points in Requirement E.A.14 for each generation resource in its Area to the Generator Operator. Dated letters, e-mail, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource are acceptable as evidence. | 2018-04-01 | [5 empty] | MRO-SK | [6 empty] | 2300000
VAR-001-4.2 (Saskatchewan) | 83750000000567 | E.A.15. | 837500000008064 | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning, Same-Day Operations | Medium | The Generator Operator failed to convert at least one voltage schedule in Requirement E.A.13 into the voltage set point for the AVR for less than 25% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 25% or more but less than 50% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 50% or more but less than 75% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 75% or more of the voltage schedules. | Each Generator Operator shall have and provide upon request, evidence that it converted a voltage schedule as described in Requirement E.A.13 into a voltage set point for the AVR. Dated spreadsheets, logs, reports, or other documentation are acceptable as evidence. | 2018-04-01 | [5 empty] | MRO-SK | [6 empty] | 2400000
VAR-001-4.2 (Saskatchewan) | 83750000000567 | E.A.16. | 837500000008065 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | The Generator Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2018-04-01 | [5 empty] | MRO-SK | [6 empty] | 2500000
VAR-001-4.2 (Saskatchewan) | 83750000000567 | E.A.17. | 837500000008066 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator. Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator. Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. | The Transmission Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2018-04-01 | [5 empty] | MRO-SK | [6 empty] | 2600000
VAR-001-4.2 (Saskatchewan) | 83750000000567 | E.A.18. | 837500000008067 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the automatic voltage regulators (AVR) to manage Mvar loading: |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | The Generator Operator did not meet the control loop specifications in EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 through EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | If the Generator Operator uses outside control loops to manage Mvar loading, the Generator Operator shall have and provide upon request, evidence that it met the control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design specifications with identified agreed-upon control loops, system reports, or other dated documentation are acceptable as evidence. | 2018-04-01 | [5 empty] | MRO-SK | [6 empty] | 2700000
VAR-001-4.2 (Saskatchewan) | 83750000000567 | R1. | 837500000008050 | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | 2018-04-01 | [5 empty] | MRO-SK | [6 empty] | 10000000
VAR-001-4.2 (Saskatchewan) | 83750000000567 | R2. | 837500000008053 | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operations planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | 2018-04-01 | [5 empty] | MRO-SK | [6 empty] | 20000000
VAR-001-4.2 (Saskatchewan) | 83750000000567 | R3. | 837500000008054 | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include, but is not limited to, instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | 2018-04-01 | [5 empty] | MRO-SK | [6 empty] | 30000000
VAR-001-4.2 (Saskatchewan) | 83750000000567 | R4. | 837500000008055 | Each Transmission Operator shall specify the criteria that will exempt generators: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | 2018-04-01 | [5 empty] | MRO-SK | [6 empty] | 40000000
VAR-001-4.2 (Saskatchewan) | 83750000000567 | R5. | 837500000008057 | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. OR The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | 2018-04-01 | [5 empty] | MRO-SK | [6 empty] | 50000000
VAR-001-4.2 (Saskatchewan) | 83750000000567 | R6. | 837500000008061 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | 2018-04-01 | [5 empty] | MRO-SK | [6 empty] | 60000000
VAR-001-4 (Manitoba) | 77660000000443 | E.A.13 | 776600000005440 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: •A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are online and part of the BES in the Transmission Operator Area. | M.E.A.13 Each Transmission Operator shall have and provide upon request, evidence that it provided the voltage schedules to the Generator Operator. Dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13 are acceptable as evidence. | 2016-07-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 2200000
VAR-001-4 (Manitoba) | 77660000000443 | E.A.14 | 776600000005441 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. •The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | M.E.A.14 The Transmission Operator shall have and provide upon request, evidence that it provided one of the voltage schedule reference points in Requirement E.A.14 for each generation resource in its Area to the Generator Operator. Dated letters, e-mail, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource are acceptable as evidence. | 2016-07-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 2300000
VAR-001-4 (Manitoba) | 77660000000443 | E.A.15 | 776600000005442 | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning, Same-Day Operations | Medium | The Generator Operator failed to convert at least one voltage schedule in Requirement E.A.13 into the voltage set point for the AVR for less than 25% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 25% or more but less than 50% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 50% or more but less than 75% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 75% or more of the voltage schedules. | M.E.A.15 Each Generator Operator shall have and provide upon request, evidence that it converted a voltage schedule as described in Requirement E.A.13 into a voltage set point for the AVR. Dated spreadsheets, logs, reports, or other documentation are acceptable as evidence. | 2016-07-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 2400000
VAR-001-4 (Manitoba) | 77660000000443 | E.A.16 | 776600000005443 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | M.E.A.16 The Generator Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2016-07-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 2500000
VAR-001-4 (Manitoba) | 77660000000443 | E.A.17 | 776600000005444 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator. Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator. Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. | M.E.A.17 The Transmission Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2016-07-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 2600000
VAR-001-4 (Manitoba) | 77660000000443 | E.A.18 | 776600000005445 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the Automatic Voltage Regulators (AVR) to manage MVar loading: E.A.18.1. Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. E.A.18.2. Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | The Generator Operator did not meet the control loop specifications in EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 through EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | M.E.A.18 If the Generator Operator uses outside control loops to manage MVar loading, the Generator Operator shall have and provide upon request, evidence that it met the control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design specifications with identified agreed-upon control loops, system reports, or other dated documentation are acceptable as evidence. | 2016-07-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 2700000
VAR-001-4 (Manitoba) | 77660000000443 | R1. | 776600000005431 | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | 2016-07-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
VAR-001-4 (Manitoba) | 77660000000443 | R2. | 776600000005432 | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | M2. Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operational planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | 2016-07-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
VAR-001-4 (Manitoba) | 77660000000443 | R3. | 776600000005433 | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | 2016-07-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
VAR-001-4 (Manitoba) | 77660000000443 | R4. | 776600000005434 | The Transmission Operator shall specify the criteria that will exempt generators from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | M4. Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | 2016-07-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 40000000
VAR-001-4 (Manitoba) | 77660000000443 | R5. | 776600000005435 | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. Or The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power Schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | 2016-07-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 50000000
VAR-001-4 (Manitoba) | 77660000000443 | R6. | 776600000005436 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | 2016-07-01 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 60000000
VAR-001-4 (Ontario) | 79780000443 | E.A.13 | 79780005440 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: &lt;br/&gt;•A voltage set point with a voltage tolerance band and a specified period.&lt;br/&gt;• An initial volt-ampere reactive output or initial power factor output with a voltage&lt;br/&gt;tolerance band for a specified period that the Generator Operator uses to&lt;br/&gt;establish a generator bus voltage set point.&lt;br/&gt;• A voltage band for a specified period. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium |  |  |  |  | M.E.A.13 Each Transmission Operator shall have and provide upon request, evidence that it provided the voltage schedules to the Generator Operator. Dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13 are acceptable as evidence. | 2014-08-01 |  | 2015-11-12 |  |  |  | NPCC-ON | [6 empty] | 2200000
VAR-001-4 (Ontario) | 79780000443 | E.A.14 | 79780005441 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. &lt;br/&gt;•The generator terminals.&lt;br/&gt;• The high side of the generator step-up transformer.&lt;br/&gt;• The point of interconnection.&lt;br/&gt;• A location designated by mutual agreement between the Transmission Operator&lt;br/&gt;and Generator Operator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium |  |  |  |  | M.E.A.14 The Transmission Operator shall have and provide upon request, evidence that it provided one of the voltage schedule reference points in Requirement E.A.14 for each generation resource in its Area to the Generator Operator. Dated letters, e-mail, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource are acceptable as evidence. | 2014-08-01 |  | 2015-11-12 |  |  |  | NPCC-ON | [6 empty] | 2300000
VAR-001-4 (Ontario) | 79780000443 | E.A.15 | 79780005442 | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning, Same-Day Operations | Medium |  |  |  |  | M.E.A.15 Each Generator Operator shall have and provide upon request, evidence that it converted a voltage schedule as described in Requirement E.A.13 into a voltage set point for the AVR. Dated spreadsheets, logs, reports, or other documentation are acceptable as evidence. | 2014-08-01 |  | 2015-11-12 |  |  |  | NPCC-ON | [6 empty] | 2400000
VAR-001-4 (Ontario) | 79780000443 | E.A.16 | 79780005443 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning | Low |  |  |  |  | M.E.A.16 The Generator Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2014-08-01 |  | 2015-11-12 |  |  |  | NPCC-ON | [6 empty] | 2500000
VAR-001-4 (Ontario) | 79780000443 | E.A.17 | 79780005444 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low |  |  |  |  | M.E.A.17 The Transmission Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2014-01-01 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 2600000
VAR-001-4 (Ontario) | 79780000443 | E.A.18 | 79780005445 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the Automatic Voltage Regulators (AVR) to manage MVar loading: &lt;br/&gt;E.A.18.1. Each control loop’s design incorporates the AVR’s automatic voltage&lt;br/&gt;controlled response to voltage deviations during System Disturbances.&lt;br/&gt;E.A.18.2. Each control loop is only used by mutual agreement between the Generator&lt;br/&gt;Operator and the Transmission Operator affected by the control loop. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium |  |  |  |  | M.E.A.18 If the Generator Operator uses outside control loops to manage MVar loading, the Generator Operator shall have and provide upon request, evidence that it met the control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design specifications with identified agreed-upon control loops, system reports, or other dated documentation are acceptable as evidence. | 2014-01-01 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 2700000
VAR-001-4 (Ontario) | 79780000443 | R1. | 79780005431 | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High |  |  |  |  | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using&lt;br/&gt;either a range or a target value with an associated tolerance band.&lt;br/&gt;For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is&lt;br/&gt;either a range or a target value with an associated tolerance band) were provided to its Reliability&lt;br/&gt;Coordinator and adjacent Transmission Operators within 30 days of a request. Evidence may include,&lt;br/&gt;but is not limited to, emails, website postings, and meeting minutes. | 2014-10-01 |  | 2015-11-12 |  |  |  | NPCC-ON | [6 empty] | 10000000
VAR-001-4 (Ontario) | 79780000443 | R2. | 79780005432 | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High |  |  |  |  | M2. Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on&lt;br/&gt;their assessments of the system. For the operational planning time horizon, Transmission Operators&lt;br/&gt;shall have evidence of assessments used as the basis for how resources were scheduled. | 2014-10-01 |  | 2015-11-12 |  |  |  | NPCC-ON | [6 empty] | 20000000
VAR-001-4 (Ontario) | 79780000443 | R3. | 79780005433 | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High |  |  |  |  | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and&lt;br/&gt;inductive resources as necessary in Real-time. This may include instructions to Generator Operators&lt;br/&gt;to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | 2014-10-01 |  | 2015-11-12 |  |  |  | NPCC-ON | [6 empty] | 30000000
VAR-001-4 (Ontario) | 79780000443 | R4. | 79780005434 | The Transmission Operator shall specify the criteria that will exempt generators from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low |  |  |  |  | M4. Each Transmission Operator shall have evidence of the documented criteria for generator&lt;br/&gt;exemptions.&lt;br/&gt;For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in&lt;br/&gt;its area that is exempt from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having&lt;br/&gt;to make any notifications, the associated Generator Operator was notified of this exemption. | 2014-10-01 |  | 2015-11-12 |  |  |  | NPCC-ON | [6 empty] | 40000000
VAR-001-4 (Ontario) | 79780000443 | R5. | 79780005435 | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium |  |  |  |  | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power Schedule&lt;br/&gt;(which is either a range or a target value with an associated tolerance band).&lt;br/&gt;For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power&lt;br/&gt;schedule (which is either a range or a target value with an associated tolerance band) to the&lt;br/&gt;applicable Generator Operators, and that the Generator Operator was directed to comply with the&lt;br/&gt;schedule in automatic voltage control mode, unless exempted.&lt;br/&gt;For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for&lt;br/&gt;deviations from the voltage or Reactive Power schedule (which is either a range or a target value&lt;br/&gt;with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it&lt;br/&gt;provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a&lt;br/&gt;range or a target value with an associated tolerance band) within 30 days of receiving a request by a&lt;br/&gt;Generator Operator. | 2014-10-01 |  | 2015-11-12 |  |  |  | NPCC-ON | [6 empty] | 50000000
VAR-001-4 (Ontario) | 79780000443 | R6. | 79780005436 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low |  |  |  |  | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator&lt;br/&gt;Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with&lt;br/&gt;the requirement and that it consulted with the Generator Owner. | 2014-08-01 |  | 2015-11-12 |  |  |  | NPCC-ON | [6 empty] | 60000000
VAR-001-4 (Saskatchewan) | 83750000000443 | E.A.13 | 837500000005440 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: •A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are online and part of the BES in the Transmission Operator Area. | M.E.A.13 Each Transmission Operator shall have and provide upon request, evidence that it provided the voltage schedules to the Generator Operator. Dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13 are acceptable as evidence. | 2015-07-01 |  | 2016-03-31 |  |  |  | MRO-SK | [6 empty] | 2200000
VAR-001-4 (Saskatchewan) | 83750000000443 | E.A.14 | 837500000005441 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. •The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | M.E.A.14 The Transmission Operator shall have and provide upon request, evidence that it provided one of the voltage schedule reference points in Requirement E.A.14 for each generation resource in its Area to the Generator Operator. Dated letters, e-mail, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource are acceptable as evidence. | 2015-07-01 |  | 2016-03-31 |  |  |  | MRO-SK | [6 empty] | 2300000
VAR-001-4 (Saskatchewan) | 83750000000443 | E.A.15 | 837500000005442 | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning, Same-Day Operations | Medium | The Generator Operator failed to convert at least one voltage schedule in Requirement E.A.13 into the voltage set point for the AVR for less than 25% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 25% or more but less than 50% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 50% or more but less than 75% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 75% or more of the voltage schedules. | M.E.A.15 Each Generator Operator shall have and provide upon request, evidence that it converted a voltage schedule as described in Requirement E.A.13 into a voltage set point for the AVR. Dated spreadsheets, logs, reports, or other documentation are acceptable as evidence. | 2015-07-01 |  | 2016-03-31 |  |  |  | MRO-SK | [6 empty] | 2400000
VAR-001-4 (Saskatchewan) | 83750000000443 | E.A.16 | 837500000005443 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | M.E.A.16 The Generator Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2015-07-01 |  | 2016-03-31 |  |  |  | MRO-SK | [6 empty] | 2500000
VAR-001-4 (Saskatchewan) | 83750000000443 | E.A.17 | 837500000005444 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator. Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator. Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. | M.E.A.17 The Transmission Operator shall have and provide upon request, evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology. Dated reports, spreadsheets, or other documentation are acceptable as evidence. | 2015-07-01 |  | 2016-03-31 |  |  |  | MRO-SK | [6 empty] | 2600000
VAR-001-4 (Saskatchewan) | 83750000000443 | E.A.18 | 837500000005445 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the Automatic Voltage Regulators (AVR) to manage MVar loading: E.A.18.1. Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. E.A.18.2. Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | The Generator Operator did not meet the control loop specifications in EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 through EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | M.E.A.18 If the Generator Operator uses outside control loops to manage MVar loading, the Generator Operator shall have and provide upon request, evidence that it met the control loop specifications in sub-parts E.A.18.1 through E.A.18.2. Design specifications with identified agreed-upon control loops, system reports, or other dated documentation are acceptable as evidence. | 2015-07-01 |  | 2016-03-31 |  |  |  | MRO-SK | [6 empty] | 2700000
VAR-001-4 (Saskatchewan) | 83750000000443 | R1. | 837500000005431 | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | 2015-07-01 |  | 2016-03-31 |  |  |  | MRO-SK | [6 empty] | 10000000
VAR-001-4 (Saskatchewan) | 83750000000443 | R2. | 837500000005432 | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | M2. Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operational planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | 2015-07-01 |  | 2016-03-31 |  |  |  | MRO-SK | [6 empty] | 20000000
VAR-001-4 (Saskatchewan) | 83750000000443 | R3. | 837500000005433 | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | 2015-07-01 |  | 2016-03-31 |  |  |  | MRO-SK | [6 empty] | 30000000
VAR-001-4 (Saskatchewan) | 83750000000443 | R4. | 837500000005434 | The Transmission Operator shall specify the criteria that will exempt generators from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | M4. Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | 2015-07-01 |  | 2016-03-31 |  |  |  | MRO-SK | [6 empty] | 40000000
VAR-001-4 (Saskatchewan) | 83750000000443 | R5. | 837500000005435 | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. Or The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power Schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | 2015-07-01 |  | 2016-03-31 |  |  |  | MRO-SK | [6 empty] | 50000000
VAR-001-4 (Saskatchewan) | 83750000000443 | R6. | 837500000005436 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | 2015-07-01 |  | 2016-03-31 |  |  |  | MRO-SK | [6 empty] | 60000000
VAR-001-5 | 587 | E.A.13. | 8443 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | M.E.A.13 Each Transmission Operator will have evidence that it provided the voltage schedules to the Generator Operator, as required in E.A.13. Evidence may include, but is not limited to, dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13. | 2018-10-15 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2200000
VAR-001-5 | 587 | E.A.14. | 8444 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | M.E.A.14 The Transmission Operator will have evidence that it provided one of the voltage schedule reference points for each generation resource in its area to the Generator Operator, as required in E.A.14. Evidence may include, but is not limited to dated letters, e-mail, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource. | 2018-10-15 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2300000
VAR-001-5 | 587 | E.A.15. | 8445 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | M.E.A.15 The Generator Operator will have evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals, as required in E.A.15. Evidence may include, but is not limited to, dated reports, spreadsheets, or other documentation. | 2018-10-15 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2400000
VAR-001-5 | 587 | E.A.16. | 8446 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator. Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator. Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. | M.E.A.16 The Transmission Operator will have evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology, as required in E.A.16. Evidence may include, but is not limited to, dated reports, spreadsheets, or other documentation. | 2018-10-15 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2500000
VAR-001-5 | 587 | E.A.17. | 8447 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the automatic voltage regulators (AVR) to manage Mvar loading: |  | GOP | [5 empty] | GOP | [15 empty] | Long-Term Planning, Real-Time Operations | Medium | N/A | The Generator Operator did not meet the control loop specifications in E.A.17.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in E.A.17.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in E.A.17.1 through E.A.17.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | M.E.A.17 If the Generator Operator uses outside control loops to manage Mvar loading, the Generator Operator will have evidence that it met the control loop specifications in sub-parts E.A.17.1 through E.A.17.2, as required in E.A.17 and its sub-parts. Evidence may include, but is not limited to, design specifications with identified agreed-upon control loops, system reports, or other dated documentation. | 2017-09-26 |  | 2018-12-31 |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2600000
VAR-001-5 | 587 | R1. | 8433 | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | 2019-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
VAR-001-5 | 587 | R2. | 8435 | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | M2. Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operations planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | 2019-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
VAR-001-5 | 587 | R3. | 8436 | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include, but is not limited to, instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | 2019-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
VAR-001-5 | 587 | R4. | 8437 | Each Transmission Operator shall specify the criteria that will exempt generators: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | M4. Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | 2019-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
VAR-001-5 | 587 | R5. | 8438 | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. Or The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | 2019-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
VAR-001-5 | 587 | R6. | 8439 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | 2019-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
VAR-001-5 (British Columbia) | 666700000010314 | E.A.13. | 666700000011917 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | M.E.A.13 Each Transmission Operator will have evidence that it provided the voltage schedules to the Generator Operator, as required in E.A.13. Evidence may include, but is not limited to, dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13. | 2019-10-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | WECC-BC | [6 empty] | 2200000
VAR-001-5 (British Columbia) | 666700000010314 | E.A.14. | 666700000011918 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | M.E.A.14 The Transmission Operator will have evidence that it provided one of the voltage schedule reference points for each generation resource in its area to the Generator Operator, as required in E.A.14. Evidence may include, but is not limited to dated letters, e-mail, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource. | 2019-10-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | WECC-BC | [6 empty] | 2300000
VAR-001-5 (British Columbia) | 666700000010314 | E.A.15. | 666700000011919 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | M.E.A.15 The Generator Operator will have evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals, as required in E.A.15. Evidence may include, but is not limited to, dated reports, spreadsheets, or other documentation. | 2019-10-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | WECC-BC | [6 empty] | 2400000
VAR-001-5 (British Columbia) | 666700000010314 | E.A.16. | 666700000011920 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator. Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator. Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. | M.E.A.16 The Transmission Operator will have evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology, as required in E.A.16. Evidence may include, but is not limited to, dated reports, spreadsheets, or other documentation. | 2019-10-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | WECC-BC | [6 empty] | 2500000
VAR-001-5 (British Columbia) | 666700000010314 | E.A.17. | 666700000011921 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the automatic voltage regulators (AVR) to manage Mvar loading: |  | GOP | [5 empty] | GOP | [15 empty] | Long-Term Planning, Real-Time Operations | Medium | N/A | The Generator Operator did not meet the control loop specifications in E.A.17.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in E.A.17.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in E.A.17.1 through E.A.17.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | M.E.A.17 If the Generator Operator uses outside control loops to manage Mvar loading, the Generator Operator will have evidence that it met the control loop specifications in sub-parts E.A.17.1 through E.A.17.2, as required in E.A.17 and its sub-parts. Evidence may include, but is not limited to, design specifications with identified agreed-upon control loops, system reports, or other dated documentation. | 2019-10-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | WECC-BC | [6 empty] | 2600000
VAR-001-5 (British Columbia) | 666700000010314 | R1. | 666700000011922 | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | 2019-10-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | WECC-BC | [6 empty] | 10000000
VAR-001-5 (British Columbia) | 666700000010314 | R2. | 666700000011923 | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | M2. Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operations planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | 2019-10-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | WECC-BC | [6 empty] | 20000000
VAR-001-5 (British Columbia) | 666700000010314 | R3. | 666700000011924 | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include, but is not limited to, instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | 2019-10-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | WECC-BC | [6 empty] | 30000000
VAR-001-5 (British Columbia) | 666700000010314 | R4. | 666700000011925 | Each Transmission Operator shall specify the criteria that will exempt generators: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | M4. Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | 2019-10-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | WECC-BC | [6 empty] | 40000000
VAR-001-5 (British Columbia) | 666700000010314 | R5. | 666700000011926 | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. Or The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | 2019-10-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | WECC-BC | [6 empty] | 50000000
VAR-001-5 (British Columbia) | 666700000010314 | R6. | 666700000011927 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | 2019-10-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | WECC-BC | [6 empty] | 60000000
VAR-001-5 (Manitoba) | 77660000000587 | E.A.13. | 776600000008443 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | M.E.A.13 Each Transmission Operator will have evidence that it provided the voltage schedules to the Generator Operator, as required in E.A.13. Evidence may include, but is not limited to, dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13. | 2021-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | MRO-MB | [6 empty] | 2200000
VAR-001-5 (Manitoba) | 77660000000587 | E.A.14. | 776600000008444 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | M.E.A.14 The Transmission Operator will have evidence that it provided one of the voltage schedule reference points for each generation resource in its area to the Generator Operator, as required in E.A.14. Evidence may include, but is not limited to dated letters, e-mail, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource. | 2021-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | MRO-MB | [6 empty] | 2300000
VAR-001-5 (Manitoba) | 77660000000587 | E.A.15. | 776600000008445 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | M.E.A.15 The Generator Operator will have evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals, as required in E.A.15. Evidence may include, but is not limited to, dated reports, spreadsheets, or other documentation. | 2021-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | MRO-MB | [6 empty] | 2400000
VAR-001-5 (Manitoba) | 77660000000587 | E.A.16. | 776600000008446 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator. Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator. Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. | M.E.A.16 The Transmission Operator will have evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology, as required in E.A.16. Evidence may include, but is not limited to, dated reports, spreadsheets, or other documentation. | 2021-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | MRO-MB | [6 empty] | 2500000
VAR-001-5 (Manitoba) | 77660000000587 | E.A.17. | 776600000008447 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the automatic voltage regulators (AVR) to manage Mvar loading: |  | GOP | [5 empty] | GOP | [15 empty] | Long-Term Planning, Real-Time Operations | Medium | N/A | The Generator Operator did not meet the control loop specifications in E.A.17.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in E.A.17.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in E.A.17.1 through E.A.17.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | M.E.A.17 If the Generator Operator uses outside control loops to manage Mvar loading, the Generator Operator will have evidence that it met the control loop specifications in sub-parts E.A.17.1 through E.A.17.2, as required in E.A.17 and its sub-parts. Evidence may include, but is not limited to, design specifications with identified agreed-upon control loops, system reports, or other dated documentation. | 2021-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | MRO-MB | [6 empty] | 2600000
VAR-001-5 (Manitoba) | 77660000000587 | R1. | 776600000008433 | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | 2021-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | MRO-MB | [6 empty] | 10000000
VAR-001-5 (Manitoba) | 77660000000587 | R2. | 776600000008435 | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | M2. Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operations planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | 2021-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | MRO-MB | [6 empty] | 20000000
VAR-001-5 (Manitoba) | 77660000000587 | R3. | 776600000008436 | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include, but is not limited to, instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | 2021-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | MRO-MB | [6 empty] | 30000000
VAR-001-5 (Manitoba) | 77660000000587 | R4. | 776600000008437 | Each Transmission Operator shall specify the criteria that will exempt generators: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | M4. Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | 2021-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | MRO-MB | [6 empty] | 40000000
VAR-001-5 (Manitoba) | 77660000000587 | R5. | 776600000008438 | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. Or The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | 2021-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | MRO-MB | [6 empty] | 50000000
VAR-001-5 (Manitoba) | 77660000000587 | R6. | 776600000008439 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | 2021-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | MRO-MB | [6 empty] | 60000000
VAR-001-5 (Nova Scotia) | 78830000000587 | R1. | 788300000008433 | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | 2019-07-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | NPCC-NS | [6 empty] | 10000000
VAR-001-5 (Nova Scotia) | 78830000000587 | R2. | 788300000008435 | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | M2. Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operations planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | 2019-07-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | NPCC-NS | [6 empty] | 20000000
VAR-001-5 (Nova Scotia) | 78830000000587 | R3. | 788300000008436 | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include, but is not limited to, instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | 2019-07-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | NPCC-NS | [6 empty] | 30000000
VAR-001-5 (Nova Scotia) | 78830000000587 | R4. | 788300000008437 | Each Transmission Operator shall specify the criteria that will exempt generators: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | M4. Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | 2019-07-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | NPCC-NS | [6 empty] | 40000000
VAR-001-5 (Nova Scotia) | 78830000000587 | R5. | 788300000008438 | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. Or The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | 2019-07-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | NPCC-NS | [6 empty] | 50000000
VAR-001-5 (Nova Scotia) | 78830000000587 | R6. | 788300000008439 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | 2019-07-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | NPCC-NS | [6 empty] | 60000000
VAR-001-5 (Ontario) | 79780000587 | R1. | 79780008433 | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band.&lt;br/&gt;For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | 2019-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | NPCC-ON | [6 empty] | 10000000
VAR-001-5 (Ontario) | 79780000587 | R2. | 79780008435 | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | M2. Each Transmission Operator shall have evidence of scheduling sufficient reactive resources based on their assessments of the system. For the operations planning time horizon, Transmission Operators shall have evidence of assessments used as the basis for how resources were scheduled. | 2019-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | NPCC-ON | [6 empty] | 20000000
VAR-001-5 (Ontario) | 79780000587 | R3. | 79780008436 | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Real-Time Operations, Same-Day Operations | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include, but is not limited to, instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. | 2019-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | NPCC-ON | [6 empty] | 30000000
VAR-001-5 (Ontario) | 79780000587 | R4. | 79780008437 | Each Transmission Operator shall specify the criteria that will exempt generators: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | &lt;p&gt;M4. Each Transmission Operator shall have evidence of the documented criteria for generator exemptions.&lt;/p&gt; &lt;p&gt;For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption.&lt;/p&gt; &lt;p/&gt; | 2019-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | NPCC-ON | [6 empty] | 40000000
VAR-001-5 (Ontario) | 79780000587 | R5. | 79780008438 | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. Or The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | &lt;p&gt;M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band).&lt;/p&gt; &lt;p&gt;For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted.&lt;/p&gt; &lt;p&gt;For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator.&lt;/p&gt; &lt;p/&gt; | 2019-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | NPCC-ON | [6 empty] | 50000000
VAR-001-5 (Ontario) | 79780000587 | R6. | 79780008439 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. | 2019-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | NPCC-ON | [6 empty] | 60000000
VAR-001-6 | 604 | E.A.13. | 8792 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | M.E.A.13 Each Transmission Operator will have evidence that it provided the voltage schedules to the Generator Operator, as required in E.A.13. Evidence may include, but is not limited to, dated spreadsheets, reports, voice recordings, or other documentation containing the voltage schedule including set points, tolerance bands, and specified periods as required in Requirement E.A.13. |  |  | 2020-05-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2200000
VAR-001-6 | 604 | E.A.14. | 8793 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | TOP | [18 empty] | TOP |  |  | Operations Planning, Same-Day Operations | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | M.E.A.14 The Transmission Operator will have evidence that it provided one of the voltage schedule reference points for each generation resource in its area to the Generator Operator, as required in E.A.14. Evidence may include, but is not limited to dated letters, e-mail, or other documentation that contains notification to the Generator Operator of the voltage schedule reference point for each generation resource. |  |  | 2020-05-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2300000
VAR-001-6 | 604 | E.A.15. | 8794 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Planning | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | M.E.A.15 The Generator Operator will have evidence that within 30 calendar days of request by its Transmission Operator it provided its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals, as required in E.A.15. Evidence may include, but is not limited to, dated reports, spreadsheets, or other documentation. |  |  | 2020-05-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2400000
VAR-001-6 | 604 | E.A.16. | 8795 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator. Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator. Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. | M.E.A.16 The Transmission Operator will have evidence that within 30 calendar days of request by its Generator Operator it provided data to support development of the voltage set point conversion methodology, as required in E.A.16. Evidence may include, but is not limited to, dated reports, spreadsheets, or other documentation. |  |  | 2020-05-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2500000
VAR-001-6 | 604 | E.A.17. | 8796 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the automatic voltage regulators (AVR) to manage Mvar loading: |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | The Generator Operator did not meet the control loop specifications in E.A.17.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in E.A.17.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in E.A.17.1 through E.A.17.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | M.E.A.17 If the Generator Operator uses outside control loops to manage Mvar loading, the Generator Operator will have evidence that it met the control loop specifications in sub-parts E.A.17.1 through E.A.17.2, as required in E.A.17 and its sub-parts. Evidence may include, but is not limited to, design specifications with identified agreed-upon control loops, system reports, or other dated documentation. | 2019-01-01 |  | 2020-05-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 2600000
VAR-001-6 | 604 | R1. | 8799 | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. . |  |  | 2020-05-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
VAR-001-6 | 604 | R2. | 8801 | Reserved. | [29 empty] | Reserved |  |  | 2020-05-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
VAR-001-6 | 604 | R3. | 8802 | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include, but is not limited to, instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. |  |  | 2020-05-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
VAR-001-6 | 604 | R4. | 8803 | Each Transmission Operator shall specify the criteria that will exempt generators: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | M4. Each Transmission Operator shall have evidence of the documented criteria for generator exemptions. For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. |  |  | 2020-05-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
VAR-001-6 | 604 | R5. | 8805 | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. Or The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. |  |  | 2020-05-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
VAR-001-6 | 604 | R6. | 8809 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. |  |  | 2020-05-14 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
VAR-001-6 (Ontario) | 79780000604 | R1. | 79780008799 | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | M1. The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band.&lt;br/&gt;&lt;br/&gt;For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes.&lt;br/&gt;. |  |  | 2020-05-14 |  |  |  | NPCC-ON | [6 empty] | 10000000
VAR-001-6 (Ontario) | 79780000604 | R2. | 79780008801 | Reserved. | [25 empty] | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | Reserved |  |  | 2020-05-14 |  |  |  | NPCC-ON | [6 empty] | 20000000
VAR-001-6 (Ontario) | 79780000604 | R3. | 79780008802 | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | M3. Each Transmission Operator shall have evidence that actions were taken to operate capacitive and inductive resources as necessary in Real-time. This may include, but is not limited to, instructions to Generator Operators to: 1) provide additional voltage support; 2) bring resources on-line; or 3) make manual adjustments. |  |  | 2020-05-14 |  |  |  | NPCC-ON | [6 empty] | 30000000
VAR-001-6 (Ontario) | 79780000604 | R4. | 79780008803 | Each Transmission Operator shall specify the criteria that will exempt generators: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | M4. Each Transmission Operator shall have evidence of the documented criteria for generator exemptions.&lt;br/&gt;&lt;br/&gt;For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. |  |  | 2020-05-14 |  |  |  | NPCC-ON | [6 empty] | 40000000
VAR-001-6 (Ontario) | 79780000604 | R5. | 79780008805 | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. Or The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | M5. The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band).&lt;br/&gt;&lt;br/&gt;For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted.&lt;br/&gt;&lt;br/&gt;For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. |  |  | 2020-05-14 |  |  |  | NPCC-ON | [6 empty] | 50000000
VAR-001-6 (Ontario) | 79780000604 | R6. | 79780008809 | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | TOP | [18 empty] | TOP |  |  | Operations Planning | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | M6. The Transmission Operator shall have evidence that it provided documentation to the Generator Owner when a change was needed to a generating unit’s step-up transformer tap in accordance with the requirement and that it consulted with the Generator Owner. |  |  | 2020-05-14 |  |  |  | NPCC-ON | [6 empty] | 60000000
VAR-001-AB-4 (Alberta) | 656600000009061 | R1. | 656600000009300 | The ISO must specify a system voltage range with an associated tolerance band, as part of its plan to operate within system operating limits and interconnection reliability operating limits. |  | ISO | [28 empty] | 2016-04-01 | [5 empty] | WECC-AB | [6 empty] | 10000000
VAR-001-AB-4 (Alberta) | 656600000009061 | R2. | 656600000009301 | The ISO must operate with sufficient reactive power resources available within Alberta to protect the voltage levels of the transmission system under normal and contingency conditions. |  | ISO | [28 empty] | 2016-04-01 | [5 empty] | WECC-AB | [6 empty] | 20000000
VAR-001-AB-4 (Alberta) | 656600000009061 | R3. | 656600000009302 | The ISO must be able to regulate transmission voltage and reactive power flow by issuing directives or instructions to operate the devices necessary to do so. |  | ISO | [28 empty] | 2016-04-01 | [5 empty] | WECC-AB | [6 empty] | 30000000
VAR-001-AB-4 (Alberta) | 656600000009061 | R4. | 656600000009303 | The ISO must specify the criteria that will exempt a generating unit or an aggregated generating facility from: a) following a voltage or reactive power instruction or directive; b) having its automatic voltage regulator or voltage regulating system in service or being in voltage control mode; or c) making any associated notifications. |  | ISO | [28 empty] | 2016-04-01 | [5 empty] | WECC-AB | [6 empty] | 40000000
VAR-001-AB-4 (Alberta) | 656600000009061 | R5. | 656600000009304 | The ISO, when issuing directives or instructions for voltage level or reactive power, to the operator of a generating unit or the operator of an aggregated generating facility, must specify the following: a) the voltage level at the point of connection between the transmission system and a generating unit or an aggregated generating facility, including those in a power plant or an industrial complex; or b) the reactive power to be achieved by the generating unit, aggregated generating facility, power plant or industrial complex. |  | ISO | [28 empty] | 2016-04-01 | [5 empty] | WECC-AB | [6 empty] | 50000000
VAR-001-AB-4 (Alberta) | 656600000009061 | R6. | 656600000009305 | The ISO must, after a review with the legal owner of a generating unit or the legal owner of an aggregated generating facility regarding necessary off-load tap changes for the step-up transformer that connects to the transmission system, provide documentation to the legal owner of a generating unit or the legal owner of an aggregated generating facility specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | ISO | [28 empty] | 2016-04-01 | [5 empty] | WECC-AB | [6 empty] | 60000000
VAR-002-1 | 196 | R1. | 2246 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2007-08-02 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
VAR-002-1 | 196 | R2. | 2247 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power output (within applicable Facility Ratings. [1] as directed by the Transmission Operator |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2007-08-02 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
VAR-002-1 | 196 | R3. | 2250 | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2007-08-02 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
VAR-002-1 | 196 | R4. | 2253 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [17 empty] | Low | [5 empty] | 2007-08-02 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
VAR-002-1 | 196 | R5. | 2259 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [17 empty] | Medium | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
VAR-002-1.1a | 197 | R1. | 2261 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2009-05-13 |  | 2010-09-15 |  |  | VAR-002-1a R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
VAR-002-1.1a | 197 | R2. | 2262 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power output (within applicable Facility Ratings ) as directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2009-05-13 |  | 2010-09-15 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
VAR-002-1.1a | 197 | R3. | 2265 | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2009-05-13 |  | 2010-09-15 |  |  | VAR-002-1a R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
VAR-002-1.1a | 197 | R4. | 2268 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [17 empty] | Low | [5 empty] | 2009-05-13 |  | 2010-09-15 |  |  | VAR-002-1a R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
VAR-002-1.1a | 197 | R5. | 2274 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [17 empty] | Medium | [5 empty] | 2007-08-02 |  | 2008-08-26 |  |  | VAR-002-1a R5. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
VAR-002-1.1a (British Columbia) | 666700000010315 | R1. | 666700000011928 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2011-01-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 10000000
VAR-002-1.1a (British Columbia) | 666700000010315 | R2. | 666700000011929 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power output (within applicable Facility Ratings ) as directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2011-01-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 20000000
VAR-002-1.1a (British Columbia) | 666700000010315 | R3. | 666700000011930 | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2011-01-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 30000000
VAR-002-1.1a (British Columbia) | 666700000010315 | R4. | 666700000011931 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [17 empty] | Low | [5 empty] | 2011-01-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 40000000
VAR-002-1.1a (British Columbia) | 666700000010315 | R5. | 666700000011932 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [17 empty] | Medium | [5 empty] | 2011-01-01 |  | 2011-10-29 |  |  |  | WECC-BC | [6 empty] | 50000000
VAR-002-1.1a (Ontario) | 79780000197 | R1. | 79780002261 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | The Generator Operator failed to notify the Transmission Operator as identified in R1 for less than 25% of its generators. | The Generator Operator failed to notify the Transmission Operator as identified in R1 for 25% or more but less tan 50% of its generators. | The Generator Operator failed to notify the Transmission Operator as identified in R1 for 50% or more but less tan 75% of its generators. | The Generator Operator failed to notify the Transmission Operator as identified in R1 for 75% or more of its generators. |  | 2009-05-13 |  | 2010-09-15 |  |  |  | NPCC-ON | [6 empty] | 10000000
VAR-002-1.1a (Ontario) | 79780000197 | R2. | 79780002262 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power output (within applicable Facility Ratings ) as directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | The Generator Operator failed to maintain a voltage or reactive power schedule for less than 25% of its generators. | The Generator Operator failed to maintain a voltage or reactive power schedule for 25% or more but less tan 50% of its generators. | The Generator Operator failed to maintain a voltage or reactive power schedule for 50% or more but less tan 75% of its generators. | The Generator Operator failed to maintain a voltage or reactive power schedule for 75% or more of its generators. |  | 2009-05-13 |  | 2010-09-15 |  |  |  | NPCC-ON | [6 empty] | 20000000
VAR-002-1.1a (Ontario) | 79780000197 | R3. | 79780002265 | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | The Generator Operator had one incident of failing to notify the Transmission Operator as identified in R3. | The Generator Operator had more than one but less than five incidents of failing to notify the Transmission as identified in R3.1 R3.2. | The Generator Operator had more than five but less than ten incidents of failing to notify the Transmission Operator as identified in R3.1 R3.2 | The Generator Operator had ten or more incidents of failing to notify the Transmission Operator as identified in R3.1 R3.2. |  | 2009-05-13 |  | 2010-09-15 |  |  |  | NPCC-ON | [6 empty] | 30000000
VAR-002-1.1a (Ontario) | 79780000197 | R4. | 79780002268 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [17 empty] | Low | The Generator Owner had one (1) incident of failing to notify its associated Transmission Operator and Transmission Planner within 30 calendar days of a request for information, as described in R4.1.1 through R4.1.4, regarding generator step-up transform | The Generator Owner had more than one (1) incident but less than five (5) incidents of failing to notify its associated Transmission Operator and Transmission Planner within 30 calendar days of a request for information, as described in R4.1.1 through R4. | The Generator Owner had more than five (5) incidents but less than ten (10) incidents of failing to notify its associated Transmission Operator and Transmission Planner within 30 calendar days of a request for information, as described in R4.1.1 through R | The Generator Owner had more than ten (10) incidents of failing to notify its associated Transmission Operator and Transmission Planner within 30 calendar days of a request for information, as described in R4.1.1 through R4.1.4, regarding generator step-u |  | 2009-05-13 |  | 2010-09-15 |  |  |  | NPCC-ON | [6 empty] | 40000000
VAR-002-1.1a (Ontario) | 79780000197 | R5. | 79780002274 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [17 empty] | Medium | The Generator Owner had one (1) incident of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would not have violated safety, an equipment rating, a regulat | The Generator Owner had more than one (1) incident but less than or equal to five (5) incidents of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would n | The Generator Owner had more than five (5) incident but less than or equal to ten (10) incidents of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would | The Generator Owner had more than ten (10) incidents of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would not have violated safety, an equipment ratin |  | 2007-08-02 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 50000000
VAR-002-1.1b | 198 | R1. | 2276 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2010-09-16 |  | 2013-06-30 |  |  | VAR-002-1.1a R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
VAR-002-1.1b | 198 | R2. | 2277 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power output (within applicable Facility Ratings ) as directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2010-09-16 |  | 2013-06-30 |  |  | VAR-002-1.1a R2. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
VAR-002-1.1b | 198 | R3. | 2280 | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2010-09-16 |  | 2013-06-30 |  |  | VAR-002-1.1a R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
VAR-002-1.1b | 198 | R4. | 2283 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [17 empty] | Low | [5 empty] | 2010-09-16 |  | 2013-06-30 |  |  | VAR-002-1.1a R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
VAR-002-1.1b | 198 | R5. | 2289 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [17 empty] | Medium | [5 empty] | 2009-05-13 |  | 2010-09-15 |  |  | VAR-002-1.1a R5. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
VAR-002-1.1b (British Columbia) | 666700000010316 | R1. | 666700000011933 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2011-10-30 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 10000000
VAR-002-1.1b (British Columbia) | 666700000010316 | R2. | 666700000011934 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power output (within applicable Facility Ratings ) as directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2011-10-30 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 20000000
VAR-002-1.1b (British Columbia) | 666700000010316 | R3. | 666700000011935 | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2011-10-30 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 30000000
VAR-002-1.1b (British Columbia) | 666700000010316 | R4. | 666700000011936 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [17 empty] | Low | [5 empty] | 2011-10-30 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 40000000
VAR-002-1.1b (British Columbia) | 666700000010316 | R5. | 666700000011937 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [17 empty] | Medium | [5 empty] | 2011-10-30 |  | 2014-07-31 |  |  |  | WECC-BC | [6 empty] | 50000000
VAR-002-1.1b (Manitoba) | 77660000000198 | R1. | 776600000002276 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
VAR-002-1.1b (Manitoba) | 77660000000198 | R2. | 776600000002277 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power output (within applicable Facility Ratings ) as directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
VAR-002-1.1b (Manitoba) | 77660000000198 | R3. | 776600000002280 | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
VAR-002-1.1b (Manitoba) | 77660000000198 | R4. | 776600000002283 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [17 empty] | Low | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 40000000
VAR-002-1.1b (Manitoba) | 77660000000198 | R5. | 776600000002289 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [17 empty] | Medium | [5 empty] | 2014-02-14 |  | 2017-06-30 |  |  |  | MRO-MB | [6 empty] | 50000000
VAR-002-1.1b (Ontario) | 79780000198 | R1. | 79780002276 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | The Generator Operator failed to notify the Transmission Operator as identified in R1 for less than 25% of its generators. | The Generator Operator failed to notify the Transmission Operator as identified in R1 for 25% or more but less tan 50% of its generators. | The Generator Operator failed to notify the Transmission Operator as identified in R1 for 50% or more but less tan 75% of its generators. | The Generator Operator failed to notify the Transmission Operator as identified in R1 for 75% or more of its generators. |  | 2010-09-16 |  | 2013-06-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
VAR-002-1.1b (Ontario) | 79780000198 | R2. | 79780002277 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power output (within applicable Facility Ratings ) as directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | The Generator Operator failed to maintain a voltage or reactive power schedule for less than 25% of its generators. | The Generator Operator failed to maintain a voltage or reactive power schedule for 25% or more but less tan 50% of its generators. | The Generator Operator failed to maintain a voltage or reactive power schedule for 50% or more but less tan 75% of its generators. | The Generator Operator failed to maintain a voltage or reactive power schedule for 75% or more of its generators. |  | 2010-09-16 |  | 2013-06-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
VAR-002-1.1b (Ontario) | 79780000198 | R3. | 79780002280 | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | The Generator Operator had one incident of failing to notify the Transmission Operator as identified in R3. | The Generator Operator had more than one but less than five incidents of failing to notify the Transmission as identified in R3.1 R3.2. | The Generator Operator had more than five but less than ten incidents of failing to notify the Transmission Operator as identified in R3.1 R3.2 | The Generator Operator had ten or more incidents of failing to notify the Transmission Operator as identified in R3.1 R3.2. |  | 2010-09-16 |  | 2013-06-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
VAR-002-1.1b (Ontario) | 79780000198 | R4. | 79780002283 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [17 empty] | Low | The Generator Owner had one (1) incident of failing to notify its associated Transmission Operator and Transmission Planner within 30 calendar days of a request for information, as described in R4.1.1 through R4.1.4, regarding generator step-up transform | The Generator Owner had more than one (1) incident but less than five (5) incidents of failing to notify its associated Transmission Operator and Transmission Planner within 30 calendar days of a request for information, as described in R4.1.1 through R4. | The Generator Owner had more than five (5) incidents but less than ten (10) incidents of failing to notify its associated Transmission Operator and Transmission Planner within 30 calendar days of a request for information, as described in R4.1.1 through R | The Generator Owner had more than ten (10) incidents of failing to notify its associated Transmission Operator and Transmission Planner within 30 calendar days of a request for information, as described in R4.1.1 through R4.1.4, regarding generator step-u |  | 2010-09-16 |  | 2013-06-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
VAR-002-1.1b (Ontario) | 79780000198 | R5. | 79780002289 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [17 empty] | Medium | The Generator Owner had one (1) incident of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would not have violated safety, an equipment rating, a regulat | The Generator Owner had more than one (1) incident but less than or equal to five (5) incidents of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would n | The Generator Owner had more than five (5) incident but less than or equal to ten (10) incidents of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would | The Generator Owner had more than ten (10) incidents of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would not have violated safety, an equipment ratin |  | 2009-05-13 |  | 2010-09-15 |  |  |  | NPCC-ON | [6 empty] | 50000000
VAR-002-1.1b (Saskatchewan) | 83750000000198 | R1. | 837500000002276 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 10000000
VAR-002-1.1b (Saskatchewan) | 83750000000198 | R2. | 837500000002277 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power output (within applicable Facility Ratings ) as directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 20000000
VAR-002-1.1b (Saskatchewan) | 83750000000198 | R3. | 837500000002280 | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 30000000
VAR-002-1.1b (Saskatchewan) | 83750000000198 | R4. | 837500000002283 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [17 empty] | Low | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 40000000
VAR-002-1.1b (Saskatchewan) | 83750000000198 | R5. | 837500000002289 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [17 empty] | Medium | [5 empty] | 2010-03-30 |  | 2014-03-31 |  |  |  | MRO-SK | [6 empty] | 50000000
VAR-002-1a | 199 | R1. | 2291 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator. |  | GOP | [5 empty] | GOP | [22 empty] | 2008-08-27 |  | 2009-05-12 |  |  | VAR-002-1 R1. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
VAR-002-1a | 199 | R2. | 2292 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power output (within applicable Facility Ratings [see footnote in standard]) as directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [22 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
VAR-002-1a | 199 | R3. | 2295 | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  | GOP | [5 empty] | GOP | [22 empty] | 2008-08-27 |  | 2009-05-12 |  |  | VAR-002-1 R3. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
VAR-002-1a | 199 | R4. | 2298 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [23 empty] | 2008-08-27 |  | 2009-05-12 |  |  | VAR-002-1 R4. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
VAR-002-1a | 199 | R5. | 2304 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [18 empty] | The Generator Owner had one (1) incident of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would not have violated safety, an equipment rating, a regulat | The Generator Owner had more than one (1) incident but less than or equal to five (5) incidents of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would n | The Generator Owner had more than five (5) incident but less than or equal to ten (10) incidents of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would | The Generator Owner had more than ten (10) incidents of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would not have violated safety, an equipment ratin |  | 2010-09-16 |  | 2013-06-30 |  |  | VAR-002-1 R5. | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
VAR-002-1a (British Columbia) | 666700000010317 | R1. | 666700000011938 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator. |  | GOP | [5 empty] | GOP | [22 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 10000000
VAR-002-1a (British Columbia) | 666700000010317 | R2. | 666700000011939 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power output (within applicable Facility Ratings [see footnote in standard]) as directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [22 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 20000000
VAR-002-1a (British Columbia) | 666700000010317 | R3. | 666700000011940 | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  | GOP | [5 empty] | GOP | [22 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 30000000
VAR-002-1a (British Columbia) | 666700000010317 | R4. | 666700000011941 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [23 empty] | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 40000000
VAR-002-1a (British Columbia) | 666700000010317 | R5. | 666700000011942 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [18 empty] | The Generator Owner had one (1) incident of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would not have violated safety, an equipment rating, a regulat | The Generator Owner had more than one (1) incident but less than or equal to five (5) incidents of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would n | The Generator Owner had more than five (5) incident but less than or equal to ten (10) incidents of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would | The Generator Owner had more than ten (10) incidents of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would not have violated safety, an equipment ratin |  | 2010-11-01 |  | 2010-12-31 |  |  |  | WECC-BC | [6 empty] | 50000000
VAR-002-1a (Ontario) | 79780000199 | R1. | 79780002291 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator. |  | GOP | [5 empty] | GOP | [17 empty] | The Generator Operator failed to notify the Transmission Operator as identified in R1 for less than 25% of its generators. | The Generator Operator failed to notify the Transmission Operator as identified in R1 for 25% or more but less tan 50% of its generators. | The Generator Operator failed to notify the Transmission Operator as identified in R1 for 50% or more but less tan 75% of its generators. | The Generator Operator failed to notify the Transmission Operator as identified in R1 for 75% or more of its generators. |  | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 10000000
VAR-002-1a (Ontario) | 79780000199 | R2. | 79780002292 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power output (within applicable Facility Ratings [see footnote in standard]) as directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [17 empty] | The Generator Operator failed to maintain a voltage or reactive power schedule for less than 25% of its generators. | The Generator Operator failed to maintain a voltage or reactive power schedule for 25% or more but less tan 50% of its generators. | The Generator Operator failed to maintain a voltage or reactive power schedule for 50% or more but less tan 75% of its generators. | The Generator Operator failed to maintain a voltage or reactive power schedule for 75% or more of its generators. |  | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 20000000
VAR-002-1a (Ontario) | 79780000199 | R3. | 79780002295 | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  | GOP | [5 empty] | GOP | [17 empty] | The Generator Operator had one incident of failing to notify the Transmission Operator as identified in R3. | The Generator Operator had more than one but less than five incidents of failing to notify the Transmission as identified in R3.1 R3.2. | The Generator Operator had more than five but less than ten incidents of failing to notify the Transmission Operator as identified in R3.1 R3.2 | The Generator Operator had ten or more incidents of failing to notify the Transmission Operator as identified in R3.1 R3.2. |  | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 30000000
VAR-002-1a (Ontario) | 79780000199 | R4. | 79780002298 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [18 empty] | The Generator Owner had one (1) incident of failing to notify its associated Transmission Operator and Transmission Planner within 30 calendar days of a request for information, as described in R4.1.1 through R4.1.4, regarding generator step-up transform | The Generator Owner had more than one (1) incident but less than five (5) incidents of failing to notify its associated Transmission Operator and Transmission Planner within 30 calendar days of a request for information, as described in R4.1.1 through R4. | The Generator Owner had more than five (5) incidents but less than ten (10) incidents of failing to notify its associated Transmission Operator and Transmission Planner within 30 calendar days of a request for information, as described in R4.1.1 through R | The Generator Owner had more than ten (10) incidents of failing to notify its associated Transmission Operator and Transmission Planner within 30 calendar days of a request for information, as described in R4.1.1 through R4.1.4, regarding generator step-u |  | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 40000000
VAR-002-1a (Ontario) | 79780000199 | R5. | 79780002304 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [18 empty] | The Generator Owner had one (1) incident of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would not have violated safety, an equipment rating, a regulat | The Generator Owner had more than one (1) incident but less than or equal to five (5) incidents of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would n | The Generator Owner had more than five (5) incident but less than or equal to ten (10) incidents of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would | The Generator Owner had more than ten (10) incidents of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would not have violated safety, an equipment ratin |  | 2010-09-16 |  | 2013-06-30 |  |  |  | NPCC-ON | [6 empty] | 50000000
VAR-002-1 (Manitoba) | 77660000000196 | R1. | 776600000002246 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 10000000
VAR-002-1 (Manitoba) | 77660000000196 | R2. | 776600000002247 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power output (within applicable Facility Ratings. [1] as directed by the Transmission Operator |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 20000000
VAR-002-1 (Manitoba) | 77660000000196 | R3. | 776600000002250 | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 30000000
VAR-002-1 (Manitoba) | 77660000000196 | R4. | 776600000002253 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [17 empty] | Low | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 40000000
VAR-002-1 (Manitoba) | 77660000000196 | R5. | 776600000002259 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [17 empty] | Medium | [5 empty] | 2012-04-01 |  | 2014-02-13 |  |  |  | MRO-MB | [6 empty] | 50000000
VAR-002-1 (Ontario) | 79780000196 | R1. | 79780002246 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2007-08-02 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 10000000
VAR-002-1 (Ontario) | 79780000196 | R2. | 79780002247 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power output (within applicable Facility Ratings. [1] as directed by the Transmission Operator |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2007-08-02 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 20000000
VAR-002-1 (Ontario) | 79780000196 | R3. | 79780002250 | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2007-08-02 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 30000000
VAR-002-1 (Ontario) | 79780000196 | R4. | 79780002253 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [17 empty] | Low | [5 empty] | 2007-08-02 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 40000000
VAR-002-1 (Ontario) | 79780000196 | R5. | 79780002259 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [17 empty] | Medium | [5 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | NPCC-ON | [6 empty] | 50000000
VAR-002-2b | 336 | R1. | 4398 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator of one of the following: -That the generator is being operated in start-up or shutdown mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or -That the generator is not being operated in the automatic voltage control mode for a reason other than start-up or shutdown. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | N/A | N/A | N/A | The responsible entity did not operate each generator in the automatic voltage control mode and failed to notify the Transmission Operator as identified in R1. |  | 2013-07-01 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
VAR-002-2b | 336 | R2. | 4399 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule (within applicable Facility Ratings as directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | When directed by the Transmission Operator to maintain the generator voltage or reactive power schedule the Generator Operator failed to meet the directed values for up to and including 45 minutes. | When directed by the Transmission Operator to maintain the generator voltage or reactive power schedule the Generator Operator failed to meet the directed values for more than 45 minutes up to and including 60 minutes. OR When a generator’s automatic voltage regulator is out of service, the Generator Operator failed to use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. OR The Generator Operator failed to provide an explanation of why the voltage schedule could not be met. | When directed by the Transmission Operator to maintain the generator voltage or reactive power schedule the Generator Operator failed to meet the directed values for more than 60 minutes up to and including 75 minutes. | When directed by the Transmission Operator to maintain the generator voltage or reactive power schedule the Generator Operator failed to meet the directed values for more than 75 minutes. OR When a generator’s automatic voltage regulator is out of service, the Generator Operator failed to use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator and the Generator Operator failed to provide an explanation of why the voltage schedule could not be met. |  | 2013-07-01 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
VAR-002-2b | 336 | R3. | 4402 | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | N/A | N/A | The Generator Operator failed to notify the Transmission Operator within 30 minutes of the information as specified in either R3.1 or R3.2 | The Generator Operator failed to notify the Transmission Operator within 30 minutes of the information as specified in both R3.1 and R3.2 |  | 2013-07-01 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
VAR-002-2b | 336 | R4. | 4405 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [17 empty] | Low | The Responsible entity failed to provide to its associated Transmission Operator and Transmission Planner one of the types of data as specified in R4.1.1 or R 4.1.2 or 4.1.3 or 4.1.4 OR The information was provided in more than 30, but less than or equal to 35 calendar days of the request. | The Responsible entity failed to provide to its associated Transmission Operator and Transmission Planner two of the types of data as specified in R4.1.1 or R 4.1.2 or 4.1.3 or 4.1.4 OR The information was provided in more than 35, but less than or equal to 40 calendar days of the request. | The Responsible entity failed to provide to its associated Transmission Operator and Transmission Planner three of the types of data as specified in R4.1.1 or R 4.1.2 or 4.1.3 or 4.1.4 OR The information was provided in more than 40, but less than or equal to 45 calendar days of the request. | The Responsible entity failed to provide to its associated Transmission Operator and Transmission Planner any of the types of data as specified in R4.1.1 and R 4.1.2 and 4.1.3 and 4.1.4 OR The information was provided in more than 45 calendar days of the request. |  | 2013-07-01 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
VAR-002-2b | 336 | R5. | 4411 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [17 empty] | Medium | N/A | N/A | N/A | The responsible entity failed to ensure that transformer tap positions were changed according to the specifications provided by the Transmission Operator when said actions would not have violated safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | 2008-08-27 |  | 2009-05-12 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
VAR-002-2b (British Columbia) | 666700000010318 | R1. | 666700000011943 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator of one of the following: -That the generator is being operated in start-up or shutdown mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or -That the generator is not being operated in the automatic voltage control mode for a reason other than start-up or shutdown. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | N/A | N/A | N/A | The responsible entity did not operate each generator in the automatic voltage control mode and failed to notify the Transmission Operator as identified in R1. |  | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
VAR-002-2b (British Columbia) | 666700000010318 | R2. | 666700000011944 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule (within applicable Facility Ratings as directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | When directed by the Transmission Operator to maintain the generator voltage or reactive power schedule the Generator Operator failed to meet the directed values for up to and including 45 minutes. | When directed by the Transmission Operator to maintain the generator voltage or reactive power schedule the Generator Operator failed to meet the directed values for more than 45 minutes up to and including 60 minutes. OR When a generator’s automatic voltage regulator is out of service, the Generator Operator failed to use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. OR The Generator Operator failed to provide an explanation of why the voltage schedule could not be met. | When directed by the Transmission Operator to maintain the generator voltage or reactive power schedule the Generator Operator failed to meet the directed values for more than 60 minutes up to and including 75 minutes. | When directed by the Transmission Operator to maintain the generator voltage or reactive power schedule the Generator Operator failed to meet the directed values for more than 75 minutes. OR When a generator’s automatic voltage regulator is out of service, the Generator Operator failed to use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator and the Generator Operator failed to provide an explanation of why the voltage schedule could not be met. |  | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 20000000
VAR-002-2b (British Columbia) | 666700000010318 | R3. | 666700000011945 | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | N/A | N/A | The Generator Operator failed to notify the Transmission Operator within 30 minutes of the information as specified in either R3.1 or R3.2 | The Generator Operator failed to notify the Transmission Operator within 30 minutes of the information as specified in both R3.1 and R3.2 |  | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 30000000
VAR-002-2b (British Columbia) | 666700000010318 | R4. | 666700000011946 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [17 empty] | Low | The Responsible entity failed to provide to its associated Transmission Operator and Transmission Planner one of the types of data as specified in R4.1.1 or R 4.1.2 or 4.1.3 or 4.1.4 OR The information was provided in more than 30, but less than or equal to 35 calendar days of the request. | The Responsible entity failed to provide to its associated Transmission Operator and Transmission Planner two of the types of data as specified in R4.1.1 or R 4.1.2 or 4.1.3 or 4.1.4 OR The information was provided in more than 35, but less than or equal to 40 calendar days of the request. | The Responsible entity failed to provide to its associated Transmission Operator and Transmission Planner three of the types of data as specified in R4.1.1 or R 4.1.2 or 4.1.3 or 4.1.4 OR The information was provided in more than 40, but less than or equal to 45 calendar days of the request. | The Responsible entity failed to provide to its associated Transmission Operator and Transmission Planner any of the types of data as specified in R4.1.1 and R 4.1.2 and 4.1.3 and 4.1.4 OR The information was provided in more than 45 calendar days of the request. |  | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 40000000
VAR-002-2b (British Columbia) | 666700000010318 | R5. | 666700000011947 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [17 empty] | Medium | N/A | N/A | N/A | The responsible entity failed to ensure that transformer tap positions were changed according to the specifications provided by the Transmission Operator when said actions would not have violated safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | 2014-08-01 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 50000000
VAR-002-2b (Ontario) | 79780000336 | R1. | 79780004398 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator of one of the following:&lt;br/&gt;-That the generator is being operated in start-up or shutdown mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or&lt;br/&gt;-That the generator is not being operated in the automatic voltage control mode for a reason other than start-up or shutdown. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | N/A | N/A | N/A | The responsible entity did not operate each generator in the automatic voltage control mode and failed to notify the Transmission Operator as identified in R1. |  | 2013-07-01 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 10000000
VAR-002-2b (Ontario) | 79780000336 | R2. | 79780004399 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule (within applicable Facility Ratings as directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | When directed by the Transmission Operator to maintain the generator voltage or reactive power schedule the Generator Operator failed to meet the directed values for up to and including 45 minutes. | When directed by the Transmission Operator to maintain the generator voltage or reactive power schedule the Generator Operator failed to meet the directed values for more than 45 minutes up to and including 60 minutes. OR When a generator’s automatic voltage regulator is out of service, the Generator Operator failed to use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. OR The Generator Operator failed to provide an explanation of why the voltage schedule could not be met. | When directed by the Transmission Operator to maintain the generator voltage or reactive power schedule the Generator Operator failed to meet the directed values for more than 60 minutes up to and including 75 minutes. | When directed by the Transmission Operator to maintain the generator voltage or reactive power schedule the Generator Operator failed to meet the directed values for more than 75 minutes. OR When a generator’s automatic voltage regulator is out of service, the Generator Operator failed to use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator and the Generator Operator failed to provide an explanation of why the voltage schedule could not be met. |  | 2013-07-01 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 20000000
VAR-002-2b (Ontario) | 79780000336 | R3. | 79780004402 | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | N/A | N/A | The Generator Operator failed to notify the Transmission Operator within 30 minutes of the information as specified in either R3.1 or R3.2 | The Generator Operator failed to notify the Transmission Operator within 30 minutes of the information as specified in both R3.1 and R3.2 |  | 2013-07-01 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 30000000
VAR-002-2b (Ontario) | 79780000336 | R4. | 79780004405 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [17 empty] | Low | The Responsible entity failed to provide to its associated Transmission Operator and Transmission Planner one of the types of data as specified in R4.1.1 or R 4.1.2 or 4.1.3 or 4.1.4 OR The information was provided in more than 30, but less than or equal to 35 calendar days of the request. | The Responsible entity failed to provide to its associated Transmission Operator and Transmission Planner two of the types of data as specified in R4.1.1 or R 4.1.2 or 4.1.3 or 4.1.4 OR The information was provided in more than 35, but less than or equal to 40 calendar days of the request. | The Responsible entity failed to provide to its associated Transmission Operator and Transmission Planner three of the types of data as specified in R4.1.1 or R 4.1.2 or 4.1.3 or 4.1.4 OR The information was provided in more than 40, but less than or equal to 45 calendar days of the request. | The Responsible entity failed to provide to its associated Transmission Operator and Transmission Planner any of the types of data as specified in R4.1.1 and R 4.1.2 and 4.1.3 and 4.1.4 OR The information was provided in more than 45 calendar days of the request. |  | 2013-07-01 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 40000000
VAR-002-2b (Ontario) | 79780000336 | R5. | 79780004411 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [17 empty] | Medium | N/A | N/A | N/A | The responsible entity failed to ensure that transformer tap positions were changed according to the specifications provided by the Transmission Operator when said actions would not have violated safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | 2008-08-27 |  | 2009-05-12 |  |  |  | NPCC-ON | [6 empty] | 50000000
VAR-002-2b (Saskatchewan) | 83750000000336 | R1. | 837500000004398 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator of one of the following: -That the generator is being operated in start-up or shutdown mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or -That the generator is not being operated in the automatic voltage control mode for a reason other than start-up or shutdown. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | N/A | N/A | N/A | The responsible entity did not operate each generator in the automatic voltage control mode and failed to notify the Transmission Operator as identified in R1. |  | 2014-04-01 |  | 2015-07-15 |  |  |  | MRO-SK | [6 empty] | 10000000
VAR-002-2b (Saskatchewan) | 83750000000336 | R2. | 837500000004399 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule (within applicable Facility Ratings as directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | When directed by the Transmission Operator to maintain the generator voltage or reactive power schedule the Generator Operator failed to meet the directed values for up to and including 45 minutes. | When directed by the Transmission Operator to maintain the generator voltage or reactive power schedule the Generator Operator failed to meet the directed values for more than 45 minutes up to and including 60 minutes. OR When a generator’s automatic voltage regulator is out of service, the Generator Operator failed to use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. OR The Generator Operator failed to provide an explanation of why the voltage schedule could not be met. | When directed by the Transmission Operator to maintain the generator voltage or reactive power schedule the Generator Operator failed to meet the directed values for more than 60 minutes up to and including 75 minutes. | When directed by the Transmission Operator to maintain the generator voltage or reactive power schedule the Generator Operator failed to meet the directed values for more than 75 minutes. OR When a generator’s automatic voltage regulator is out of service, the Generator Operator failed to use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator and the Generator Operator failed to provide an explanation of why the voltage schedule could not be met. |  | 2014-04-01 |  | 2015-07-15 |  |  |  | MRO-SK | [6 empty] | 20000000
VAR-002-2b (Saskatchewan) | 83750000000336 | R3. | 837500000004402 | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: |  | GOP | [5 empty] | GOP | [16 empty] | Medium | N/A | N/A | The Generator Operator failed to notify the Transmission Operator within 30 minutes of the information as specified in either R3.1 or R3.2 | The Generator Operator failed to notify the Transmission Operator within 30 minutes of the information as specified in both R3.1 and R3.2 |  | 2014-04-01 |  | 2015-07-15 |  |  |  | MRO-SK | [6 empty] | 30000000
VAR-002-2b (Saskatchewan) | 83750000000336 | R4. | 837500000004405 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [17 empty] | Low | The Responsible entity failed to provide to its associated Transmission Operator and Transmission Planner one of the types of data as specified in R4.1.1 or R 4.1.2 or 4.1.3 or 4.1.4 OR The information was provided in more than 30, but less than or equal to 35 calendar days of the request. | The Responsible entity failed to provide to its associated Transmission Operator and Transmission Planner two of the types of data as specified in R4.1.1 or R 4.1.2 or 4.1.3 or 4.1.4 OR The information was provided in more than 35, but less than or equal to 40 calendar days of the request. | The Responsible entity failed to provide to its associated Transmission Operator and Transmission Planner three of the types of data as specified in R4.1.1 or R 4.1.2 or 4.1.3 or 4.1.4 OR The information was provided in more than 40, but less than or equal to 45 calendar days of the request. | The Responsible entity failed to provide to its associated Transmission Operator and Transmission Planner any of the types of data as specified in R4.1.1 and R 4.1.2 and 4.1.3 and 4.1.4 OR The information was provided in more than 45 calendar days of the request. |  | 2014-04-01 |  | 2015-07-15 |  |  |  | MRO-SK | [6 empty] | 40000000
VAR-002-2b (Saskatchewan) | 83750000000336 | R5. | 837500000004411 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [17 empty] | Medium | N/A | N/A | N/A | The responsible entity failed to ensure that transformer tap positions were changed according to the specifications provided by the Transmission Operator when said actions would not have violated safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | 2014-04-01 |  | 2015-07-15 |  |  |  | MRO-SK | [6 empty] | 50000000
VAR-002-3 | 445 | R1. | 5446 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: • That the generator is being operated in start-up, shutdown, or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | N/A | N/A | N/A | Unless exempted, the Generator Operator did not operate each generator connected to the interconnected transmission system in the automatic voltage control mode or in a different control mode as instructed by the Transmission Operator, and failed to provide the required notifications to Transmission Operator as identified in Requirement R1. | The Generator Operator shall have evidence to show that it notified its associated Transmission Operator any time it failed to operate a generator in the automatic voltage control mode or in a different control mode as specified in Requirement R1. If a generator is being started up or shut down with the automatic voltage control off, or is being tested, and no notification of the AVR status is made to the Transmission Operator, the Generator Operator will have evidence that it notified the Transmission Operator of its procedure for placing the unit into automatic voltage control mode as required in Requirement R1. Such evidence may include, but is not limited to, dated evidence of transmittal of the procedure such as an electronic message or a transmittal letter with the procedure included or attached. If a generator is exempted, the Generator Operator shall also have evidence that the generator is exempted from being in automatic voltage control mode (with its AVR in service and controlling voltage). | 2014-10-01 |  | 2015-05-28 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
VAR-002-3 | 445 | R2. | 5447 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule (within each generating Facility’s capabilities ) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | N/A | N/A | The Generator Operator did not have a conversion methodology when it monitors voltage at a location different from the schedule provided by the Transmission Operator. | The Generator Operator did not maintain the voltage or Reactive Power schedule as instructed by the Transmission Operator and did not make the necessary notifications required by the Transmission Operator. OR The Generator Operator did not have an operating AVR, and the responsible entity did not use an alternative method for controlling voltage. OR The Generator Operator did not modify voltage when directed, and the responsible entity did not provide any explanation. | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | 2014-10-01 |  | 2015-05-28 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
VAR-002-3 | 445 | R3. | 5448 | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change |  | GOP | [5 empty] | GOP | [16 empty] | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of the status change. |  | 2014-10-01 |  | 2015-05-28 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
VAR-002-3 | 445 | R4. | 5449 | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. |  | GOP | [5 empty] | GOP | [15 empty] | Long-Term Planning | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of becoming aware of the capability change. |  | 2014-10-01 |  | 2015-05-28 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
VAR-002-3 | 445 | R5. | 5450 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [17 empty] | Low | N/A | N/A | The Generator Owner failed to provide its associated Transmission Operator and Transmission Planner one of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | The Generator Owner failed to provide to its associated Transmission Operator and Transmission Planner two or more of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. |  | 2013-07-01 |  | 2014-09-30 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
VAR-002-3 | 445 | R6. | 5451 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [17 empty] | Low | N/A | N/A | N/A | The Generator Owner did not ensure the tap changes were made according the Transmission Operator’s specifications. OR The Generator Owner failed to perform the tap changes, and the Generator Owner did not provide technical justification for why it could not comply with the Transmission Operator specifications. |  | 2014-08-01 |  | 2015-05-28 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
VAR-002-3 (Ontario) | 79780000445 | R1. | 79780005446 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following:&lt;br/&gt;• That the generator is being operated in start-up, shutdown, or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or&lt;br/&gt;• That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | N/A | N/A | N/A | Unless exempted, the Generator Operator did not operate each generator connected to the interconnected transmission system in the automatic voltage control mode or in a different control mode as instructed by the Transmission Operator, and failed to provide the required notifications to Transmission Operator as identified in Requirement R1. |  | 2014-10-01 |  | 2015-05-28 |  |  |  | NPCC-ON | [6 empty] | 10000000
VAR-002-3 (Ontario) | 79780000445 | R2. | 79780005447 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule (within each generating Facility’s capabilities ) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | N/A | N/A | The Generator Operator did not have a conversion methodology when it monitors voltage at a location different from the schedule provided by the Transmission Operator. | The Generator Operator did not maintain the voltage or Reactive Power schedule as instructed by the Transmission Operator and did not make the necessary notifications required by the Transmission Operator. OR The Generator Operator did not have an operating AVR, and the responsible entity did not use an alternative method for controlling voltage. OR The Generator Operator did not modify voltage when directed, and the responsible entity did not provide any explanation. |  | 2014-10-01 |  | 2015-05-28 |  |  |  | NPCC-ON | [6 empty] | 20000000
VAR-002-3 (Ontario) | 79780000445 | R3. | 79780005448 | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change |  | GOP | [5 empty] | GOP | [16 empty] | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of the status change. |  | 2014-10-01 |  | 2015-05-28 |  |  |  | NPCC-ON | [6 empty] | 30000000
VAR-002-3 (Ontario) | 79780000445 | R4. | 79780005449 | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. |  | GOP | [5 empty] | GOP | [15 empty] | Long-Term Planning | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of becoming aware of the capability change. |  | 2014-10-01 |  | 2015-05-28 |  |  |  | NPCC-ON | [6 empty] | 40000000
VAR-002-3 (Ontario) | 79780000445 | R5. | 79780005450 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [17 empty] | Low | N/A | N/A | The Generator Owner failed to provide its associated Transmission Operator and Transmission Planner one of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | The Generator Owner failed to provide to its associated Transmission Operator and Transmission Planner two or more of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. |  | 2013-07-01 |  | 2014-09-30 |  |  |  | NPCC-ON | [6 empty] | 50000000
VAR-002-3 (Ontario) | 79780000445 | R6. | 79780005451 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [17 empty] | Low | N/A | N/A | N/A | The Generator Owner did not ensure the tap changes were made according the Transmission Operator’s specifications. OR The Generator Owner failed to perform the tap changes, and the Generator Owner did not provide technical justification for why it could not comply with the Transmission Operator specifications. |  | 2014-08-01 |  | 2015-05-28 |  |  |  | NPCC-ON | [6 empty] | 60000000
VAR-002-3 (Saskatchewan) | 83750000000445 | R1. | 837500000005446 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: • That the generator is being operated in start-up, shutdown, or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | N/A | N/A | N/A | Unless exempted, the Generator Operator did not operate each generator connected to the interconnected transmission system in the automatic voltage control mode or in a different control mode as instructed by the Transmission Operator, and failed to provide the required notifications to Transmission Operator as identified in Requirement R1. | The Generator Operator shall have evidence to show that it notified its associated Transmission Operator any time it failed to operate a generator in the automatic voltage control mode or in a different control mode as specified in Requirement R1. If a generator is being started up or shut down with the automatic voltage control off, or is being tested, and no notification of the AVR status is made to the Transmission Operator, the Generator Operator will have evidence that it notified the Transmission Operator of its procedure for placing the unit into automatic voltage control mode as required in Requirement R1. Such evidence may include, but is not limited to, dated evidence of transmittal of the procedure such as an electronic message or a transmittal letter with the procedure included or attached. If a generator is exempted, the Generator Operator shall also have evidence that the generator is exempted from being in automatic voltage control mode (with its AVR in service and controlling voltage). | 2015-07-01 |  | 2015-07-15 |  |  |  | MRO-SK | [6 empty] | 10000000
VAR-002-3 (Saskatchewan) | 83750000000445 | R2. | 837500000005447 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule (within each generating Facility’s capabilities ) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | Medium | N/A | N/A | The Generator Operator did not have a conversion methodology when it monitors voltage at a location different from the schedule provided by the Transmission Operator. | The Generator Operator did not maintain the voltage or Reactive Power schedule as instructed by the Transmission Operator and did not make the necessary notifications required by the Transmission Operator. OR The Generator Operator did not have an operating AVR, and the responsible entity did not use an alternative method for controlling voltage. OR The Generator Operator did not modify voltage when directed, and the responsible entity did not provide any explanation. | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | 2015-07-01 |  | 2015-07-15 |  |  |  | MRO-SK | [6 empty] | 20000000
VAR-002-3 (Saskatchewan) | 83750000000445 | R3. | 837500000005448 | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change |  | GOP | [5 empty] | GOP | [16 empty] | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of the status change. |  | 2015-07-01 |  | 2015-07-15 |  |  |  | MRO-SK | [6 empty] | 30000000
VAR-002-3 (Saskatchewan) | 83750000000445 | R4. | 837500000005449 | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. |  | GOP | [5 empty] | GOP | [15 empty] | Long-Term Planning | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of becoming aware of the capability change. |  | 2015-07-01 |  | 2015-07-15 |  |  |  | MRO-SK | [6 empty] | 40000000
VAR-002-3 (Saskatchewan) | 83750000000445 | R5. | 837500000005450 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [17 empty] | Low | N/A | N/A | The Generator Owner failed to provide its associated Transmission Operator and Transmission Planner one of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | The Generator Owner failed to provide to its associated Transmission Operator and Transmission Planner two or more of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. |  | 2015-07-01 |  | 2015-07-15 |  |  |  | MRO-SK | [6 empty] | 50000000
VAR-002-3 (Saskatchewan) | 83750000000445 | R6. | 837500000005451 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [17 empty] | Low | N/A | N/A | N/A | The Generator Owner did not ensure the tap changes were made according the Transmission Operator’s specifications. OR The Generator Owner failed to perform the tap changes, and the Generator Owner did not provide technical justification for why it could not comply with the Transmission Operator specifications. |  | 2015-07-01 |  | 2015-07-15 |  |  |  | MRO-SK | [6 empty] | 60000000
VAR-002-4 | 510 | R1. | 6077 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: • That the generator is being operated in start-up,1 shutdown,2 or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | Unless exempted, the Generator Operator did not operate each generator connected to the interconnected transmission system in the automatic voltage control mode or in a different control mode as instructed by the Transmission Operator, and failed to provide the required notifications to Transmission Operator as identified in Requirement R1. | The Generator Operator shall have evidence to show that it notified its associated Transmission Operator any time it failed to operate a generator in the automatic voltage control mode or in a different control mode as specified in Requirement R1. If a generator is being started up or shut down with the automatic voltage control off, or is being tested, and no notification of the AVR status is made to the Transmission Operator, the Generator Operator will have evidence that it notified the Transmission Operator of its procedure for placing the unit into automatic voltage control mode as required in Requirement R1. Such evidence may include, but is not limited to, dated evidence of transmittal of the procedure such as an electronic message or a transmittal letter with the procedure included or attached. If a generator is exempted, the Generator Operator shall also have evidence that the generator is exempted from being in automatic voltage control mode (with its AVR in service and controlling voltage). | 2015-05-29 |  | 2017-09-25 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
VAR-002-4 | 510 | R2. | 6078 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule3 (within each generating Facility’s capabilities4) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator.[See standard for additional information.] |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | The Generator Operator did not have a conversion methodology when it monitors voltage at a location different from the schedule provided by the Transmission Operator. | The Generator Operator did not maintain the voltage or Reactive Power schedule as instructed by the Transmission Operator and did not make the necessary notifications required by the Transmission Operator. OR The Generator Operator did not have an operating AVR, and the responsible entity did not use an alternative method for controlling voltage. OR The Generator Operator did not modify voltage when directed, and the responsible entity did not provide any explanation. | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | 2015-05-29 |  | 2017-09-25 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
VAR-002-4 | 510 | R3. | 6079 | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of the status change. | The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of any status change identified in Requirement R3. If the status has been restored within the first 30 minutes, no notification is necessary. | 2015-05-29 |  | 2017-09-25 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
VAR-002-4 | 510 | R4. | 6080 | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. [Violation Risk Factor: • Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of becoming aware of the capability change. | The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability in accordance with Requirement R4. If the capability has been restored within the first 30 minutes, no notification is necessary. | 2015-05-29 |  | 2017-09-25 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
VAR-002-4 | 510 | R5. | 6081 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. [See standard for additional information.] |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Low | N/A | N/A | The Generator Owner failed to provide its associated Transmission Operator and Transmission Planner one of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | The Generator Owner failed to provide to its associated Transmission Operator and Transmission Planner two or more of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | 2015-05-29 |  | 2017-09-25 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
VAR-002-4 | 510 | R6. | 6082 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. [See standard for additional information.] |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Low | N/A | N/A | N/A | The Generator Owner did not ensure the tap changes were made according the Transmission Operator’s specifications. OR The Generator Owner failed to perform the tap changes, and the Generator Owner did not provide technical justification for why it could not comply with the Transmission Operator specifications. | The Generator Owner shall have evidence that its step-up transformer taps were modified per the Transmission Operator’s documentation in accordance with Requirement R6. The Generator Owner shall have evidence that it notified its associated Transmission Operator when it could not comply with the Transmission Operator’s step-up transformer tap specifications in accordance with Requirement R6, Part 6.1. | 2014-10-01 |  | 2015-05-28 |  |  |  | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
VAR-002-4.1 | 568 | R1. | 8070 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: • That the generator is being operated in start-up, shutdown, or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. Footnote: Start-up is deemed to have ended when the generator is ramped up to its minimum continuously sustainable load and the generator is prepared for continuous operation. Shutdown is deemed to begin when the generator is ramped down to its minimum continuously sustainable load and the generator is prepared to go offline. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | Unless exempted, the Generator Operator did not operate each generator connected to the interconnected transmission system in the automatic voltage control mode or in a different control mode as instructed by the Transmission Operator, and failed to provide the required notifications to Transmission Operator as identified in Requirement R1. | M1. The Generator Operator shall have evidence to show that it notified its associated Transmission Operator any time it failed to operate a generator in the automatic voltage control mode or in a different control mode as specified in Requirement R1. If a generator is being started up or shut down with the automatic voltage control off, or is being tested, and no notification of the AVR status is made to the Transmission Operator, the Generator Operator will have evidence that it notified the Transmission Operator of its procedure for placing the unit into automatic voltage control mode as required in Requirement R1. Such evidence may include, but is not limited to, dated evidence of transmittal of the procedure such as an electronic message or a transmittal letter with the procedure included or attached. If a generator is exempted, the Generator Operator shall also have evidence that the generator is exempted from being in automatic voltage control mode (with its AVR in service and controlling voltage). | 2017-09-26 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
VAR-002-4.1 | 568 | R2. | 8071 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule (within each generating Facility’s capabilities ) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. (Footnote: The voltage or Reactive Power schedule is a target value with a tolerance band or a voltage or Reactive Power range communicated by the Transmission Operator to the Generator Operator. Generating Facility capability may be established by test or other means, and may not be sufficient at times to pull the system voltage within the schedule tolerance band. Also, when a generator is operating in manual control, Reactive Power capability may change based on stability considerations.) |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | The Generator Operator did not have a conversion methodology when it monitors voltage at a location different from the schedule provided by the Transmission Operator. | The Generator Operator did not maintain the voltage or Reactive Power schedule as instructed by the Transmission Operator and did not make the necessary notifications required by the Transmission Operator. OR The Generator Operator did not have an operating AVR, and the responsible entity did not use an alternative method for controlling voltage. OR The Generator Operator did not modify voltage when directed, and the responsible entity did not provide any explanation. | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | 2017-09-26 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
VAR-002-4.1 | 568 | R3. | 8075 | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of the status change. | M3. The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of any status change identified in Requirement R3. If the status has been restored within the first 30 minutes, no notification is necessary. | 2017-09-26 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
VAR-002-4.1 | 568 | R4. | 8076 | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. • Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of becoming aware of the capability change. | M4. The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability in accordance with Requirement R4. If the capability has been restored within the first 30 minutes, no notification is necessary. | 2017-09-26 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
VAR-002-4.1 | 568 | R5. | 8077 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Low | N/A | N/A | The Generator Owner failed to provide its associated Transmission Operator and Transmission Planner one of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | The Generator Owner failed to provide to its associated Transmission Operator and Transmission Planner two or more of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | M5. The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | 2017-09-26 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
VAR-002-4.1 | 568 | R6. | 8083 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Low | N/A | N/A | N/A | The Generator Owner did not ensure the tap changes were made according the Transmission Operator’s specifications. OR The Generator Owner failed to perform the tap changes, and the Generator Owner did not provide technical justification for why it could not comply with the Transmission Operator specifications. | M6. The Generator Owner shall have evidence that its step-up transformer taps were modified per the Transmission Operator’s documentation in accordance with Requirement R6. The Generator Owner shall have evidence that it notified its associated Transmission Operator when it could not comply with the Transmission Operator’s step-up transformer tap specifications in accordance with Requirement R6, Part 6.1. | 2017-09-26 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 60000000
VAR-002-4.1 (British Columbia) | 666700000010320 | R1. | 666700000011954 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: • That the generator is being operated in start-up, shutdown, or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. Footnote: Start-up is deemed to have ended when the generator is ramped up to its minimum continuously sustainable load and the generator is prepared for continuous operation. Shutdown is deemed to begin when the generator is ramped down to its minimum continuously sustainable load and the generator is prepared to go offline. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | Unless exempted, the Generator Operator did not operate each generator connected to the interconnected transmission system in the automatic voltage control mode or in a different control mode as instructed by the Transmission Operator, and failed to provide the required notifications to Transmission Operator as identified in Requirement R1. | M1. The Generator Operator shall have evidence to show that it notified its associated Transmission Operator any time it failed to operate a generator in the automatic voltage control mode or in a different control mode as specified in Requirement R1. If a generator is being started up or shut down with the automatic voltage control off, or is being tested, and no notification of the AVR status is made to the Transmission Operator, the Generator Operator will have evidence that it notified the Transmission Operator of its procedure for placing the unit into automatic voltage control mode as required in Requirement R1. Such evidence may include, but is not limited to, dated evidence of transmittal of the procedure such as an electronic message or a transmittal letter with the procedure included or attached. If a generator is exempted, the Generator Operator shall also have evidence that the generator is exempted from being in automatic voltage control mode (with its AVR in service and controlling voltage). | 2018-10-01 | [5 empty] | WECC-BC | [6 empty] | 10000000
VAR-002-4.1 (British Columbia) | 666700000010320 | R2. | 666700000011955 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule (within each generating Facility’s capabilities ) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. (Footnote: The voltage or Reactive Power schedule is a target value with a tolerance band or a voltage or Reactive Power range communicated by the Transmission Operator to the Generator Operator. Generating Facility capability may be established by test or other means, and may not be sufficient at times to pull the system voltage within the schedule tolerance band. Also, when a generator is operating in manual control, Reactive Power capability may change based on stability considerations.) |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | The Generator Operator did not have a conversion methodology when it monitors voltage at a location different from the schedule provided by the Transmission Operator. | The Generator Operator did not maintain the voltage or Reactive Power schedule as instructed by the Transmission Operator and did not make the necessary notifications required by the Transmission Operator. OR The Generator Operator did not have an operating AVR, and the responsible entity did not use an alternative method for controlling voltage. OR The Generator Operator did not modify voltage when directed, and the responsible entity did not provide any explanation. | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | 2018-10-01 | [5 empty] | WECC-BC | [6 empty] | 20000000
VAR-002-4.1 (British Columbia) | 666700000010320 | R3. | 666700000011956 | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of the status change. | M3. The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of any status change identified in Requirement R3. If the status has been restored within the first 30 minutes, no notification is necessary. | 2018-10-01 | [5 empty] | WECC-BC | [6 empty] | 30000000
VAR-002-4.1 (British Columbia) | 666700000010320 | R4. | 666700000011957 | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. • Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of becoming aware of the capability change. | M4. The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability in accordance with Requirement R4. If the capability has been restored within the first 30 minutes, no notification is necessary. | 2018-10-01 | [5 empty] | WECC-BC | [6 empty] | 40000000
VAR-002-4.1 (British Columbia) | 666700000010320 | R5. | 666700000011958 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Low | N/A | N/A | The Generator Owner failed to provide its associated Transmission Operator and Transmission Planner one of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | The Generator Owner failed to provide to its associated Transmission Operator and Transmission Planner two or more of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | M5. The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | 2018-10-01 | [5 empty] | WECC-BC | [6 empty] | 50000000
VAR-002-4.1 (British Columbia) | 666700000010320 | R6. | 666700000011959 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Low | N/A | N/A | N/A | The Generator Owner did not ensure the tap changes were made according the Transmission Operator’s specifications. OR The Generator Owner failed to perform the tap changes, and the Generator Owner did not provide technical justification for why it could not comply with the Transmission Operator specifications. | M6. The Generator Owner shall have evidence that its step-up transformer taps were modified per the Transmission Operator’s documentation in accordance with Requirement R6. The Generator Owner shall have evidence that it notified its associated Transmission Operator when it could not comply with the Transmission Operator’s step-up transformer tap specifications in accordance with Requirement R6, Part 6.1. | 2018-10-01 | [5 empty] | WECC-BC | [6 empty] | 60000000
VAR-002-4.1 (Manitoba) | 77660000000568 | R1. | 776600000008070 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: • That the generator is being operated in start-up, shutdown, or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. Footnote: Start-up is deemed to have ended when the generator is ramped up to its minimum continuously sustainable load and the generator is prepared for continuous operation. Shutdown is deemed to begin when the generator is ramped down to its minimum continuously sustainable load and the generator is prepared to go offline. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | Unless exempted, the Generator Operator did not operate each generator connected to the interconnected transmission system in the automatic voltage control mode or in a different control mode as instructed by the Transmission Operator, and failed to provide the required notifications to Transmission Operator as identified in Requirement R1. | M1. The Generator Operator shall have evidence to show that it notified its associated Transmission Operator any time it failed to operate a generator in the automatic voltage control mode or in a different control mode as specified in Requirement R1. If a generator is being started up or shut down with the automatic voltage control off, or is being tested, and no notification of the AVR status is made to the Transmission Operator, the Generator Operator will have evidence that it notified the Transmission Operator of its procedure for placing the unit into automatic voltage control mode as required in Requirement R1. Such evidence may include, but is not limited to, dated evidence of transmittal of the procedure such as an electronic message or a transmittal letter with the procedure included or attached. If a generator is exempted, the Generator Operator shall also have evidence that the generator is exempted from being in automatic voltage control mode (with its AVR in service and controlling voltage). | 2019-07-01 | [5 empty] | MRO-MB | [6 empty] | 10000000
VAR-002-4.1 (Manitoba) | 77660000000568 | R2. | 776600000008071 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule (within each generating Facility’s capabilities ) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. (Footnote: The voltage or Reactive Power schedule is a target value with a tolerance band or a voltage or Reactive Power range communicated by the Transmission Operator to the Generator Operator. Generating Facility capability may be established by test or other means, and may not be sufficient at times to pull the system voltage within the schedule tolerance band. Also, when a generator is operating in manual control, Reactive Power capability may change based on stability considerations.) |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | The Generator Operator did not have a conversion methodology when it monitors voltage at a location different from the schedule provided by the Transmission Operator. | The Generator Operator did not maintain the voltage or Reactive Power schedule as instructed by the Transmission Operator and did not make the necessary notifications required by the Transmission Operator. OR The Generator Operator did not have an operating AVR, and the responsible entity did not use an alternative method for controlling voltage. OR The Generator Operator did not modify voltage when directed, and the responsible entity did not provide any explanation. | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | 2019-07-01 | [5 empty] | MRO-MB | [6 empty] | 20000000
VAR-002-4.1 (Manitoba) | 77660000000568 | R3. | 776600000008075 | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of the status change. | M3. The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of any status change identified in Requirement R3. If the status has been restored within the first 30 minutes, no notification is necessary. | 2019-07-01 | [5 empty] | MRO-MB | [6 empty] | 30000000
VAR-002-4.1 (Manitoba) | 77660000000568 | R4. | 776600000008076 | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. • Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of becoming aware of the capability change. | M4. The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability in accordance with Requirement R4. If the capability has been restored within the first 30 minutes, no notification is necessary. | 2019-07-01 | [5 empty] | MRO-MB | [6 empty] | 40000000
VAR-002-4.1 (Manitoba) | 77660000000568 | R5. | 776600000008077 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Low | N/A | N/A | The Generator Owner failed to provide its associated Transmission Operator and Transmission Planner one of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | The Generator Owner failed to provide to its associated Transmission Operator and Transmission Planner two or more of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | M5. The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | 2019-07-01 | [5 empty] | MRO-MB | [6 empty] | 50000000
VAR-002-4.1 (Manitoba) | 77660000000568 | R6. | 776600000008083 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Low | N/A | N/A | N/A | The Generator Owner did not ensure the tap changes were made according the Transmission Operator’s specifications. OR The Generator Owner failed to perform the tap changes, and the Generator Owner did not provide technical justification for why it could not comply with the Transmission Operator specifications. | M6. The Generator Owner shall have evidence that its step-up transformer taps were modified per the Transmission Operator’s documentation in accordance with Requirement R6. The Generator Owner shall have evidence that it notified its associated Transmission Operator when it could not comply with the Transmission Operator’s step-up transformer tap specifications in accordance with Requirement R6, Part 6.1. | 2019-07-01 | [5 empty] | MRO-MB | [6 empty] | 60000000
VAR-002-4.1 (Nova Scotia) | 78830000000568 | R1. | 788300000008070 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: • That the generator is being operated in start-up, shutdown, or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. Footnote: Start-up is deemed to have ended when the generator is ramped up to its minimum continuously sustainable load and the generator is prepared for continuous operation. Shutdown is deemed to begin when the generator is ramped down to its minimum continuously sustainable load and the generator is prepared to go offline. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | Unless exempted, the Generator Operator did not operate each generator connected to the interconnected transmission system in the automatic voltage control mode or in a different control mode as instructed by the Transmission Operator, and failed to provide the required notifications to Transmission Operator as identified in Requirement R1. | M1. The Generator Operator shall have evidence to show that it notified its associated Transmission Operator any time it failed to operate a generator in the automatic voltage control mode or in a different control mode as specified in Requirement R1. If a generator is being started up or shut down with the automatic voltage control off, or is being tested, and no notification of the AVR status is made to the Transmission Operator, the Generator Operator will have evidence that it notified the Transmission Operator of its procedure for placing the unit into automatic voltage control mode as required in Requirement R1. Such evidence may include, but is not limited to, dated evidence of transmittal of the procedure such as an electronic message or a transmittal letter with the procedure included or attached. If a generator is exempted, the Generator Operator shall also have evidence that the generator is exempted from being in automatic voltage control mode (with its AVR in service and controlling voltage). | 2018-04-01 | [5 empty] | NPCC-NS | [6 empty] | 10000000
VAR-002-4.1 (Nova Scotia) | 78830000000568 | R2. | 788300000008071 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule (within each generating Facility’s capabilities ) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. (Footnote: The voltage or Reactive Power schedule is a target value with a tolerance band or a voltage or Reactive Power range communicated by the Transmission Operator to the Generator Operator. Generating Facility capability may be established by test or other means, and may not be sufficient at times to pull the system voltage within the schedule tolerance band. Also, when a generator is operating in manual control, Reactive Power capability may change based on stability considerations.) |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | The Generator Operator did not have a conversion methodology when it monitors voltage at a location different from the schedule provided by the Transmission Operator. | The Generator Operator did not maintain the voltage or Reactive Power schedule as instructed by the Transmission Operator and did not make the necessary notifications required by the Transmission Operator. OR The Generator Operator did not have an operating AVR, and the responsible entity did not use an alternative method for controlling voltage. OR The Generator Operator did not modify voltage when directed, and the responsible entity did not provide any explanation. | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | 2018-04-01 | [5 empty] | NPCC-NS | [6 empty] | 20000000
VAR-002-4.1 (Nova Scotia) | 78830000000568 | R3. | 788300000008075 | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of the status change. | M3. The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of any status change identified in Requirement R3. If the status has been restored within the first 30 minutes, no notification is necessary. | 2018-04-01 | [5 empty] | NPCC-NS | [6 empty] | 30000000
VAR-002-4.1 (Nova Scotia) | 78830000000568 | R4. | 788300000008076 | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. • Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of becoming aware of the capability change. | M4. The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability in accordance with Requirement R4. If the capability has been restored within the first 30 minutes, no notification is necessary. | 2018-04-01 | [5 empty] | NPCC-NS | [6 empty] | 40000000
VAR-002-4.1 (Nova Scotia) | 78830000000568 | R5. | 788300000008077 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Low | N/A | N/A | The Generator Owner failed to provide its associated Transmission Operator and Transmission Planner one of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | The Generator Owner failed to provide to its associated Transmission Operator and Transmission Planner two or more of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | M5. The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | 2018-04-01 | [5 empty] | NPCC-NS | [6 empty] | 50000000
VAR-002-4.1 (Nova Scotia) | 78830000000568 | R6. | 788300000008083 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Low | N/A | N/A | N/A | The Generator Owner did not ensure the tap changes were made according the Transmission Operator’s specifications. OR The Generator Owner failed to perform the tap changes, and the Generator Owner did not provide technical justification for why it could not comply with the Transmission Operator specifications. | M6. The Generator Owner shall have evidence that its step-up transformer taps were modified per the Transmission Operator’s documentation in accordance with Requirement R6. The Generator Owner shall have evidence that it notified its associated Transmission Operator when it could not comply with the Transmission Operator’s step-up transformer tap specifications in accordance with Requirement R6, Part 6.1. | 2018-04-01 | [5 empty] | NPCC-NS | [6 empty] | 60000000
VAR-002-4.1 (Ontario) | 79780000568 | R1. | 79780008070 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following:&lt;br/&gt;• That the generator is being operated in start-up, shutdown, or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or&lt;br/&gt;• That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing.&lt;br/&gt;Footnote: Start-up is deemed to have ended when the generator is ramped up to its minimum continuously sustainable load and the generator is prepared for continuous operation.&lt;br/&gt; Shutdown is deemed to begin when the generator is ramped down to its minimum continuously sustainable load and the generator is prepared to go offline. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | Unless exempted, the Generator Operator did not operate each generator connected to the interconnected transmission system in the automatic voltage control mode or in a different control mode as instructed by the Transmission Operator, and failed to provide the required notifications to Transmission Operator as identified in Requirement R1. | M1. The Generator Operator shall have evidence to show that it notified its associated Transmission Operator any time it failed to operate a generator in the automatic voltage control mode or in a different control mode as specified in Requirement R1. If a generator is being started up or shut down with the automatic voltage control off, or is being tested, and no notification of the AVR status is made to the Transmission Operator, the Generator Operator will have evidence that it notified the Transmission Operator of its procedure for placing the unit into automatic voltage control mode as required in Requirement R1. Such evidence may include, but is not limited to, dated evidence of transmittal of the procedure such as an electronic message or a transmittal letter with the procedure included or attached. If a generator is exempted, the Generator Operator shall also have evidence that the generator is exempted from being in automatic voltage control mode (with its AVR in service and controlling voltage). | 2017-09-26 | [5 empty] | NPCC-ON | [6 empty] | 10000000
VAR-002-4.1 (Ontario) | 79780000568 | R2. | 79780008071 | &lt;p&gt;Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule (within each generating Facility’s capabilities ) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator.&lt;/p&gt; &lt;p&gt;(Footnote: The voltage or Reactive Power schedule is a target value with a tolerance band or a voltage or Reactive Power range communicated by the Transmission Operator to the Generator Operator.&lt;br/&gt;Generating Facility capability may be established by test or other means, and may not be sufficient at times to pull the system voltage within the schedule tolerance band. Also, when a generator is operating in manual control, Reactive Power capability may change based on stability considerations.)&lt;/p&gt; |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | The Generator Operator did not have a conversion methodology when it monitors voltage at a location different from the schedule provided by the Transmission Operator. | The Generator Operator did not maintain the voltage or Reactive Power schedule as instructed by the Transmission Operator and did not make the necessary notifications required by the Transmission Operator. OR The Generator Operator did not have an operating AVR, and the responsible entity did not use an alternative method for controlling voltage. OR The Generator Operator did not modify voltage when directed, and the responsible entity did not provide any explanation. | &lt;p&gt;In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator.&lt;/p&gt; &lt;p&gt;Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule.&lt;/p&gt; &lt;p&gt;For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator.&lt;/p&gt; &lt;p&gt;For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs.&lt;/p&gt; &lt;p&gt;For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator.&lt;/p&gt; &lt;p/&gt; | 2017-09-26 | [5 empty] | NPCC-ON | [6 empty] | 20000000
VAR-002-4.1 (Ontario) | 79780000568 | R3. | 79780008075 | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of the status change. | M3. The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of any status change identified in Requirement R3. If the status has been restored within the first 30 minutes, no notification is necessary. | 2017-09-26 | [5 empty] | NPCC-ON | [6 empty] | 30000000
VAR-002-4.1 (Ontario) | 79780000568 | R4. | 79780008076 | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability.&lt;br/&gt; • Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of becoming aware of the capability change. | M4. The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability in accordance with Requirement R4. If the capability has been restored within the first 30 minutes, no notification is necessary. | 2017-09-26 | [5 empty] | NPCC-ON | [6 empty] | 40000000
VAR-002-4.1 (Ontario) | 79780000568 | R5. | 79780008077 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Low | N/A | N/A | The Generator Owner failed to provide its associated Transmission Operator and Transmission Planner one of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | The Generator Owner failed to provide to its associated Transmission Operator and Transmission Planner two or more of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | M5. The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | 2017-09-26 | [5 empty] | NPCC-ON | [6 empty] | 50000000
VAR-002-4.1 (Ontario) | 79780000568 | R6. | 79780008083 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Low | N/A | N/A | N/A | The Generator Owner did not ensure the tap changes were made according the Transmission Operator’s specifications. OR The Generator Owner failed to perform the tap changes, and the Generator Owner did not provide technical justification for why it could not comply with the Transmission Operator specifications. | M6. The Generator Owner shall have evidence that its step-up transformer taps were modified per the Transmission Operator’s documentation in accordance with Requirement R6. The Generator Owner shall have evidence that it notified its associated Transmission Operator when it could not comply with the Transmission Operator’s step-up transformer tap specifications in accordance with Requirement R6, Part 6.1. | 2017-09-26 | [5 empty] | NPCC-ON | [6 empty] | 60000000
VAR-002-4.1 (Saskatchewan) | 83750000000568 | R1. | 837500000008070 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: • That the generator is being operated in start-up, shutdown, or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. Footnote: Start-up is deemed to have ended when the generator is ramped up to its minimum continuously sustainable load and the generator is prepared for continuous operation. Shutdown is deemed to begin when the generator is ramped down to its minimum continuously sustainable load and the generator is prepared to go offline. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | Unless exempted, the Generator Operator did not operate each generator connected to the interconnected transmission system in the automatic voltage control mode or in a different control mode as instructed by the Transmission Operator, and failed to provide the required notifications to Transmission Operator as identified in Requirement R1. | M1. The Generator Operator shall have evidence to show that it notified its associated Transmission Operator any time it failed to operate a generator in the automatic voltage control mode or in a different control mode as specified in Requirement R1. If a generator is being started up or shut down with the automatic voltage control off, or is being tested, and no notification of the AVR status is made to the Transmission Operator, the Generator Operator will have evidence that it notified the Transmission Operator of its procedure for placing the unit into automatic voltage control mode as required in Requirement R1. Such evidence may include, but is not limited to, dated evidence of transmittal of the procedure such as an electronic message or a transmittal letter with the procedure included or attached. If a generator is exempted, the Generator Operator shall also have evidence that the generator is exempted from being in automatic voltage control mode (with its AVR in service and controlling voltage). | 2018-01-25 | [5 empty] | MRO-SK | [6 empty] | 10000000
VAR-002-4.1 (Saskatchewan) | 83750000000568 | R2. | 837500000008071 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule (within each generating Facility’s capabilities ) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. (Footnote: The voltage or Reactive Power schedule is a target value with a tolerance band or a voltage or Reactive Power range communicated by the Transmission Operator to the Generator Operator. Generating Facility capability may be established by test or other means, and may not be sufficient at times to pull the system voltage within the schedule tolerance band. Also, when a generator is operating in manual control, Reactive Power capability may change based on stability considerations.) |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | The Generator Operator did not have a conversion methodology when it monitors voltage at a location different from the schedule provided by the Transmission Operator. | The Generator Operator did not maintain the voltage or Reactive Power schedule as instructed by the Transmission Operator and did not make the necessary notifications required by the Transmission Operator. OR The Generator Operator did not have an operating AVR, and the responsible entity did not use an alternative method for controlling voltage. OR The Generator Operator did not modify voltage when directed, and the responsible entity did not provide any explanation. | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | 2018-01-25 | [5 empty] | MRO-SK | [6 empty] | 20000000
VAR-002-4.1 (Saskatchewan) | 83750000000568 | R3. | 837500000008075 | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of the status change. | M3. The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of any status change identified in Requirement R3. If the status has been restored within the first 30 minutes, no notification is necessary. | 2018-01-25 | [5 empty] | MRO-SK | [6 empty] | 30000000
VAR-002-4.1 (Saskatchewan) | 83750000000568 | R4. | 837500000008076 | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. • Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of becoming aware of the capability change. | M4. The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability in accordance with Requirement R4. If the capability has been restored within the first 30 minutes, no notification is necessary. | 2018-01-25 | [5 empty] | MRO-SK | [6 empty] | 40000000
VAR-002-4.1 (Saskatchewan) | 83750000000568 | R5. | 837500000008077 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Low | N/A | N/A | The Generator Owner failed to provide its associated Transmission Operator and Transmission Planner one of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | The Generator Owner failed to provide to its associated Transmission Operator and Transmission Planner two or more of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | M5. The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | 2018-01-25 | [5 empty] | MRO-SK | [6 empty] | 50000000
VAR-002-4.1 (Saskatchewan) | 83750000000568 | R6. | 837500000008083 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Low | N/A | N/A | N/A | The Generator Owner did not ensure the tap changes were made according the Transmission Operator’s specifications. OR The Generator Owner failed to perform the tap changes, and the Generator Owner did not provide technical justification for why it could not comply with the Transmission Operator specifications. | M6. The Generator Owner shall have evidence that its step-up transformer taps were modified per the Transmission Operator’s documentation in accordance with Requirement R6. The Generator Owner shall have evidence that it notified its associated Transmission Operator when it could not comply with the Transmission Operator’s step-up transformer tap specifications in accordance with Requirement R6, Part 6.1. | 2018-01-25 | [5 empty] | MRO-SK | [6 empty] | 60000000
VAR-002-4 (British Columbia) | 666700000010319 | R1. | 666700000011948 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: • That the generator is being operated in start-up,1 shutdown,2 or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | Unless exempted, the Generator Operator did not operate each generator connected to the interconnected transmission system in the automatic voltage control mode or in a different control mode as instructed by the Transmission Operator, and failed to provide the required notifications to Transmission Operator as identified in Requirement R1. | The Generator Operator shall have evidence to show that it notified its associated Transmission Operator any time it failed to operate a generator in the automatic voltage control mode or in a different control mode as specified in Requirement R1. If a generator is being started up or shut down with the automatic voltage control off, or is being tested, and no notification of the AVR status is made to the Transmission Operator, the Generator Operator will have evidence that it notified the Transmission Operator of its procedure for placing the unit into automatic voltage control mode as required in Requirement R1. Such evidence may include, but is not limited to, dated evidence of transmittal of the procedure such as an electronic message or a transmittal letter with the procedure included or attached. If a generator is exempted, the Generator Operator shall also have evidence that the generator is exempted from being in automatic voltage control mode (with its AVR in service and controlling voltage). | 2016-10-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
VAR-002-4 (British Columbia) | 666700000010319 | R2. | 666700000011949 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule3 (within each generating Facility’s capabilities4) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator.[See standard for additional information.] |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | The Generator Operator did not have a conversion methodology when it monitors voltage at a location different from the schedule provided by the Transmission Operator. | The Generator Operator did not maintain the voltage or Reactive Power schedule as instructed by the Transmission Operator and did not make the necessary notifications required by the Transmission Operator. OR The Generator Operator did not have an operating AVR, and the responsible entity did not use an alternative method for controlling voltage. OR The Generator Operator did not modify voltage when directed, and the responsible entity did not provide any explanation. | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | 2016-10-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 20000000
VAR-002-4 (British Columbia) | 666700000010319 | R3. | 666700000011950 | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of the status change. | The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of any status change identified in Requirement R3. If the status has been restored within the first 30 minutes, no notification is necessary. | 2016-10-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 30000000
VAR-002-4 (British Columbia) | 666700000010319 | R4. | 666700000011951 | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. [Violation Risk Factor: • Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of becoming aware of the capability change. | The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability in accordance with Requirement R4. If the capability has been restored within the first 30 minutes, no notification is necessary. | 2016-10-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 40000000
VAR-002-4 (British Columbia) | 666700000010319 | R5. | 666700000011952 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. [See standard for additional information.] |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Low | N/A | N/A | The Generator Owner failed to provide its associated Transmission Operator and Transmission Planner one of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | The Generator Owner failed to provide to its associated Transmission Operator and Transmission Planner two or more of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | 2016-10-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 50000000
VAR-002-4 (British Columbia) | 666700000010319 | R6. | 666700000011953 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. [See standard for additional information.] |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Low | N/A | N/A | N/A | The Generator Owner did not ensure the tap changes were made according the Transmission Operator’s specifications. OR The Generator Owner failed to perform the tap changes, and the Generator Owner did not provide technical justification for why it could not comply with the Transmission Operator specifications. | The Generator Owner shall have evidence that its step-up transformer taps were modified per the Transmission Operator’s documentation in accordance with Requirement R6. The Generator Owner shall have evidence that it notified its associated Transmission Operator when it could not comply with the Transmission Operator’s step-up transformer tap specifications in accordance with Requirement R6, Part 6.1. | 2016-10-01 |  | 2018-09-30 |  |  |  | WECC-BC | [6 empty] | 60000000
VAR-002-4 (Manitoba) | 77660000000510 | R1. | 776600000006077 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: • That the generator is being operated in start-up,1 shutdown,2 or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | Unless exempted, the Generator Operator did not operate each generator connected to the interconnected transmission system in the automatic voltage control mode or in a different control mode as instructed by the Transmission Operator, and failed to provide the required notifications to Transmission Operator as identified in Requirement R1. | The Generator Operator shall have evidence to show that it notified its associated Transmission Operator any time it failed to operate a generator in the automatic voltage control mode or in a different control mode as specified in Requirement R1. If a generator is being started up or shut down with the automatic voltage control off, or is being tested, and no notification of the AVR status is made to the Transmission Operator, the Generator Operator will have evidence that it notified the Transmission Operator of its procedure for placing the unit into automatic voltage control mode as required in Requirement R1. Such evidence may include, but is not limited to, dated evidence of transmittal of the procedure such as an electronic message or a transmittal letter with the procedure included or attached. If a generator is exempted, the Generator Operator shall also have evidence that the generator is exempted from being in automatic voltage control mode (with its AVR in service and controlling voltage). | 2016-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 10000000
VAR-002-4 (Manitoba) | 77660000000510 | R2. | 776600000006078 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule3 (within each generating Facility’s capabilities4) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator.[See standard for additional information.] |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | The Generator Operator did not have a conversion methodology when it monitors voltage at a location different from the schedule provided by the Transmission Operator. | The Generator Operator did not maintain the voltage or Reactive Power schedule as instructed by the Transmission Operator and did not make the necessary notifications required by the Transmission Operator. OR The Generator Operator did not have an operating AVR, and the responsible entity did not use an alternative method for controlling voltage. OR The Generator Operator did not modify voltage when directed, and the responsible entity did not provide any explanation. | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | 2016-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 20000000
VAR-002-4 (Manitoba) | 77660000000510 | R3. | 776600000006079 | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of the status change. | The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of any status change identified in Requirement R3. If the status has been restored within the first 30 minutes, no notification is necessary. | 2016-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 30000000
VAR-002-4 (Manitoba) | 77660000000510 | R4. | 776600000006080 | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. [Violation Risk Factor: • Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of becoming aware of the capability change. | The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability in accordance with Requirement R4. If the capability has been restored within the first 30 minutes, no notification is necessary. | 2016-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 40000000
VAR-002-4 (Manitoba) | 77660000000510 | R5. | 776600000006081 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. [See standard for additional information.] |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Low | N/A | N/A | The Generator Owner failed to provide its associated Transmission Operator and Transmission Planner one of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | The Generator Owner failed to provide to its associated Transmission Operator and Transmission Planner two or more of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | 2016-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 50000000
VAR-002-4 (Manitoba) | 77660000000510 | R6. | 776600000006082 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. [See standard for additional information.] |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Low | N/A | N/A | N/A | The Generator Owner did not ensure the tap changes were made according the Transmission Operator’s specifications. OR The Generator Owner failed to perform the tap changes, and the Generator Owner did not provide technical justification for why it could not comply with the Transmission Operator specifications. | The Generator Owner shall have evidence that its step-up transformer taps were modified per the Transmission Operator’s documentation in accordance with Requirement R6. The Generator Owner shall have evidence that it notified its associated Transmission Operator when it could not comply with the Transmission Operator’s step-up transformer tap specifications in accordance with Requirement R6, Part 6.1. | 2016-07-01 |  | 2019-06-30 |  |  |  | MRO-MB | [6 empty] | 60000000
VAR-002-4 (Ontario) | 79780000510 | R1. | 79780006077 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: &lt;br/&gt;• That the generator is being operated in start-up,1 shutdown,2 or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or&lt;br/&gt;• That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;&lt;br/&gt;Unless exempted, the Generator Operator did not operate each generator connected to the interconnected transmission system in the &lt;br/&gt;automatic voltage control mode or in a different control mode as instructed by the Transmission &lt;br/&gt;Operator, and failed to provide the required notifications to Transmission Operator as identified &lt;br/&gt;in Requirement R1.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;The Generator Operator shall have evidence to show that it notified its associated Transmission Operator any time it failed to operate a generator in the automatic voltage control &lt;br/&gt;mode or in a different control mode as specified in Requirement R1. If a generator is being &lt;br/&gt;started up or shut down with the automatic voltage control off, or is being tested, and no &lt;br/&gt;notification of the AVR status is made to the Transmission Operator, the Generator Operator will &lt;br/&gt;have evidence that it notified the Transmission Operator of its procedure for placing the unit into &lt;br/&gt;automatic voltage control mode as required in Requirement R1. Such evidence may include, but is not &lt;br/&gt;limited to, dated evidence of transmittal of the procedure such as an electronic message or a &lt;br/&gt;transmittal letter with the procedure included or attached. If a generator is exempted, the &lt;br/&gt;Generator Operator shall also have evidence that the generator is exempted from being in automatic &lt;br/&gt;voltage control mode (with its AVR in service and controlling voltage).&lt;/p&gt; &lt;p/&gt; | 2015-05-29 |  | 2017-09-25 |  |  |  | NPCC-ON | [6 empty] | 10000000
VAR-002-4 (Ontario) | 79780000510 | R2. | 79780006078 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule3 (within each generating Facility’s capabilities4) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator.[See standard for additional information.] |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;The Generator Operator did not have a conversion methodology when it monitors voltage at a location different from the &lt;br/&gt;schedule provided by the Transmission Operator.&lt;/p&gt; &lt;p/&gt; |  | &lt;p&gt;&lt;br/&gt;In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator &lt;br/&gt;shall have evidence to show that the generator maintained the voltage or Reactive Power schedule &lt;br/&gt;provided by the Transmission Operator, or shall have evidence of meeting the conditions of &lt;br/&gt;notification for deviations from the voltage or Reactive Power schedule provided by the &lt;br/&gt;Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other &lt;br/&gt;notifications that would alert the Transmission Operator or otherwise demonstrate that the &lt;br/&gt;Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule.&lt;/p&gt; &lt;p&gt;For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a &lt;br/&gt;Generator Operator shall have evidence to show an alternative method was used to control the &lt;br/&gt;generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator.&lt;/p&gt; &lt;p&gt;For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the &lt;br/&gt;Transmission Operator of why the Generator Operator was unable to comply with the instruction. &lt;br/&gt;Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs.&lt;/p&gt; &lt;p&gt;For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on &lt;br/&gt; the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the &lt;br/&gt; scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator.&lt;/p&gt; &lt;p/&gt; | 2015-05-29 |  | 2017-09-25 |  |  |  | NPCC-ON | [6 empty] | 20000000
VAR-002-4 (Ontario) | 79780000510 | R3. | 79780006079 | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;The Generator Operator did not make&lt;/p&gt; &lt;p&gt;the required notification within 30&lt;/p&gt; &lt;p&gt;minutes of the status change.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;&lt;br/&gt;The Generator Operator shall have evidence it notified its associated Transmission Operator&lt;/p&gt; &lt;p&gt;within 30 minutes of any status change identified in Requirement R3. If the status has been&lt;/p&gt; &lt;p&gt;restored within the first 30 minutes, no notification is necessary.&lt;/p&gt; &lt;p/&gt; | 2015-05-29 |  | 2017-09-25 |  |  |  | NPCC-ON | [6 empty] | 30000000
VAR-002-4 (Ontario) | 79780000510 | R4. | 79780006080 | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. [Violation Risk Factor: &lt;br/&gt;• Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;The Generator Operator did not make the required notification within 30 minutes of becoming aware of the capability change.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability in accordance with Requirement R4. If the capability has been restored within the first 30 minutes, no notification is necessary.&lt;/p&gt; &lt;p/&gt; | 2015-05-29 |  | 2017-09-25 |  |  |  | NPCC-ON | [6 empty] | 40000000
VAR-002-4 (Ontario) | 79780000510 | R5. | 79780006081 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. [See standard for additional information.] |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Low | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;The Generator Owner failed to provide its associated Transmission Operator and Transmission Planner one of the types of &lt;br/&gt;data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;The Generator Owner failed to provide to its associated Transmission Operator and Transmission Planner two or more of the types of data &lt;br/&gt;specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;&lt;br/&gt;The Generator Owner shall have evidence it provided its associated Transmission Operator&lt;/p&gt; &lt;p&gt;and Transmission Planner with information on its step-up and auxiliary transformers as&lt;/p&gt; &lt;p&gt;required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days.&lt;/p&gt; &lt;p/&gt; | 2015-05-29 |  | 2017-09-25 |  |  |  | NPCC-ON | [6 empty] | 50000000
VAR-002-4 (Ontario) | 79780000510 | R6. | 79780006082 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. [See standard for additional information.] |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Low | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;N/A&lt;/p&gt; | &lt;p&gt;The Generator Owner did not ensure the tap changes were made according the Transmission Operator’s specifications.&lt;/p&gt; &lt;p&gt;OR&lt;/p&gt; &lt;p&gt;The Generator Owner failed to perform the tap changes, and the Generator Owner did not provide technical justification for why it could &lt;br/&gt;not comply with the Transmission Operator specifications.&lt;/p&gt; &lt;p/&gt; | &lt;p&gt;The Generator Owner shall have evidence that its step-up transformer taps were modified per the Transmission Operator’s documentation in accordance with Requirement R6. The Generator Owner shall have evidence that it notified its associated Transmission Operator when it could not &lt;br/&gt;comply with the Transmission Operator’s step-up transformer tap specifications in accordance with Requirement R6, Part 6.1.&lt;/p&gt; &lt;p/&gt; | 2014-10-01 |  | 2015-05-28 |  |  |  | NPCC-ON | [6 empty] | 60000000
VAR-002-4 (Saskatchewan) | 83750000000510 | R1. | 837500000006077 | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: • That the generator is being operated in start-up,1 shutdown,2 or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | Unless exempted, the Generator Operator did not operate each generator connected to the interconnected transmission system in the automatic voltage control mode or in a different control mode as instructed by the Transmission Operator, and failed to provide the required notifications to Transmission Operator as identified in Requirement R1. | The Generator Operator shall have evidence to show that it notified its associated Transmission Operator any time it failed to operate a generator in the automatic voltage control mode or in a different control mode as specified in Requirement R1. If a generator is being started up or shut down with the automatic voltage control off, or is being tested, and no notification of the AVR status is made to the Transmission Operator, the Generator Operator will have evidence that it notified the Transmission Operator of its procedure for placing the unit into automatic voltage control mode as required in Requirement R1. Such evidence may include, but is not limited to, dated evidence of transmittal of the procedure such as an electronic message or a transmittal letter with the procedure included or attached. If a generator is exempted, the Generator Operator shall also have evidence that the generator is exempted from being in automatic voltage control mode (with its AVR in service and controlling voltage). | 2015-07-16 |  | 2018-01-24 |  |  |  | MRO-SK | [6 empty] | 10000000
VAR-002-4 (Saskatchewan) | 83750000000510 | R2. | 837500000006078 | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule3 (within each generating Facility’s capabilities4) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator.[See standard for additional information.] |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | The Generator Operator did not have a conversion methodology when it monitors voltage at a location different from the schedule provided by the Transmission Operator. | The Generator Operator did not maintain the voltage or Reactive Power schedule as instructed by the Transmission Operator and did not make the necessary notifications required by the Transmission Operator. OR The Generator Operator did not have an operating AVR, and the responsible entity did not use an alternative method for controlling voltage. OR The Generator Operator did not modify voltage when directed, and the responsible entity did not provide any explanation. | In order to identify when a generator is deviating from its schedule, the Generator Operator will monitor voltage based on existing equipment at its Facility. The Generator Operator shall have evidence to show that the generator maintained the voltage or Reactive Power schedule provided by the Transmission Operator, or shall have evidence of meeting the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. Evidence may include, but is not limited to, operator logs, SCADA data, phone logs, and any other notifications that would alert the Transmission Operator or otherwise demonstrate that the Generator Operator complied with the Transmission Operator’s instructions for addressing deviations from the voltage or Reactive Power schedule. For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | 2015-07-16 |  | 2018-01-24 |  |  |  | MRO-SK | [6 empty] | 20000000
VAR-002-4 (Saskatchewan) | 83750000000510 | R3. | 837500000006079 | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of the status change. | The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of any status change identified in Requirement R3. If the status has been restored within the first 30 minutes, no notification is necessary. | 2015-07-16 |  | 2018-01-24 |  |  |  | MRO-SK | [6 empty] | 30000000
VAR-002-4 (Saskatchewan) | 83750000000510 | R4. | 837500000006080 | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. [Violation Risk Factor: • Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. |  | GOP | [5 empty] | GOP | [15 empty] | Real-Time Operations | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of becoming aware of the capability change. | The Generator Operator shall have evidence it notified its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability in accordance with Requirement R4. If the capability has been restored within the first 30 minutes, no notification is necessary. | 2015-07-16 |  | 2018-01-24 |  |  |  | MRO-SK | [6 empty] | 40000000
VAR-002-4 (Saskatchewan) | 83750000000510 | R5. | 837500000006081 | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. [See standard for additional information.] |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Low | N/A | N/A | The Generator Owner failed to provide its associated Transmission Operator and Transmission Planner one of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | The Generator Owner failed to provide to its associated Transmission Operator and Transmission Planner two or more of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | 2015-07-16 |  | 2018-01-24 |  |  |  | MRO-SK | [6 empty] | 50000000
VAR-002-4 (Saskatchewan) | 83750000000510 | R6. | 837500000006082 | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. [See standard for additional information.] |  | GO |  |  |  |  | GO | [16 empty] | Real-Time Operations | Low | N/A | N/A | N/A | The Generator Owner did not ensure the tap changes were made according the Transmission Operator’s specifications. OR The Generator Owner failed to perform the tap changes, and the Generator Owner did not provide technical justification for why it could not comply with the Transmission Operator specifications. | The Generator Owner shall have evidence that its step-up transformer taps were modified per the Transmission Operator’s documentation in accordance with Requirement R6. The Generator Owner shall have evidence that it notified its associated Transmission Operator when it could not comply with the Transmission Operator’s step-up transformer tap specifications in accordance with Requirement R6, Part 6.1. | 2015-07-16 |  | 2018-01-24 |  |  |  | MRO-SK | [6 empty] | 60000000
VAR-002-WECC-1 | 200 | R1. | 2306 | Generator Operators and Transmission Operators shall have AVR in service and in automatic voltage control mode 98% of all operating hours for synchronous generators or synchronous condensers. Generator Operators and Transmission Operators may exclude hours for R1.1 through R1.10 to achieve the 98% requirement. [Time Horizon: Operations Assessment] |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | Medium | [5 empty] | 2011-07-01 |  | 2015-03-31 |  |  |  | WECC-US | [5 empty] | WECC-US | 10000000
VAR-002-WECC-1 | 200 | R2. | 2317 | Generator Operators and Transmission Operators shall have documentation identifying the number of hours excluded for each requirement in R1.1 through R1.10. [Time Horizon: Operations Assessment] |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | Low | [5 empty] | 2011-06-27 |  | 2015-03-31 |  |  |  | WECC-US | [5 empty] | WECC-US | 20000000
VAR-002-WECC-1 (British Columbia) | 666700000010321 | R1. | 666700000011960 | Generator Operators and Transmission Operators shall have AVR in service and in automatic voltage control mode 98% of all operating hours for synchronous generators or synchronous condensers. Generator Operators and Transmission Operators may exclude hours for R1.1 through R1.10 to achieve the 98% requirement. [Time Horizon: Operations Assessment] |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | Medium | [5 empty] | 2014-01-15 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
VAR-002-WECC-1 (British Columbia) | 666700000010321 | R2. | 666700000011961 | Generator Operators and Transmission Operators shall have documentation identifying the number of hours excluded for each requirement in R1.1 through R1.10. [Time Horizon: Operations Assessment] |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | Low | [5 empty] | 2014-01-15 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 20000000
VAR-002-WECC-2 | 461 | R1. | 5531 | Generator Operators and Transmission Operators shall have AVR in service and in automatic voltage control mode 98% of all operating hours for synchronous generators or synchronous condensers. Generator Operators and Transmission Operators may exclude hours for R1.1 through R1.10 to achieve the 98% requirement. [See Standard for additional information.] |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  | Operations Assessment | Medium | There shall be a Lower Level of non-compliance if AVR is in service less than 98% but at least 90% or more of all hours during which the synchronous generating unit or synchronous condenser is on line for each calendar quarter. | There shall be a Moderate Level of non- compliance if AVR is in service less than 90% but at least 80% or more of all hours during which the synchronous generating unit or synchronous condenser is on line for each calendar quarter. | There shall be a High Level of non- compliance if AVR is in service less than 80% but at least 70% or more of all hours during which the synchronous generating unit or synchronous condenser is on line for each calendar quarter. | There shall be a Severe Level of non- compliance if AVR is in service less than 70% of all hours during which the synchronous generating unit or synchronous condenser is on line for each calendar quarter. | Generator Operators and Transmission Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator and synchronous condenser of the following: M1.1 The actual number of hours the synchronous generator or synchronous condenser was on line. M1.2 The actual number of hours the AVR was out of service. M1.3 The AVR in service percentage. M1.4 If excluding AVR out of service hours as allowed in R1.1 through R1.10, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted AVR in-service percentage, M1.4.3 The date of the outage. | 2015-04-01 |  | 2018-09-05 |  |  |  | WECC-US | [5 empty] | WECC-US | 10000000
VAR-002-WECC-2 (British Columbia) | 666700000010322 | R1. | 666700000011962 | Generator Operators and Transmission Operators shall have AVR in service and in automatic voltage control mode 98% of all operating hours for synchronous generators or synchronous condensers. Generator Operators and Transmission Operators may exclude hours for R1.1 through R1.10 to achieve the 98% requirement. [See Standard for additional information.] |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  | Operations Assessment | Medium | There shall be a Lower Level of non-compliance if AVR is in service less than 98% but at least 90% or more of all hours during which the synchronous generating unit or synchronous condenser is on line for each calendar quarter. | There shall be a Moderate Level of non- compliance if AVR is in service less than 90% but at least 80% or more of all hours during which the synchronous generating unit or synchronous condenser is on line for each calendar quarter. | There shall be a High Level of non- compliance if AVR is in service less than 80% but at least 70% or more of all hours during which the synchronous generating unit or synchronous condenser is on line for each calendar quarter. | There shall be a Severe Level of non- compliance if AVR is in service less than 70% of all hours during which the synchronous generating unit or synchronous condenser is on line for each calendar quarter. | Generator Operators and Transmission Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator and synchronous condenser of the following: M1.1 The actual number of hours the synchronous generator or synchronous condenser was on line. M1.2 The actual number of hours the AVR was out of service. M1.3 The AVR in service percentage. M1.4 If excluding AVR out of service hours as allowed in R1.1 through R1.10, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted AVR in-service percentage, M1.4.3 The date of the outage. | 2016-10-01 | [5 empty] | WECC-BC | [6 empty] | 10000000
VAR-501-WECC-1 | 201 | R1. | 2318 | Generator Operators shall have PSS in service 98% of all operating hours for synchronous generators equipped with PSS. Generator Operators may exclude hours for R1.1 through R1.12 to achieve the 98% requirement. [Time Horizon: Operations Assessment] |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2011-07-01 |  | 2015-03-31 |  |  |  | WECC-US | [5 empty] | WECC-US | 10000000
VAR-501-WECC-1 | 201 | R2. | 2331 | Generator Operators shall have documentation identifying the number of hours excluded for each requirement in R1.1 through R1.12. [Time Horizon: Operations Assessment] |  | GOP | [5 empty] | GOP | [16 empty] | Low | [5 empty] | 2011-06-27 |  | 2015-03-31 |  |  |  | WECC-US | [5 empty] | WECC-US | 20000000
VAR-501-WECC-1 (British Columbia) | 666700000010323 | R1. | 666700000011963 | Generator Operators shall have PSS in service 98% of all operating hours for synchronous generators equipped with PSS. Generator Operators may exclude hours for R1.1 through R1.12 to achieve the 98% requirement. [Time Horizon: Operations Assessment] |  | GOP | [5 empty] | GOP | [16 empty] | Medium | [5 empty] | 2014-01-15 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
VAR-501-WECC-1 (British Columbia) | 666700000010323 | R2. | 666700000011964 | Generator Operators shall have documentation identifying the number of hours excluded for each requirement in R1.1 through R1.12. [Time Horizon: Operations Assessment] |  | GOP | [5 empty] | GOP | [16 empty] | Low | [5 empty] | 2014-01-15 |  | 2016-09-30 |  |  |  | WECC-BC | [6 empty] | 20000000
VAR-501-WECC-2 | 463 | R1. | 5533 | Generator Operators shall have PSS in service 98% of all operating hours for synchronous generators equipped with PSS. Generator Operators may exclude hours for R1.1 through R1.12 to achieve the 98% requirement. [See Standard for additional information.] |  | GOP | [5 empty] | GOP | [15 empty] | Operations Assessment | Medium | There shall be a Lower Level of non-compliance if PSS is in service less than 98% but at least 90% or more of all hours during which the synchronous generating unit is on line for each calendar quarter. | There shall be a Moderate Level of non-compliance if PSS is in service less than 90% but at least 80% or more of all hours during which the synchronous generating unit is on line for each calendar quarter. | There shall be a High Level of non- compliance if is in service less than 80% but at least 70% or more of all hours during which the synchronous generating unit is on line for each calendar quarter. | There shall be a Severe Level of non- compliance if PSS is in service less than 70% of all hours during which the synchronous generating unit is on line for each calendar quarter. | Generators Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator of the following: M1.1 The number of hours the synchronous generator was on line. M1.2 The number of hours the PSS was out of service with generator on line. M1.3 The PSS in service percentage M1.4 If excluding PSS out of service hours as allowed in R1.1 through R1.12, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted PSS in-service percentage, M1.4.3 Date of the outage. | 2015-04-01 |  | 2017-06-30 |  |  |  | WECC-US | [5 empty] | WECC-US | 10000000
VAR-501-WECC-2 (British Columbia) | 666700000010324 | R1. | 666700000011965 | Generator Operators shall have PSS in service 98% of all operating hours for synchronous generators equipped with PSS. Generator Operators may exclude hours for R1.1 through R1.12 to achieve the 98% requirement. [See Standard for additional information.] |  | GOP | [5 empty] | GOP | [15 empty] | Operations Assessment | Medium | There shall be a Lower Level of non-compliance if PSS is in service less than 98% but at least 90% or more of all hours during which the synchronous generating unit is on line for each calendar quarter. | There shall be a Moderate Level of non-compliance if PSS is in service less than 90% but at least 80% or more of all hours during which the synchronous generating unit is on line for each calendar quarter. | There shall be a High Level of non- compliance if is in service less than 80% but at least 70% or more of all hours during which the synchronous generating unit is on line for each calendar quarter. | There shall be a Severe Level of non- compliance if PSS is in service less than 70% of all hours during which the synchronous generating unit is on line for each calendar quarter. | Generators Operators shall provide quarterly reports to the compliance monitor and have evidence for each synchronous generator of the following: M1.1 The number of hours the synchronous generator was on line. M1.2 The number of hours the PSS was out of service with generator on line. M1.3 The PSS in service percentage M1.4 If excluding PSS out of service hours as allowed in R1.1 through R1.12, provide: M1.4.1 The number of hours excluded, M1.4.2 The adjusted PSS in-service percentage, M1.4.3 Date of the outage. | 2016-10-01 |  | 2020-09-30 |  |  |  | WECC-BC | [6 empty] | 10000000
VAR-501-WECC-3 | 562 | R1. | 7974 | Each Generator Owner shall provide to its Transmission Operator, the Generator Owner’s written Operating Procedure or other document(s) describing those known circumstances during which the Generator Owner’s PSS will not be providing an active signal to the Automatic Voltage Regulator (AVR), within 180 days of any of the following events: • The effective date of this standard; • The PSS’s Commercial Operation date, or; • Any changes to the PSS operating specifications. |  | GO |  |  |  |  | GO | [16 empty] | Operations Assessment | Low | N/A | N/A | N/A | The Generator Owner failed to provide its PSS operating specifications to the Transmission Planner as required in Requirement R1. | Each Generator Owner will have documented evidence that it provided to its Transmission Operator, within the time allotted as described in the procedures required under Requirement R1, written Operating Procedures or other document(s) describing those known circumstances during which the Generator Owner’s PSS will not be providing an active signal to the AVR. For auditing purposes, because Requirement R1 conditions are intended to be unchanged unless the Transmission Operator is otherwise notified, the Generator Owner only needs to provide the documentation to the Transmission Operator one time, or whenever the operating specifications change. For auditing purposes, if a PSS is in service but is not providing an active signal to the AVR as described in Requirement R1, the disabled period does not count against the Requirement R2 mandate to be in service except as otherwise allowed. | 2017-07-01 |  | 2017-09-25 |  |  |  | WECC-US | [5 empty] | WECC-US | 10000000
VAR-501-WECC-3 | 562 | R2. | 7975 | Each Generator Operator shall have its PSS in service while synchronized, except during any of the following: • Component failure • Testing of a Bulk Electric System Element affecting or affected by the PSS • Maintenance • As agreed upon by the Generator Operator and the Transmission Operator A PSS that is out of service for less than 30 minutes does not create a violation of this Requirement, regardless of cause. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Assessment | Medium | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 30 minutes but less than 60 minutes. | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 60 minutes but less than 120 minutes. | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 120 minutes but less than 180 minutes. | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 180 minutes. | Each Generator Operator will have documentation of each claimed exception specified in Requirement R2. Documentation may include, but is not limited to: • A written explanation covering the bulleted exception that describes the circumstances of the exception as allowed in Requirement R2. • Documented evidence that the Generator Operator and the Transmission Operator agreed the PSS would not be operating during a specified set of circumstances, where the exception is claimed under the last bullet of Requirement R2. For auditing purposes, the presumption is that the PSS was in service unless otherwise exempted in Requirement R2. Evidence need only be provided to prove the circumstances during which the PSS was not in service for periods in excess of 30 minutes. | 2017-07-01 |  | 2017-09-25 |  |  |  | WECC-US | [5 empty] | WECC-US | 20000000
VAR-501-WECC-3 | 562 | R3. | 7976 | Each Generator Owner shall tune its PSS to meet the following inter-area mode criteria, except as specified in Requirement R3, Part 3.5 below: |  | GO |  |  |  |  | GO | [16 empty] | Operations Assessment | Medium | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, two times or fewer during the audit period. | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, three times during the audit period. | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, four times during the audit period. | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, five times or more during the audit period. | Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3. If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | 2017-07-01 |  | 2017-09-25 |  |  |  | WECC-US | [5 empty] | WECC-US | 30000000
VAR-501-WECC-3 | 562 | R4. | 7982 | Each Generator Owner shall install and complete start-up testing of a PSS on its generator within 180 days of either of the following events: • The Generator Owner connects a generator to the BES, after achieving Commercial Operation, and after the Effective Date of this standard. • The Generator Owner replaces the voltage regulator on its existing excitation system, after achieving Commercial Operation for its generator that is connected to the BES, and after the Effective Date of this standard. |  | GO |  |  |  |  | GO | [16 empty] | Operations Assessment | Medium | N/A | N/A | N/A | The Generator Owner failed to install on its generator a PSS, as required in Requirement R4. | Each Generator Owner will have evidence that it installed and completed start- up testing of a PSS on its generator within 180 days of either of the conditions described in Requirement R4, and when those conditions occur after the Effective Date of this standard. For auditing purposes of Requirement R4, bullet one only applies to equipment on its initial (first energization) connection to the BES. | 2017-04-28 |  | 2017-09-25 |  |  |  | WECC-US | [5 empty] | WECC-US | 40000000
VAR-501-WECC-3 | 562 | R5. | 7983 | Each Generator Owner shall repair or replace a PSS within 24 months of that PSS becoming incapable of meeting the tuning specifications stated in Requirement R3. |  | GO |  |  |  |  | GO | [16 empty] | Operations Assessment | Medium | N/A | N/A | N/A | The Generator Owner failed to repair or replace a non-operational PSS as required in Requirement R5. | Each Generator Owner will have evidence that it repaired or replaced its PSS within 24 months of that PSS becoming incapable of meeting the tuning specifications of Requirement R3. Evidence may include, but is not limited to, documentation of the date the PSS became incapable of meeting the Requirement R3 tuning specifications, and the date the PSS was returned to service, demonstrating that the span of time between the two events was less than 24 months. | 2017-04-28 |  | 2017-09-25 |  |  |  | WECC-US | [5 empty] | WECC-US | 50000000
VAR-501-WECC-3.1 | 576 | R1. | 8264 | Each Generator Owner shall provide to its Transmission Operator, the Generator Owner’s written Operating Procedure or other document(s) describing those known circumstances during which the Generator Owner’s PSS will not be providing an active signal to the Automatic Voltage Regulator (AVR), within 180 days of any of the following events: • The effective date of this standard; • The PSS’s Commercial Operation date; or • Any changes to the PSS operating specifications. |  | GO |  |  |  |  | GO | [16 empty] | Operations Planning, Real-Time Operations | Low | N/A | N/A | N/A | The Generator Owner failed to provide its PSS operating specifications to the Transmission Operator as required in Requirement R1. | Each Generator Owner will have documented evidence that it provided to its Transmission Operator, within the time allotted as described in the procedures required under Requirement R1, written Operating Procedures or other document(s) describing those known circumstances during which the Generator Owner’s PSS will not be providing an active signal to the AVR. For auditing purposes, because Requirement R1 conditions are intended to be unchanged unless the Transmission Operator is otherwise notified, the Generator Owner only needs to provide the documentation to the Transmission Operator one time, or whenever the operating specifications change. For auditing purposes, if a PSS is in service but is not providing an active signal to the AVR as described in Requirement R1, the disabled period does not count against the Requirement R2 mandate to be in service except as otherwise allowed. | 2017-09-26 | X | 2024-03-31 | Requirement R3 has an effective date of July 1, 2017 for first-time service after regulatory approval; R3 has an effective date of July 1, 2022 for units placed in service prior to final regulatory approval. | 5. Facilities: This standard applies to synchronous generators, connected to the Bulk Electric System, that meet the definition of Commercial Operation. |  | WECC-US | [5 empty] | WECC-US | 10000000
VAR-501-WECC-3.1 | 576 | R2. | 8265 | Each Generator Operator shall have its PSS in service while synchronized, except during any of the following: • Component failure • Testing of a Bulk Electric System Element affecting or affected by the PSS • Maintenance • As agreed upon by the Generator Operator and the Transmission Operator A PSS that is out of service for less than 30 minutes does not create a violation of this Requirement, regardless of cause. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Assessment | Medium | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 30 minutes but less than 60 minutes. | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 60 minutes but less than 120 minutes. | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 120 minutes but less than 180 minutes. | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 180 minutes. | M2. Each Generator Operator will have documentation of each claimed exception specified in Requirement R2. Documentation may include, but is not limited to: • A written explanation covering the bulleted exception that describes the circumstances of the exception as allowed in Requirement R2. • Documented evidence that the Generator Operator and the Transmission Operator agreed the PSS would not be operating during a specified set of circumstances, where the exception is claimed under the last bullet of Requirement R2. For auditing purposes, the presumption is that the PSS was in service unless otherwise exempted in Requirement R2. Evidence need only be provided to prove the circumstances | 2017-09-26 | X | 2024-03-31 |  | 5. Facilities: This standard applies to synchronous generators, connected to the Bulk Electric System, that meet the definition of Commercial Operation. |  | WECC-US | [5 empty] | WECC-US | 20000000
VAR-501-WECC-3.1 | 576 | R3. | 8266 | Each Generator Owner shall tune its PSS to meet the following inter-area mode criteria, except as specified in Requirement R3, Part 3.5 below: |  | GO |  |  |  |  | GO | [16 empty] | Operations Assessment | Medium | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, two times or fewer during the audit period. | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, three times during the audit period. | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, four times during the audit period. | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, five times or more during the audit period. | M3. Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3. If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | 2017-09-26 | X | 2024-03-31 | Requirement R3 has an effective date of July 1, 2017 for first-time service after regulatory approval; R3 has an effective date of July 1, 2022 for units placed in service prior to final regulatory approval. | 5. Facilities: This standard applies to synchronous generators, connected to the Bulk Electric System, that meet the definition of Commercial Operation. |  | WECC-US | [5 empty] | WECC-US | 30000000
VAR-501-WECC-3.1 | 576 | R4. | 8272 | Each Generator Owner shall install and complete start-up testing of a PSS on its generator within 180 days of either of the following events: • The Generator Owner connects a generator to the BES, after achieving Commercial Operation, and after the Effective Date of this standard. • The Generator Owner replaces the voltage regulator on its existing excitation system, after achieving Commercial Operation for its generator that is connected to the BES, and after the Effective Date of this standard. |  | GO |  |  |  |  | GO | [16 empty] | Operations Assessment | Medium | N/A | N/A | N/A | The Generator Owner failed to install on its generator a PSS, as required in Requirement R4. | M4. Each Generator Owner will have evidence that it installed and completed start-up testing of a PSS on its generator within 180 days of either of the conditions described in Requirement R4, and when those conditions occur after the Effective Date of this standard. For auditing purposes of Requirement R4, bullet one only applies to equipment on its initial (first energization) connection to the BES. | 2017-09-26 | X | 2024-03-31 |  | 5. Facilities: This standard applies to synchronous generators, connected to the Bulk Electric System, that meet the definition of Commercial Operation. |  | WECC-US | [5 empty] | WECC-US | 40000000
VAR-501-WECC-3.1 | 576 | R5. | 8273 | Each Generator Owner shall repair or replace a PSS within 24 months of that PSS becoming incapable of meeting the tuning specifications stated in Requirement R3. |  | GO |  |  |  |  | GO | [16 empty] | Operations Assessment | Medium | N/A | N/A | N/A | The Generator Owner failed to repair or replace a non-operational PSS as required in Requirement R5. | Each Generator Owner will have evidence that it repaired or replaced its PSS within 24 months of that PSS becoming incapable of meeting the tuning specifications of Requirement R3. Evidence may include, but is not limited to, documentation of the date the PSS became incapable of meeting the Requirement R3 tuning specifications, and the date the PSS was returned to service, demonstrating that the span of time between the two events was less than 24 months. | 2017-09-26 | X | 2024-03-31 |  | 5. Facilities: This standard applies to synchronous generators, connected to the Bulk Electric System, that meet the definition of Commercial Operation. |  | WECC-US | [5 empty] | WECC-US | 50000000
VAR-501-WECC-3.1 (British Columbia) | 666700000010325 | R1. | 666700000011966 | Each Generator Owner shall provide to its Transmission Operator, the Generator Owner’s written Operating Procedure or other document(s) describing those known circumstances during which the Generator Owner’s PSS will not be providing an active signal to the Automatic Voltage Regulator (AVR), within 180 days of any of the following events: • The effective date of this standard; • The PSS’s Commercial Operation date; or • Any changes to the PSS operating specifications. |  | GO |  |  |  |  | GO | [16 empty] | Operations Planning, Real-Time Operations | Low | N/A | N/A | N/A | The Generator Owner failed to provide its PSS operating specifications to the Transmission Operator as required in Requirement R1. | Each Generator Owner will have documented evidence that it provided to its Transmission Operator, within the time allotted as described in the procedures required under Requirement R1, written Operating Procedures or other document(s) describing those known circumstances during which the Generator Owner’s PSS will not be providing an active signal to the AVR. For auditing purposes, because Requirement R1 conditions are intended to be unchanged unless the Transmission Operator is otherwise notified, the Generator Owner only needs to provide the documentation to the Transmission Operator one time, or whenever the operating specifications change. For auditing purposes, if a PSS is in service but is not providing an active signal to the AVR as described in Requirement R1, the disabled period does not count against the Requirement R2 mandate to be in service except as otherwise allowed. | 2020-10-01 |  |  | Requirement R3 has an effective date of July 1, 2017 for first-time service after regulatory approval; R3 has an effective date of July 1, 2022 for units placed in service prior to final regulatory approval. | 5. Facilities: This standard applies to synchronous generators, connected to the Bulk Electric System, that meet the definition of Commercial Operation. |  | WECC-BC | [6 empty] | 10000000
VAR-501-WECC-3.1 (British Columbia) | 666700000010325 | R2. | 666700000011967 | Each Generator Operator shall have its PSS in service while synchronized, except during any of the following: • Component failure • Testing of a Bulk Electric System Element affecting or affected by the PSS • Maintenance • As agreed upon by the Generator Operator and the Transmission Operator A PSS that is out of service for less than 30 minutes does not create a violation of this Requirement, regardless of cause. |  | GOP | [5 empty] | GOP | [15 empty] | Operations Assessment | Medium | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 30 minutes but less than 60 minutes. | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 60 minutes but less than 120 minutes. | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 120 minutes but less than 180 minutes. | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 180 minutes. | M2. Each Generator Operator will have documentation of each claimed exception specified in Requirement R2. Documentation may include, but is not limited to: • A written explanation covering the bulleted exception that describes the circumstances of the exception as allowed in Requirement R2. • Documented evidence that the Generator Operator and the Transmission Operator agreed the PSS would not be operating during a specified set of circumstances, where the exception is claimed under the last bullet of Requirement R2. For auditing purposes, the presumption is that the PSS was in service unless otherwise exempted in Requirement R2. Evidence need only be provided to prove the circumstances | 2020-10-01 |  |  |  | 5. Facilities: This standard applies to synchronous generators, connected to the Bulk Electric System, that meet the definition of Commercial Operation. |  | WECC-BC | [6 empty] | 20000000
VAR-501-WECC-3.1 (British Columbia) | 666700000010325 | R3. | 666700000011968 | Each Generator Owner shall tune its PSS to meet the following inter-area mode criteria, except as specified in Requirement R3, Part 3.5 below: |  | GO |  |  |  |  | GO | [16 empty] | Operations Assessment | Medium | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, two times or fewer during the audit period. | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, three times during the audit period. | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, four times during the audit period. | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, five times or more during the audit period. | M3. Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3. If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | 2020-10-01 |  |  | Requirement R3 has an effective date of July 1, 2017 for first-time service after regulatory approval; R3 has an effective date of July 1, 2022 for units placed in service prior to final regulatory approval. | 5. Facilities: This standard applies to synchronous generators, connected to the Bulk Electric System, that meet the definition of Commercial Operation. |  | WECC-BC | [6 empty] | 30000000
VAR-501-WECC-3.1 (British Columbia) | 666700000010325 | R4. | 666700000011969 | Each Generator Owner shall install and complete start-up testing of a PSS on its generator within 180 days of either of the following events: • The Generator Owner connects a generator to the BES, after achieving Commercial Operation, and after the Effective Date of this standard. • The Generator Owner replaces the voltage regulator on its existing excitation system, after achieving Commercial Operation for its generator that is connected to the BES, and after the Effective Date of this standard. |  | GO |  |  |  |  | GO | [16 empty] | Operations Assessment | Medium | N/A | N/A | N/A | The Generator Owner failed to install on its generator a PSS, as required in Requirement R4. | M4. Each Generator Owner will have evidence that it installed and completed start-up testing of a PSS on its generator within 180 days of either of the conditions described in Requirement R4, and when those conditions occur after the Effective Date of this standard. For auditing purposes of Requirement R4, bullet one only applies to equipment on its initial (first energization) connection to the BES. | 2020-10-01 |  |  |  | 5. Facilities: This standard applies to synchronous generators, connected to the Bulk Electric System, that meet the definition of Commercial Operation. |  | WECC-BC | [6 empty] | 40000000
VAR-501-WECC-3.1 (British Columbia) | 666700000010325 | R5. | 666700000011970 | Each Generator Owner shall repair or replace a PSS within 24 months of that PSS becoming incapable of meeting the tuning specifications stated in Requirement R3. |  | GO |  |  |  |  | GO | [16 empty] | Operations Assessment | Medium | N/A | N/A | N/A | The Generator Owner failed to repair or replace a non-operational PSS as required in Requirement R5. | Each Generator Owner will have evidence that it repaired or replaced its PSS within 24 months of that PSS becoming incapable of meeting the tuning specifications of Requirement R3. Evidence may include, but is not limited to, documentation of the date the PSS became incapable of meeting the Requirement R3 tuning specifications, and the date the PSS was returned to service, demonstrating that the span of time between the two events was less than 24 months. | 2020-10-01 |  |  |  | 5. Facilities: This standard applies to synchronous generators, connected to the Bulk Electric System, that meet the definition of Commercial Operation. |  | WECC-BC | [6 empty] | 50000000
VAR-501-WECC-4 | ST-2023-08-15-0000002 | R1. | RQ-2023-08-15-0000004 | Each Generator Owner shall provide to its Transmission Operator, the Generator Owner’s written Operating Procedure or other document(s) describing those known circumstances during which the Generator Owner’s PSS will not be providing an active signal to the Automatic Voltage Regulator (AVR), within 180 days of any of the following events: [Violation Risk Factor: Low] [Time Horizon: Planning Horizon] · The effective date of this standard; · The PSS’s Commercial Operation date; or · Any changes to the PSS operating specifications. |  | GO, GOP |  |  |  |  | GO | GOP | [15 empty] | Long-Term Planning | Low | NA | NA | NA | The Generator Owner failed to provide its PSS operating specifications to the Transmission Operator as required in Requirement R1. | Each Generator Owner will have documented evidence that it provided to its Transmission Operator, within the time allotted as described in the procedures required under Requirement R1, written Operating Procedures or other document(s) describing those known circumstances during which the Generator Owner’s PSS will not be providing an active signal to the AVR. For auditing purposes, because Requirement R1 conditions are intended to be unchanged unless the Transmission Operator is otherwise notified, the Generator Owner only needs to provide the documentation to the Transmission Operator one time, or whenever the operating specifications change. For auditing purposes, if a PSS is in service but is not providing an active signal to the AVR as described in Requirement R1, the disabled period does not count against the Requirement R2 mandate to be in service except as otherwise allowed. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 10000000
VAR-501-WECC-4 | ST-2023-08-15-0000002 | R2. | RQ-2023-08-15-0000005 | Each Generator Operator shall have its PSS in service while synchronized, except during any of the following: - Component failure - Testing of a Bulk Electric System Element affecting or affected by the PSS - Maintenance - As agreed upon by the Generator Operator and the Transmission Operator A PSS that is out of service for less than 30 minutes does not create a violation of this Requirement, regardless of cause. |  | GO, GOP |  |  |  |  | GO | GOP | [15 empty] | Operations Assessment | Medium | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 30 minutes but less than 60 minutes. | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 60 minutes but less than 120 minutes. | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 120 minutes but less than 180 minutes. | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 180 minutes. | Each Generator Operator will have documentation of each claimed exception specified in Requirement R2. Documentation may include, but is not limited to: - A written explanation covering the bulleted exception that describes the circumstances of the exception as allowed in Requirement R2. - Documented evidence that the Generator Operator and the Transmission Operator agreed the PSS would not be operating during a specified set of circumstances, where the exception is claimed under the last bullet of Requirement R2. For auditing purposes, the presumption is that the PSS was in service unless otherwise exempted in Requirement R2. Evidence need only be provided to prove the circumstances during which the PSS was not in service for periods in excess of 30 minutes. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 20000000
VAR-501-WECC-4 | ST-2023-08-15-0000002 | R3. | RQ-2023-08-15-0000006 | Each Generator Owner shall tune its PSS to meet the following inter-area mode criteria, except as specified in Requirement R3, Part 3.5 below |  | GO, GOP |  |  |  |  | GO | GOP | [15 empty] | Operations Assessment | Medium | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, two times or fewer during the audit period. | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, three times during the audit period. | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, four times during the audit period. | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, five times or more during the audit period. | Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3.If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 30000000
VAR-501-WECC-4 | ST-2023-08-15-0000002 | R4. | RQ-2023-08-15-0000007 | Each Generator Owner shall install and complete start-up testing of a PSS on its generator within 180 days of either of the following events: - The Generator Owner connects a generator to the BES, after achieving Commercial Operation, and after the Effective Date of this standard. - The Generator Owner replaces the voltage regulator on its existing excitation system, after achieving Commercial Operation for its generator that is connected to the BES, and after the Effective Date of this standard. |  | GO, GOP |  |  |  |  | GO | GOP | [15 empty] | Operations Assessment | Medium | NA | NA | NA | The Generator Owner failed to install on its generator a PSS, as required in Requirement R4. | Each Generator Owner will have evidence that it installed and completed start-up testing of a PSS on its generator within 180 days of either of the conditions described in Requirement R4, and when those conditions occur after the Effective Date of this standard. The first bullet of Requirement R4 only applies to equipment on its initial (first energization) connection to the BES. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 40000000
VAR-501-WECC-4 | ST-2023-08-15-0000002 | R5. | RQ-2023-08-15-0000008 | Each Generator Owner shall repair or replace a PSS within 24 months of that PSS becoming incapable of meeting the tuning specifications stated in Requirement R3. |  | GO, GOP |  |  |  |  | GO | GOP | [15 empty] | Operations Assessment | Medium | NA | NA | NA | The Generator Owner failed to repair or replace a non-operational PSS as required in Requirement R5. | Each Generator Owner will have evidence that it repaired or replaced its PSS within 24 months of that PSS becoming incapable of meeting the tuning specifications of Requirement R3. Evidence may include, but is not limited to, documentation of the date the PSS became incapable of meeting the Requirement R3 tuning specifications, and the date the PSS was returned to service, demonstrating that the span of time between the two events was less than 24 months. | 2024-04-01 | [5 empty] | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US | 50000000
VAR-STD-002a-1 | 202 | WR1. | 2332 | Automatic voltage control equipment on synchronous generators shall be kept in service at all times, unless one of the exemptions listed in Section C (Measures) applies, with outages coordinated to minimize the number out of service at any one time. All synchronous generators with automatic voltage control equipment shall normally be operated in voltage control mode and set to respond effectively to voltage deviations. (Source: WECC Criterion) |  | GOP | [5 empty] | GOP | [22 empty] | 2007-06-18 |  | 2011-06-30 |  |  |  | WECC-US | [5 empty] | WECC-US | 10000000
VAR-STD-002a-1 (British Columbia) | 666700000010326 | WR1. | 666700000011971 | Automatic voltage control equipment on synchronous generators shall be kept in service at all times, unless one of the exemptions listed in Section C (Measures) applies, with outages coordinated to minimize the number out of service at any one time. All synchronous generators with automatic voltage control equipment shall normally be operated in voltage control mode and set to respond effectively to voltage deviations. (Source: WECC Criterion) |  | GOP | [5 empty] | GOP | [22 empty] | 2010-11-01 |  | 2014-01-14 |  |  |  | WECC-BC | [6 empty] | 10000000
VAR-STD-002b-1 | 203 | WR1. | 2333 | Power System Stabilizers on generators shall be kept in service at all times, unless one of the exemptions listed in Section C (Measures) applies, and shall be properly tuned in accordance with WECC requirements. (Source: WECC Criterion) |  | GOP | [5 empty] | GOP | [22 empty] | 2007-06-18 |  | 2011-06-30 |  |  |  | WECC-US | [5 empty] | WECC-US | 10000000
VAR-STD-002b-1 (British Columbia) | 666700000010327 | WR1. | 666700000011972 | Power System Stabilizers on generators shall be kept in service at all times, unless one of the exemptions listed in Section C (Measures) applies, and shall be properly tuned in accordance with WECC requirements. (Source: WECC Criterion) |  | GOP | [5 empty] | GOP | [22 empty] | 2010-11-01 |  | 2014-01-14 |  |  |  | WECC-BC | [6 empty] | 10000000