## Data Entry
Balancing Authority | BA_1 |  |  |  |  | NERC FRS FORM 1
Date/Time |  | Point "A" Information |  | Point "B" Information |  | SEFRD | Load | Internal |  |  | Enter Data in Green Highlighted Cells
(Central Prevailing) | DelFreq | Load | NAI | Load | NAI | (MW/0.1Hz) | Contribution | Contingency | 0.8 | Unit | Send copy to: | Chris.Scheetz@nerc.net
2008-12-20 12:12 | -0.057761 | 2869.1148 | -116.9972 | 2861.1832 | -93.7505 | -40.2466 | 34.12% | N | -40.2466
2008-12-27 14:18 | -0.066093 | 2553.6094 | -138.4941 | 2576.9186 | -110.7924 | -41.9129 | -84.14% | N | -41.9129
2009-01-05 09:26 | -0.04024 | 2838.7101 | -99.1958 | 2857.8081 | -88.5325 | -26.4992 | -179.1% | N | -26.4992
2009-01-27 00:39 | -0.052525 | 2524.6843 | -94.4203 | 2522.2965 | -13.7594 | -153.5669 | 2.96% | N | -153.5669 |  | 2010 | Bias Calculation Form Year
2009-02-01 18:59 | -0.070905 | 2628.5782 | 62.2889 | 2642.9118 | 35.3913 | 37.9346 | 53.29% | N | 37.9346 |  | Eastern | Interconnection
2009-02-19 04:59 | -0.051907 | 2295.6685 | 10.1628 | 2283.7382 | 20.1183 | -19.1795 | 119.8% | N | -19.1795 |  | BA_1 | Balancing Authority
2009-03-24 21:27 | -0.058048 | 2438.2312 | -164.4543 | 2465.2617 | -161.0872 | -5.8004 | -802.8% | N | -5.8004 |  |  | Contact Name
2009-03-26 03:51 | -0.075572 | 2198.7744 | -167.5841 | 2193.6265 | -131.2497 | -48.0789 | 14.17% | Y |  | Green Valley 1 |  | Contact Phone #
2009-04-01 17:05 | -0.05638 | 2447.8687 | -185.2358 | 2436.4141 | -184.7476 | -0.866 | 2346% | N | -0.866 |  |  | Contact e-mail
2009-04-02 17:09 | -0.057333 | 2273.1077 | -124.8163 | 2269.4618 | -122.0583 | -4.8106 | 132.2% | N | -4.8106 |  | 3241 | Current Year's Actual Peak
2009-05-03 10:05 | -0.051761 | 2010.725 | -19.8886 | 2012.6499 | -6.2452 | -26.3585 | -14.11% | Y |  | Pleasant View 2 | 3882 | Internal Generating Capacity
2009-05-21 16:36 | -0.049999 | 2154.862 | -2.3187 | 2155.396 | 8.7821 | -22.2018 | -4.811% | N | -22.2018 |  | 3242 | Next Year's Projected Peak
2009-06-21 16:50 | -0.052 | 2104.4578 | 7.8209 | 2103.3636 | -12.0859 | 38.2824 | -5.496% | N | 38.2824
2009-06-25 13:52 | -0.056 | 2505.8354 | 33.3936 | 2505.2111 | 45.7191 | -22.0099 | 5.066% | N | -22.0099
2009-07-06 13:36 | -0.058498 | 2382.0347 | 30.9075 | 2383.3364 | 31.6577 | -1.2824 | -173.5% | N | -1.2824 |  | 2009 | Current year
2009-07-26 14:06 | -0.0485 | 2180.7638 | -51.5962 | 2178.8078 | -49.3661 | -4.5981 | 87.71% | N | -4.5981 |  | -15.8 | 2009 Frequency Requirement Obligation(FRO)
2009-08-04 19:48 | -0.045 | 2035.807 | 0.22308 | 2035.5427 | 9.7009 | -21.0619 | 2.789% | N | -21.0619
2009-08-15 16:07 | -0.037502 | 2103.3326 | 22.0437 | 2100.3692 | 22.399 | -0.94743 | 834% | N | -0.94743 |  | Summary Statistics
2009-09-12 13:30 | -0.047501 | 2101.7279 | -49.2669 | 2098.1863 | -47.0962 | -4.5698 | 163.2% | N | -4.5698 |  | -24.4587 | Average Frequency Response [all events] (MW/0.1Hz)
2009-09-29 11:16 | -0.0555 | 2144.0105 | -13.3053 | 2106.1429 | 16.0767 | -52.9406 | 128.9% | N | -52.9406 |  | -20.1207 | Median Frequency Response [all events] (MW/0.1Hz)
2009-10-19 09:46 | -0.047 | 2376.8797 | -103.5872 | 2372.8042 | -98.9858 | -9.7902 | 88.57% | N | -9.7902 |  | -16.213 | Regression Estimate of Frequency Response [all events] (MW/0.1Hz)
2009-10-26 14:54 | -0.06 | 2319.6964 | -4.1106 | 2322.4229 | -2.5171 | -2.6559 | -171.1% | N | -2.6559
2009-11-02 21:40 | -0.06 | 2442.348 | -154.4944 | 2488.226 | -102.1235 | -87.2848 | -87.6% | N | -87.2848 |  | -23.2987 | Average Frequency Response [external contingencies] (MW/0.1Hz)
2009-11-03 19:42 | -0.051 | 2550.655 | -1.7817 | 2549.1314 | 32.1662 | -66.5645 | 4.488% | N | -66.5645 |  | -33.8639 | Linear Regression Frequency Response [external contingencies] (MW/0.1Hz)
[11 empty] | 4.777% | Median Load Contribution (%)
Next Year's
[11 empty] | -15.8 | 2010 Frequency Requirement Obligation(FRO)
[11 empty] | -28.496 | 2010 Frequency Bias Setting - (minimum of FRM, next year's FRO, or 0.8% of Projected Peak)
[11 empty] | -14.4848 | 2009 FRM - Median Frequency Response [external contingencies] (MW/0.1Hz)
Modified Heading for Single BA Interconnection
A | B | C | D | E | F | G | H | I | J | K
Date/Time |  | Point "A" Information |  | Point "B" Information |  | SEFRD | Load
(Central Prevailing) | DelFreq | Load | Contingency | Load |  | (MW/0.1Hz) | Contribution |  |  | Unit
MW
2008-12-15 15:18 | -0.1 | 28950 | 600 | 28931 |  | -600 | 3.167%

## Variable Bias Supplemental Info
Month | Average Bias
January | -10
Feburary | -7
March | -12
April | -8
May | -27
June | -8.7
July | -8
August | -8
September | -8.2
October | -8
November | -8
December | -12
| -10.4107 | Average Annual Bias
Based on the one minute values used in BAL 001