## Instructions
Instructions
Step 1 | Enter data in all green cells on the "Data Entry" worksheet.
Step 2 | For identified events in column B of the "Data Entry" worksheet, collect data and complete one FRS Form 2 workbook for each event in the list.
Step 3 | PasteSpecial/Values data from FRS Form 2 "Form 1 Summary Data" worksheet into "BA Form 2 Event Data" worksheet of this workbook. Do this for each event in the list.
Step 4 | Save this workbook using the following file name format:NYISO_yyyy_FRS_Form1.xlsx and send a copy of this workbook and all FRS_Form 2 workbooks to NERC. (where NYISO is replaced with your Balancing Authority abbreviation)
Step 5 | "Summary" worksheet contains each event's results for your Balancing Authority.
Note | Balancing Authorities with variable Frequency Bias Settings shall calculate monthly average Frequency Bias Settings. The previous year’s monthly averages will be reported annually on FRS Form 1.

## Data Entry
| Balancing Authority | ERCO |  | NERC FRS FORM 1 20 to 52 second Value B | [7 empty] | Enter Addition Data in column R ==> |  |  | Information |  | Select Reason(s) for adjustment
Event | Date/Time |  | BA | BA | Value "A" Information |  | Value "B" Information |  | SEFRD | Exclude for |  | Enter Data in Green Highlighted Cells |  | Event | Value "A" | Value "B"
Number | (Central Prevailing) | DelFreq | Time | DelFreq | MW Lost | Adjustment | MW Lost | Adjustment | (MW/0.1Hz) | data error * | 0.8 | Send copy to: | Chris.Scheetz@nerc.net | MW Loss | Load | Load | Reason(s)
1 | 2010-12-06 11:25 | -0.101 | 40518.4763 | -0.094618 | 755.1125 | 0 | 0 | 0 | -798.0659 | N | -755.1125 |  |  | 755.3 | 35688.5645 | 35469.9483 |  | -0.057761 | 23.2467 | Dynamic schedules for joint-owned units (DS)
2 | 2010-12-09 17:34 | -0.074 | 40521.7321 | -0.10712 | 753.0677 | 0 | 0 | 0 | -703.0295 | N | -753.0677 |  |  | 718.8 | 34418.4287 | 34111.3336 |  | -0.066093 | 27.7016 | Nonconforming load (NL)
3 | 2010-12-11 23:38 | -0.166 | 40523.985 | -0.1983 | 821.1 | 0 | 0 | 0 | -414.0653 | N | -821.1 |  |  | 819.5 | 29590.7568 | 29402.9971 |  | -0.04024 | 10.6632 | Pumped hydro (PH)
4 | 2010-12-16 15:16 | -0.074 | 40528.6361 | -0.078242 | 617.0875 | 0 | 0 | 0 | -788.6901 | N | -617.0875 | 2012 | Bias Calculation Form Year | 615.8 | 31769.4482 | 31741.0732 |  | -0.052525 | 80.6609 | Ramping units (RU)
5 | 2010-12-19 02:39 | -0.111 | 40531.1106 | -0.133 | 720.3267 | 0 | 0 | 0 | -541.6013 | N | -720.3267 | Texas | Interconnection | 719.8 | 30239.7212 | 30135.1519 |  | -0.070905 | -26.8976 | Xfred Frequency Response (TFR)
6 | 2010-12-26 08:23 | -0.066 | 40538.3556 | -0.039486 | 494.4381 | 0 | 0 | 0 | -1252.1906 | N | -494.4381 | ERCO | Balancing Authority | 538 | 39597.9473 | 39185.6239 |  | -0.051907 | 9.9554 | Contingent BA adjustment for loss of units (CBA)
7 | 2011-01-09 18:52 | -0.108 | 40552.7861 | -0.10753 | 575.2194 | 0 | 0 | 0 | -534.9461 | N | -575.2194 | Ken McIntyre | Contact Name | 516.3 | 40357.3638 | 40269.5131 |  | -0.058048 | 3.367 | DS & NL
8 | 2011-01-11 06:50 | -0.091 | 40554.2849 | -0.091383 | 456.8604 | 0 | 0 | 0 | -499.9406 | N | -456.8604 | 512-248-3969 | Contact Phone # | 523 | 48145.5186 | 48054.1854 |  | -0.075572 | 36.3344 | DS & PH
9 | 2011-01-20 00:02 | -0.198 | 40563.0013 | -0.19778 | 786.0532 | 0 | 0 | 0 | -397.4399 | N | -786.0532 | kmcintyre@ercot.com | Contact e-mail | 784.9 | 28998.6179 | 28794.6882 |  | -0.05638 | 0.48825 | DS & RU
10 | 2011-01-21 03:46 | -0.171 | 40564.1572 | -0.17122 | 650 | 0 | 0 | 0 | -379.6307 | N | -650 | 63453 | Current Year's Actual Peak | 624 | 40462.4668 | 40291.5407 |  | -0.057333 | 2.758 | DS & TFR
11 | 2011-01-23 14:53 | -0.149 | 40566.6203 | -0.14864 | 403.7147 | 0 | 0 | 0 | -271.6049 | N | -403.7147 | 75314 | Internal Generating Capacity | 400.1 | 31488.7808 | 31483.8087 |  | -0.051761 | 13.6434 | DS & CBA
12 | 2011-01-28 05:21 | -0.058 | 40571.2234 | -0.055963 | 311.4662 | 0 | 0 | 0 | -556.5569 | N | -311.4662 | 63783 | Next Year's Projected Peak | 324.9 | 32641.7061 | 32711.8081 |  | -0.049999 | 11.1007 | DS & NL & PH
13 | 2011-01-29 22:29 | -0.122 | 40572.9371 | -0.082338 | 646.2125 | 0 | 351.2895 | 0 |  | Y |  |  |  | 532 | 27748.9937 | 27729.3223 |  | -0.052 | -19.9068 | DS & NL & RU
14 | 2011-02-01 22:28 | -0.078 | 40575.9359 | -0.077912 | 459.3271 | 0 | 0 | 0 | -589.5444 | N | -459.3271 |  |  | 459.3 | 51871.748 | 51714.2688 |  | -0.056 | 12.3255 | JOU DS & NL & TFR
15 | 2011-02-02 02:18 | -0.158 | 40576.0963 | -0.15844 | 716.9337 | 0 | 0 | 0 | -452.4933 | N | -716.9337 | 2011 | Current year | 717 | 49441.4014 | 49290.7323 |  | -0.058498 | 0.75019 | DS & NL & CBA
16 | 2011-02-02 05:39 | -0.125 | 40576.2356 | -0.1239 | 578.4939 | 0 | 0 | 0 | -466.9144 | N | -578.4939 | -286 | 2011 Frequency Response Obligation (FRO) | 520 | 52943.4199 | 52864.7093 |  | -0.0485 | 2.2301 | DS & NL & PH & RU
17 | 2011-02-02 08:24 | -0.188 | 40576.3503 | -0.18743 | 775.257 | 0 | 0 | 0 | -413.6183 | N | -775.257 |  |  | 776 | 52047.5054 | 51917.6827 |  | -0.045 | 9.4779 | DS & NL & PH & TFR
18 | 2011-02-02 10:55 | -0.19 | 40576.4553 | -0.18951 | 840.8931 | 0 | 0 | 0 | -443.7096 | N | -840.8931 | Summary Statistics |  | 840.91 | 52733.0312 | 52604.594 |  | -0.037502 | 0.35531 | DS & NL & PH & CBA
19 | 2011-02-09 13:01 | -0.114 | 40583.5428 | -0.11379 | 598.686 | 0 | 11.1633 | 0 | -516.3359 | N | -587.5227 | -533.8388 | Average Frequency Response (MW/0.1Hz) | 581.8 | 50685.1836 | 50619.0839 |  | -0.047501 | 2.1707 | DS & NL & PH & RU & TFR
20 | 2011-02-15 16:40 | -0.216 | 40589.6945 | -0.21589 | 769.9818 | 0 | 0 | 0 | -356.6558 | N | -769.9818 |  |  | 770 | 31612.45 | 31388.6676 |  | -0.0555 | 29.3821 | DS & NL & PH & RU & CBA
21 | 2011-02-16 09:25 | -0.197 | 40590.3928 | -0.1754 | 569.8584 | 0 | 0 | 0 | -324.8819 | N | -569.8584 | -33.7706 | Regression Estimate of Frequency Response (MW/0.1Hz) | 601.6 | 31135.6406 | 31020.1496 |  | -0.047 | 4.6014 | DS & NL & PH & RU & TFR & CBA
22 | 2011-03-03 11:17 | -0.094 | 40605.4705 | -0.094214 | 440.4526 | 0 | 0 | 0 | -467.5043 | N | -440.4526 |  |  | 440.9 | 31497.3516 | 31443.4837 |  | -0.06 | 1.5935 | NL & PH
23 | 2011-03-14 06:09 | -0.208 | 40616.2566 | -0.20762 | 970.6714 | 0 | 0 | 0 | -467.5293 | N | -970.6714 |  |  | 924 | 26752.5693 | 26597.6325 |  | -0.06 | 52.3709 | NL & RU
24 | 2011-03-14 07:08 | -0.127 | 40616.2974 | -0.12732 | 486.9663 | 0 | 0 | 0 | -382.4857 | N | -486.9663 |  |  | 487.4 | 29065.1851 | 29088.0671 |  | -0.051 | 33.9479 | NL & TFR
25 | 2011-03-16 20:45 | -0.074 | 40618.8647 | -0.073859 | 397.5629 | 0 | 0 | 0 | -538.2712 | N | -397.5629 |  |  | 397.8 | 33412.5537 | 33257.8378 |  | -0.1 | 100 | NL & CBA
26 | 2011-03-23 14:46 | -0.063 | 40625.6158 | -0.062515 | 621.1687 | 0 | 0 | 0 | -993.6345 | N | -621.1687 |  |  | 1013.6 | 38733.6201 | 38255.9157 |  |  |  | NL & PH & RU
27 | 2011-03-24 13:59 | -0.182 | 40626.5827 | -0.17701 | 498.3148 | 0 | 0 | 0 | -281.5223 | N | -498.3148 |  | Next Year's | 568.8 | 35353.7969 | 35240.8045 |  |  |  | NL & PH & TFR
28 | 2011-03-25 16:13 | -0.172 | 40627.676 | -0.16843 | 553.3828 | 0 | 67.0523 | 0 | -288.7507 | N | -486.3305 | -286 | 2012 Frequency Response Obligation (FRO) | 591.4 | 40151.54 | 39989.0825 |  |  |  | NL & PH & BAA
29 | 2011-03-29 06:43 | -0.099 | 40631.2799 | -0.099441 | 742.8181 | 0 | 0 | 0 | -746.9936 | N | -742.8181 | -556.388 | 2012 Frequency Bias Setting - (minimum of FRM, next year's FRO, or 0.8% of Projected Peak [Load + Gen]/2) | 735.3 | 31093.9292 | 31034.9238 |  |  |  | NL & PH & RU & TFR
30 | 2011-03-31 12:21 | -0.112 | 40633.5149 | -0.11179 | 421.0469 | 0 | 0 | 0 | -376.6259 | N | -421.0469 |  |  | 420.3 | 31970.3716 | 31774.6436 |  |  | N | NL & PH & RU & CBA
31 | 2011-04-05 22:02 | -0.09 | 40638.9181 | -0.089661 | 518.4755 | 0 | 0 | 0 | -578.262 | N | -518.4755 | -504.3586 | 2011 FRM - Median Frequency Response (MW/0.1Hz) | 519.4 | 30986.4536 | 30848.2909 |  |  | Y | NL & PH & RU & TFR & CBA
32 | 2011-04-20 13:40 | -0.145 | 40653.5701 | -0.14457 | 785.5412 | 0 | 0 | 0 | -543.3742 | N | -785.5412 |  |  | 787.9 | 41619.9902 | 41463.4122 |  |  |  | PH & RU
33 | 2011-04-27 23:27 | -0.133 | 40660.9771 | -0.13291 | 691.8045 | 0 | 0 | 0 | -520.5021 | N | -691.8045 |  |  | 697.2 | 29943.1245 | 29703.5409 |  |  |  | PH & TFR
34 | 2011-05-11 14:04 | -0.121 | 40674.5866 | -0.12124 | 726.0243 | 0 | 0 | 0 | -598.8298 | N | -726.0243 | N | Do you RECEIVE Overlap regulation? | 723 | 42265.9336 | 42113.4274 |  |  |  | PH & CBA
35 | 2011-05-16 08:06 | -0.101 | 40679.3379 | -0.10147 | 471.0875 | 0 | 0 | 0 | -464.2821 | N | -471.0875 |  | If Yes, list the BA name and the associated Bias of that BA | 471 | 30202.7422 | 30136.7695 |  |  |  | PH & RU & TFR
36 | 2011-05-19 14:08 | -0.197 | 40682.5888 | -0.19718 | 995.0827 | 0 | 0 | 0 | -504.6492 | N | -995.0827 |  |  | 1162.3 | 42909.6079 | 42610.2337 |  |  |  | PH & RU & CBA
37 | 2011-05-23 17:34 | -0.092 | 40686.7324 | -0.092072 | 533.3253 | 0 | 0 | 0 | -579.245 | N | -533.3253 | Bias -MW/0.1 Hz | Balancing Authority | 552 | 50589.6709 | 50488.2642 |  |  |  | PH & TFR
38 | 2011-05-29 22:03 | -0.118 | 40692.9188 | -0.11794 | 762.3234 | 0 | 0 | 0 | -646.3608 | N | -762.3234 |  |  | 761.9 | 44769.7285 | 44477.9926 |  |  |  | PH & CBA
39 | 2011-06-22 13:18 | 0.08 | 40716.5546 | 0.031317 | -258.56 | 0 | 0 | 0 | -825.6283 | N | 258.56 |  |  | -258.56 | 44769.1958 | 44456.9752 |  |  |  | PH & RU & TFR
40 | 2011-06-27 12:54 | -0.149 | 40721.5375 | -0.1311 | 661.2317 | 0 | 0 | 0 | -504.3586 | N | -661.2317 |  |  | 659.5 | 56971.1396 | 56832.6572 |  |  |  | PH & RU & CBA
41 | 2011-07-18 09:13 | -0.097 | 40742.3842 | -0.094273 | 386.25 | 0 | 0 | 0 | -409.7153 | N | -386.25 |  |  | 464 | 45315.0059 | 45296.7034 |  |  |  | PH & TFR
42 | 2011-07-18 20:50 | -0.119 | 40742.8685 | -0.12767 | 596.1496 | 0 | 0 | 0 | -466.9492 | N | -596.1496 |  |  | 593.3 | 57050.2559 | 56884.0016 |  |  |  | PH & CBA
PH & RU & TFR & CBA
RU & TFR
RU & CBA
RU & TFR & CBA
TFR & CBA
[12 empty] | N | Do you PROVIDE Overlap regulation?
If Yes, list the BA name and the associated Bias of that BA
[12 empty] | Bias -MW/0.1 Hz | Balancing Authority
N
Y
Instructions
| Step 1 | Enter data in all green cells on this "Data Entry" worksheet.
| Step 2 | For identified events in column B, collect data and complete FRS Form 2 for each event in the list.
| Step 3 | PasteSpecial/Values data from FRS Form 2 "Form 1 Summary Data" into "BA Form 2 Data" worksheet of this workbook. Do this for each event in the list.
| Step 4 | Save this workbook using the following file name format:NYISO_yyyy_FRS_Form1.xlsx and send a copy of this workbook and all FRS_Form 2 workbooks to NERC. (where NYISO is replaced with your BA name)
| Note: | Only one set of average periods of evaluation is displayed. Other worksheets for the additional average periods are hidden.

## Adjustments
| Balancing Authority | ERCO | JOU Dynamic Schedules |  | Non conforming Load |  | Pumped Hydro |  | Ramping Units |  | Transferred Frequency Response |  | Contingent BA Adjustment |  | Net Total Adjustments
Event | Date/Time |  | Value A | Value B | Value A | Value B | Value A | Value B | Value A | Value B | Value A | Value B | Value A | Value B | Value B 12 to 24 seconds
Number | (Central Prevailing) | DelFreq | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment
1 | 2010-12-06 11:25 | -0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2010-12-09 17:34 | -0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2010-12-11 23:38 | -0.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2010-12-16 15:16 | -0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2010-12-19 02:39 | -0.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2010-12-26 08:23 | -0.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2011-01-09 18:52 | -0.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2011-01-11 06:50 | -0.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2011-01-20 00:02 | -0.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2011-01-21 03:46 | -0.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2011-01-23 14:53 | -0.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2011-01-28 05:21 | -0.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 2011-01-29 22:29 | -0.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 2011-02-01 22:28 | -0.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 2011-02-02 02:18 | -0.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 2011-02-02 05:39 | -0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2011-02-02 08:24 | -0.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 2011-02-02 10:55 | -0.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 2011-02-09 13:01 | -0.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 2011-02-15 16:40 | -0.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 2011-02-16 09:25 | -0.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 2011-03-03 11:17 | -0.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 2011-03-14 06:09 | -0.208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2011-03-14 07:08 | -0.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 2011-03-16 20:45 | -0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 2011-03-23 14:46 | -0.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 2011-03-24 13:59 | -0.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 2011-03-25 16:13 | -0.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 2011-03-29 06:43 | -0.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 2011-03-31 12:21 | -0.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 2011-04-05 22:02 | -0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 2011-04-20 13:40 | -0.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 2011-04-27 23:27 | -0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 2011-05-11 14:04 | -0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 2011-05-16 08:06 | -0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 2011-05-19 14:08 | -0.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 2011-05-23 17:34 | -0.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 2011-05-29 22:03 | -0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 2011-06-22 13:18 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 2011-06-27 12:54 | -0.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 2011-04-27 23:27 | -0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 2011-05-11 14:04 | -0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sign Convention for scan data collected in Form 2 |  | Imports: MWs are - Exports: MWs are + |  | Loads in MW as - |  | Load MW as - Generation MW as + |  | Enter Gen MW as + |  | The transactional amount in MW Receiver enters - Deliverer enters + on Form 2 Data sheet |  | Generation MW as + (If load occurs due to gen loss, enter MW as - at value B)
Notes:
| 1) | Balancing Authorities making adjustments must retain evidence to verify: - Adjustment values are determined from scan-cycle data using Value A and Value B averaging periods. Scan-cycle data must be available if adjustments are made. - Adjustments are necessary to improve accuracy of calculations compared to using Net Actual Interchange (contingency size for single BA interconnections) solely. Said differently, unless an adjustment compensates for significant known error, it should not be made. However, as noted in the next item, once a decision to include an adjustment for one or more of the six types is made for one event, the entity must calculate adjustments for that (those) type(s) for all events. - Adjustments are included consistently for all events (e.g. if adjustments for nonconforming load are made for one event, the load must be included for all events, etc.).
| 2) | Dynamic Schedules: - Values use schedule sign convention. - Adjustments should include only dynamic schedules accounting for joint-owned units. Other dynamic schedules should be ignored.
| 3) | Nonconforming Loads: - Values must be entered as negative numbers.
| 4) | Pumped Hydro: - Values for pumping must be entered as negative values. - Values for generating must be entered as positive values.
| 5) | Rampling Units: - Values are entered as positive values.
| 6) | Transferred Frequency Response: - This value is the amount agreed upon between the entities expressed in MW/0.1 Hz. Form 2 will adjust this amount for the frequency deviation experienced. (e.g. if an entity agrees to provide 20 MW/0.1 Hz to another entity and a frequency event with a deviation of 50 mHz occurs, the delivering entity should enter +20 in the data column of Form 2 and the receiving entity should enter - 20. The spreadsheet will adjust the SEFRD for each entity by the 10 for this event.) - Values for the entity receiving the response must be entered as a negative number. - Values for the entity delivering the response must be entered as a positive number. - Values between entities must sum to zero.
| 7) | Contingent Balancing Authority Adjustment: - Value for Value A is the pre-contingency generation from the contingent unit(s). - Value for Value B is usually 0 MW, but may be the load that remains on the system that was "netted" out by the now offline generation.

## Data Entry1224
| Balancing Authority | ERCO |  | NERC FRS FORM 1 12 to 24 second Value B | [9 empty] | Information
Event | Date/Time |  | BA | BA | Value "A" Information |  | Value "B" Information |  | SEFRD | Exclude for |  |  |  | Value "A" | Value "B"
Number | (Central Prevailing) | DelFreq | Time | DelFreq | MW Lost | Adjustment | MW Lost | Adjustment | (MW/0.1Hz) | data error * | 0.8 |  |  | Load | Load
1 | 2010-12-06 11:25 | -0.101 | 40518.4763 | -0.10264 | 755.1125 | 0 | 0 | 0 | -735.6692 | N | -755.1125 |  |  | 35688.5645 | 35448.9286 | -0.057761 | 23.2467 | Dynamic schedules for joint-owned units (DS)
2 | 2010-12-09 17:34 | -0.074 | 40521.7321 | -0.11143 | 753.0677 | 0 | 0 | 0 | -675.8265 | N | -753.0677 |  |  | 34418.4287 | 34067.3248 | -0.066093 | 27.7016 | Nonconforming load (NL)
3 | 2010-12-11 23:38 | -0.166 | 40523.985 | -0.18513 | 821.1 | 0 | 0 | 0 | -443.5376 | N | -821.1 |  |  | 29590.7568 | 29332.9386 | -0.04024 | 10.6632 | Pumped hydro (PH)
4 | 2010-12-16 15:16 | -0.074 | 40528.6361 | -0.081696 | 617.0875 | 0 | 0 | 0 | -755.3489 | N | -617.0875 | 2012 | Bias Calculation Form Year | 31769.4482 | 31711.4741 | -0.052525 | 80.6609 | Ramping units (RU)
5 | 2010-12-19 02:39 | -0.111 | 40531.1106 | -0.112 | 720.3267 | 0 | 0 | 0 | -643.152 | N | -720.3267 | Texas | Interconnection | 30239.7212 | 30095.928 | -0.070905 | -26.8976 | Xfred Frequency Response (TFR)
6 | 2010-12-26 08:23 | -0.066 | 40538.3556 | -0.05968 | 494.4381 | 0 | 0 | 0 | -828.4813 | N | -494.4381 | ERCO | Balancing Authority | 39597.9473 | 39157.4738 | -0.051907 | 9.9554 | Contingent BA adjustment for loss of units (CBA)
7 | 2011-01-09 18:52 | -0.108 | 40552.7861 | -0.12171 | 575.2194 | 0 | 0 | 0 | -472.5995 | N | -575.2194 | Ken McIntyre | Contact Name | 40357.3638 | 40313.0413 | -0.058048 | 3.367 | DS & NL
8 | 2011-01-11 06:50 | -0.091 | 40554.2849 | -0.096501 | 456.8604 | 0 | 0 | 0 | -473.4269 | N | -456.8604 | 512-248-3969 | Contact Phone # | 48145.5186 | 48119.3449 | -0.075572 | 36.3344 | DS & PH
9 | 2011-01-20 00:02 | -0.198 | 40563.0013 | -0.18911 | 786.0532 | 0 | 0 | 0 | -415.6661 | N | -786.0532 | kmcintyre@ercot.com | Contact e-mail | 28998.6179 | 28706.8792 | -0.05638 | 0.48825 | DS & RU
10 | 2011-01-21 03:46 | -0.171 | 40564.1572 | -0.15746 | 650 | 0 | 0 | 0 | -412.7947 | N | -650 | 63453 | Current Year's Actual Peak | 40462.4668 | 40291.4487 | -0.057333 | 2.758 | DS & TFR
11 | 2011-01-23 14:53 | -0.149 | 40566.6203 | -0.13588 | 403.7147 | 0 | 0 | 0 | -297.121 | N | -403.7147 | 75314 | Internal Generating Capacity | 31488.7808 | 31381.1364 | -0.051761 | 13.6434 | DS & CBA
12 | 2011-01-28 05:21 | -0.058 | 40571.2234 | -0.067804 | 311.4662 | 0 | 0 | 0 | -459.3635 | N | -311.4662 | 63783 | Next Year's Projected Peak | 32641.7061 | 32677.88 | -0.049999 | 11.1007 | DS & NL & PH
13 | 2011-01-29 22:29 | -0.122 | 40572.9371 | -0.12304 | 646.2125 | 0 | 113.9128 | 0 |  | Y |  |  |  | 27748.9937 | 27564.7109 | -0.052 | -19.9068 | DS & NL & RU
14 | 2011-02-01 22:28 | -0.078 | 40575.9359 | -0.081501 | 459.3271 | 0 | 0 | 0 | -563.5836 | N | -459.3271 |  |  | 51871.748 | 51739.0904 | -0.056 | 12.3255 | JOU DS & NL & TFR
15 | 2011-02-02 02:18 | -0.158 | 40576.0963 | -0.15479 | 716.9337 | 0 | 0 | 0 | -463.1797 | N | -716.9337 | 2011 | Current year | 49441.4014 | 49253.6618 | -0.058498 | 0.75019 | DS & NL & CBA
16 | 2011-02-02 05:39 | -0.125 | 40576.2356 | -0.11382 | 578.4939 | 0 | 0 | 0 | -508.2463 | N | -578.4939 | -286 | 2011 Frequency Response Obligation (FRO) | 52943.4199 | 52893.3103 | -0.0485 | 2.2301 | DS & NL & PH & RU
17 | 2011-02-02 08:24 | -0.188 | 40576.3503 | -0.16737 | 775.257 | 0 | 0 | 0 | -463.1868 | N | -775.257 |  |  | 52047.5054 | 51826.673 | -0.045 | 9.4779 | DS & NL & PH & TFR
18 | 2011-02-02 10:55 | -0.19 | 40576.4553 | -0.18746 | 840.8931 | 0 | 0 | 0 | -448.563 | N | -840.8931 | Summary Statistics |  | 52733.0312 | 52504.3354 | -0.037502 | 0.35531 | DS & NL & PH & CBA
19 | 2011-02-09 13:01 | -0.114 | 40583.5428 | -0.10509 | 598.686 | 0 | 17.3057 | 0 | -553.2228 | N | -581.3803 | -499.5585 | Average Frequency Response (MW/0.1Hz) | 50685.1836 | 50470.2879 | -0.047501 | 2.1707 | DS & NL & PH & RU & TFR
20 | 2011-02-15 16:40 | -0.216 | 40589.6945 | -0.20384 | 769.9818 | 0 | 0 | 0 | -377.741 | N | -769.9818 |  |  | 31612.45 | 31207.5229 | -0.0555 | 29.3821 | DS & NL & PH & RU & CBA
21 | 2011-02-16 09:25 | -0.197 | 40590.3928 | -0.17745 | 569.8584 | 0 | 0 | 0 | -321.1436 | N | -569.8584 | -33.7706 | Regression Estimate of Frequency Response (MW/0.1Hz) | 31135.6406 | 30972.9414 | -0.047 | 4.6014 | DS & NL & PH & RU & TFR & CBA
22 | 2011-03-03 11:17 | -0.094 | 40605.4705 | -0.097911 | 440.4526 | 0 | 0 | 0 | -449.8511 | N | -440.4526 |  |  | 31497.3516 | 31383.2949 | -0.06 | 1.5935 | NL & PH
23 | 2011-03-14 06:09 | -0.208 | 40616.2566 | -0.20521 | 970.6714 | 0 | 0 | 0 | -473.0054 | N | -970.6714 |  |  | 26752.5693 | 26452.9353 | -0.06 | 52.3709 | NL & RU
24 | 2011-03-14 07:08 | -0.127 | 40616.2974 | -0.12709 | 486.9663 | 0 | 0 | 0 | -383.1717 | N | -486.9663 |  |  | 29065.1851 | 29072.7718 | -0.051 | 33.9479 | NL & TFR
25 | 2011-03-16 20:45 | -0.074 | 40618.8647 | -0.088766 | 397.5629 | 0 | 0 | 0 | -447.8776 | N | -397.5629 |  |  | 33412.5537 | 33249.2561 | -0.1 | 100 | NL & CBA
26 | 2011-03-23 14:46 | -0.063 | 40625.6158 | -0.082465 | 621.1687 | 0 | 0 | 0 | -753.251 | N | -621.1687 |  |  | 38733.6201 | 38263.9715 |  |  | NL & PH & RU
27 | 2011-03-24 13:59 | -0.182 | 40626.5827 | -0.18584 | 498.3148 | 0 | 0 | 0 | -268.1437 | N | -498.3148 |  | Next Year's | 35353.7969 | 35176.6434 |  |  | NL & PH & TFR
28 | 2011-03-25 16:13 | -0.172 | 40627.676 | -0.18653 | 553.3828 | 0 | 66.7328 | 0 | -260.8899 | N | -486.65 | -286 | 2012 Frequency Response Obligation (FRO) | 40151.54 | 39958.5318 |  |  | NL & PH & BAA
29 | 2011-03-29 06:43 | -0.099 | 40631.2799 | -0.12293 | 742.8181 | 0 | 0 | 0 | -604.2672 | N | -742.8181 | -556.388 | 2012 Frequency Bias Setting - (minimum of FRM, next year's FRO, or 0.8% of Projected Peak [Load + Gen]/2) | 31093.9292 | 30933.7891 |  |  | NL & PH & RU & TFR
30 | 2011-03-31 12:21 | -0.112 | 40633.5149 | -0.11207 | 421.0469 | 0 | 0 | 0 | -375.6953 | N | -421.0469 |  |  | 31970.3716 | 31779.4676 |  | N | NL & PH & RU & CBA
31 | 2011-04-05 22:02 | -0.09 | 40638.9181 | -0.083248 | 518.4755 | 0 | 0 | 0 | -622.8058 | N | -518.4755 | -463.1868 | 2011 FRM - Median Frequency Response (MW/0.1Hz) | 30986.4536 | 30797.5086 |  | Y | NL & PH & RU & TFR & CBA
32 | 2011-04-20 13:40 | -0.145 | 40653.5701 | -0.16234 | 785.5412 | 0 | 0 | 0 | -483.8875 | N | -785.5412 |  |  | 41619.9902 | 41377.9392 |  |  | PH & RU
33 | 2011-04-27 23:27 | -0.133 | 40660.9771 | -0.13221 | 691.8045 | 0 | 0 | 0 | -523.2474 | N | -691.8045 |  |  | 29943.1245 | 29643.5089 |  |  | PH & TFR
34 | 2011-05-11 14:04 | -0.121 | 40674.5866 | -0.12648 | 726.0243 | 0 | 0 | 0 | -574.0275 | N | -726.0243 |  |  | 42265.9336 | 42054.1066 |  |  | PH & CBA
35 | 2011-05-16 08:06 | -0.101 | 40679.3379 | -0.11028 | 471.0875 | 0 | 0 | 0 | -427.1691 | N | -471.0875 |  |  | 30202.7422 | 30090.8742 |  |  | PH & RU & TFR
36 | 2011-05-19 14:08 | -0.197 | 40682.5888 | -0.22273 | 995.0827 | 0 | 0 | 0 | -446.7656 | N | -995.0827 |  |  | 42909.6079 | 42473.9933 |  |  | PH & RU & CBA
37 | 2011-05-23 17:34 | -0.092 | 40686.7324 | -0.11206 | 533.3253 | 0 | 0 | 0 | -475.9404 | N | -533.3253 |  |  | 50589.6709 | 50457.8744 |  |  | PH & TFR
38 | 2011-05-29 22:03 | -0.118 | 40692.9188 | -0.13286 | 762.3234 | 0 | 0.0075805 | 0 | -573.7889 | N | -762.3158 |  |  | 44769.7285 | 44439.2321 |  |  | PH & CBA
39 | 2011-06-22 13:18 | 0.08 | 40716.5546 | 0.036091 | -258.56 | 0 | 0 | 0 | -716.4197 | N | 258.56 |  |  | 44769.1958 | 44674.7623 |  |  | PH & RU & TFR
40 | 2011-06-27 12:54 | -0.149 | 40721.5375 | -0.14404 | 661.2317 | 0 | 0 | 0 | -459.0741 | N | -661.2317 |  |  | 56971.1396 | 56795.8538 |  |  | PH & RU & CBA
41 | 2011-07-18 09:13 | -0.097 | 40742.3842 | -0.095769 | 386.25 | 0 | 0 | 0 | -403.3157 | N | -386.25 |  |  | 45315.0059 | 45257.7578 |  |  | PH & TFR
42 | 2011-07-18 20:50 | -0.119 | 40742.8685 | -0.13323 | 596.1496 | 0 | 0 | 0 | -447.451 | N | -596.1496 |  |  | 57050.2559 | 56857.5725 |  |  | PH & CBA
PH & RU & TFR & CBA
RU & TFR
RU & CBA
RU & TFR & CBA
TFR & CBA
N
Y

## Data Entry1830 (hidden)
| Balancing Authority | ERCO |  | NERC FRS FORM 1 18 to 30 second Value B | [9 empty] | Information
Event | Date/Time |  | BA | BA | Value "A" Information |  | Value "B" Information |  | SEFRD | Exclude for |  |  |  | Value "A" | Value "B"
Number | (Central Prevailing) | DelFreq | Time | DelFreq | MW Lost | Adjustment | MW Lost | Adjustment | (MW/0.1Hz) | data error * | 0.8 |  |  | Load | Load
1 | 2010-12-06 11:25 | -0.101 | 40518.4763 | -0.10064 | 755.1125 | 0 | 0 | 0 | -750.2845 | N | -755.1125 |  |  | 35688.5645 | 35339.7472 | -0.057761 | 23.2467 | Dynamic schedules for joint-owned units (DS)
2 | 2010-12-09 17:34 | -0.074 | 40521.7321 | -0.10471 | 753.0677 | 0 | 0 | 0 | -719.1612 | N | -753.0677 |  |  | 34418.4287 | 34085.0898 | -0.066093 | 27.7016 | Nonconforming load (NL)
3 | 2010-12-11 23:38 | -0.166 | 40523.985 | -0.20027 | 821.1 | 0 | 0 | 0 | -409.9996 | N | -821.1 |  |  | 29590.7568 | 29362.8086 | -0.04024 | 10.6632 | Pumped hydro (PH)
4 | 2010-12-16 15:16 | -0.074 | 40528.6361 | -0.08541 | 617.0875 | 0 | 0 | 0 | -722.4993 | N | -617.0875 | 2012 | Bias Calculation Form Year | 31769.4482 | 31747.0725 | -0.052525 | 80.6609 | Ramping units (RU)
5 | 2010-12-19 02:39 | -0.111 | 40531.1106 | -0.12557 | 720.3267 | 0 | 0 | 0 | -573.6433 | N | -720.3267 | Texas | Interconnection | 30239.7212 | 30116.4506 | -0.070905 | -26.8976 | Xfred Frequency Response (TFR)
6 | 2010-12-26 08:23 | -0.066 | 40538.3556 | -0.053965 | 494.4381 | 0 | 0 | 0 | -916.2184 | N | -494.4381 | ERCO | Balancing Authority | 39597.9473 | 39175.5993 | -0.051907 | 9.9554 | Contingent BA adjustment for loss of units (CBA)
7 | 2011-01-09 18:52 | -0.108 | 40552.7861 | -0.111 | 575.2194 | 0 | 0 | 0 | -518.2204 | N | -575.2194 | Ken McIntyre | Contact Name | 40357.3638 | 40208.2556 | -0.058048 | 3.367 | DS & NL
8 | 2011-01-11 06:50 | -0.091 | 40554.2849 | -0.094786 | 456.8604 | 0 | 0 | 0 | -481.9899 | N | -456.8604 | 512-248-3969 | Contact Phone # | 48145.5186 | 48008.269 | -0.075572 | 36.3344 | DS & PH
9 | 2011-01-20 00:02 | -0.198 | 40563.0013 | -0.19768 | 786.0532 | 0 | 0 | 0 | -397.6422 | N | -786.0532 | kmcintyre@ercot.com | Contact e-mail | 28998.6179 | 28783.6582 | -0.05638 | 0.48825 | DS & RU
10 | 2011-01-21 03:46 | -0.171 | 40564.1572 | -0.16418 | 650 | 0 | 0 | 0 | -395.9138 | N | -650 | 63453 | Current Year's Actual Peak | 40462.4668 | 40274.2706 | -0.057333 | 2.758 | DS & TFR
11 | 2011-01-23 14:53 | -0.149 | 40566.6203 | -0.14473 | 403.7147 | 0 | 0 | 0 | -278.9371 | N | -403.7147 | 75314 | Internal Generating Capacity | 31488.7808 | 31467.2852 | -0.051761 | 13.6434 | DS & CBA
12 | 2011-01-28 05:21 | -0.058 | 40571.2234 | -0.065089 | 311.4662 | 0 | 0 | 0 | -478.5204 | N | -311.4662 | 63783 | Next Year's Projected Peak | 32641.7061 | 32692.8532 | -0.049999 | 11.1007 | DS & NL & PH
13 | 2011-01-29 22:29 | -0.122 | 40572.9371 | -0.12446 | 646.2125 | 0 | 113.8159 | 0 |  | Y |  |  |  | 27748.9937 | 27600.2771 | -0.052 | -19.9068 | DS & NL & RU
14 | 2011-02-01 22:28 | -0.078 | 40575.9359 | -0.078787 | 459.3271 | 0 | 0 | 0 | -583.0007 | N | -459.3271 |  |  | 51871.748 | 51716.8158 | -0.056 | 12.3255 | JOU DS & NL & TFR
15 | 2011-02-02 02:18 | -0.158 | 40576.0963 | -0.15379 | 716.9337 | 0 | 0 | 0 | -466.1915 | N | -716.9337 | 2011 | Current year | 49441.4014 | 49279.5268 | -0.058498 | 0.75019 | DS & NL & CBA
16 | 2011-02-02 05:39 | -0.125 | 40576.2356 | -0.11468 | 578.4939 | 0 | 0 | 0 | -504.4472 | N | -578.4939 | -286 | 2011 Frequency Response Obligation (FRO) | 52943.4199 | 52827.3566 | -0.0485 | 2.2301 | DS & NL & PH & RU
17 | 2011-02-02 08:24 | -0.188 | 40576.3503 | -0.17909 | 775.257 | 0 | 0 | 0 | -432.8919 | N | -775.257 |  |  | 52047.5054 | 51915.3705 | -0.045 | 9.4779 | DS & NL & PH & TFR
18 | 2011-02-02 10:55 | -0.19 | 40576.4553 | -0.18503 | 840.8931 | 0 | 0 | 0 | -454.4511 | N | -840.8931 | Summary Statistics |  | 52733.0312 | 52602.7729 | -0.037502 | 0.35531 | DS & NL & PH & CBA
19 | 2011-02-09 13:01 | -0.114 | 40583.5428 | -0.11066 | 598.686 | 0 | 17.2691 | 0 | -525.4045 | N | -581.417 | -517.5602 | Average Frequency Response (MW/0.1Hz) | 50685.1836 | 50564.4972 | -0.047501 | 2.1707 | DS & NL & PH & RU & TFR
20 | 2011-02-15 16:40 | -0.216 | 40589.6945 | -0.1997 | 769.9818 | 0 | 0 | 0 | -385.5763 | N | -769.9818 |  |  | 31612.45 | 31373.7377 | -0.0555 | 29.3821 | DS & NL & PH & RU & CBA
21 | 2011-02-16 09:25 | -0.197 | 40590.3928 | -0.1753 | 569.8584 | 0 | 0 | 0 | -325.068 | N | -569.8584 | -33.7706 | Regression Estimate of Frequency Response (MW/0.1Hz) | 31135.6406 | 30997.2439 | -0.047 | 4.6014 | DS & NL & PH & RU & TFR & CBA
22 | 2011-03-03 11:17 | -0.094 | 40605.4705 | -0.096197 | 440.4526 | 0 | 0 | 0 | -457.8659 | N | -440.4526 |  |  | 31497.3516 | 31421.3245 | -0.06 | 1.5935 | NL & PH
23 | 2011-03-14 06:09 | -0.208 | 40616.2566 | -0.20564 | 970.6714 | 0 | 0 | 0 | -472.0189 | N | -970.6714 |  |  | 26752.5693 | 26534.329 | -0.06 | 52.3709 | NL & RU
24 | 2011-03-14 07:08 | -0.127 | 40616.2974 | -0.12795 | 486.9663 | 0 | 0 | 0 | -380.6028 | N | -486.9663 |  |  | 29065.1851 | 29071.8895 | -0.051 | 33.9479 | NL & TFR
25 | 2011-03-16 20:45 | -0.074 | 40618.8647 | -0.079052 | 397.5629 | 0 | 0 | 0 | -502.9124 | N | -397.5629 |  |  | 33412.5537 | 33242.6055 | -0.1 | 100 | NL & CBA
26 | 2011-03-23 14:46 | -0.063 | 40625.6158 | -0.065036 | 621.1687 | 0 | 0 | 0 | -955.1119 | N | -621.1687 |  |  | 38733.6201 | 38265.808 |  |  | NL & PH & RU
27 | 2011-03-24 13:59 | -0.182 | 40626.5827 | -0.1757 | 498.3148 | 0 | 0 | 0 | -283.6234 | N | -498.3148 |  | Next Year's | 35353.7969 | 35214.6395 |  |  | NL & PH & TFR
28 | 2011-03-25 16:13 | -0.172 | 40627.676 | -0.17982 | 553.3828 | 0 | 66.8728 | 0 | -270.5528 | N | -486.51 | -286 | 2012 Frequency Response Obligation (FRO) | 40151.54 | 39985.1523 |  |  | NL & PH & BAA
29 | 2011-03-29 06:43 | -0.099 | 40631.2799 | -0.10064 | 742.8181 | 0 | 0 | 0 | -738.0702 | N | -742.8181 | -556.388 | 2012 Frequency Bias Setting - (minimum of FRM, next year's FRO, or 0.8% of Projected Peak [Load + Gen]/2) | 31093.9292 | 31019.3119 |  |  | NL & PH & RU & TFR
30 | 2011-03-31 12:21 | -0.112 | 40633.5149 | -0.11093 | 421.0469 | 0 | 0 | 0 | -379.5638 | N | -421.0469 |  |  | 31970.3716 | 31784.7109 |  | N | NL & PH & RU & CBA
31 | 2011-04-05 22:02 | -0.09 | 40638.9181 | -0.084392 | 518.4755 | 0 | 0 | 0 | -614.3682 | N | -518.4755 | -481.9899 | 2011 FRM - Median Frequency Response (MW/0.1Hz) | 30986.4536 | 30837.1769 |  | Y | NL & PH & RU & TFR & CBA
32 | 2011-04-20 13:40 | -0.145 | 40653.5701 | -0.14877 | 785.5412 | 0 | 0 | 0 | -528.029 | N | -785.5412 |  |  | 41619.9902 | 41434.293 |  |  | PH & RU
33 | 2011-04-27 23:27 | -0.133 | 40660.9771 | -0.1315 | 691.8045 | 0 | 0 | 0 | -526.088 | N | -691.8045 |  |  | 29943.1245 | 29684.8485 |  |  | PH & TFR
34 | 2011-05-11 14:04 | -0.121 | 40674.5866 | -0.11854 | 726.0243 | 0 | 0 | 0 | -612.449 | N | -726.0243 |  |  | 42265.9336 | 42103.4453 |  |  | PH & CBA
35 | 2011-05-16 08:06 | -0.101 | 40679.3379 | -0.10668 | 471.0875 | 0 | 0 | 0 | -441.6066 | N | -471.0875 |  |  | 30202.7422 | 30112.8644 |  |  | PH & RU & TFR
36 | 2011-05-19 14:08 | -0.197 | 40682.5888 | -0.20722 | 995.0827 | 0 | 0 | 0 | -480.1988 | N | -995.0827 |  |  | 42909.6079 | 42560.7667 |  |  | PH & RU & CBA
37 | 2011-05-23 17:34 | -0.092 | 40686.7324 | -0.10264 | 533.3253 | 0 | 0 | 0 | -519.6282 | N | -533.3253 |  |  | 50589.6709 | 50477.8532 |  |  | PH & TFR
38 | 2011-05-29 22:03 | -0.118 | 40692.9188 | -0.12257 | 762.3234 | 0 | 0 | 0 | -621.9416 | N | -762.3234 |  |  | 44769.7285 | 44479.8186 |  |  | PH & CBA
39 | 2011-06-22 13:18 | 0.08 | 40716.5546 | 0.033948 | -258.56 | 0 | 0 | 0 | -761.6397 | N | 258.56 |  |  | 44769.1958 | 44560.394 |  |  | PH & RU & TFR
40 | 2011-06-27 12:54 | -0.149 | 40721.5375 | -0.13661 | 661.2317 | 0 | 0 | 0 | -484.0371 | N | -661.2317 |  |  | 56971.1396 | 56805.8644 |  |  | PH & RU & CBA
41 | 2011-07-18 09:13 | -0.097 | 40742.3842 | -0.095198 | 386.25 | 0 | 0 | 0 | -405.7353 | N | -386.25 |  |  | 45315.0059 | 45274.106 |  |  | PH & TFR
42 | 2011-07-18 20:50 | -0.119 | 40742.8685 | -0.12852 | 596.1496 | 0 | 0 | 0 | -463.8648 | N | -596.1496 |  |  | 57050.2559 | 56872.1323 |  |  | PH & CBA
PH & RU & TFR & CBA
RU & TFR
RU & CBA
RU & TFR & CBA
TFR & CBA
N
Y

## Adjustments1830 (hidden)
| Balancing Authority | ERCO | JOU Dynamic Schedules |  | Non conforming Load |  | Pumped Hydro |  | Ramping Units |  | Transferred Frequency Response |  | Contingent BA Adjustment |  | Net Total Adjustments
Event | Date/Time |  | Value A | Value B | Value A | Value B | Value A | Value B | Value A | Value B | Value A | Value B | Value A | Value B | Value B 18 to 30 seconds
Number | (Central Prevailing) | DelFreq | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment
1 | 2010-12-06 11:25 | -0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2010-12-09 17:34 | -0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2010-12-11 23:38 | -0.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2010-12-16 15:16 | -0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2010-12-19 02:39 | -0.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2010-12-26 08:23 | -0.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2011-01-09 18:52 | -0.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2011-01-11 06:50 | -0.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2011-01-20 00:02 | -0.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2011-01-21 03:46 | -0.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2011-01-23 14:53 | -0.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2011-01-28 05:21 | -0.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 2011-01-29 22:29 | -0.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 2011-02-01 22:28 | -0.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 2011-02-02 02:18 | -0.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 2011-02-02 05:39 | -0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2011-02-02 08:24 | -0.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 2011-02-02 10:55 | -0.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 2011-02-09 13:01 | -0.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 2011-02-15 16:40 | -0.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 2011-02-16 09:25 | -0.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 2011-03-03 11:17 | -0.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 2011-03-14 06:09 | -0.208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2011-03-14 07:08 | -0.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 2011-03-16 20:45 | -0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 2011-03-23 14:46 | -0.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 2011-03-24 13:59 | -0.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 2011-03-25 16:13 | -0.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 2011-03-29 06:43 | -0.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 2011-03-31 12:21 | -0.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 2011-04-05 22:02 | -0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 2011-04-20 13:40 | -0.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 2011-04-27 23:27 | -0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 2011-05-11 14:04 | -0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 2011-05-23 17:34 | -0.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 2011-05-29 22:03 | -0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 2011-04-27 23:27 | -0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 2011-05-11 14:04 | -0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sign Convention for scan data collected in Form 2 |  | Imports: MWs are - Exports: MWs are + |  | Loads in MW as - |  | Load MW as - Generation MW as + |  | Enter Gen MW as + |  | The transactional amount in MW Receiver enters - Deliverer enters + on Form 2 Data sheet |  | Generation MW as + (If load occurs due to gen loss, enter MW as - at value B)
Notes:
| 1) | Balancing Authorities making adjustments must retain evidence to verify: - Adjustment values are determined from scan-cycle data using Value A and Value B averaging periods. Scan-cycle data must be available if adjustments are made. - Adjustments are necessary to improve accuracy of calculations compared to using Net Actual Interchange (contingency size for single BA interconnections) solely. Said differently, unless an adjustment compensates for significant known error, it should not be made. However, as noted in the next item, once a decision to include an adjustment for one or more of the six types is made for one event, the entity must calculate adjustments for that (those) type(s) for all events. - Adjustments are included consistently for all events (e.g. if adjustments for nonconforming load are made for one event, the load must be included for all events, etc.).
| 2) | Dynamic Schedules: - Values use schedule sign convention. - Adjustments should include only dynamic schedules accounting for joint-owned units. Other dynamic schedules should be ignored.
| 3) | Nonconforming Loads: - Values must be entered as negative numbers.
| 4) | Pumped Hydro: - Values for pumping must be entered as negative values. - Values for generating must be entered as positive values.
| 5) | Rampling Units: - Values are entered as positive values.
| 6) | Transferred Frequency Response: - This value is the amount agreed upon between the entities expressed in MW/0.1 Hz. Form 2 will adjust this amount for the frequency deviation experienced. (e.g. if an entity agrees to provide 20 MW/0.1 Hz to another entity and a frequency event with a deviation of 50 mHz occurs, the delivering entity should enter +20 in the data column of Form 2 and the receiving entity should enter - 20. The spreadsheet will adjust the SEFRD for each entity by the 10 for this event.) - Values for the entity receiving the response must be entered as a negative number. - Values for the entity delivering the response must be entered as a positive number. - Values between entities must sum to zero.
| 7) | Contingent Balancing Authority Adjustment: - Value for Value A is the pre-contingency generation from the contingent unit(s). - Value for Value B is usually 0 MW, but may be the load that remains on the system that was "netted" out by the now offline generation.

## Data Entry2040
| Balancing Authority | ERCO |  | NERC FRS FORM 1 20 to 40 second Value B | [9 empty] | Information
Event | Date/Time |  | BA | BA | Value "A" Information |  | Value "B" Information |  | SEFRD | Exclude for |  |  |  | Value "A" | Value "B"
Number | (Central Prevailing) | DelFreq | Time | DelFreq | MW Lost | Adjustment | MW Lost | Adjustment | (MW/0.1Hz) | data error * | 0.8 |  |  | Load | Load
1 | 2010-12-06 11:25 | -0.101 | 40518.4763 | -0.0975 | 755.1125 | 0 | 0 | 0 | -774.4725 | N | -755.1125 |  |  | 35688.5645 | 35410.9137 | -0.057761 | 23.2467 | Dynamic schedules for joint-owned units (DS)
2 | 2010-12-09 17:34 | -0.074 | 40521.7321 | -0.10518 | 753.0677 | 0 | 0 | 0 | -715.967 | N | -753.0677 |  |  | 34418.4287 | 34096.6463 | -0.066093 | 27.7016 | Nonconforming load (NL)
3 | 2010-12-11 23:38 | -0.166 | 40523.985 | -0.19985 | 821.1 | 0 | 0 | 0 | -410.8525 | N | -821.1 |  |  | 29590.7568 | 29391.6209 | -0.04024 | 10.6632 | Pumped hydro (PH)
4 | 2010-12-16 15:16 | -0.074 | 40528.6361 | -0.082579 | 617.0875 | 0 | 0 | 0 | -747.27 | N | -617.0875 | 2012 | Bias Calculation Form Year | 31769.4482 | 31745.2623 | -0.052525 | 80.6609 | Ramping units (RU)
5 | 2010-12-19 02:39 | -0.111 | 40531.1106 | -0.13273 | 720.3267 | 0 | 0 | 0 | -542.7146 | N | -720.3267 | Texas | Interconnection | 30239.7212 | 30120.0483 | -0.070905 | -26.8976 | Xfred Frequency Response (TFR)
6 | 2010-12-26 08:23 | -0.066 | 40538.3556 | -0.04716 | 494.4381 | 0 | 0 | 0 | -1048.4341 | N | -494.4381 | ERCO | Balancing Authority | 39597.9473 | 39181.9535 | -0.051907 | 9.9554 | Contingent BA adjustment for loss of units (CBA)
7 | 2011-01-09 18:52 | -0.108 | 40552.7861 | -0.10736 | 575.2194 | 0 | 0 | 0 | -535.7727 | N | -575.2194 | Ken McIntyre | Contact Name | 40357.3638 | 40236.1726 | -0.058048 | 3.367 | DS & NL
8 | 2011-01-11 06:50 | -0.091 | 40554.2849 | -0.094137 | 456.8604 | 0 | 0 | 0 | -485.3159 | N | -456.8604 | 512-248-3969 | Contact Phone # | 48145.5186 | 48020.9428 | -0.075572 | 36.3344 | DS & PH
9 | 2011-01-20 00:02 | -0.198 | 40563.0013 | -0.19579 | 786.0532 | 0 | 0 | 0 | -401.4676 | N | -786.0532 | kmcintyre@ercot.com | Contact e-mail | 28998.6179 | 28787.2116 | -0.05638 | 0.48825 | DS & RU
10 | 2011-01-21 03:46 | -0.171 | 40564.1572 | -0.16839 | 650 | 0 | 0 | 0 | -386.0197 | N | -650 | 63453 | Current Year's Actual Peak | 40462.4668 | 40282.1555 | -0.057333 | 2.758 | DS & TFR
11 | 2011-01-23 14:53 | -0.149 | 40566.6203 | -0.14669 | 403.7147 | 0 | 0 | 0 | -275.2089 | N | -403.7147 | 75314 | Internal Generating Capacity | 31488.7808 | 31481.4739 | -0.051761 | 13.6434 | DS & CBA
12 | 2011-01-28 05:21 | -0.058 | 40571.2234 | -0.061738 | 311.4662 | 0 | 0 | 0 | -504.4927 | N | -311.4662 | 63783 | Next Year's Projected Peak | 32641.7061 | 32700.5955 | -0.049999 | 11.1007 | DS & NL & PH
13 | 2011-01-29 22:29 | -0.122 | 40572.9371 | -0.12111 | 646.2125 | 0 | 203.7093 | 0 |  | Y |  |  |  | 27748.9937 | 27623.1301 | -0.052 | -19.9068 | DS & NL & RU
14 | 2011-02-01 22:28 | -0.078 | 40575.9359 | -0.079773 | 459.3271 | 0 | 0 | 0 | -575.7899 | N | -459.3271 |  |  | 51871.748 | 51712.3473 | -0.056 | 12.3255 | JOU DS & NL & TFR
15 | 2011-02-02 02:18 | -0.158 | 40576.0963 | -0.1565 | 716.9337 | 0 | 0 | 0 | -458.1059 | N | -716.9337 | 2011 | Current year | 49441.4014 | 49287.5707 | -0.058498 | 0.75019 | DS & NL & CBA
16 | 2011-02-02 05:39 | -0.125 | 40576.2356 | -0.1198 | 578.4939 | 0 | 0 | 0 | -482.9011 | N | -578.4939 | -286 | 2011 Frequency Response Obligation (FRO) | 52943.4199 | 52850.229 | -0.0485 | 2.2301 | DS & NL & PH & RU
17 | 2011-02-02 08:24 | -0.188 | 40576.3503 | -0.18519 | 775.257 | 0 | 0 | 0 | -418.6234 | N | -775.257 |  |  | 52047.5054 | 51925.9769 | -0.045 | 9.4779 | DS & NL & PH & TFR
18 | 2011-02-02 10:55 | -0.19 | 40576.4553 | -0.18757 | 840.8931 | 0 | 0 | 0 | -448.315 | N | -840.8931 | Summary Statistics |  | 52733.0312 | 52612.364 | -0.037502 | 0.35531 | DS & NL & PH & CBA
19 | 2011-02-09 13:01 | -0.114 | 40583.5428 | -0.11438 | 598.686 | 0 | 17.2524 | 0 | -508.3564 | N | -581.4337 | -523.1811 | Average Frequency Response (MW/0.1Hz) | 50685.1836 | 50612.092 | -0.047501 | 2.1707 | DS & NL & PH & RU & TFR
20 | 2011-02-15 16:40 | -0.216 | 40589.6945 | -0.20903 | 769.9818 | 0 | 0 | 0 | -368.3526 | N | -769.9818 |  |  | 31612.45 | 31367.8141 | -0.0555 | 29.3821 | DS & NL & PH & RU & CBA
21 | 2011-02-16 09:25 | -0.197 | 40590.3928 | -0.17488 | 569.8584 | 0 | 0 | 0 | -325.8651 | N | -569.8584 | -33.7706 | Regression Estimate of Frequency Response (MW/0.1Hz) | 31135.6406 | 31008.921 | -0.047 | 4.6014 | DS & NL & PH & RU & TFR & CBA
22 | 2011-03-03 11:17 | -0.094 | 40605.4705 | -0.095262 | 440.4526 | 0 | 0 | 0 | -462.3608 | N | -440.4526 |  |  | 31497.3516 | 31438.8647 | -0.06 | 1.5935 | NL & PH
23 | 2011-03-14 06:09 | -0.208 | 40616.2566 | -0.20668 | 970.6714 | 0 | 0 | 0 | -469.6455 | N | -970.6714 |  |  | 26752.5693 | 26582.445 | -0.06 | 52.3709 | NL & RU
24 | 2011-03-14 07:08 | -0.127 | 40616.2974 | -0.12828 | 486.9663 | 0 | 0 | 0 | -379.5998 | N | -486.9663 |  |  | 29065.1851 | 29079.8132 | -0.051 | 33.9479 | NL & TFR
25 | 2011-03-16 20:45 | -0.074 | 40618.8647 | -0.078533 | 397.5629 | 0 | 0 | 0 | -506.2395 | N | -397.5629 |  |  | 33412.5537 | 33251.9169 | -0.1 | 100 | NL & CBA
26 | 2011-03-23 14:46 | -0.063 | 40625.6158 | -0.064477 | 621.1687 | 0 | 0 | 0 | -963.3899 | N | -621.1687 |  |  | 38733.6201 | 38253.6957 |  |  | NL & PH & RU
27 | 2011-03-24 13:59 | -0.182 | 40626.5827 | -0.17449 | 498.3148 | 0 | 0 | 0 | -285.5865 | N | -498.3148 |  | Next Year's | 35353.7969 | 35226.4599 |  |  | NL & PH & TFR
28 | 2011-03-25 16:13 | -0.172 | 40627.676 | -0.17352 | 553.3828 | 0 | 67.0127 | 0 | -280.2929 | N | -486.3701 | -286 | 2012 Frequency Response Obligation (FRO) | 40151.54 | 39984.1218 |  |  | NL & PH & BAA
29 | 2011-03-29 06:43 | -0.099 | 40631.2799 | -0.10095 | 742.8181 | 0 | 0 | 0 | -735.7938 | N | -742.8181 | -556.388 | 2012 Frequency Bias Setting - (minimum of FRM, next year's FRO, or 0.8% of Projected Peak [Load + Gen]/2) | 31093.9292 | 31034.6021 |  |  | NL & PH & RU & TFR
30 | 2011-03-31 12:21 | -0.112 | 40633.5149 | -0.11314 | 421.0469 | 0 | 0 | 0 | -372.1574 | N | -421.0469 |  |  | 31970.3716 | 31784.3129 |  | N | NL & PH & RU & CBA
31 | 2011-04-05 22:02 | -0.09 | 40638.9181 | -0.086522 | 518.4755 | 0 | 0 | 0 | -599.2426 | N | -518.4755 | -497.7586 | 2011 FRM - Median Frequency Response (MW/0.1Hz) | 30986.4536 | 30850.3342 |  | Y | NL & PH & RU & TFR & CBA
32 | 2011-04-20 13:40 | -0.145 | 40653.5701 | -0.14717 | 785.5412 | 0 | 0 | 0 | -533.7589 | N | -785.5412 |  |  | 41619.9902 | 41449.7543 |  |  | PH & RU
33 | 2011-04-27 23:27 | -0.133 | 40660.9771 | -0.1325 | 691.8045 | 0 | 0 | 0 | -522.1183 | N | -691.8045 |  |  | 29943.1245 | 29706.4893 |  |  | PH & TFR
34 | 2011-05-11 14:04 | -0.121 | 40674.5866 | -0.1213 | 726.0243 | 0 | 0 | 0 | -598.5237 | N | -726.0243 |  |  | 42265.9336 | 42114.0866 |  |  | PH & CBA
35 | 2011-05-16 08:06 | -0.101 | 40679.3379 | -0.10319 | 471.0875 | 0 | 0 | 0 | -456.5152 | N | -471.0875 |  |  | 30202.7422 | 30124.5707 |  |  | PH & RU & TFR
36 | 2011-05-19 14:08 | -0.197 | 40682.5888 | -0.19982 | 995.0827 | 0 | 0 | 0 | -498.0014 | N | -995.0827 |  |  | 42909.6079 | 42598.7379 |  |  | PH & RU & CBA
37 | 2011-05-23 17:34 | -0.092 | 40686.7324 | -0.096525 | 533.3253 | 0 | 0 | 0 | -552.5239 | N | -533.3253 |  |  | 50589.6709 | 50481.6939 |  |  | PH & TFR
38 | 2011-05-29 22:03 | -0.118 | 40692.9188 | -0.11745 | 762.3234 | 0 | 0 | 0 | -649.0375 | N | -762.3234 |  |  | 44769.7285 | 44483.343 |  |  | PH & CBA
39 | 2011-06-22 13:18 | 0.08 | 40716.5546 | 0.032648 | -258.56 | 0 | 0 | 0 | -791.9522 | N | 258.56 |  |  | 44769.1958 | 44477.2418 |  |  | PH & RU & TFR
40 | 2011-06-27 12:54 | -0.149 | 40721.5375 | -0.13284 | 661.2317 | 0 | 0 | 0 | -497.7586 | N | -661.2317 |  |  | 56971.1396 | 56824.3253 |  |  | PH & RU & CBA
41 | 2011-07-18 09:13 | -0.097 | 40742.3842 | -0.092717 | 386.25 | 0 | 0 | 0 | -416.5903 | N | -386.25 |  |  | 45315.0059 | 45285.6325 |  |  | PH & TFR
42 | 2011-07-18 20:50 | -0.119 | 40742.8685 | -0.12819 | 596.1496 | 0 | 0 | 0 | -465.0404 | N | -596.1496 |  |  | 57050.2559 | 56878.6644 |  |  | PH & CBA
PH & RU & TFR & CBA
RU & TFR
RU & CBA
RU & TFR & CBA
TFR & CBA
N
Y

## Adjustments2040 (hidden)
| Balancing Authority | ERCO | JOU Dynamic Schedules |  | Non conforming Load |  | Pumped Hydro |  | Ramping Units |  | Transferred Frequency Response |  | Contingent BA Adjustment |  | Net Total Adjustments
Event | Date/Time |  | Value A | Value B | Value A | Value B | Value A | Value B | Value A | Value B | Value A | Value B | Value A | Value B | Value B 20 to 40 seconds
Number | (Central Prevailing) | DelFreq | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment
1 | 2010-12-06 11:25 | -0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2010-12-09 17:34 | -0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2010-12-11 23:38 | -0.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2010-12-16 15:16 | -0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2010-12-19 02:39 | -0.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2010-12-26 08:23 | -0.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2011-01-09 18:52 | -0.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2011-01-11 06:50 | -0.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2011-01-20 00:02 | -0.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2011-01-21 03:46 | -0.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2011-01-23 14:53 | -0.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2011-01-28 05:21 | -0.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 2011-01-29 22:29 | -0.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 2011-02-01 22:28 | -0.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 2011-02-02 02:18 | -0.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 2011-02-02 05:39 | -0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2011-02-02 08:24 | -0.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 2011-02-02 10:55 | -0.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 2011-02-09 13:01 | -0.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 2011-02-15 16:40 | -0.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 2011-02-16 09:25 | -0.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 2011-03-03 11:17 | -0.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 2011-03-14 06:09 | -0.208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2011-03-14 07:08 | -0.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 2011-03-16 20:45 | -0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 2011-03-23 14:46 | -0.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 2011-03-24 13:59 | -0.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 2011-03-25 16:13 | -0.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 2011-03-29 06:43 | -0.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 2011-03-31 12:21 | -0.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 2011-04-05 22:02 | -0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 2011-04-20 13:40 | -0.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 2011-04-27 23:27 | -0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 2011-05-11 14:04 | -0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 2011-05-23 17:34 | -0.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 2011-05-29 22:03 | -0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 2011-04-27 23:27 | -0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 2011-05-11 14:04 | -0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sign Convention for scan data collected in Form 2 |  | Imports: MWs are - Exports: MWs are + |  | Loads in MW as - |  | Load MW as - Generation MW as + |  | Enter Gen MW as + |  | The transactional amount in MW Receiver enters - Deliverer enters + on Form 2 Data sheet |  | Generation MW as + (If load occurs due to gen loss, enter MW as - at value B)
Notes:
| 1) | Balancing Authorities making adjustments must retain evidence to verify: - Adjustment values are determined from scan-cycle data using Value A and Value B averaging periods. Scan-cycle data must be available if adjustments are made. - Adjustments are necessary to improve accuracy of calculations compared to using Net Actual Interchange (contingency size for single BA interconnections) solely. Said differently, unless an adjustment compensates for significant known error, it should not be made. However, as noted in the next item, once a decision to include an adjustment for one or more of the six types is made for one event, the entity must calculate adjustments for that (those) type(s) for all events. - Adjustments are included consistently for all events (e.g. if adjustments for nonconforming load are made for one event, the load must be included for all events, etc.).
| 2) | Dynamic Schedules: - Values use schedule sign convention. - Adjustments should include only dynamic schedules accounting for joint-owned units. Other dynamic schedules should be ignored.
| 3) | Nonconforming Loads: - Values must be entered as negative numbers.
| 4) | Pumped Hydro: - Values for pumping must be entered as negative values. - Values for generating must be entered as positive values.
| 5) | Rampling Units: - Values are entered as positive values.
| 6) | Transferred Frequency Response: - This value is the amount agreed upon between the entities expressed in MW/0.1 Hz. Form 2 will adjust this amount for the frequency deviation experienced. (e.g. if an entity agrees to provide 20 MW/0.1 Hz to another entity and a frequency event with a deviation of 50 mHz occurs, the delivering entity should enter +20 in the data column of Form 2 and the receiving entity should enter - 20. The spreadsheet will adjust the SEFRD for each entity by the 10 for this event.) - Values for the entity receiving the response must be entered as a negative number. - Values for the entity delivering the response must be entered as a positive number. - Values between entities must sum to zero.
| 7) | Contingent Balancing Authority Adjustment: - Value for Value A is the pre-contingency generation from the contingent unit(s). - Value for Value B is usually 0 MW, but may be the load that remains on the system that was "netted" out by the now offline generation.

## Data Entry1852
| Balancing Authority | ERCO |  | NERC FRS FORM 1 18 to 52 second Value B | [9 empty] | Information
Event | Date/Time |  | BA | BA | Value "A" Information |  | Value "B" Information |  | SEFRD | Exclude for |  |  |  | Value "A" | Value "B"
Number | (Central Prevailing) | DelFreq | Time | DelFreq | MW Lost | Adjustment | MW Lost | Adjustment | (MW/0.1Hz) | data error * | 0.8 |  |  | Load | Load
1 | 2010-12-06 11:25 | -0.101 | 40518.4763 | -0.095222 | 755.1125 | 0 | 0 | 0 | -792.9987 | N | -755.1125 |  |  | 35688.5645 | 35459.2561 | -0.057761 | 23.2467 | Dynamic schedules for joint-owned units (DS)
2 | 2010-12-09 17:34 | -0.074 | 40521.7321 | -0.10717 | 753.0677 | 0 | 0 | 0 | -702.7078 | N | -753.0677 |  |  | 34418.4287 | 34109.5052 | -0.066093 | 27.7016 | Nonconforming load (NL)
3 | 2010-12-11 23:38 | -0.166 | 40523.985 | -0.19801 | 821.1 | 0 | 0 | 0 | -414.6667 | N | -821.1 |  |  | 29590.7568 | 29398.6697 | -0.04024 | 10.6632 | Pumped hydro (PH)
4 | 2010-12-16 15:16 | -0.074 | 40528.6361 | -0.078347 | 617.0875 | 0 | 0 | 0 | -787.6382 | N | -617.0875 | 2012 | Bias Calculation Form Year | 31769.4482 | 31741.8678 | -0.052525 | 80.6609 | Ramping units (RU)
5 | 2010-12-19 02:39 | -0.111 | 40531.1106 | -0.13161 | 720.3267 | 0 | 0 | 0 | -547.3171 | N | -720.3267 | Texas | Interconnection | 30239.7212 | 30135.6774 | -0.070905 | -26.8976 | Xfred Frequency Response (TFR)
6 | 2010-12-26 08:23 | -0.066 | 40538.3556 | -0.04064 | 494.4381 | 0 | 0 | 0 | -1216.6439 | N | -494.4381 | ERCO | Balancing Authority | 39597.9473 | 39184.2808 | -0.051907 | 9.9554 | Contingent BA adjustment for loss of units (CBA)
7 | 2011-01-09 18:52 | -0.108 | 40552.7861 | -0.10811 | 575.2194 | 0 | 0 | 0 | -532.0675 | N | -575.2194 | Ken McIntyre | Contact Name | 40357.3638 | 40275.8123 | -0.058048 | 3.367 | DS & NL
8 | 2011-01-11 06:50 | -0.091 | 40554.2849 | -0.091667 | 456.8604 | 0 | 0 | 0 | -498.3896 | N | -456.8604 | 512-248-3969 | Contact Phone # | 48145.5186 | 48065.0161 | -0.075572 | 36.3344 | DS & PH
9 | 2011-01-20 00:02 | -0.198 | 40563.0013 | -0.19703 | 786.0532 | 0 | 0 | 0 | -398.9559 | N | -786.0532 | kmcintyre@ercot.com | Contact e-mail | 28998.6179 | 28794.4275 | -0.05638 | 0.48825 | DS & RU
10 | 2011-01-21 03:46 | -0.171 | 40564.1572 | -0.17047 | 650 | 0 | 0 | 0 | -381.2974 | N | -650 | 63453 | Current Year's Actual Peak | 40462.4668 | 40290.967 | -0.057333 | 2.758 | DS & TFR
11 | 2011-01-23 14:53 | -0.149 | 40566.6203 | -0.14815 | 403.7147 | 0 | 0 | 0 | -272.4976 | N | -403.7147 | 75314 | Internal Generating Capacity | 31488.7808 | 31481.7595 | -0.051761 | 13.6434 | DS & CBA
12 | 2011-01-28 05:21 | -0.058 | 40571.2234 | -0.056653 | 311.4662 | 0 | 0 | 0 | -549.7822 | N | -311.4662 | 63783 | Next Year's Projected Peak | 32641.7061 | 32710.6393 | -0.049999 | 11.1007 | DS & NL & PH
13 | 2011-01-29 22:29 | -0.122 | 40572.9371 | -0.084583 | 646.2125 | 0 | 338.136 | 0 |  | Y |  |  |  | 27748.9937 | 27719.212 | -0.052 | -19.9068 | DS & NL & RU
14 | 2011-02-01 22:28 | -0.078 | 40575.9359 | -0.078112 | 459.3271 | 0 | 0 | 0 | -588.04 | N | -459.3271 |  |  | 51871.748 | 51714.5777 | -0.056 | 12.3255 | JOU DS & NL & TFR
15 | 2011-02-02 02:18 | -0.158 | 40576.0963 | -0.15833 | 716.9337 | 0 | 0 | 0 | -452.8012 | N | -716.9337 | 2011 | Current year | 49441.4014 | 49289.5894 | -0.058498 | 0.75019 | DS & NL & CBA
16 | 2011-02-02 05:39 | -0.125 | 40576.2356 | -0.12325 | 578.4939 | 0 | 0 | 0 | -469.3658 | N | -578.4939 | -286 | 2011 Frequency Response Obligation (FRO) | 52943.4199 | 52861.151 | -0.0485 | 2.2301 | DS & NL & PH & RU
17 | 2011-02-02 08:24 | -0.188 | 40576.3503 | -0.18565 | 775.257 | 0 | 0 | 0 | -417.5864 | N | -775.257 |  |  | 52047.5054 | 51915.5757 | -0.045 | 9.4779 | DS & NL & PH & TFR
18 | 2011-02-02 10:55 | -0.19 | 40576.4553 | -0.18914 | 840.8931 | 0 | 0 | 0 | -444.5914 | N | -840.8931 | Summary Statistics |  | 52733.0312 | 52601.4974 | -0.037502 | 0.35531 | DS & NL & PH & CBA
19 | 2011-02-09 13:01 | -0.114 | 40583.5428 | -0.11338 | 598.686 | 0 | 11.5059 | 0 | -517.9091 | N | -587.1801 | -532.0167 | Average Frequency Response (MW/0.1Hz) | 50685.1836 | 50613.5269 | -0.047501 | 2.1707 | DS & NL & PH & RU & TFR
20 | 2011-02-15 16:40 | -0.216 | 40589.6945 | -0.21507 | 769.9818 | 0 | 0 | 0 | -358.016 | N | -769.9818 |  |  | 31612.45 | 31388.4785 | -0.0555 | 29.3821 | DS & NL & PH & RU & CBA
21 | 2011-02-16 09:25 | -0.197 | 40590.3928 | -0.17549 | 569.8584 | 0 | 0 | 0 | -324.7306 | N | -569.8584 | -33.7706 | Regression Estimate of Frequency Response (MW/0.1Hz) | 31135.6406 | 31018.523 | -0.047 | 4.6014 | DS & NL & PH & RU & TFR & CBA
22 | 2011-03-03 11:17 | -0.094 | 40605.4705 | -0.094348 | 440.4526 | 0 | 0 | 0 | -466.8401 | N | -440.4526 |  |  | 31497.3516 | 31440.8917 | -0.06 | 1.5935 | NL & PH
23 | 2011-03-14 06:09 | -0.208 | 40616.2566 | -0.20783 | 970.6714 | 0 | 0 | 0 | -467.0441 | N | -970.6714 |  |  | 26752.5693 | 26588.3353 | -0.06 | 52.3709 | NL & RU
24 | 2011-03-14 07:08 | -0.127 | 40616.2974 | -0.12726 | 486.9663 | 0 | 0 | 0 | -382.6431 | N | -486.9663 |  |  | 29065.1851 | 29087.1309 | -0.051 | 33.9479 | NL & TFR
25 | 2011-03-16 20:45 | -0.074 | 40618.8647 | -0.074068 | 397.5629 | 0 | 0 | 0 | -536.7511 | N | -397.5629 |  |  | 33412.5537 | 33257.7374 | -0.1 | 100 | NL & CBA
26 | 2011-03-23 14:46 | -0.063 | 40625.6158 | -0.062917 | 621.1687 | 0 | 0 | 0 | -987.285 | N | -621.1687 |  |  | 38733.6201 | 38257.7561 |  |  | NL & PH & RU
27 | 2011-03-24 13:59 | -0.182 | 40626.5827 | -0.17762 | 498.3148 | 0 | 0 | 0 | -280.5435 | N | -498.3148 |  | Next Year's | 35353.7969 | 35238.0857 |  |  | NL & PH & TFR
28 | 2011-03-25 16:13 | -0.172 | 40627.676 | -0.1693 | 553.3828 | 0 | 67.0333 | 0 | -287.2628 | N | -486.3495 | -286 | 2012 Frequency Response Obligation (FRO) | 40151.54 | 39989.8819 |  |  | NL & PH & BAA
29 | 2011-03-29 06:43 | -0.099 | 40631.2799 | -0.10028 | 742.8181 | 0 | 0 | 0 | -740.7611 | N | -742.8181 | -556.388 | 2012 Frequency Bias Setting - (minimum of FRM, next year's FRO, or 0.8% of Projected Peak [Load + Gen]/2) | 31093.9292 | 31031.3079 |  |  | NL & PH & RU & TFR
30 | 2011-03-31 12:21 | -0.112 | 40633.5149 | -0.11178 | 421.0469 | 0 | 0 | 0 | -376.681 | N | -421.0469 |  |  | 31970.3716 | 31774.7697 |  | N | NL & PH & RU & CBA
31 | 2011-04-05 22:02 | -0.09 | 40638.9181 | -0.088749 | 518.4755 | 0 | 0 | 0 | -584.203 | N | -518.4755 | -501.627 | 2011 FRM - Median Frequency Response (MW/0.1Hz) | 30986.4536 | 30845.3815 |  | Y | NL & PH & RU & TFR & CBA
32 | 2011-04-20 13:40 | -0.145 | 40653.5701 | -0.14579 | 785.5412 | 0 | 0 | 0 | -538.8071 | N | -785.5412 |  |  | 41619.9902 | 41460.3151 |  |  | PH & RU
33 | 2011-04-27 23:27 | -0.133 | 40660.9771 | -0.13255 | 691.8045 | 0 | 0 | 0 | -521.901 | N | -691.8045 |  |  | 29943.1245 | 29700.7563 |  |  | PH & TFR
34 | 2011-05-11 14:04 | -0.121 | 40674.5866 | -0.12122 | 726.0243 | 0 | 0 | 0 | -598.9475 | N | -726.0243 |  |  | 42265.9336 | 42111.5734 |  |  | PH & CBA
35 | 2011-05-16 08:06 | -0.101 | 40679.3379 | -0.10189 | 471.0875 | 0 | 0 | 0 | -462.3408 | N | -471.0875 |  |  | 30202.7422 | 30134.4171 |  |  | PH & RU & TFR
36 | 2011-05-19 14:08 | -0.197 | 40682.5888 | -0.19837 | 995.0827 | 0 | 0 | 0 | -501.627 | N | -995.0827 |  |  | 42909.6079 | 42602.5289 |  |  | PH & RU & CBA
37 | 2011-05-23 17:34 | -0.092 | 40686.7324 | -0.093175 | 533.3253 | 0 | 0 | 0 | -572.3939 | N | -533.3253 |  |  | 50589.6709 | 50486.375 |  |  | PH & TFR
38 | 2011-05-29 22:03 | -0.118 | 40692.9188 | -0.11872 | 762.3234 | 0 | 0 | 0 | -642.1082 | N | -762.3234 |  |  | 44769.7285 | 44476.4353 |  |  | PH & CBA
39 | 2011-06-22 13:18 | 0.08 | 40716.5546 | 0.031542 | -258.56 | 0 | 0 | 0 | -819.726 | N | 258.56 |  |  | 44769.1958 | 44473.3103 |  |  | PH & RU & TFR
40 | 2011-06-27 12:54 | -0.149 | 40721.5375 | -0.13181 | 661.2317 | 0 | 0 | 0 | -501.6704 | N | -661.2317 |  |  | 56971.1396 | 56831.1452 |  |  | PH & RU & CBA
41 | 2011-07-18 09:13 | -0.097 | 40742.3842 | -0.094403 | 386.25 | 0 | 0 | 0 | -409.1481 | N | -386.25 |  |  | 45315.0059 | 45294.8707 |  |  | PH & TFR
42 | 2011-07-18 20:50 | -0.119 | 40742.8685 | -0.12793 | 596.1496 | 0 | 0 | 0 | -465.9948 | N | -596.1496 |  |  | 57050.2559 | 56882.8589 |  |  | PH & CBA
PH & RU & TFR & CBA
RU & TFR
RU & CBA
RU & TFR & CBA
TFR & CBA
N
Y

## Adjustments1852 (hidden)
| Balancing Authority | ERCO | JOU Dynamic Schedules |  | Non conforming Load |  | Pumped Hydro |  | Ramping Units |  | Transferred Frequency Response |  | Contingent BA Adjustment |  | Net Total Adjustments
Event | Date/Time |  | Value A | Value B | Value A | Value B | Value A | Value B | Value A | Value B | Value A | Value B | Value A | Value B | Value B 18 to 52 seconds
Number | (Central Prevailing) | DelFreq | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment
1 | 2010-12-06 11:25 | -0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2010-12-09 17:34 | -0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2010-12-11 23:38 | -0.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2010-12-16 15:16 | -0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2010-12-19 02:39 | -0.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2010-12-26 08:23 | -0.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2011-01-09 18:52 | -0.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2011-01-11 06:50 | -0.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2011-01-20 00:02 | -0.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2011-01-21 03:46 | -0.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2011-01-23 14:53 | -0.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2011-01-28 05:21 | -0.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 2011-01-29 22:29 | -0.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 2011-02-01 22:28 | -0.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 2011-02-02 02:18 | -0.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 2011-02-02 05:39 | -0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2011-02-02 08:24 | -0.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 2011-02-02 10:55 | -0.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 2011-02-09 13:01 | -0.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 2011-02-15 16:40 | -0.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 2011-02-16 09:25 | -0.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 2011-03-03 11:17 | -0.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 2011-03-14 06:09 | -0.208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2011-03-14 07:08 | -0.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 2011-03-16 20:45 | -0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 2011-03-23 14:46 | -0.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 2011-03-24 13:59 | -0.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 2011-03-25 16:13 | -0.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 2011-03-29 06:43 | -0.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 2011-03-31 12:21 | -0.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 2011-04-05 22:02 | -0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 2011-04-20 13:40 | -0.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 2011-04-27 23:27 | -0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 2011-05-11 14:04 | -0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 2011-05-23 17:34 | -0.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 2011-05-29 22:03 | -0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 2011-04-27 23:27 | -0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 2011-05-11 14:04 | -0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sign Convention for scan data collected in Form 2 |  | Imports: MWs are - Exports: MWs are + |  | Loads in MW as - |  | Load MW as - Generation MW as + |  | Enter Gen MW as + |  | The transactional amount in MW Receiver enters - Deliverer enters + on Form 2 Data sheet |  | Generation MW as + (If load occurs due to gen loss, enter MW as - at value B)
Notes:
| 1) | Balancing Authorities making adjustments must retain evidence to verify: - Adjustment values are determined from scan-cycle data using Value A and Value B averaging periods. Scan-cycle data must be available if adjustments are made. - Adjustments are necessary to improve accuracy of calculations compared to using Net Actual Interchange (contingency size for single BA interconnections) solely. Said differently, unless an adjustment compensates for significant known error, it should not be made. However, as noted in the next item, once a decision to include an adjustment for one or more of the six types is made for one event, the entity must calculate adjustments for that (those) type(s) for all events. - Adjustments are included consistently for all events (e.g. if adjustments for nonconforming load are made for one event, the load must be included for all events, etc.).
| 2) | Dynamic Schedules: - Values use schedule sign convention. - Adjustments should include only dynamic schedules accounting for joint-owned units. Other dynamic schedules should be ignored.
| 3) | Nonconforming Loads: - Values must be entered as negative numbers.
| 4) | Pumped Hydro: - Values for pumping must be entered as negative values. - Values for generating must be entered as positive values.
| 5) | Rampling Units: - Values are entered as positive values.
| 6) | Transferred Frequency Response: - This value is the amount agreed upon between the entities expressed in MW/0.1 Hz. Form 2 will adjust this amount for the frequency deviation experienced. (e.g. if an entity agrees to provide 20 MW/0.1 Hz to another entity and a frequency event with a deviation of 50 mHz occurs, the delivering entity should enter +20 in the data column of Form 2 and the receiving entity should enter - 20. The spreadsheet will adjust the SEFRD for each entity by the 10 for this event.) - Values for the entity receiving the response must be entered as a negative number. - Values for the entity delivering the response must be entered as a positive number. - Values between entities must sum to zero.
| 7) | Contingent Balancing Authority Adjustment: - Value for Value A is the pre-contingency generation from the contingent unit(s). - Value for Value B is usually 0 MW, but may be the load that remains on the system that was "netted" out by the now offline generation.

## Data Entry2052 (hidden)
| Balancing Authority | ERCO |  | NERC FRS FORM 1 20 to 52 second Value B | [9 empty] | Information
Event | Date/Time |  | BA | BA | Value "A" Information |  | Value "B" Information |  | SEFRD | Exclude for |  |  |  | Value "A" | Value "B"
Number | (Central Prevailing) | DelFreq | Time | DelFreq | MW Lost | Adjustment | MW Lost | Adjustment | (MW/0.1Hz) | data error * | 0.8 |  |  | Load | Load
1 | 2010-12-06 11:25 | -0.101 | 40518.4763 | -0.094618 | 755.1125 | 0 | 0 | 0 | -798.0659 | N | -755.1125 |  |  | 35688.5645 | 35469.9483 | -0.057761 | 23.2467 | Dynamic schedules for joint-owned units (DS)
2 | 2010-12-09 17:34 | -0.074 | 40521.7321 | -0.10712 | 753.0677 | 0 | 0 | 0 | -703.0295 | N | -753.0677 |  |  | 34418.4287 | 34111.3336 | -0.066093 | 27.7016 | Nonconforming load (NL)
3 | 2010-12-11 23:38 | -0.166 | 40523.985 | -0.1983 | 821.1 | 0 | 0 | 0 | -414.0653 | N | -821.1 |  |  | 29590.7568 | 29402.9971 | -0.04024 | 10.6632 | Pumped hydro (PH)
4 | 2010-12-16 15:16 | -0.074 | 40528.6361 | -0.078242 | 617.0875 | 0 | 0 | 0 | -788.6901 | N | -617.0875 | 2012 | Bias Calculation Form Year | 31769.4482 | 31741.0732 | -0.052525 | 80.6609 | Ramping units (RU)
5 | 2010-12-19 02:39 | -0.111 | 40531.1106 | -0.133 | 720.3267 | 0 | 0 | 0 | -541.6013 | N | -720.3267 | Texas | Interconnection | 30239.7212 | 30135.1519 | -0.070905 | -26.8976 | Xfred Frequency Response (TFR)
6 | 2010-12-26 08:23 | -0.066 | 40538.3556 | -0.039486 | 494.4381 | 0 | 0 | 0 | -1252.1906 | N | -494.4381 | ERCO | Balancing Authority | 39597.9473 | 39185.6239 | -0.051907 | 9.9554 | Contingent BA adjustment for loss of units (CBA)
7 | 2011-01-09 18:52 | -0.108 | 40552.7861 | -0.10753 | 575.2194 | 0 | 0 | 0 | -534.9461 | N | -575.2194 | Ken McIntyre | Contact Name | 40357.3638 | 40269.5131 | -0.058048 | 3.367 | DS & NL
8 | 2011-01-11 06:50 | -0.091 | 40554.2849 | -0.091383 | 456.8604 | 0 | 0 | 0 | -499.9406 | N | -456.8604 | 512-248-3969 | Contact Phone # | 48145.5186 | 48054.1854 | -0.075572 | 36.3344 | DS & PH
9 | 2011-01-20 00:02 | -0.198 | 40563.0013 | -0.19778 | 786.0532 | 0 | 0 | 0 | -397.4399 | N | -786.0532 | kmcintyre@ercot.com | Contact e-mail | 28998.6179 | 28794.6882 | -0.05638 | 0.48825 | DS & RU
10 | 2011-01-21 03:46 | -0.171 | 40564.1572 | -0.17122 | 650 | 0 | 0 | 0 | -379.6307 | N | -650 | 63453 | Current Year's Actual Peak | 40462.4668 | 40291.5407 | -0.057333 | 2.758 | DS & TFR
11 | 2011-01-23 14:53 | -0.149 | 40566.6203 | -0.14864 | 403.7147 | 0 | 0 | 0 | -271.6049 | N | -403.7147 | 75314 | Internal Generating Capacity | 31488.7808 | 31483.8087 | -0.051761 | 13.6434 | DS & CBA
12 | 2011-01-28 05:21 | -0.058 | 40571.2234 | -0.055963 | 311.4662 | 0 | 0 | 0 | -556.5569 | N | -311.4662 | 63783 | Next Year's Projected Peak | 32641.7061 | 32711.8081 | -0.049999 | 11.1007 | DS & NL & PH
13 | 2011-01-29 22:29 | -0.122 | 40572.9371 | -0.082338 | 646.2125 | 0 | 351.2895 | 0 |  | Y |  |  |  | 27748.9937 | 27729.3223 | -0.052 | -19.9068 | DS & NL & RU
14 | 2011-02-01 22:28 | -0.078 | 40575.9359 | -0.077912 | 459.3271 | 0 | 0 | 0 | -589.5444 | N | -459.3271 |  |  | 51871.748 | 51714.2688 | -0.056 | 12.3255 | JOU DS & NL & TFR
15 | 2011-02-02 02:18 | -0.158 | 40576.0963 | -0.15844 | 716.9337 | 0 | 0 | 0 | -452.4933 | N | -716.9337 | 2011 | Current year | 49441.4014 | 49290.7323 | -0.058498 | 0.75019 | DS & NL & CBA
16 | 2011-02-02 05:39 | -0.125 | 40576.2356 | -0.1239 | 578.4939 | 0 | 0 | 0 | -466.9144 | N | -578.4939 | -286 | 2011 Frequency Response Obligation (FRO) | 52943.4199 | 52864.7093 | -0.0485 | 2.2301 | DS & NL & PH & RU
17 | 2011-02-02 08:24 | -0.188 | 40576.3503 | -0.18743 | 775.257 | 0 | 0 | 0 | -413.6183 | N | -775.257 |  |  | 52047.5054 | 51917.6827 | -0.045 | 9.4779 | DS & NL & PH & TFR
18 | 2011-02-02 10:55 | -0.19 | 40576.4553 | -0.18951 | 840.8931 | 0 | 0 | 0 | -443.7096 | N | -840.8931 | Summary Statistics |  | 52733.0312 | 52604.594 | -0.037502 | 0.35531 | DS & NL & PH & CBA
19 | 2011-02-09 13:01 | -0.114 | 40583.5428 | -0.11379 | 598.686 | 0 | 11.1633 | 0 | -516.3359 | N | -587.5227 | -533.8388 | Average Frequency Response (MW/0.1Hz) | 50685.1836 | 50619.0839 | -0.047501 | 2.1707 | DS & NL & PH & RU & TFR
20 | 2011-02-15 16:40 | -0.216 | 40589.6945 | -0.21589 | 769.9818 | 0 | 0 | 0 | -356.6558 | N | -769.9818 |  |  | 31612.45 | 31388.6676 | -0.0555 | 29.3821 | DS & NL & PH & RU & CBA
21 | 2011-02-16 09:25 | -0.197 | 40590.3928 | -0.1754 | 569.8584 | 0 | 0 | 0 | -324.8819 | N | -569.8584 | -33.7706 | Regression Estimate of Frequency Response (MW/0.1Hz) | 31135.6406 | 31020.1496 | -0.047 | 4.6014 | DS & NL & PH & RU & TFR & CBA
22 | 2011-03-03 11:17 | -0.094 | 40605.4705 | -0.094214 | 440.4526 | 0 | 0 | 0 | -467.5043 | N | -440.4526 |  |  | 31497.3516 | 31443.4837 | -0.06 | 1.5935 | NL & PH
23 | 2011-03-14 06:09 | -0.208 | 40616.2566 | -0.20762 | 970.6714 | 0 | 0 | 0 | -467.5293 | N | -970.6714 |  |  | 26752.5693 | 26597.6325 | -0.06 | 52.3709 | NL & RU
24 | 2011-03-14 07:08 | -0.127 | 40616.2974 | -0.12732 | 486.9663 | 0 | 0 | 0 | -382.4857 | N | -486.9663 |  |  | 29065.1851 | 29088.0671 | -0.051 | 33.9479 | NL & TFR
25 | 2011-03-16 20:45 | -0.074 | 40618.8647 | -0.073859 | 397.5629 | 0 | 0 | 0 | -538.2712 | N | -397.5629 |  |  | 33412.5537 | 33257.8378 | -0.1 | 100 | NL & CBA
26 | 2011-03-23 14:46 | -0.063 | 40625.6158 | -0.062515 | 621.1687 | 0 | 0 | 0 | -993.6345 | N | -621.1687 |  |  | 38733.6201 | 38255.9157 |  |  | NL & PH & RU
27 | 2011-03-24 13:59 | -0.182 | 40626.5827 | -0.17701 | 498.3148 | 0 | 0 | 0 | -281.5223 | N | -498.3148 |  | Next Year's | 35353.7969 | 35240.8045 |  |  | NL & PH & TFR
28 | 2011-03-25 16:13 | -0.172 | 40627.676 | -0.16843 | 553.3828 | 0 | 67.0523 | 0 | -288.7507 | N | -486.3305 | -286 | 2012 Frequency Response Obligation (FRO) | 40151.54 | 39989.0825 |  |  | NL & PH & BAA
29 | 2011-03-29 06:43 | -0.099 | 40631.2799 | -0.099441 | 742.8181 | 0 | 0 | 0 | -746.9936 | N | -742.8181 | -556.388 | 2012 Frequency Bias Setting - (minimum of FRM, next year's FRO, or 0.8% of Projected Peak [Load + Gen]/2) | 31093.9292 | 31034.9238 |  |  | NL & PH & RU & TFR
30 | 2011-03-31 12:21 | -0.112 | 40633.5149 | -0.11179 | 421.0469 | 0 | 0 | 0 | -376.6259 | N | -421.0469 |  |  | 31970.3716 | 31774.6436 |  | N | NL & PH & RU & CBA
31 | 2011-04-05 22:02 | -0.09 | 40638.9181 | -0.089661 | 518.4755 | 0 | 0 | 0 | -578.262 | N | -518.4755 | -504.3586 | 2011 FRM - Median Frequency Response (MW/0.1Hz) | 30986.4536 | 30848.2909 |  | Y | NL & PH & RU & TFR & CBA
32 | 2011-04-20 13:40 | -0.145 | 40653.5701 | -0.14457 | 785.5412 | 0 | 0 | 0 | -543.3742 | N | -785.5412 |  |  | 41619.9902 | 41463.4122 |  |  | PH & RU
33 | 2011-04-27 23:27 | -0.133 | 40660.9771 | -0.13291 | 691.8045 | 0 | 0 | 0 | -520.5021 | N | -691.8045 |  |  | 29943.1245 | 29703.5409 |  |  | PH & TFR
34 | 2011-05-11 14:04 | -0.121 | 40674.5866 | -0.12124 | 726.0243 | 0 | 0 | 0 | -598.8298 | N | -726.0243 |  |  | 42265.9336 | 42113.4274 |  |  | PH & CBA
35 | 2011-05-16 08:06 | -0.101 | 40679.3379 | -0.10147 | 471.0875 | 0 | 0 | 0 | -464.2821 | N | -471.0875 |  |  | 30202.7422 | 30136.7695 |  |  | PH & RU & TFR
36 | 2011-05-19 14:08 | -0.197 | 40682.5888 | -0.19718 | 995.0827 | 0 | 0 | 0 | -504.6492 | N | -995.0827 |  |  | 42909.6079 | 42610.2337 |  |  | PH & RU & CBA
37 | 2011-05-23 17:34 | -0.092 | 40686.7324 | -0.092072 | 533.3253 | 0 | 0 | 0 | -579.245 | N | -533.3253 |  |  | 50589.6709 | 50488.2642 |  |  | PH & TFR
38 | 2011-05-29 22:03 | -0.118 | 40692.9188 | -0.11794 | 762.3234 | 0 | 0 | 0 | -646.3608 | N | -762.3234 |  |  | 44769.7285 | 44477.9926 |  |  | PH & CBA
39 | 2011-06-22 13:18 | 0.08 | 40716.5546 | 0.031317 | -258.56 | 0 | 0 | 0 | -825.6283 | N | 258.56 |  |  | 44769.1958 | 44456.9752 |  |  | PH & RU & TFR
40 | 2011-06-27 12:54 | -0.149 | 40721.5375 | -0.1311 | 661.2317 | 0 | 0 | 0 | -504.3586 | N | -661.2317 |  |  | 56971.1396 | 56832.6572 |  |  | PH & RU & CBA
41 | 2011-07-18 09:13 | -0.097 | 40742.3842 | -0.094273 | 386.25 | 0 | 0 | 0 | -409.7153 | N | -386.25 |  |  | 45315.0059 | 45296.7034 |  |  | PH & TFR
42 | 2011-07-18 20:50 | -0.119 | 40742.8685 | -0.12767 | 596.1496 | 0 | 0 | 0 | -466.9492 | N | -596.1496 |  |  | 57050.2559 | 56884.0016 |  |  | PH & CBA
PH & RU & TFR & CBA
RU & TFR
RU & CBA
RU & TFR & CBA
TFR & CBA
N
Y

## Adjustments2052 (hidden)
| Balancing Authority | ERCO | JOU Dynamic Schedules |  | Non conforming Load |  | Pumped Hydro |  | Ramping Units |  | Transferred Frequency Response |  | Contingent BA Adjustment |  | Net Total Adjustments
Event | Date/Time |  | Value A | Value B | Value A | Value B | Value A | Value B | Value A | Value B | Value A | Value B | Value A | Value B | Value B 20 to 52 seconds
Number | (Central Prevailing) | DelFreq | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment
1 | 2010-12-06 11:25 | -0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2010-12-09 17:34 | -0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2010-12-11 23:38 | -0.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2010-12-16 15:16 | -0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2010-12-19 02:39 | -0.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2010-12-26 08:23 | -0.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2011-01-09 18:52 | -0.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2011-01-11 06:50 | -0.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2011-01-20 00:02 | -0.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2011-01-21 03:46 | -0.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2011-01-23 14:53 | -0.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2011-01-28 05:21 | -0.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 2011-01-29 22:29 | -0.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 2011-02-01 22:28 | -0.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 2011-02-02 02:18 | -0.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 2011-02-02 05:39 | -0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2011-02-02 08:24 | -0.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 2011-02-02 10:55 | -0.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 2011-02-09 13:01 | -0.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 2011-02-15 16:40 | -0.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 2011-02-16 09:25 | -0.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 2011-03-03 11:17 | -0.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 2011-03-14 06:09 | -0.208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2011-03-14 07:08 | -0.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 2011-03-16 20:45 | -0.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 2011-03-23 14:46 | -0.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 2011-03-24 13:59 | -0.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 2011-03-25 16:13 | -0.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 2011-03-29 06:43 | -0.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 2011-03-31 12:21 | -0.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 2011-04-05 22:02 | -0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 2011-04-20 13:40 | -0.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 2011-04-27 23:27 | -0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 2011-05-11 14:04 | -0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 2011-05-23 17:34 | -0.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 2011-05-29 22:03 | -0.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 2011-04-27 23:27 | -0.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 2011-05-11 14:04 | -0.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sign Convention for scan data collected in Form 2 |  | Imports: MWs are - Exports: MWs are + |  | Loads in MW as - |  | Load MW as - Generation MW as + |  | Enter Gen MW as + |  | The transactional amount in MW Receiver enters - Deliverer enters + on Form 2 Data sheet |  | Generation MW as + (If load occurs due to gen loss, enter MW as - at value B)
Notes:
| 1) | Balancing Authorities making adjustments must retain evidence to verify: - Adjustment values are determined from scan-cycle data using Value A and Value B averaging periods. Scan-cycle data must be available if adjustments are made. - Adjustments are necessary to improve accuracy of calculations compared to using Net Actual Interchange (contingency size for single BA interconnections) solely. Said differently, unless an adjustment compensates for significant known error, it should not be made. However, as noted in the next item, once a decision to include an adjustment for one or more of the six types is made for one event, the entity must calculate adjustments for that (those) type(s) for all events. - Adjustments are included consistently for all events (e.g. if adjustments for nonconforming load are made for one event, the load must be included for all events, etc.).
| 2) | Dynamic Schedules: - Values use schedule sign convention. - Adjustments should include only dynamic schedules accounting for joint-owned units. Other dynamic schedules should be ignored.
| 3) | Nonconforming Loads: - Values must be entered as negative numbers.
| 4) | Pumped Hydro: - Values for pumping must be entered as negative values. - Values for generating must be entered as positive values.
| 5) | Rampling Units: - Values are entered as positive values.
| 6) | Transferred Frequency Response: - This value is the amount agreed upon between the entities expressed in MW/0.1 Hz. Form 2 will adjust this amount for the frequency deviation experienced. (e.g. if an entity agrees to provide 20 MW/0.1 Hz to another entity and a frequency event with a deviation of 50 mHz occurs, the delivering entity should enter +20 in the data column of Form 2 and the receiving entity should enter - 20. The spreadsheet will adjust the SEFRD for each entity by the 10 for this event.) - Values for the entity receiving the response must be entered as a negative number. - Values for the entity delivering the response must be entered as a positive number. - Values between entities must sum to zero.
| 7) | Contingent Balancing Authority Adjustment: - Value for Value A is the pre-contingency generation from the contingent unit(s). - Value for Value B is usually 0 MW, but may be the load that remains on the system that was "netted" out by the now offline generation.

## Summary
| Balancing Authority | ERCO |  | NERC FRS FORM 1 | [6 empty] | 12 to 24 P.U. Performance |  |  | 18 to 30 P.U. Performance |  |  | 20 to 40 P.U. Performance |  |  | 18 to 52 P.U. Performance |  |  | 20 to 52 P.U. Performance
Event | Date/Time |  | BA | BA | 12 to 24 | 18 to 30 | 20 to 40 | 18 to 52 | 20 to 52 | Exclude for | Initial | Initial | Sustained | Initial | Initial | Sustained | Initial | Initial | Sustained | Initial | Initial | Sustained | Initial | Initial | Sustained
Number | (Central Prevailing) | DelFreq | Time | DelFreq | SEFRD | SEFRD | SEFRD | SEFRD | SEFRD | data error * | Adjusted | Unadjusted |  | Adjusted | Unadjusted |  | Adjusted | Unadjusted |  | Adjusted | Unadjusted |  | Adjusted | Unadjusted
1 | 2010-12-06 11:25 | -0.101 | 40518.4763 | -0.10064 | -736.3771 | -750.9388 | -775.4611 | -795.6689 | -800.3705 | N | 2.5723 | 2.5723 | No Evaluation | 2.6234 | 2.6234 | No Evaluation | 2.7079 | 2.7079 | No Evaluation | 2.7727 | 2.7727 | No Evaluation | 2.7904 | 2.7904 | No Evaluation
2 | 2010-12-09 17:34 | -0.074 | 40521.7321 | -0.10471 | -682.1016 | -720.024 | -716.5637 | -703.5578 | -703.9269 | N | 2.363 | 2.363 | No Evaluation | 2.5145 | 2.5145 | No Evaluation | 2.5034 | 2.5034 | No Evaluation | 2.457 | 2.457 | No Evaluation | 2.4581 | 2.4581 | No Evaluation
3 | 2010-12-11 23:38 | -0.166 | 40523.985 | -0.20027 | -445.2562 | -411.1327 | -411.601 | -415.1978 | -414.6116 | N | 1.5508 | 1.5508 | No Evaluation | 1.4336 | 1.4336 | No Evaluation | 1.4365 | 1.4365 | No Evaluation | 1.4499 | 1.4499 | No Evaluation | 1.4478 | 1.4478 | No Evaluation
4 | 2010-12-16 15:16 | -0.074 | 40528.6361 | -0.08541 | -757.1747 | -723.271 | -750.8428 | -794.9381 | -796.3947 | N | 2.6411 | 2.6411 | No Evaluation | 2.5262 | 2.5262 | No Evaluation | 2.6128 | 2.6128 | No Evaluation | 2.754 | 2.754 | No Evaluation | 2.7577 | 2.7577 | No Evaluation
5 | 2010-12-19 02:39 | -0.111 | 40531.1106 | -0.12557 | -653.1513 | -578.5567 | -545.2899 | -550.2629 | -543.3972 | N | 2.2488 | 2.2488 | No Evaluation | 2.0057 | 2.0057 | No Evaluation | 1.8976 | 1.8976 | No Evaluation | 1.9137 | 1.9137 | No Evaluation | 1.8937 | 1.8937 | No Evaluation
6 | 2010-12-26 08:23 | -0.066 | 40538.3556 | -0.053965 | -832.9666 | -921.4768 | -1074.5468 | -1364.8772 | -1396.8923 | N | 2.8968 | 2.8968 | No Evaluation | 3.2036 | 3.2036 | No Evaluation | 3.6659 | 3.6659 | No Evaluation | 4.254 | 4.254 | No Evaluation | 4.3783 | 4.3783 | No Evaluation
7 | 2011-01-09 18:52 | -0.108 | 40552.7861 | -0.111 | -475.9519 | -518.8739 | -536.4286 | -532.7948 | -535.4607 | N | 1.6524 | 1.6524 | No Evaluation | 1.812 | 1.812 | No Evaluation | 1.8733 | 1.8733 | No Evaluation | 1.8604 | 1.8604 | No Evaluation | 1.8704 | 1.8704 | No Evaluation
8 | 2011-01-11 06:50 | -0.091 | 40554.2849 | -0.094786 | -473.9273 | -482.1383 | -485.7788 | -499.6324 | -501.1742 | N | 1.6553 | 1.6553 | No Evaluation | 1.6853 | 1.6853 | No Evaluation | 1.6969 | 1.6969 | No Evaluation | 1.7426 | 1.7426 | No Evaluation | 1.748 | 1.748 | No Evaluation
9 | 2011-01-20 00:02 | -0.198 | 40563.0013 | -0.19768 | -417.1969 | -398.2749 | -401.8856 | -399.4232 | -397.8233 | N | 1.4534 | 1.4534 | No Evaluation | 1.3904 | 1.3904 | No Evaluation | 1.4037 | 1.4037 | No Evaluation | 1.395 | 1.395 | No Evaluation | 1.3897 | 1.3897 | No Evaluation
10 | 2011-01-21 03:46 | -0.171 | 40564.1572 | -0.16418 | -413.4372 | -396.1562 | -386.2991 | -381.8103 | -380.0314 | N | 1.4433 | 1.4433 | No Evaluation | 1.3843 | 1.3843 | No Evaluation | 1.3497 | 1.3497 | No Evaluation | 1.3332 | 1.3332 | No Evaluation | 1.3274 | 1.3274 | No Evaluation
11 | 2011-01-23 14:53 | -0.149 | 40566.6203 | -0.14473 | -298.186 | -279.1287 | -275.3312 | -272.7222 | -271.7868 | N | 1.0389 | 1.0389 | No Evaluation | 0.9753 | 0.9753 | No Evaluation | 0.96227 | 0.96227 | No Evaluation | 0.95279 | 0.95279 | No Evaluation | 0.94967 | 0.94967 | No Evaluation
12 | 2011-01-28 05:21 | -0.058 | 40571.2234 | -0.065089 | -459.8215 | -478.9585 | -506.3958 | -564.3632 | -570.7658 | N | 1.6062 | 1.6062 | No Evaluation | 1.6731 | 1.6731 | No Evaluation | 1.764 | 1.764 | No Evaluation | 1.9223 | 1.9223 | No Evaluation | 1.946 | 1.946 | No Evaluation
13 | 2011-01-29 22:29 | -0.122 | 40572.9371 | -0.12446 | [5 empty] | Y | 1.5127 | 1.5127 | No Evaluation | 1.4956 | 1.4956 | No Evaluation | 1.2775 | 1.2775 | No Evaluation | 1.2735 | 1.2735 | No Evaluation | 1.2524 | 1.2524 | No Evaluation
14 | 2011-02-01 22:28 | -0.078 | 40575.9359 | -0.078787 | -564.6147 | -583.2068 | -576.1361 | -588.9589 | -590.4511 | N | 1.9706 | 1.9706 | No Evaluation | 2.0385 | 2.0385 | No Evaluation | 2.0133 | 2.0133 | No Evaluation | 2.0561 | 2.0561 | No Evaluation | 2.0613 | 2.0613 | No Evaluation
15 | 2011-02-02 02:18 | -0.158 | 40576.0963 | -0.15379 | -463.2835 | -466.2577 | -458.3899 | -453.1171 | -452.8239 | N | 1.6195 | 1.6195 | No Evaluation | 1.63 | 1.63 | No Evaluation | 1.6018 | 1.6018 | No Evaluation | 1.5832 | 1.5832 | No Evaluation | 1.5821 | 1.5821 | No Evaluation
16 | 2011-02-02 05:39 | -0.125 | 40576.2356 | -0.11468 | -508.5374 | -504.8655 | -484.2149 | -471.2855 | -468.6926 | N | 1.7771 | 1.7771 | No Evaluation | 1.7638 | 1.7638 | No Evaluation | 1.6885 | 1.6885 | No Evaluation | 1.6411 | 1.6411 | No Evaluation | 1.6326 | 1.6326 | No Evaluation
17 | 2011-02-02 08:24 | -0.188 | 40576.3503 | -0.17909 | -464.7462 | -435.7627 | -419.6579 | -419.1269 | -414.4306 | N | 1.6195 | 1.6195 | No Evaluation | 1.5136 | 1.5136 | No Evaluation | 1.4637 | 1.4637 | No Evaluation | 1.4601 | 1.4601 | No Evaluation | 1.4462 | 1.4462 | No Evaluation
18 | 2011-02-02 10:55 | -0.19 | 40576.4553 | -0.18503 | -448.8902 | -454.4881 | -448.4298 | -444.7788 | -443.8754 | N | 1.5684 | 1.5684 | No Evaluation | 1.589 | 1.589 | No Evaluation | 1.5675 | 1.5675 | No Evaluation | 1.5545 | 1.5545 | No Evaluation | 1.5514 | 1.5514 | No Evaluation
19 | 2011-02-09 13:01 | -0.114 | 40583.5428 | -0.11066 | -560.2882 | -531.2173 | -514.3666 | -518.7858 | -516.8136 | N | 1.9343 | 1.9343 | No Evaluation | 1.8371 | 1.8371 | No Evaluation | 1.7775 | 1.7775 | No Evaluation | 1.8109 | 1.8109 | No Evaluation | 1.8054 | 1.8054 | No Evaluation
20 | 2011-02-15 16:40 | -0.216 | 40589.6945 | -0.1997 | -379.1384 | -386.1377 | -369.7027 | -359.5567 | -358.1872 | N | 1.3208 | 1.3208 | No Evaluation | 1.3482 | 1.3482 | No Evaluation | 1.2879 | 1.2879 | No Evaluation | 1.2518 | 1.2518 | No Evaluation | 1.247 | 1.247 | No Evaluation
21 | 2011-02-16 09:25 | -0.197 | 40590.3928 | -0.1753 | -321.1692 | -325.1444 | -325.9642 | -324.8264 | -324.9821 | N | 1.1229 | 1.1229 | No Evaluation | 1.1366 | 1.1366 | No Evaluation | 1.1394 | 1.1394 | No Evaluation | 1.1354 | 1.1354 | No Evaluation | 1.136 | 1.136 | No Evaluation
22 | 2011-03-03 11:17 | -0.094 | 40605.4705 | -0.096197 | -450.2504 | -458.3971 | -462.9224 | -467.4041 | -468.0848 | N | 1.5729 | 1.5729 | No Evaluation | 1.6009 | 1.6009 | No Evaluation | 1.6166 | 1.6166 | No Evaluation | 1.6323 | 1.6323 | No Evaluation | 1.6346 | 1.6346 | No Evaluation
23 | 2011-03-14 06:09 | -0.208 | 40616.2566 | -0.20564 | -473.1516 | -472.0986 | -469.7268 | -467.1296 | -467.611 | N | 1.6539 | 1.6539 | No Evaluation | 1.6504 | 1.6504 | No Evaluation | 1.6421 | 1.6421 | No Evaluation | 1.633 | 1.633 | No Evaluation | 1.6347 | 1.6347 | No Evaluation
24 | 2011-03-14 07:08 | -0.127 | 40616.2974 | -0.12795 | -383.2163 | -380.6679 | -379.652 | -382.8648 | -382.7192 | N | 1.3398 | 1.3398 | No Evaluation | 1.3308 | 1.3308 | No Evaluation | 1.3273 | 1.3273 | No Evaluation | 1.3379 | 1.3379 | No Evaluation | 1.3374 | 1.3374 | No Evaluation
25 | 2011-03-16 20:45 | -0.074 | 40618.8647 | -0.079052 | -455.886 | -503.0237 | -507.2286 | -542.0638 | -543.8227 | N | 1.566 | 1.566 | No Evaluation | 1.7584 | 1.7584 | No Evaluation | 1.7701 | 1.7701 | No Evaluation | 1.8768 | 1.8768 | No Evaluation | 1.8821 | 1.8821 | No Evaluation
26 | 2011-03-23 14:46 | -0.063 | 40625.6158 | -0.065036 | -807.1876 | -956.5729 | -964.2482 | -990.4233 | -996.2987 | N | 2.6337 | 2.6337 | No Evaluation | 3.3396 | 3.3396 | No Evaluation | 3.3685 | 3.3685 | No Evaluation | 3.452 | 3.452 | No Evaluation | 3.4742 | 3.4742 | No Evaluation
27 | 2011-03-24 13:59 | -0.182 | 40626.5827 | -0.1757 | -268.7678 | -283.9551 | -285.693 | -280.7817 | -281.7167 | N | 0.93757 | 0.93757 | No Evaluation | 0.99169 | 0.99169 | No Evaluation | 0.99855 | 0.99855 | No Evaluation | 0.98092 | 0.98092 | No Evaluation | 0.98434 | 0.98434 | No Evaluation
28 | 2011-03-25 16:13 | -0.172 | 40627.676 | -0.17982 | -261.0249 | -270.5909 | -280.7618 | -288.1984 | -289.6245 | N | 0.9122 | 0.9122 | No Evaluation | 0.94599 | 0.94599 | No Evaluation | 0.98005 | 0.98005 | No Evaluation | 1.0044 | 1.0044 | No Evaluation | 1.0096 | 1.0096 | No Evaluation
29 | 2011-03-29 06:43 | -0.099 | 40631.2799 | -0.10064 | -630.9477 | -741.8099 | -737.6064 | -743.0239 | -748.5698 | N | 2.1128 | 2.1128 | No Evaluation | 2.5807 | 2.5807 | No Evaluation | 2.5727 | 2.5727 | No Evaluation | 2.5901 | 2.5901 | No Evaluation | 2.6119 | 2.6119 | No Evaluation
30 | 2011-03-31 12:21 | -0.112 | 40633.5149 | -0.11093 | -375.7795 | -379.5978 | -372.3801 | -378.8763 | -378.9502 | N | 1.3136 | 1.3136 | No Evaluation | 1.3271 | 1.3271 | No Evaluation | 1.3012 | 1.3012 | No Evaluation | 1.3171 | 1.3171 | No Evaluation | 1.3169 | 1.3169 | No Evaluation
31 | 2011-04-05 22:02 | -0.09 | 40638.9181 | -0.084392 | -628.6462 | -616.9437 | -599.7632 | -587.131 | -580.0309 | N | 2.1776 | 2.1776 | No Evaluation | 2.1481 | 2.1481 | No Evaluation | 2.0953 | 2.0953 | No Evaluation | 2.0427 | 2.0427 | No Evaluation | 2.0219 | 2.0219 | No Evaluation
32 | 2011-04-20 13:40 | -0.145 | 40653.5701 | -0.14877 | -486.5853 | -529.8426 | -534.279 | -540.168 | -544.2105 | N | 1.6919 | 1.6919 | No Evaluation | 1.8463 | 1.8463 | No Evaluation | 1.8663 | 1.8663 | No Evaluation | 1.8839 | 1.8839 | No Evaluation | 1.8999 | 1.8999 | No Evaluation
33 | 2011-04-27 23:27 | -0.133 | 40660.9771 | -0.1315 | -524.8812 | -526.7018 | -522.4341 | -522.2102 | -520.7586 | N | 1.8295 | 1.8295 | No Evaluation | 1.8395 | 1.8395 | No Evaluation | 1.8256 | 1.8256 | No Evaluation | 1.8248 | 1.8248 | No Evaluation | 1.8199 | 1.8199 | No Evaluation
34 | 2011-05-11 14:04 | -0.121 | 40674.5866 | -0.11854 | -577.2223 | -612.6334 | -599.1221 | -599.3345 | -599.2391 | N | 2.0071 | 2.0071 | No Evaluation | 2.1414 | 2.1414 | No Evaluation | 2.0927 | 2.0927 | No Evaluation | 2.0942 | 2.0942 | No Evaluation | 2.0938 | 2.0938 | No Evaluation
35 | 2011-05-16 08:06 | -0.101 | 40679.3379 | -0.10668 | -427.6693 | -441.6688 | -457.1399 | -463.1042 | -464.9541 | N | 1.4936 | 1.4936 | No Evaluation | 1.5441 | 1.5441 | No Evaluation | 1.5962 | 1.5962 | No Evaluation | 1.6166 | 1.6166 | No Evaluation | 1.6234 | 1.6234 | No Evaluation
36 | 2011-05-19 14:08 | -0.197 | 40682.5888 | -0.20722 | -449.0124 | -480.6398 | -498.6519 | -502.4673 | -505.2433 | N | 1.5621 | 1.5621 | No Evaluation | 1.679 | 1.679 | No Evaluation | 1.7413 | 1.7413 | No Evaluation | 1.7539 | 1.7539 | No Evaluation | 1.7645 | 1.7645 | No Evaluation
37 | 2011-05-23 17:34 | -0.092 | 40686.7324 | -0.10264 | -476.745 | -522.1166 | -555.203 | -577.956 | -583.9198 | N | 1.6641 | 1.6641 | No Evaluation | 1.8169 | 1.8169 | No Evaluation | 1.9319 | 1.9319 | No Evaluation | 2.0014 | 2.0014 | No Evaluation | 2.0253 | 2.0253 | No Evaluation
38 | 2011-05-29 22:03 | -0.118 | 40692.9188 | -0.12257 | -574.8064 | -624.6141 | -651.1735 | -643.9486 | -647.8566 | N | 2.0063 | 2.0063 | No Evaluation | 2.1746 | 2.1746 | No Evaluation | 2.2694 | 2.2694 | No Evaluation | 2.2451 | 2.2451 | No Evaluation | 2.26 | 2.26 | No Evaluation
39 | 2011-06-22 13:18 | 0.08 | 40716.5546 | 0.033948 | -721.6185 | -761.9839 | -794.9615 | -825.6014 | -831.1721 | N | 2.505 | 2.505 | No Evaluation | 2.6631 | 2.6631 | No Evaluation | 2.7691 | 2.7691 | No Evaluation | 2.8662 | 2.8662 | No Evaluation | 2.8868 | 2.8868 | No Evaluation
40 | 2011-06-27 12:54 | -0.149 | 40721.5375 | -0.13661 | -459.8245 | -484.4445 | -498.1424 | -502.2992 | -504.7879 | N | 1.6052 | 1.6052 | No Evaluation | 1.6924 | 1.6924 | No Evaluation | 1.7404 | 1.7404 | No Evaluation | 1.7541 | 1.7541 | No Evaluation | 1.7635 | 1.7635 | No Evaluation
41 | 2011-07-18 09:13 | -0.097 | 40742.3842 | -0.095198 | -403.4077 | -405.7845 | -417.1324 | -409.7193 | -410.3063 | N | 1.4102 | 1.4102 | No Evaluation | 1.4187 | 1.4187 | No Evaluation | 1.4566 | 1.4566 | No Evaluation | 1.4306 | 1.4306 | No Evaluation | 1.4326 | 1.4326 | No Evaluation
42 | 2011-07-18 20:50 | -0.119 | 40742.8685 | -0.12852 | -448.2121 | -463.9878 | -465.0911 | -466.0866 | -467.0124 | N | 1.5645 | 1.5645 | No Evaluation | 1.6219 | 1.6219 | No Evaluation | 1.626 | 1.626 | No Evaluation | 1.6294 | 1.6294 | No Evaluation | 1.6327 | 1.6327 | No Evaluation
| Average Frequency Response (MW/0.1Hz) |  |  |  | -499.5585 | -517.5602 | -523.1811 | -532.0167 | -533.8388 |  | 1.7411 | 1.7411 |  | 1.8022 | 1.8022 |  | 1.8162 | 1.8162 |  | 1.8462 | 1.8462 |  | 1.8519 | 1.8519
| 2012 FRM - Median Frequency Response (MW/0.1Hz) |  |  |  | -463.1868 | -481.9899 | -497.7586 | -501.627 | -504.3586
| Regression Estimate of Frequency Response (MW/0.1Hz) |  |  |  | -33.7706 | -33.7706 | -33.7706 | -33.7706 | -33.7706
| 2012 Frequency Response Obligation (FRO) |  |  |  | -286 | -286 | -286 | -286 | -286

## Variable Bias Supplemental Info
Month | Minimum FBS* for month | Maximum FBS* for month | Time weighted ** average FBS* for month
January |  |  | -10
Feburary |  |  | -7
March |  |  | -12
April |  |  | -8
May |  |  | -27
June |  |  | -8.7
July |  |  | -8
August |  |  | -8
September |  |  | -8.2
October |  |  | -8
November |  |  | -8
December |  |  | -12
|  |  | -10.4107 | Average Annual Bias
* Frequency Bias Setting (FBS)
** Based on the one minute values used in BAL 001

## BA Form 2 Event Data
|  |  | PasteSpecial/Values the data copied from FRS Form 2 for each event. | [5 empty] | Interconnection Performance | [9 empty] | Value A Data |  | BA Performance | [8 empty] | Value B |  | 12 to 24 second Average Period Evaluation | [11 empty] | Value B | 18 to 30 second Average Period Evaluation | [12 empty] | Value B | 20 to 40 second Average Period Evaluation | [12 empty] | Value B | 18 to 52 second Average Period Evaluation | [12 empty] | Value B | 20 to 52 second Average Period Evaluation
[21 empty] | JOU | Non- |  |  | Transferred | Contingent | [5 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent
|  |  | Date | A Point | FPointA | A Value | t(0) Time | C Value | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias
|  |  |  | Time | Hz | Hz |  | Hz | 12 to 24 sec | 12 to 24 sec | 18 to 30 sec | 18 to 30 sec | 20 to 40 sec | 20 to 40 sec | 18 to 52 sec | 18 to 52 sec | 20 to 52 sec | 20 to 52 sec |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting
Event | Date/Time | [7 empty] | Average | Average | Average | Average | Average | Average | Average | Average | Average | Average | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR
Number | (Central Prevailing) | DelFreq | [6 empty] | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Hz | MW | MW | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW | Hz | MW | MW | MW | MW | MW | MW | MW | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | P.U. | P.U. | P.U. | MW | MW | MW | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | P.U. | P.U. | P.U. | MW | MW | MW | Hz | MW | MW | MW | MW | MW | MW | MW | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW | Hz | MW | MW | MW | MW | MW | MW | MW | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW
1 | 2010-12-06 11:25 | -0.101 | 2010-12-06 11:26 | 40518.4763 | 59.997 | 59.9965 | 40518.4763 | 59.81 | 59.8939 | -736.3771 | 59.8959 | -750.9388 | 59.9019 | -775.4611 | 59.9013 | -795.6689 | 59.9019 | -800.3705 | 59.9965 | 755.1125 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 35688.5645 | 22.858 | 59.8939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5723 | 2.5723 | No Evaluation | -653 | 35448.9286 | 693.1164 | 59.8959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6234 | 2.6234 | No Evaluation | -653 | 35339.7472 | 680.0601 | 59.899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7079 | 2.7079 | No Evaluation | -653 | 35410.9137 | 659.5346 | 59.9013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7727 | 2.7727 | No Evaluation | -653 | 35459.2561 | 644.6604 | 59.9019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7904 | 2.7904 | No Evaluation | -653 | 35469.9483 | 640.7123
2 | 2010-12-09 17:34 | -0.074 | 2010-12-09 17:34 | 40521.7321 | 59.993 | 59.998 | 40521.7321 | 59.804 | 59.8866 | -682.1016 | 59.8933 | -720.024 | 59.8909 | -716.5637 | 59.8908 | -703.5578 | 59.8909 | -703.9269 | 59.998 | 753.0677 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 34418.4287 | 13.0622 | 59.8866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.363 | 2.363 | No Evaluation | -653 | 34067.3248 | 740.6945 | 59.8933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5145 | 2.5145 | No Evaluation | -653 | 34085.0898 | 696.8494 | 59.8928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5034 | 2.5034 | No Evaluation | -653 | 34096.6463 | 699.9 | 59.8908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.457 | 2.457 | No Evaluation | -653 | 34109.5052 | 712.8598 | 59.8909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4581 | 2.4581 | No Evaluation | -653 | 34111.3336 | 712.5395
3 | 2010-12-11 23:38 | -0.166 | 2010-12-11 23:38 | 40523.985 | 60.009 | 60.0061 | 40523.985 | 59.747 | 59.821 | -445.2562 | 59.8059 | -411.1327 | 59.8078 | -411.601 | 59.8081 | -415.1978 | 59.8078 | -414.6116 | 60.0061 | 821.1 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 29590.7568 | -39.9992 | 59.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5508 | 1.5508 | No Evaluation | -653 | 29332.9386 | 1168.8685 | 59.8059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4336 | 1.4336 | No Evaluation | -653 | 29362.8086 | 1267.7539 | 59.8063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4365 | 1.4365 | No Evaluation | -653 | 29391.6209 | 1265.0394 | 59.8081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4499 | 1.4499 | No Evaluation | -653 | 29398.6697 | 1253.0353 | 59.8078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4478 | 1.4478 | No Evaluation | -653 | 29402.9971 | 1254.9132
4 | 2010-12-16 15:16 | -0.074 | 2010-12-16 15:16 | 40528.6361 | 59.971 | 59.9731 | 40528.6361 | 59.811 | 59.8914 | -757.1747 | 59.8877 | -723.271 | 59.8949 | -750.8428 | 59.8948 | -794.9381 | 59.8949 | -796.3947 | 59.9731 | 617.0875 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 31769.4482 | 175.497 | 59.8914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6411 | 2.6411 | No Evaluation | -653 | 31711.4741 | 708.9699 | 59.8877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5262 | 2.5262 | No Evaluation | -653 | 31747.0725 | 733.2251 | 59.8905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6128 | 2.6128 | No Evaluation | -653 | 31745.2623 | 714.7373 | 59.8948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.754 | 2.754 | No Evaluation | -653 | 31741.8678 | 687.1001 | 59.8949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7577 | 2.7577 | No Evaluation | -653 | 31741.0732 | 686.4178
5 | 2010-12-19 02:39 | -0.111 | 2010-12-19 02:39 | 40531.1106 | 59.993 | 59.987 | 40531.1107 | 59.806 | 59.875 | -653.1513 | 59.8614 | -578.5567 | 59.854 | -545.2899 | 59.8554 | -550.2629 | 59.854 | -543.3972 | 59.987 | 720.3267 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 30239.7212 | 84.8901 | 59.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2488 | 2.2488 | No Evaluation | -653 | 30095.928 | 816.2464 | 59.8614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0057 | 2.0057 | No Evaluation | -653 | 30116.4506 | 904.8655 | 59.8543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8976 | 1.8976 | No Evaluation | -653 | 30120.0483 | 951.5949 | 59.8554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9137 | 1.9137 | No Evaluation | -653 | 30135.6774 | 944.3066 | 59.854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8937 | 1.8937 | No Evaluation | -653 | 30135.1519 | 953.3765
6 | 2010-12-26 08:23 | -0.066 | 2010-12-26 08:32 | 40538.3556 | 59.934 | 59.9443 | 40538.3556 | 59.826 | 59.8846 | -832.9666 | 59.8903 | -921.4768 | 59.9048 | -1074.5468 | 59.9036 | -1364.8772 | 59.9048 | -1396.8923 | 59.9443 | 494.4381 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 39597.9473 | 364.0437 | 59.8846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8968 | 2.8968 | No Evaluation | -653 | 39157.4738 | 753.7544 | 59.8903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2036 | 3.2036 | No Evaluation | -653 | 39175.5993 | 716.4357 | 59.8971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6659 | 3.6659 | No Evaluation | -653 | 39181.9535 | 671.9963 | 59.9036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.254 | 4.254 | No Evaluation | -653 | 39184.2808 | 629.4197 | 59.9048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3783 | 4.3783 | No Evaluation | -653 | 39185.6239 | 621.8863
7 | 2011-01-09 18:52 | -0.108 | 2011-01-09 18:52 | 40552.7861 | 59.988 | 59.988 | 40552.7861 | 59.841 | 59.8663 | -475.9519 | 59.877 | -518.8739 | 59.8805 | -536.4286 | 59.8799 | -532.7948 | 59.8805 | -535.4607 | 59.988 | 575.2194 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 40357.3638 | 78.3668 | 59.8663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6524 | 1.6524 | No Evaluation | -653 | 40313.0413 | 873.1586 | 59.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.812 | 1.812 | No Evaluation | -653 | 40208.2556 | 803.1901 | 59.8806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8733 | 1.8733 | No Evaluation | -653 | 40236.1726 | 779.4444 | 59.8799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8604 | 1.8604 | No Evaluation | -653 | 40275.8123 | 784.3265 | 59.8805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8704 | 1.8704 | No Evaluation | -653 | 40269.5131 | 780.5276
8 | 2011-01-11 06:50 | -0.091 | 2011-01-11 06:50 | 40554.2849 | 59.978 | 59.9805 | 40554.2849 | 59.87 | 59.884 | -473.9273 | 59.8857 | -482.1383 | 59.8891 | -485.7788 | 59.8888 | -499.6324 | 59.8891 | -501.1742 | 59.9805 | 456.8604 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 48145.5186 | 127.3304 | 59.884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6553 | 1.6553 | No Evaluation | -653 | 48119.3449 | 757.4803 | 59.8857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6853 | 1.6853 | No Evaluation | -653 | 48008.269 | 746.285 | 59.8864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6969 | 1.6969 | No Evaluation | -653 | 48020.9428 | 742.0432 | 59.8888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7426 | 1.7426 | No Evaluation | -653 | 48065.0161 | 725.9181 | 59.8891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.748 | 1.748 | No Evaluation | -653 | 48054.1854 | 724.0611
9 | 2011-01-20 00:02 | -0.198 | 2011-01-20 00:02 | 40563.0013 | 60.017 | 60.0062 | 40563.0013 | 59.761 | 59.8171 | -417.1969 | 59.8086 | -398.2749 | 59.8085 | -401.8856 | 59.8092 | -399.4232 | 59.8085 | -397.8233 | 60.0062 | 786.0532 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 28998.6179 | -40.8119 | 59.8171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4534 | 1.4534 | No Evaluation | -653 | 28706.8792 | 1194.056 | 59.8086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3904 | 1.3904 | No Evaluation | -653 | 28783.6582 | 1250.0287 | 59.8105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4037 | 1.4037 | No Evaluation | -653 | 28787.2116 | 1237.729 | 59.8092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.395 | 1.395 | No Evaluation | -653 | 28794.4275 | 1245.7782 | 59.8085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3897 | 1.3897 | No Evaluation | -653 | 28794.6882 | 1250.6858
10 | 2011-01-21 03:46 | -0.171 | 2011-01-21 03:46 | 40564.1572 | 60.044 | 60.0447 | 40564.1573 | 59.887 | 59.8873 | -413.4372 | 59.8806 | -396.1562 | 59.8735 | -386.2991 | 59.8743 | -381.8103 | 59.8735 | -380.0314 | 60.0447 | 650 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 40462.4668 | -292.2096 | 59.8873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4433 | 1.4433 | No Evaluation | -653 | 40291.4487 | 736.0257 | 59.8806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3843 | 1.3843 | No Evaluation | -653 | 40274.2706 | 779.8672 | 59.8764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3497 | 1.3497 | No Evaluation | -653 | 40282.1555 | 807.3458 | 59.8743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3332 | 1.3332 | No Evaluation | -653 | 40290.967 | 820.9635 | 59.8735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3274 | 1.3274 | No Evaluation | -653 | 40291.5407 | 825.8506
11 | 2011-01-23 14:53 | -0.149 | 2011-01-23 14:53 | 40566.6203 | 59.978 | 59.9999 | 40566.6204 | 59.86 | 59.864 | -298.186 | 59.8551 | -279.1287 | 59.8512 | -275.3312 | 59.8517 | -272.7222 | 59.8512 | -271.7868 | 59.9999 | 403.7147 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 31488.7808 | 0.81269 | 59.864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0389 | 1.0389 | No Evaluation | -653 | 31381.1364 | 888.0797 | 59.8551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9753 | 0.9753 | No Evaluation | -653 | 31467.2852 | 945.9206 | 59.8532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96227 | 0.96227 | No Evaluation | -653 | 31481.4739 | 958.7237 | 59.8517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95279 | 0.95279 | No Evaluation | -653 | 31481.7595 | 968.2548 | 59.8512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94967 | 0.94967 | No Evaluation | -653 | 31483.8087 | 971.4347
12 | 2011-01-28 05:21 | -0.058 | 2011-01-28 05:22 | 40571.2234 | 59.966 | 59.9734 | 40571.2234 | 59.876 | 59.9056 | -459.8215 | 59.9083 | -478.9585 | 59.9174 | -506.3958 | 59.9167 | -564.3632 | 59.9174 | -570.7658 | 59.9734 | 311.4662 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 32641.7061 | 173.8623 | 59.9056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6062 | 1.6062 | No Evaluation | -653 | 32677.88 | 616.6215 | 59.9083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6731 | 1.6731 | No Evaluation | -653 | 32692.8532 | 598.8963 | 59.9116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.764 | 1.764 | No Evaluation | -653 | 32700.5955 | 577.0146 | 59.9167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9223 | 1.9223 | No Evaluation | -653 | 32710.6393 | 543.8041 | 59.9174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.946 | 1.946 | No Evaluation | -653 | 32711.8081 | 539.3009
13 | 2011-01-29 22:29 | -0.122 | 2011-01-29 22:30 | 40572.9371 | 60.001 | 59.9997 | 40572.9372 | 59.839 | 59.8767 | -239.9583 | 59.8753 | -237.0861 | 59.9174 | -244.0032 | 59.9152 | 1547.8746 | 59.9174 | 1653.0591 | 59.9997 | 646.2125 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 27748.9937 | 1.6347 | 59.8767 | 113.9128 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5127 | 1.5127 | No Evaluation | -653 | 27564.7109 | 805.0547 | 59.8753 | 113.8159 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4956 | 1.4956 | No Evaluation | -653 | 27600.2771 | 814.3818 | 59.8786 | 203.7093 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2775 | 1.2775 | No Evaluation | -653 | 27623.1301 | 792.5017 | 59.9152 | 338.136 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2735 | 1.2735 | No Evaluation | -653 | 27719.212 | 553.9618 | 59.9174 | 351.2895 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2524 | 1.2524 | No Evaluation | -653 | 27729.3223 | 539.3009
14 | 2011-02-01 22:28 | -0.078 | 2011-02-01 22:28 | 40575.9359 | 59.969 | 59.9695 | 40575.936 | 59.875 | 59.888 | -564.6147 | 59.8907 | -583.2068 | 59.8916 | -576.1361 | 59.8914 | -588.9589 | 59.8916 | -590.4511 | 59.9695 | 459.3271 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 51871.748 | 199.1615 | 59.888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9706 | 1.9706 | No Evaluation | -653 | 51739.0904 | 731.3639 | 59.8907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0385 | 2.0385 | No Evaluation | -653 | 51716.8158 | 713.6387 | 59.8897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0133 | 2.0133 | No Evaluation | -653 | 51712.3473 | 720.0817 | 59.8914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0561 | 2.0561 | No Evaluation | -653 | 51714.5777 | 709.2298 | 59.8916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0613 | 2.0613 | No Evaluation | -653 | 51714.2688 | 707.9282
15 | 2011-02-02 02:18 | -0.158 | 2011-02-02 02:19 | 40576.0963 | 60.015 | 60.0135 | 40576.0963 | 59.841 | 59.8587 | -463.2835 | 59.8597 | -466.2577 | 59.8551 | -458.3899 | 59.8552 | -453.1171 | 59.8551 | -452.8239 | 60.0135 | 716.9337 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 49441.4014 | -88.1533 | 59.8587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6195 | 1.6195 | No Evaluation | -653 | 49253.6618 | 922.5942 | 59.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 1.63 | No Evaluation | -653 | 49279.5268 | 916.0643 | 59.857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6018 | 1.6018 | No Evaluation | -653 | 49287.5707 | 933.7888 | 59.8552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5832 | 1.5832 | No Evaluation | -653 | 49289.5894 | 945.7611 | 59.8551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5821 | 1.5821 | No Evaluation | -653 | 49290.7323 | 946.4647
16 | 2011-02-02 05:39 | -0.125 | 2011-02-02 05:39 | 40576.2356 | 59.921 | 59.9233 | 40576.2356 | 59.806 | 59.8094 | -508.5374 | 59.8086 | -504.8655 | 59.7994 | -484.2149 | 59.8 | -471.2855 | 59.7994 | -468.6926 | 59.9233 | 578.4939 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 52943.4199 | 501.1762 | 59.8094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7771 | 1.7771 | No Evaluation | -653 | 52893.3103 | 1244.4311 | 59.8086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7638 | 1.7638 | No Evaluation | -653 | 52827.3566 | 1250.0287 | 59.8035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6885 | 1.6885 | No Evaluation | -653 | 52850.229 | 1283.4411 | 59.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6411 | 1.6411 | No Evaluation | -653 | 52861.151 | 1305.9994 | 59.7994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6326 | 1.6326 | No Evaluation | -653 | 52864.7093 | 1310.225
17 | 2011-02-02 08:24 | -0.188 | 2011-02-02 08:24 | 40576.3503 | 60.036 | 60.0354 | 40576.3503 | 59.853 | 59.868 | -464.7462 | 59.8563 | -435.7627 | 59.8479 | -419.6579 | 59.8497 | -419.1269 | 59.8479 | -414.4306 | 60.0354 | 775.257 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 52047.5054 | -230.9964 | 59.868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6195 | 1.6195 | No Evaluation | -653 | 51826.673 | 861.9598 | 59.8563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5136 | 1.5136 | No Evaluation | -653 | 51915.3705 | 938.4477 | 59.8502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4637 | 1.4637 | No Evaluation | -653 | 51925.9769 | 978.3075 | 59.8497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4601 | 1.4601 | No Evaluation | -653 | 51915.5757 | 981.3104 | 59.8479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4462 | 1.4462 | No Evaluation | -653 | 51917.6827 | 992.9408
18 | 2011-02-02 10:55 | -0.19 | 2011-02-02 10:56 | 40576.4553 | 60.009 | 60.0077 | 40576.4553 | 59.802 | 59.8203 | -448.8902 | 59.8227 | -454.4881 | 59.8182 | -448.4298 | 59.8186 | -444.7788 | 59.8182 | -443.8754 | 60.0077 | 840.8931 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 52733.0312 | -50.6046 | 59.8203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5684 | 1.5684 | No Evaluation | -653 | 52504.3354 | 1173.5337 | 59.8227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.589 | 1.589 | No Evaluation | -653 | 52602.7729 | 1157.6732 | 59.8202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5675 | 1.5675 | No Evaluation | -653 | 52612.364 | 1174.2108 | 59.8186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5545 | 1.5545 | No Evaluation | -653 | 52601.4974 | 1184.4692 | 59.8182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5514 | 1.5514 | No Evaluation | -653 | 52604.594 | 1186.9236
19 | 2011-02-09 13:01 | -0.114 | 2011-02-09 13:02 | 40583.5428 | 60.025 | 60.0224 | 40583.5428 | 59.91 | 59.9173 | -560.2882 | 59.9117 | -531.2173 | 59.9086 | -514.3666 | 59.909 | -518.7858 | 59.9086 | -516.8136 | 60.0224 | 598.686 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 50685.1836 | -146.1094 | 59.9173 | 17.3057 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9343 | 1.9343 | No Evaluation | -653 | 50470.2879 | 540.1265 | 59.9117 | 17.2691 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8371 | 1.8371 | No Evaluation | -653 | 50564.4972 | 576.5057 | 59.908 | 17.2524 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7775 | 1.7775 | No Evaluation | -653 | 50612.092 | 600.7606 | 59.909 | 11.5059 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8109 | 1.8109 | No Evaluation | -653 | 50613.5269 | 594.2302 | 59.9086 | 11.1633 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8054 | 1.8054 | No Evaluation | -653 | 50619.0839 | 596.9192
20 | 2011-02-15 16:40 | -0.216 | 2011-02-15 16:40 | 40589.6945 | 60.03 | 60.0341 | 40589.6945 | 59.757 | 59.8303 | -379.1384 | 59.8344 | -386.1377 | 59.8182 | -369.7027 | 59.8191 | -359.5567 | 59.8182 | -358.1872 | 60.0341 | 769.9818 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 31612.45 | -222.8353 | 59.8303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3208 | 1.3208 | No Evaluation | -653 | 31207.5229 | 1108.2305 | 59.8344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3482 | 1.3482 | No Evaluation | -653 | 31373.7377 | 1081.1818 | 59.8251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2879 | 1.2879 | No Evaluation | -653 | 31367.8141 | 1142.1562 | 59.8191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2518 | 1.2518 | No Evaluation | -653 | 31388.4785 | 1181.5658 | 59.8182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.247 | 1.247 | No Evaluation | -653 | 31388.6676 | 1186.9221
21 | 2011-02-16 09:25 | -0.197 | 2011-02-16 09:26 | 40590.3928 | 59.98 | 59.9919 | 40590.3928 | 59.8 | 59.8144 | -321.1692 | 59.8166 | -325.1444 | 59.8165 | -325.9642 | 59.8164 | -324.8264 | 59.8165 | -324.9821 | 59.9919 | 569.8584 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 31135.6406 | 53.0551 | 59.8144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1229 | 1.1229 | No Evaluation | -653 | 30972.9414 | 1211.7812 | 59.8166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1366 | 1.1366 | No Evaluation | -653 | 30997.2439 | 1197.7925 | 59.817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1394 | 1.1394 | No Evaluation | -653 | 31008.921 | 1194.9926 | 59.8164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1354 | 1.1354 | No Evaluation | -653 | 31018.523 | 1198.9821 | 59.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.136 | 1.136 | No Evaluation | -653 | 31020.1496 | 1198.4481
22 | 2011-03-03 11:17 | -0.094 | 2011-03-03 11:18 | 40605.4705 | 59.971 | 59.9666 | 40605.4706 | 59.839 | 59.8687 | -450.2504 | 59.8704 | -458.3971 | 59.8724 | -462.9224 | 59.8723 | -467.4041 | 59.8724 | -468.0848 | 59.9666 | 440.4526 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 31497.3516 | 217.9374 | 59.8687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5729 | 1.5729 | No Evaluation | -653 | 31383.2949 | 857.2945 | 59.8704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6009 | 1.6009 | No Evaluation | -653 | 31421.3245 | 846.1028 | 59.8714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6166 | 1.6166 | No Evaluation | -653 | 31438.8647 | 839.996 | 59.8723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6323 | 1.6323 | No Evaluation | -653 | 31440.8917 | 834.0274 | 59.8724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6346 | 1.6346 | No Evaluation | -653 | 31443.4837 | 833.1521
23 | 2011-03-14 06:09 | -0.208 | 2011-03-14 06:10 | 40616.2566 | 60.028 | 60.0315 | 40616.2566 | 59.79 | 59.8263 | -473.1516 | 59.8259 | -472.0986 | 59.8239 | -469.7268 | 59.8237 | -467.1296 | 59.8239 | -467.611 | 60.0315 | 970.6714 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 26752.5693 | -205.691 | 59.8263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6539 | 1.6539 | No Evaluation | -653 | 26452.9353 | 1134.3539 | 59.8259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6504 | 1.6504 | No Evaluation | -653 | 26534.329 | 1137.1545 | 59.8248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6421 | 1.6421 | No Evaluation | -653 | 26582.445 | 1143.9407 | 59.8237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.633 | 1.633 | No Evaluation | -653 | 26588.3353 | 1151.458 | 59.8239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6347 | 1.6347 | No Evaluation | -653 | 26597.6325 | 1150.0495
24 | 2011-03-14 07:08 | -0.127 | 2011-03-14 07:08 | 40616.2974 | 60.012 | 60.0054 | 40616.2974 | 59.841 | 59.8783 | -383.2163 | 59.8774 | -380.6679 | 59.8781 | -379.652 | 59.8781 | -382.8648 | 59.8781 | -382.7192 | 60.0054 | 486.9663 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 29065.1851 | -35.0982 | 59.8783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3398 | 1.3398 | No Evaluation | -653 | 29072.7718 | 794.7883 | 59.8774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3308 | 1.3308 | No Evaluation | -653 | 29071.8895 | 800.3895 | 59.8771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3273 | 1.3273 | No Evaluation | -653 | 29079.8132 | 802.5971 | 59.8781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3379 | 1.3379 | No Evaluation | -653 | 29087.1309 | 795.9345 | 59.8781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3374 | 1.3374 | No Evaluation | -653 | 29088.0671 | 796.2766
25 | 2011-03-16 20:45 | -0.074 | 2011-03-16 20:45 | 40618.8647 | 59.985 | 59.9876 | 40618.8647 | 59.866 | 59.8989 | -455.886 | 59.9086 | -503.0237 | 59.9138 | -507.2286 | 59.9136 | -542.0638 | 59.9138 | -543.8227 | 59.9876 | 397.5629 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 33412.5537 | 80.8142 | 59.8989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.566 | 1.566 | No Evaluation | -653 | 33249.2561 | 660.4559 | 59.9086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7584 | 1.7584 | No Evaluation | -653 | 33242.6055 | 597.0244 | 59.9091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7701 | 1.7701 | No Evaluation | -653 | 33251.9169 | 593.6318 | 59.9136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8768 | 1.8768 | No Evaluation | -653 | 33257.7374 | 564.4807 | 59.9138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8821 | 1.8821 | No Evaluation | -653 | 33257.8378 | 563.1149
26 | 2011-03-23 14:46 | -0.063 | 2011-03-23 14:47 | 40625.6158 | 59.995 | 59.9897 | 40625.6158 | 59.706 | 59.9073 | -807.1876 | 59.9247 | -956.5729 | 59.9272 | -964.2482 | 59.9268 | -990.4233 | 59.9272 | -996.2987 | 59.9897 | 621.1687 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 38733.6201 | 66.9331 | 59.9073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6337 | 2.6337 | No Evaluation | -653 | 38263.9715 | 605.4298 | 59.9247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3396 | 3.3396 | No Evaluation | -653 | 38265.808 | 491.6197 | 59.9253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3685 | 3.3685 | No Evaluation | -653 | 38253.6957 | 487.9705 | 59.9268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.452 | 3.452 | No Evaluation | -653 | 38257.7561 | 477.7802 | 59.9272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4742 | 3.4742 | No Evaluation | -653 | 38255.9157 | 475.1548
27 | 2011-03-24 13:59 | -0.182 | 2011-03-24 13:59 | 40626.5827 | 59.977 | 59.9981 | 40626.5827 | 59.799 | 59.8123 | -268.7678 | 59.8224 | -283.9551 | 59.8211 | -285.693 | 59.8205 | -280.7817 | 59.8211 | -281.7167 | 59.9981 | 498.3148 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 35353.7969 | 12.2433 | 59.8123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93757 | 0.93757 | No Evaluation | -653 | 35176.6434 | 1225.77 | 59.8224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99169 | 0.99169 | No Evaluation | -653 | 35214.6395 | 1159.5379 | 59.8236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99855 | 0.99855 | No Evaluation | -653 | 35226.4599 | 1151.6515 | 59.8205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98092 | 0.98092 | No Evaluation | -653 | 35238.0857 | 1172.1333 | 59.8211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98434 | 0.98434 | No Evaluation | -653 | 35240.8045 | 1168.1004
28 | 2011-03-25 16:13 | -0.172 | 2011-03-25 16:13 | 40627.676 | 59.996 | 60.0142 | 40627.676 | 59.813 | 59.8277 | -261.0249 | 59.8344 | -270.5909 | 59.8458 | -280.7618 | 59.8449 | -288.1984 | 59.8458 | -289.6245 | 60.0142 | 553.3828 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 40151.54 | -93.0512 | 59.8277 | 66.7328 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9122 | 0.9122 | No Evaluation | -653 | 39958.5318 | 1125.0198 | 59.8344 | 66.8728 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94599 | 0.94599 | No Evaluation | -653 | 39985.1523 | 1081.1782 | 59.8407 | 67.0127 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98005 | 0.98005 | No Evaluation | -653 | 39984.1218 | 1040.048 | 59.8449 | 67.0333 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0044 | 1.0044 | No Evaluation | -653 | 39989.8819 | 1012.5088 | 59.8458 | 67.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0096 | 1.0096 | No Evaluation | -653 | 39989.0825 | 1006.7688
29 | 2011-03-29 06:43 | -0.099 | 2011-03-29 06:43 | 40631.2799 | 59.962 | 59.9635 | 40631.28 | 59.746 | 59.8406 | -630.9477 | 59.8629 | -741.8099 | 59.8641 | -737.6064 | 59.8632 | -743.0239 | 59.8641 | -748.5698 | 59.9635 | 742.8181 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 31093.9292 | 238.3449 | 59.8406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1128 | 2.1128 | No Evaluation | -653 | 30933.7891 | 1041.0696 | 59.8629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5807 | 2.5807 | No Evaluation | -653 | 31019.3119 | 895.5456 | 59.8625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5727 | 2.5727 | No Evaluation | -653 | 31034.6021 | 897.5788 | 59.8632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5901 | 2.5901 | No Evaluation | -653 | 31031.3079 | 893.1582 | 59.8641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6119 | 2.6119 | No Evaluation | -653 | 31034.9238 | 887.6947
30 | 2011-03-31 12:21 | -0.112 | 2011-03-31 12:21 | 40633.5149 | 59.987 | 59.9865 | 40633.5149 | 59.86 | 59.8744 | -375.7795 | 59.8756 | -379.5978 | 59.8747 | -372.3801 | 59.8747 | -378.8763 | 59.8747 | -378.9502 | 59.9865 | 421.0469 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 31970.3716 | 88.1533 | 59.8744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3136 | 1.3136 | No Evaluation | -653 | 31779.4676 | 819.9794 | 59.8756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3271 | 1.3271 | No Evaluation | -653 | 31784.7109 | 812.5206 | 59.8734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3012 | 1.3012 | No Evaluation | -653 | 31784.3129 | 826.9364 | 59.8747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3171 | 1.3171 | No Evaluation | -653 | 31774.7697 | 818.0643 | 59.8747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3169 | 1.3169 | No Evaluation | -653 | 31774.6436 | 818.171
31 | 2011-04-05 22:02 | -0.09 | 2011-04-05 22:02 | 40638.9181 | 59.912 | 59.9182 | 40638.9181 | 59.717 | 59.835 | -628.6462 | 59.8339 | -616.9437 | 59.8286 | -599.7632 | 59.8295 | -587.131 | 59.8286 | -580.0309 | 59.9182 | 518.4755 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 30986.4536 | 533.8301 | 59.835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1776 | 2.1776 | No Evaluation | -653 | 30797.5086 | 1077.4417 | 59.8339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1481 | 2.1481 | No Evaluation | -653 | 30837.1769 | 1084.9076 | 59.8317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0953 | 2.0953 | No Evaluation | -653 | 30850.3342 | 1098.8174 | 59.8295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0427 | 2.0427 | No Evaluation | -653 | 30845.3815 | 1113.3623 | 59.8286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0219 | 2.0219 | No Evaluation | -653 | 30848.2909 | 1119.3165
32 | 2011-04-20 13:40 | -0.145 | 2011-04-20 13:41 | 40653.5701 | 60.022 | 60.0246 | 40653.5701 | 59.824 | 59.8623 | -486.5853 | 59.8759 | -529.8426 | 59.8801 | -534.279 | 59.8788 | -540.168 | 59.8801 | -544.2105 | 60.0246 | 785.5412 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 41619.9902 | -160.8063 | 59.8623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6919 | 1.6919 | No Evaluation | -653 | 41377.9392 | 899.2714 | 59.8759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8463 | 1.8463 | No Evaluation | -653 | 41434.293 | 810.6524 | 59.8775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8663 | 1.8663 | No Evaluation | -653 | 41449.7543 | 800.2238 | 59.8788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8839 | 1.8839 | No Evaluation | -653 | 41460.3151 | 791.2196 | 59.8801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8999 | 1.8999 | No Evaluation | -653 | 41463.4122 | 783.2179
33 | 2011-04-27 23:27 | -0.133 | 2011-04-27 23:27 | 40660.9771 | 60.003 | 60.0075 | 40660.9772 | 59.791 | 59.8753 | -524.8812 | 59.876 | -526.7018 | 59.8746 | -522.4341 | 59.8749 | -522.2102 | 59.8746 | -520.7586 | 60.0075 | 691.8045 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 29943.1245 | -48.9699 | 59.8753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8295 | 1.8295 | No Evaluation | -653 | 29643.5089 | 814.3853 | 59.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8395 | 1.8395 | No Evaluation | -653 | 29684.8485 | 809.7236 | 59.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8256 | 1.8256 | No Evaluation | -653 | 29706.4893 | 816.2523 | 59.8749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8248 | 1.8248 | No Evaluation | -653 | 29700.7563 | 816.6126 | 59.8746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8199 | 1.8199 | No Evaluation | -653 | 29703.5409 | 818.9388
34 | 2011-05-11 14:04 | -0.121 | 2011-05-11 14:05 | 40674.5866 | 60.0175 | 60.0087 | 40674.5867 | 59.8533 | 59.8822 | -577.2223 | 59.8901 | -612.6334 | 59.8874 | -599.1221 | 59.8875 | -599.3345 | 59.8874 | -599.2391 | 60.0087 | 726.0243 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 42265.9336 | -56.72 | 59.8822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0071 | 2.0071 | No Evaluation | -653 | 42054.1066 | 769.1879 | 59.8901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1414 | 2.1414 | No Evaluation | -653 | 42103.4453 | 717.3752 | 59.8874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0927 | 2.0927 | No Evaluation | -653 | 42114.0866 | 735.3854 | 59.8875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0942 | 2.0942 | No Evaluation | -653 | 42111.5734 | 734.8248 | 59.8874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0938 | 2.0938 | No Evaluation | -653 | 42113.4274 | 734.9805
35 | 2011-05-16 08:06 | -0.101 | 2011-05-16 08:07 | 40679.3379 | 60.002 | 59.9986 | 40679.3379 | 59.8701 | 59.8883 | -427.6693 | 59.892 | -441.6688 | 59.8972 | -457.1399 | 59.8967 | -463.1042 | 59.8972 | -464.9541 | 59.9986 | 471.0875 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 30202.7422 | 8.9676 | 59.8883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4936 | 1.4936 | No Evaluation | -653 | 30090.8742 | 729.1042 | 59.892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5441 | 1.5441 | No Evaluation | -653 | 30112.8644 | 705.5608 | 59.8954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5962 | 1.5962 | No Evaluation | -653 | 30124.5707 | 682.8118 | 59.8967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6166 | 1.6166 | No Evaluation | -653 | 30134.4171 | 674.3213 | 59.8972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6234 | 1.6234 | No Evaluation | -653 | 30136.7695 | 671.5392
36 | 2011-05-19 14:08 | -0.197 | 2011-05-19 14:08 | 40682.5888 | 59.9758 | 59.9756 | 40682.5889 | 59.7176 | 59.7529 | -449.0124 | 59.7684 | -480.6398 | 59.7784 | -498.6519 | 59.7772 | -502.4673 | 59.7784 | -505.2433 | 59.9756 | 995.0827 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 42909.6079 | 159.2744 | 59.7529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5621 | 1.5621 | No Evaluation | -653 | 42473.9933 | 1613.7036 | 59.7684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.679 | 1.679 | No Evaluation | -653 | 42560.7667 | 1512.441 | 59.7758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7413 | 1.7413 | No Evaluation | -653 | 42598.7379 | 1464.0678 | 59.7772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7539 | 1.7539 | No Evaluation | -653 | 42602.5289 | 1454.6373 | 59.7784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7645 | 1.7645 | No Evaluation | -653 | 42610.2337 | 1446.8797
37 | 2011-05-23 17:34 | -0.092 | 2011-05-23 17:35 | 40686.7324 | 59.9351 | 59.9352 | 40686.7324 | 59.8174 | 59.8231 | -476.745 | 59.8325 | -522.1166 | 59.8431 | -555.203 | 59.842 | -577.956 | 59.8431 | -583.9198 | 59.9352 | 533.3253 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 50589.6709 | 423.2889 | 59.8231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6641 | 1.6641 | No Evaluation | -653 | 50457.8744 | 1155.0221 | 59.8325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8169 | 1.8169 | No Evaluation | -653 | 50477.8532 | 1093.5016 | 59.8387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9319 | 1.9319 | No Evaluation | -653 | 50481.6939 | 1053.599 | 59.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0014 | 2.0014 | No Evaluation | -653 | 50486.375 | 1031.7185 | 59.8431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0253 | 2.0253 | No Evaluation | -653 | 50488.2642 | 1024.5223
38 | 2011-05-29 22:03 | -0.118 | 2011-05-29 22:03 | 40692.9188 | 59.906 | 59.906 | 40692.9188 | 59.748 | 59.7731 | -574.8064 | 59.7834 | -624.6141 | 59.7881 | -651.1735 | 59.7873 | -643.9486 | 59.7881 | -647.8566 | 59.906 | 762.3234 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 44769.7285 | 613.8253 | 59.7731 | 0.0075805 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0063 | 2.0063 | No Evaluation | -653 | 44439.2321 | 1481.3783 | 59.7834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1746 | 2.1746 | No Evaluation | -653 | 44479.8186 | 1414.2175 | 59.7885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2694 | 2.2694 | No Evaluation | -653 | 44483.343 | 1380.8028 | 59.7873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2451 | 2.2451 | No Evaluation | -653 | 44476.4353 | 1389.0797 | 59.7881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.26 | 2.26 | No Evaluation | -653 | 44477.9926 | 1383.9791
39 | 2011-06-22 13:18 | 0.08 | 2011-06-22 13:19 | 40716.5546 | 60.013 | 60.0336 | 40716.5546 | 60.081 | 60.0697 | -721.6185 | 60.0676 | -761.9839 | 60.0649 | -794.9615 | 60.0652 | -825.6014 | 60.0649 | -831.1721 | 60.0336 | -258.56 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 44769.1958 | -219.569 | 60.0697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.505 | 2.505 | No Evaluation | -653 | 44674.7623 | -455.2404 | 60.0676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6631 | 2.6631 | No Evaluation | -653 | 44560.394 | -441.2481 | 60.0663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7691 | 2.7691 | No Evaluation | -653 | 44477.2418 | -432.7632 | 60.0652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8662 | 2.8662 | No Evaluation | -653 | 44473.3103 | -425.5398 | 60.0649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8868 | 2.8868 | No Evaluation | -653 | 44456.9752 | -424.0674
40 | 2011-06-27 12:54 | -0.149 | 2011-06-27 12:54 | 40721.5375 | 59.977 | 59.9738 | 40721.5375 | 59.82 | 59.8297 | -459.8245 | 59.8371 | -484.4445 | 59.8426 | -498.1424 | 59.8419 | -502.2992 | 59.8426 | -504.7879 | 59.9738 | 661.2317 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56971.1396 | 171.4086 | 59.8297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6052 | 1.6052 | No Evaluation | -653 | 56795.8538 | 1111.9634 | 59.8371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6924 | 1.6924 | No Evaluation | -653 | 56805.8644 | 1063.4566 | 59.8409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7404 | 1.7404 | No Evaluation | -653 | 56824.3253 | 1038.8659 | 59.8419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7541 | 1.7541 | No Evaluation | -653 | 56831.1452 | 1032.1018 | 59.8426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7635 | 1.7635 | No Evaluation | -653 | 56832.6572 | 1027.5144
41 | 2011-07-18 09:13 | -0.097 | 2011-07-18 09:13 | 40742.3842 | 59.957 | 59.9576 | 40742.3842 | 59.859 | 59.8619 | -403.4077 | 59.8624 | -405.7845 | 59.8634 | -417.1324 | 59.8632 | -409.7193 | 59.8634 | -410.3063 | 59.9576 | 386.25 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 45315.0059 | 276.7062 | 59.8619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4102 | 1.4102 | No Evaluation | -653 | 45257.7578 | 902.0755 | 59.8624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4187 | 1.4187 | No Evaluation | -653 | 45274.106 | 898.3462 | 59.8649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4566 | 1.4566 | No Evaluation | -653 | 45285.6325 | 882.1482 | 59.8632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4306 | 1.4306 | No Evaluation | -653 | 45294.8707 | 893.1609 | 59.8634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4326 | 1.4326 | No Evaluation | -653 | 45296.7034 | 892.3075
42 | 2011-07-18 20:50 | -0.119 | 2011-07-18 20:51 | 40742.8685 | 60.007 | 60.0084 | 40742.8685 | 59.866 | 59.8751 | -448.2121 | 59.8799 | -463.9878 | 59.8807 | -465.0911 | 59.8804 | -466.0866 | 59.8807 | -467.0124 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -54.6898 | 59.8751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5645 | 1.5645 | No Evaluation | -653 | 56857.5725 | 815.3177 | 59.8799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6219 | 1.6219 | No Evaluation | -653 | 56872.1323 | 784.5325 | 59.8802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.626 | 1.626 | No Evaluation | -653 | 56878.6644 | 782.4109 | 59.8804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6294 | 1.6294 | No Evaluation | -653 | 56882.8589 | 780.6965 | 59.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6327 | 1.6327 | No Evaluation | -653 | 56884.0016 | 778.9891