## Instructions
Steps | To be completed for each event evaluated.
1 | Set-up Data collection in exact same order as the "Data" sheet of this work book. Data should be in this order:
Column A: Date and Time in this format, mm/dd/yy HH:MM:SS
Column B: Frequency Hz
Column C: Net Actual Interchange
Column D: Joint Owned Unit dynamic schedule
Column E: Non Conforming Load
Column F: Pumped Hydro
Column G: Ramping units
Column H: Transferred Frequency Response
Column I: Contingent BA Lost load or generation
Column J: BA Bias Setting
Column K: BA Load
2 | Note: Columns D, E, F, G and H are optional data. If you choose not to use these, leave the columns blank. Do not delete the columns. Use the sign (+/-) convention defined in FRS Form 1.
3 | Data compression must be turned off for each data point. Quality data will give you quality results in the evaluation.
4 | Data must be at 3 second sample rate for the full 25 minute minimum collection period that starts a minimum of two (2) minutes before the event begins and includes a minimum of 15 minutes after the beginning of the event.
The spreadsheet will work with up to 60 minutes of data. Be sure "Data" worksheet is clear of any old data.
If using PI historian as your data source, use "PasteSpecial/Values" to enter data into the spreadsheet. Do not include historian data collection formulas in the data. The data must be numbers not text.
5 | Once data is in place in the "Data" worksheet, determine when the beginning of the event occurred.
Scroll through the "Data" worksheet column B data of frequency and observe when frequency moves from the normal, pre-event frequency.
This will usually be a single change in frequency of 0.008 to 0.010 Hz more or less. Note the row number in the worksheet that this change occurs. In this sample data spreadsheet this occurs in row 313 of the data.
6 | Edit cell "C8" of the "Entry Data" worksheet, change the formula in the cell "C8" to reference the row number identified in step 5 above. In the sample data of this workbook this formula is: "=Data!A313"
If the correct row is selected, the "Graph 20 to 52s" worksheet will indicate the first change in frequency of the event on the center vertical grid line of the graph (Red Trend).
7 | Determine the end of the event to be evaluated. Use the same rules that are used for DCS only look at frequency instead of ACE. Scroll down the frequency data in column B of the "Data" worksheet until frequency reaches 60 Hz or the
pre-disturbance value. Note the row number in the worksheet that this occurs. In this sample data spreadsheet this occurs in row 427.
8 | Edit cell "C11" of the "Entry Data" worksheet, change the formula in the cell "C11" to reference the row number identified in step 7 above. In the sample data of this workbook this formula is: "=Data!A427"
9 | In cell "R41" of the "Evaluation" spreadsheet, enter the MW value of the unit(s) that tripped (from the Master Event List). This is only necessary for the "Interconnection" evaluation if you're interested.
It is not necessary to do this for the BA evaluation but it will provide a comparison of the BA frequency response as compared to the Interconnection frequency response.
10 | Use the "copy" button provided to copy the evaluation and event specific data for the "FRS Form 1" of this field trial. This data is summarized in the correct order on worksheet "Form 1 Summary Data" of this workbook.
Use PasteSpecial/Values when pasting the data into FRS Form 1 on the appropriate event row.
Steps | To be completed once at the initial setup of the evaluation spreadsheet for your BA.
A | Enter the Balancing Authority name as you want it to appear on the graphs in cell "B1" of the "Entry Data" worksheet. For example: "NYISO".
B | Enter your Balancing Authorities Frequency Response Obligation in cell "B2" of the "Entry Data" worksheet. For example: -80 MW/0.1 Hz (This value could change annually)
C | For informational and educational purposes, a "Sustained" performance evaluation is provided in the "Evaluation" worksheet and in the "Sustained" Graph. This evaluation uses a Time Constant (TC) to model the frequency response of your BA.
The time constant is located in cell "L13" of the "Evaluation" spreadsheet and should be edited for the types of generators in your BA. Presently this time constant is set at 0.35.
The higher the value of the time constant, the faster the delivery of frequency response is expected. Setting the TC to 1.0 effectively turns off the delay and instantaneous frequency response will be modeled. Do not set higher than 1.0.
This time constant is only used in the "Sustained" evaluation and is not used for the Field Trial evaluation of performance to the FRO.
A typical setting for this time constant is 0.08 to 0.15 for hydro units, 0.10 to 0.20 for large steam turbines and 0.20 to 0.40 for combustion turbines.
By observing the slope of your "Interchange Actual" on the "Sustained" Graph, adjust the time constant until the initial slope of the "Target" is similar.
When set appropriately, the "Target" trend on the "Sustained" graph will model what Interchange Actual should have done during the event recovery period based on your minimum FRO.
Note: For ease of use, only the necessary worksheets are displayed. If you are interested in viewing graphs and other hidden worksheets, select the "tab" at the bottom, right click, select unhide and select the worksheet you wish to unhide.

## Data
|  |  | JOU | Non- |  |  | Transferred | Contingent
|  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA
|  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load
|  | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting
Time (T) | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW
2009-10-12 02:12 | 59.981 | 3669.8784 | 350 | 351.3615 | 0 | 0 | 10 | 15 | -103 | 7500
2009-10-12 02:12 | 59.98 | 3671.6997 | 350 | 351.3615 | 0 | 0.5 | 10 | 15 | -103 | 7500.33
2009-10-12 02:12 | 59.982 | 3670.9492 | 350 | 351.3615 | 0 | 1 | 10 | 15 | -103 | 7500.66
2009-10-12 02:12 | 59.981 | 3671.5481 | 350 | 357.9475 | 0 | 1.5 | 10 | 15 | -103 | 7500.99
2009-10-12 02:12 | 59.981 | 3672.3103 | 350 | 357.9475 | 0 | 2 | 10 | 15 | -103 | 7501.32
2009-10-12 02:12 | 59.982 | 3672.1741 | 350 | 357.9475 | 0 | 2.5 | 10 | 15 | -103 | 7501.65
2009-10-12 02:12 | 59.979 | 3672.2761 | 350 | 357.9475 | 0 | 3 | 10 | 15 | -103 | 7501.98
2009-10-12 02:12 | 59.98 | 3674.5081 | 350 | 357.9475 | 0 | 3.5 | 10 | 15 | -103 | 7502.31
2009-10-12 02:12 | 59.983 | 3673.8438 | 350 | 360.2347 | 0 | 4 | 10 | 15 | -103 | 7502.64
2009-10-12 02:12 | 59.986 | 3672.1062 | 350 | 360.2347 | 0 | 4.5 | 10 | 15 | -103 | 7502.97
2009-10-12 02:12 | 59.98 | 3669.3303 | 350 | 360.2347 | 0 | 5 | 10 | 15 | -103 | 7503.3
2009-10-12 02:13 | 59.976 | 3671.5005 | 350 | 360.2347 | 0 | 5.5 | 10 | 15 | -103 | 7503.63
2009-10-12 02:13 | 59.979 | 3673.5603 | 350 | 360.2347 | 0 | 6 | 10 | 15 | -103 | 7503.96
2009-10-12 02:13 | 59.981 | 3673.8342 | 350 | 346.5259 | 0 | 6.5 | 10 | 15 | -103 | 7504.29
2009-10-12 02:13 | 59.987 | 3671.8872 | 350 | 346.5259 | 0 | 7 | 10 | 15 | -103 | 7504.62
2009-10-12 02:13 | 59.99 | 3671.2205 | 350 | 346.5259 | 0 | 7.5 | 10 | 15 | -103 | 7504.95
2009-10-12 02:13 | 59.994 | 3671.5603 | 350 | 346.5259 | 0 | 8 | 10 | 15 | -103 | 7505.28
2009-10-12 02:13 | 59.995 | 3670.772 | 350 | 346.5259 | 0 | 8.5 | 10 | 15 | -103 | 7505.61
2009-10-12 02:13 | 59.995 | 3668.3621 | 350 | 296.4434 | 0 | 9 | 10 | 15 | -103 | 7505.94
2009-10-12 02:13 | 59.995 | 3668.2446 | 350 | 296.4434 | 0 | 9.5 | 10 | 15 | -103 | 7506.27
2009-10-12 02:13 | 59.994 | 3669.2913 | 350 | 296.4434 | 0 | 10 | 10 | 15 | -103 | 7506.6
2009-10-12 02:13 | 59.994 | 3671.2539 | 350 | 296.4434 | 0 | 10.5 | 10 | 15 | -103 | 7506.93
2009-10-12 02:13 | 59.997 | 3670.6833 | 350 | 296.4434 | 0 | 11 | 10 | 15 | -103 | 7507.26
2009-10-12 02:13 | 60.001 | 3670.2117 | 350 | 341.0612 | 0 | 11.5 | 10 | 15 | -103 | 7507.59
2009-10-12 02:13 | 60.001 | 3670.7124 | 350 | 341.0612 | 0 | 12 | 10 | 15 | -103 | 7507.92
2009-10-12 02:13 | 60.003 | 3671.1836 | 350 | 341.0612 | 0 | 12.5 | 10 | 15 | -103 | 7508.25
2009-10-12 02:13 | 60.005 | 3671.2271 | 350 | 341.0612 | 0 | 13 | 10 | 15 | -103 | 7508.58
2009-10-12 02:13 | 60.003 | 3670.1897 | 350 | 341.0612 | 0 | 13.5 | 10 | 15 | -103 | 7508.91
2009-10-12 02:13 | 60.001 | 3671.0923 | 350 | 322.8263 | 0 | 14 | 10 | 15 | -103 | 7509.24
2009-10-12 02:13 | 60.003 | 3670.6699 | 350 | 322.8263 | 0 | 14.5 | 10 | 15 | -103 | 7509.57
2009-10-12 02:13 | 60.005 | 3669.8992 | 350 | 322.8263 | 0 | 15 | 10 | 15 | -103 | 7509.9
2009-10-12 02:14 | 60.001 | 3670.1995 | 350 | 322.8263 | 0 | 15.5 | 10 | 15 | -103 | 7510.23
2009-10-12 02:14 | 60.001 | 3671.6284 | 350 | 322.8263 | 0 | 16 | 10 | 15 | -103 | 7510.56
2009-10-12 02:14 | 60.004 | 3671.9683 | 350 | 321.5444 | 0 | 16.5 | 10 | 15 | -103 | 7510.89
2009-10-12 02:14 | 60.004 | 3671.4443 | 350 | 321.5444 | 0 | 17 | 10 | 15 | -103 | 7511.22
2009-10-12 02:14 | 60.004 | 3671.8752 | 350 | 321.5444 | 0 | 17.5 | 10 | 15 | -103 | 7511.55
2009-10-12 02:14 | 60.003 | 3671.0657 | 350 | 321.5444 | 0 | 18 | 10 | 15 | -103 | 7511.88
2009-10-12 02:14 | 60.002 | 3673.2351 | 350 | 321.5444 | 0 | 18.5 | 10 | 15 | -103 | 7512.21
2009-10-12 02:14 | 60.001 | 3673.4978 | 350 | 362.1363 | 0 | 19 | 10 | 15 | -103 | 7512.54
2009-10-12 02:14 | 59.999 | 3672.75 | 350 | 362.1363 | 0 | 19.5 | 10 | 15 | -103 | 7512.87
2009-10-12 02:14 | 59.997 | 3673.1863 | 350 | 362.1363 | 0 | 20 | 10 | 15 | -103 | 7513.2
2009-10-12 02:14 | 59.998 | 3673.5764 | 350 | 362.1363 | 0 | 20.5 | 10 | 15 | -103 | 7513.53
2009-10-12 02:14 | 59.995 | 3673.365 | 350 | 362.1363 | 0 | 21 | 10 | 15 | -103 | 7513.86
2009-10-12 02:14 | 59.993 | 3672.093 | 350 | 336.3118 | 0 | 21.5 | 10 | 15 | -103 | 7514.19
2009-10-12 02:14 | 59.996 | 3671.998 | 350 | 336.3118 | 0 | 22 | 10 | 15 | -103 | 7514.52
2009-10-12 02:14 | 59.999 | 3671.0725 | 350 | 336.3118 | 0 | 22.5 | 10 | 15 | -103 | 7514.85
2009-10-12 02:14 | 60.005 | 3670.9568 | 350 | 336.3118 | 0 | 23 | 10 | 15 | -103 | 7515.18
2009-10-12 02:14 | 60.007 | 3670.8928 | 350 | 336.3118 | 0 | 23.5 | 10 | 15 | -103 | 7515.51
2009-10-12 02:14 | 60.005 | 3670.1619 | 350 | 316.4431 | 0 | 24 | 10 | 15 | -103 | 7515.84
2009-10-12 02:14 | 60.002 | 3670.6199 | 350 | 316.4431 | 0 | 24.5 | 10 | 15 | -103 | 7516.17
2009-10-12 02:14 | 59.997 | 3672.7129 | 350 | 316.4431 | 0 | 25 | 10 | 15 | -103 | 7516.5
2009-10-12 02:15 | 59.999 | 3671.0703 | 350 | 316.4431 | 0 | 25.5 | 10 | 15 | -103 | 7516.83
2009-10-12 02:15 | 60.007 | 3670.8257 | 350 | 316.4431 | 0 | 26 | 10 | 15 | -103 | 7517.16
2009-10-12 02:15 | 60.01 | 3671.8091 | 350 | 325.4643 | 0 | 26.5 | 10 | 15 | -103 | 7517.49
2009-10-12 02:15 | 60.009 | 3673.3633 | 350 | 325.4643 | 0 | 27 | 10 | 15 | -103 | 7517.82
2009-10-12 02:15 | 60.003 | 3673.2554 | 350 | 325.4643 | 0 | 27.5 | 10 | 15 | -103 | 7518.15
2009-10-12 02:15 | 59.995 | 3674.4146 | 350 | 325.4643 | 0 | 28 | 10 | 15 | -103 | 7518.48
2009-10-12 02:15 | 59.994 | 3674.7546 | 350 | 325.4643 | 0 | 28.5 | 10 | 15 | -103 | 7518.81
2009-10-12 02:15 | 60 | 3674.29 | 350 | 336.6142 | 0 | 29 | 10 | 15 | -103 | 7519.14
2009-10-12 02:15 | 60.001 | 3675.1572 | 350 | 336.6142 | 0 | 29.5 | 10 | 15 | -103 | 7519.47
2009-10-12 02:15 | 59.998 | 3675.1655 | 350 | 336.6142 | 0 | 30 | 10 | 15 | -103 | 7519.8
2009-10-12 02:15 | 59.995 | 3674.4417 | 350 | 336.6142 | 0 | 30.5 | 10 | 15 | -103 | 7520.13
2009-10-12 02:15 | 59.986 | 3674.9065 | 350 | 336.6142 | 0 | 31 | 10 | 15 | -103 | 7520.46
2009-10-12 02:15 | 59.986 | 3676.7144 | 350 | 316.7262 | 0 | 31.5 | 10 | 15 | -103 | 7520.79
2009-10-12 02:15 | 59.988 | 3677.791 | 350 | 316.7262 | 0 | 32 | 10 | 15 | -103 | 7521.12
2009-10-12 02:15 | 59.989 | 3675.543 | 350 | 316.7262 | 0 | 32.5 | 10 | 15 | -103 | 7521.45
2009-10-12 02:15 | 59.987 | 3676.593 | 350 | 316.7262 | 0 | 33 | 10 | 15 | -103 | 7521.78
2009-10-12 02:15 | 59.985 | 3677.2234 | 350 | 316.7262 | 0 | 33.5 | 10 | 15 | -103 | 7522.11
2009-10-12 02:15 | 59.983 | 3677.0671 | 350 | 320.1955 | 0 | 34 | 10 | 15 | -103 | 7522.44
2009-10-12 02:15 | 59.982 | 3678.4553 | 350 | 320.1955 | 0 | 34.5 | 10 | 15 | -103 | 7522.77
2009-10-12 02:16 | 59.984 | 3679.2278 | 350 | 320.1955 | 0 | 35 | 10 | 15 | -103 | 7523.1
2009-10-12 02:16 | 59.985 | 3679.0591 | 350 | 320.1955 | 0 | 35.5 | 10 | 15 | -103 | 7523.43
2009-10-12 02:16 | 59.987 | 3677.627 | 350 | 320.1955 | 0 | 36 | 10 | 15 | -103 | 7523.76
2009-10-12 02:16 | 59.99 | 3676.4094 | 350 | 341.8661 | 0 | 36.5 | 10 | 15 | -103 | 7524.09
2009-10-12 02:16 | 59.987 | 3677.5281 | 350 | 341.8661 | 0 | 37 | 10 | 15 | -103 | 7524.42
2009-10-12 02:16 | 59.983 | 3676.9148 | 350 | 341.8661 | 0 | 37.5 | 10 | 15 | -103 | 7524.75
2009-10-12 02:16 | 59.979 | 3678.0864 | 350 | 341.8661 | 0 | 38 | 10 | 15 | -103 | 7525.08
2009-10-12 02:16 | 59.983 | 3680.1631 | 350 | 341.8661 | 0 | 38.5 | 10 | 15 | -103 | 7525.41
2009-10-12 02:16 | 59.986 | 3679.2134 | 350 | 348.5978 | 0 | 39 | 10 | 15 | -103 | 7525.74
2009-10-12 02:16 | 59.988 | 3677.6528 | 350 | 348.5978 | 0 | 39.5 | 10 | 15 | -103 | 7526.07
2009-10-12 02:16 | 59.983 | 3677.6777 | 350 | 348.5978 | 0 | 40 | 10 | 15 | -103 | 7526.4
2009-10-12 02:16 | 59.978 | 3679.2791 | 350 | 348.5978 | 0 | 40.5 | 10 | 15 | -103 | 7526.73
2009-10-12 02:16 | 59.979 | 3678.7295 | 350 | 348.5978 | 0 | 41 | 10 | 15 | -103 | 7527.06
2009-10-12 02:16 | 59.989 | 3680.2869 | 350 | 329.085 | 0 | 41.5 | 10 | 15 | -103 | 7527.39
2009-10-12 02:16 | 59.988 | 3679.0259 | 350 | 329.085 | 0 | 42 | 10 | 15 | -103 | 7527.72
2009-10-12 02:16 | 59.983 | 3678.4885 | 350 | 329.085 | 0 | 42.5 | 10 | 15 | -103 | 7528.05
2009-10-12 02:16 | 59.991 | 3678.7202 | 350 | 329.085 | 0 | 43 | 10 | 15 | -103 | 7528.38
2009-10-12 02:16 | 59.989 | 3678.9707 | 350 | 329.085 | 0 | 43.5 | 10 | 15 | -103 | 7528.71
2009-10-12 02:16 | 59.993 | 3679.3901 | 350 | 342.4182 | 0 | 44 | 10 | 15 | -103 | 7529.04
2009-10-12 02:16 | 59.995 | 3678.3301 | 350 | 342.4182 | 0 | 44.5 | 10 | 15 | -103 | 7529.37
2009-10-12 02:17 | 59.998 | 3678.4905 | 350 | 342.4182 | 0 | 45 | 10 | 15 | -103 | 7529.7
2009-10-12 02:17 | 59.998 | 3676.7632 | 350 | 342.4182 | 0 | 45.5 | 10 | 15 | -103 | 7530.03
2009-10-12 02:17 | 59.999 | 3678.9509 | 350 | 342.4182 | 0 | 46 | 10 | 15 | -103 | 7530.36
2009-10-12 02:17 | 59.995 | 3679.1484 | 350 | 338.7946 | 0 | 46.5 | 10 | 15 | -103 | 7530.69
2009-10-12 02:17 | 59.992 | 3679.9033 | 350 | 338.7946 | 0 | 47 | 10 | 15 | -103 | 7531.02
2009-10-12 02:17 | 59.995 | 3678.9966 | 350 | 338.7946 | 0 | 47.5 | 10 | 15 | -103 | 7531.35
2009-10-12 02:17 | 60.001 | 3677.8604 | 350 | 338.7946 | 0 | 48 | 10 | 15 | -103 | 7531.68
2009-10-12 02:17 | 60.003 | 3678.2668 | 350 | 338.7946 | 0 | 48.5 | 10 | 15 | -103 | 7532.01
2009-10-12 02:17 | 60.009 | 3677.6855 | 350 | 335.931 | 0 | 49 | 10 | 15 | -103 | 7532.34
2009-10-12 02:17 | 60.009 | 3678.3638 | 350 | 335.931 | 0 | 49.5 | 10 | 15 | -103 | 7532.67
2009-10-12 02:17 | 60.012 | 3679.2087 | 350 | 335.931 | 0 | 50 | 10 | 15 | -103 | 7533
2009-10-12 02:17 | 60.011 | 3678.6526 | 350 | 335.931 | 0 | 50.5 | 10 | 15 | -103 | 7533.33
2009-10-12 02:17 | 60.008 | 3679.0566 | 350 | 335.931 | 0 | 51 | 10 | 15 | -103 | 7533.66
2009-10-12 02:17 | 60.007 | 3680.6042 | 350 | 339.7124 | 0 | 51.5 | 10 | 15 | -103 | 7533.99
2009-10-12 02:17 | 60.012 | 3679.8059 | 350 | 339.7124 | 0 | 52 | 10 | 15 | -103 | 7534.32
2009-10-12 02:17 | 60.013 | 3680.2627 | 350 | 339.7124 | 0 | 52.5 | 10 | 15 | -103 | 7534.65
2009-10-12 02:17 | 60.01 | 3679.8511 | 350 | 339.7124 | 0 | 53 | 10 | 15 | -103 | 7534.98
2009-10-12 02:17 | 60.007 | 3679.946 | 350 | 339.7124 | 0 | 53.5 | 10 | 15 | -103 | 7535.31
2009-10-12 02:17 | 60.009 | 3679.4399 | 350 | 332.0247 | 0 | 54 | 10 | 15 | -103 | 7535.64
2009-10-12 02:17 | 60.006 | 3679.5166 | 350 | 332.0247 | 0 | 54.5 | 10 | 15 | -103 | 7535.97
2009-10-12 02:18 | 60.009 | 3679.8879 | 350 | 332.0247 | 0 | 55 | 10 | 15 | -103 | 7536.3
2009-10-12 02:18 | 60.009 | 3679.0596 | 350 | 332.0247 | 0 | 55.5 | 10 | 15 | -103 | 7536.63
2009-10-12 02:18 | 60.009 | 3679.2607 | 350 | 332.0247 | 0 | 56 | 10 | 15 | -103 | 7536.96
2009-10-12 02:18 | 60.009 | 3679.0247 | 350 | 330.759 | 0 | 56.5 | 10 | 15 | -103 | 7537.29
2009-10-12 02:18 | 60.004 | 3679.1521 | 350 | 330.759 | 0 | 57 | 10 | 15 | -103 | 7537.62
2009-10-12 02:18 | 60.001 | 3678.2952 | 350 | 330.759 | 0 | 57.5 | 10 | 15 | -103 | 7537.95
2009-10-12 02:18 | 59.993 | 3678.2488 | 350 | 330.759 | 0 | 58 | 10 | 15 | -103 | 7538.28
2009-10-12 02:18 | 59.991 | 3677.8296 | 350 | 330.759 | 0 | 58.5 | 10 | 15 | -103 | 7538.61
2009-10-12 02:18 | 59.992 | 3677.9548 | 350 | 323.42 | 0 | 59 | 10 | 15 | -103 | 7538.94
2009-10-12 02:18 | 59.994 | 3676.6658 | 350 | 323.42 | 0 | 59.5 | 10 | 15 | -103 | 7539.27
2009-10-12 02:18 | 59.994 | 3677.0933 | 350 | 323.42 | 0 | 60 | 10 | 15 | -103 | 7539.6
2009-10-12 02:18 | 59.995 | 3676.4006 | 350 | 323.42 | 0 | 60.5 | 10 | 15 | -103 | 7539.93
2009-10-12 02:18 | 59.99 | 3678.5156 | 350 | 323.42 | 0 | 61 | 10 | 15 | -103 | 7540.26
2009-10-12 02:18 | 59.99 | 3680.1965 | 350 | 342.3509 | 0 | 61.5 | 10 | 15 | -103 | 7540.59
2009-10-12 02:18 | 59.983 | 3678.7432 | 350 | 342.3509 | 0 | 62 | 10 | 15 | -103 | 7540.92
2009-10-12 02:18 | 59.977 | 3677.9211 | 350 | 342.3509 | 0 | 62.5 | 10 | 15 | -103 | 7541.25
2009-10-12 02:18 | 59.989 | 3680.2537 | 350 | 342.3509 | 0 | 63 | 10 | 15 | -103 | 7541.58
2009-10-12 02:18 | 59.995 | 3681.3293 | 350 | 342.3509 | 0 | 63.5 | 10 | 15 | -103 | 7541.91
2009-10-12 02:18 | 59.994 | 3678.6555 | 350 | 345.0818 | 0 | 64 | 10 | 15 | -103 | 7542.24
2009-10-12 02:18 | 59.989 | 3677.78 | 350 | 345.0818 | 0 | 64.5 | 10 | 15 | -103 | 7542.57
2009-10-12 02:18 | 59.986 | 3678.4268 | 350 | 345.0818 | 0 | 65 | 10 | 15 | -103 | 7542.9
2009-10-12 02:19 | 59.984 | 3678.2778 | 350 | 345.0818 | 0 | 65.5 | 10 | 15 | -103 | 7543.23
2009-10-12 02:19 | 59.985 | 3677.8223 | 350 | 345.0818 | 0 | 66 | 10 | 15 | -103 | 7543.56
2009-10-12 02:19 | 59.986 | 3677.3975 | 350 | 346.5374 | 0 | 66.5 | 10 | 15 | -103 | 7543.89
2009-10-12 02:19 | 59.986 | 3677.917 | 350 | 346.5374 | 0 | 67 | 10 | 15 | -103 | 7544.22
2009-10-12 02:19 | 59.98 | 3678.6167 | 350 | 346.5374 | 0 | 67.5 | 10 | 15 | -103 | 7544.55
2009-10-12 02:19 | 59.981 | 3678.9626 | 350 | 346.5374 | 0 | 68 | 10 | 15 | -103 | 7544.88
2009-10-12 02:19 | 59.989 | 3680.7373 | 350 | 346.5374 | 0 | 68.5 | 10 | 15 | -103 | 7545.21
2009-10-12 02:19 | 60.007 | 3680.0449 | 350 | 342.9058 | 0 | 69 | 10 | 15 | -103 | 7545.54
2009-10-12 02:19 | 60.007 | 3674.0762 | 350 | 342.9058 | 0 | 69.5 | 10 | 15 | -103 | 7545.87
2009-10-12 02:19 | 59.986 | 3676.2222 | 350 | 342.9058 | 0 | 70 | 10 | 15 | -103 | 7546.2
2009-10-12 02:19 | 59.981 | 3677.4971 | 350 | 342.9058 | 0 | 70.5 | 10 | 15 | -103 | 7546.53
2009-10-12 02:19 | 59.974 | 3677.49 | 350 | 342.9058 | 0 | 71 | 10 | 15 | -103 | 7546.86
2009-10-12 02:19 | 59.976 | 3675.437 | 350 | 340.0944 | 0 | 71.5 | 10 | 15 | -103 | 7547.19
2009-10-12 02:19 | 59.974 | 3680.4509 | 350 | 340.0944 | 0 | 72 | 10 | 15 | -103 | 7547.52
2009-10-12 02:19 | 59.977 | 3683.8286 | 350 | 340.0944 | 0 | 72.5 | 10 | 15 | -103 | 7547.85
2009-10-12 02:19 | 59.979 | 3682.8433 | 350 | 340.0944 | 0 | 73 | 10 | 15 | -103 | 7548.18
2009-10-12 02:19 | 59.982 | 3680.5657 | 350 | 340.0944 | 0 | 73.5 | 10 | 15 | -103 | 7548.51
2009-10-12 02:19 | 59.987 | 3678.229 | 350 | 342.7712 | 0 | 74 | 10 | 15 | -103 | 7548.84
2009-10-12 02:19 | 59.988 | 3675.7593 | 350 | 342.7712 | 0 | 74.5 | 10 | 15 | -103 | 7549.17
2009-10-12 02:20 | 59.987 | 3671.9424 | 350 | 342.7712 | 0 | 75 | 10 | 15 | -103 | 7549.5
2009-10-12 02:20 | 59.987 | 3670.4758 | 350 | 342.7712 | 0 | 75.5 | 10 | 15 | -103 | 7549.83
2009-10-12 02:20 | 59.985 | 3670.1287 | 350 | 342.7712 | 0 | 76 | 10 | 15 | -103 | 7550.16
2009-10-12 02:20 | 59.984 | 3672.0479 | 350 | 342.9099 | 0 | 76.5 | 10 | 15 | -103 | 7550.49
2009-10-12 02:20 | 59.983 | 3671.5757 | 350 | 342.9099 | 0 | 77 | 10 | 15 | -103 | 7550.82
2009-10-12 02:20 | 59.989 | 3672.4136 | 350 | 342.9099 | 0 | 77.5 | 10 | 15 | -103 | 7551.15
2009-10-12 02:20 | 59.988 | 3671.8823 | 350 | 342.9099 | 0 | 78 | 10 | 15 | -103 | 7551.48
2009-10-12 02:20 | 59.984 | 3671.3359 | 350 | 342.9099 | 0 | 78.5 | 10 | 15 | -103 | 7551.81
2009-10-12 02:20 | 59.983 | 3670.7258 | 350 | 343.286 | 0 | 79 | 10 | 15 | -103 | 7552.14
2009-10-12 02:20 | 59.981 | 3671.364 | 350 | 343.286 | 0 | 79.5 | 10 | 15 | -103 | 7552.47
2009-10-12 02:20 | 59.983 | 3671.4009 | 350 | 343.286 | 0 | 80 | 10 | 15 | -103 | 7552.8
2009-10-12 02:20 | 59.986 | 3672.1814 | 350 | 343.286 | 0 | 80.5 | 10 | 15 | -103 | 7553.13
2009-10-12 02:20 | 59.987 | 3670.2964 | 350 | 343.286 | 0 | 81 | 10 | 15 | -103 | 7553.46
2009-10-12 02:20 | 59.985 | 3668.5896 | 350 | 331.853 | 0 | 81.5 | 10 | 15 | -103 | 7553.79
2009-10-12 02:20 | 59.98 | 3669.9082 | 350 | 331.853 | 0 | 82 | 10 | 15 | -103 | 7554.12
2009-10-12 02:20 | 59.983 | 3670.2627 | 350 | 331.853 | 0 | 82.5 | 10 | 15 | -103 | 7554.45
2009-10-12 02:20 | 59.979 | 3669.3823 | 350 | 331.853 | 0 | 83 | 10 | 15 | -103 | 7554.78
2009-10-12 02:20 | 59.979 | 3670.4375 | 350 | 331.853 | 0 | 83.5 | 10 | 15 | -103 | 7555.11
2009-10-12 02:20 | 59.981 | 3671.4026 | 350 | 329.9882 | 0 | 84 | 10 | 15 | -103 | 7555.44
2009-10-12 02:20 | 59.98 | 3672.3718 | 350 | 329.9882 | 0 | 84.5 | 10 | 15 | -103 | 7555.77
2009-10-12 02:20 | 59.981 | 3671.947 | 350 | 329.9882 | 0 | 85 | 10 | 15 | -103 | 7556.1
2009-10-12 02:21 | 59.98 | 3670.7046 | 350 | 329.9882 | 0 | 85.5 | 10 | 15 | -103 | 7556.43
2009-10-12 02:21 | 59.977 | 3670.1372 | 350 | 329.9882 | 0 | 86 | 10 | 15 | -103 | 7556.76
2009-10-12 02:21 | 59.979 | 3672.3909 | 350 | 255.4442 | 0 | 86.5 | 10 | 15 | -103 | 7557.09
2009-10-12 02:21 | 59.979 | 3672.5579 | 350 | 255.4442 | 0 | 87 | 10 | 15 | -103 | 7557.42
2009-10-12 02:21 | 59.976 | 3672.6265 | 350 | 255.4442 | 0 | 87.5 | 10 | 15 | -103 | 7557.75
2009-10-12 02:21 | 59.972 | 3671.8003 | 350 | 255.4442 | 0 | 88 | 10 | 15 | -103 | 7558.08
2009-10-12 02:21 | 59.971 | 3673.8735 | 350 | 255.4442 | 0 | 88.5 | 10 | 15 | -103 | 7558.41
2009-10-12 02:21 | 59.973 | 3676.2627 | 350 | 254.8383 | 0 | 89 | 10 | 15 | -103 | 7558.74
2009-10-12 02:21 | 59.973 | 3676.8699 | 350 | 254.8383 | 0 | 89.5 | 10 | 15 | -103 | 7559.07
2009-10-12 02:21 | 59.971 | 3676.543 | 350 | 254.8383 | 0 | 90 | 10 | 15 | -103 | 7559.4
2009-10-12 02:21 | 59.975 | 3675.7524 | 350 | 254.8383 | 0 | 90.5 | 10 | 15 | -103 | 7559.73
2009-10-12 02:21 | 59.977 | 3675.2559 | 350 | 254.8383 | 0 | 91 | 10 | 15 | -103 | 7560.06
2009-10-12 02:21 | 59.975 | 3671.2769 | 350 | 257.147 | 0 | 91.5 | 10 | 15 | -103 | 7560.39
2009-10-12 02:21 | 59.98 | 3671.5933 | 350 | 257.147 | 0 | 92 | 10 | 15 | -103 | 7560.72
2009-10-12 02:21 | 59.979 | 3669.9629 | 350 | 257.147 | 0 | 92.5 | 10 | 15 | -103 | 7561.05
2009-10-12 02:21 | 59.982 | 3669.54 | 350 | 257.147 | 0 | 93 | 10 | 15 | -103 | 7561.38
2009-10-12 02:21 | 59.982 | 3668.7056 | 350 | 257.147 | 0 | 93.5 | 10 | 15 | -103 | 7561.71
2009-10-12 02:21 | 59.982 | 3667.6765 | 350 | 262.2894 | 0 | 94 | 10 | 15 | -103 | 7562.04
2009-10-12 02:21 | 59.981 | 3666.5994 | 350 | 262.2894 | 0 | 94.5 | 10 | 15 | -103 | 7562.37
2009-10-12 02:22 | 59.984 | 3666.9106 | 350 | 262.2894 | 0 | 95 | 10 | 15 | -103 | 7562.7
2009-10-12 02:22 | 59.985 | 3666.4048 | 350 | 262.2894 | 0 | 95.5 | 10 | 15 | -103 | 7563.03
2009-10-12 02:22 | 59.989 | 3667.4563 | 350 | 262.2894 | 0 | 96 | 10 | 15 | -103 | 7563.36
2009-10-12 02:22 | 59.993 | 3665.2617 | 350 | 256.6479 | 0 | 96.5 | 10 | 15 | -103 | 7563.69
2009-10-12 02:22 | 59.998 | 3664.031 | 350 | 256.6479 | 0 | 97 | 10 | 15 | -103 | 7564.02
2009-10-12 02:22 | 59.998 | 3663.2288 | 350 | 256.6479 | 0 | 97.5 | 10 | 15 | -103 | 7564.35
2009-10-12 02:22 | 60.007 | 3662.0549 | 350 | 256.6479 | 0 | 98 | 10 | 15 | -103 | 7564.68
2009-10-12 02:22 | 60.01 | 3662.0762 | 350 | 256.6479 | 0 | 98.5 | 10 | 15 | -103 | 7565.01
2009-10-12 02:22 | 60.014 | 3662.2239 | 350 | 256.3073 | 0 | 99 | 10 | 15 | -103 | 7565.34
2009-10-12 02:22 | 60.013 | 3663.7944 | 350 | 256.3073 | 0 | 99.5 | 10 | 15 | -103 | 7565.67
2009-10-12 02:22 | 60.008 | 3664.1392 | 350 | 256.3073 | 0 | 100 | 10 | 15 | -103 | 7566
2009-10-12 02:22 | 60.01 | 3664.1587 | 350 | 256.3073 | 0 | 100.5 | 10 | 15 | -103 | 7566.33
2009-10-12 02:22 | 60.019 | 3663.2646 | 350 | 256.3073 | 0 | 101 | 10 | 15 | -103 | 7566.66
2009-10-12 02:22 | 60.023 | 3661.9292 | 350 | 249.0864 | 0 | 101.5 | 10 | 15 | -103 | 7566.99
2009-10-12 02:22 | 60.02 | 3661.5122 | 350 | 249.0864 | 0 | 102 | 10 | 15 | -103 | 7567.32
2009-10-12 02:22 | 60.021 | 3658.6614 | 350 | 249.0864 | 0 | 102.5 | 10 | 15 | -103 | 7567.65
2009-10-12 02:22 | 60.02 | 3656.7854 | 350 | 249.0864 | 0 | 103 | 10 | 15 | -103 | 7567.98
2009-10-12 02:22 | 60.019 | 3658.126 | 350 | 249.0864 | 0 | 103.5 | 10 | 15 | -103 | 7568.31
2009-10-12 02:22 | 60.022 | 3657.7104 | 350 | 253.7425 | 0 | 104 | 10 | 15 | -103 | 7568.64
2009-10-12 02:22 | 60.025 | 3660.2275 | 350 | 253.7425 | 0 | 104.5 | 10 | 15 | -103 | 7568.97
2009-10-12 02:22 | 60.026 | 3659.2236 | 350 | 253.7425 | 0 | 105 | 10 | 15 | -103 | 7569.3
2009-10-12 02:23 | 60.02 | 3658.6687 | 350 | 253.7425 | 0 | 105.5 | 10 | 15 | -103 | 7569.63
2009-10-12 02:23 | 60.018 | 3658.1545 | 350 | 253.7425 | 0 | 106 | 10 | 15 | -103 | 7569.96
2009-10-12 02:23 | 60.018 | 3659.7776 | 350 | 257.4212 | 0 | 106.5 | 10 | 15 | -103 | 7570.29
2009-10-12 02:23 | 60.019 | 3660.8196 | 350 | 257.4212 | 0 | 107 | 10 | 15 | -103 | 7570.62
2009-10-12 02:23 | 60.019 | 3662.3872 | 350 | 257.4212 | 0 | 107.5 | 10 | 15 | -103 | 7570.95
2009-10-12 02:23 | 60.022 | 3662.0789 | 350 | 257.4212 | 0 | 108 | 10 | 15 | -103 | 7571.28
2009-10-12 02:23 | 60.022 | 3662.6782 | 350 | 257.4212 | 0 | 108.5 | 10 | 15 | -103 | 7571.61
2009-10-12 02:23 | 60.02 | 3663.5767 | 350 | 261.7382 | 0 | 109 | 10 | 15 | -103 | 7571.94
2009-10-12 02:23 | 60.02 | 3662.9592 | 350 | 261.7382 | 0 | 109.5 | 10 | 15 | -103 | 7572.27
2009-10-12 02:23 | 60.02 | 3662.5525 | 350 | 261.7382 | 0 | 110 | 10 | 15 | -103 | 7572.6
2009-10-12 02:23 | 60.02 | 3663.6006 | 350 | 261.7382 | 0 | 110.5 | 10 | 15 | -103 | 7572.93
2009-10-12 02:23 | 60.021 | 3663.9097 | 350 | 261.7382 | 0 | 111 | 10 | 15 | -103 | 7573.26
2009-10-12 02:23 | 60.018 | 3662.7913 | 350 | 271.876 | 0 | 111.5 | 10 | 15 | -103 | 7573.59
2009-10-12 02:23 | 60.014 | 3663.3958 | 350 | 271.876 | 0 | 112 | 10 | 15 | -103 | 7573.92
2009-10-12 02:23 | 60.014 | 3664.3154 | 350 | 271.876 | 0 | 112.5 | 10 | 15 | -103 | 7574.25
2009-10-12 02:23 | 60.013 | 3665.313 | 350 | 271.876 | 0 | 113 | 10 | 15 | -103 | 7574.58
2009-10-12 02:23 | 60.01 | 3666.1411 | 350 | 271.876 | 0 | 113.5 | 10 | 15 | -103 | 7574.91
2009-10-12 02:23 | 60.011 | 3666.7258 | 350 | 262.0735 | 0 | 114 | 10 | 15 | -103 | 7575.24
2009-10-12 02:23 | 60.011 | 3667.5454 | 350 | 262.0735 | 0 | 114.5 | 10 | 15 | -103 | 7575.57
2009-10-12 02:24 | 60.012 | 3666.6882 | 350 | 262.0735 | 0 | 115 | 10 | 15 | -103 | 7575.9
2009-10-12 02:24 | 60.009 | 3666.7104 | 350 | 262.0735 | 0 | 115.5 | 10 | 15 | -103 | 7576.23
2009-10-12 02:24 | 60.009 | 3667.696 | 350 | 262.0735 | 0 | 116 | 10 | 15 | -103 | 7576.56
2009-10-12 02:24 | 60.009 | 3667.043 | 350 | 260.3644 | 0 | 116.5 | 10 | 15 | -103 | 7576.89
2009-10-12 02:24 | 60.002 | 3666.6235 | 350 | 260.3644 | 0 | 117 | 10 | 15 | -103 | 7577.22
2009-10-12 02:24 | 59.999 | 3665.8796 | 350 | 260.3644 | 0 | 117.5 | 10 | 15 | -103 | 7577.55
2009-10-12 02:24 | 59.995 | 3665.4033 | 350 | 260.3644 | 0 | 118 | 10 | 15 | -103 | 7577.88
2009-10-12 02:24 | 59.997 | 3665.6797 | 350 | 260.3644 | 0 | 118.5 | 10 | 15 | -103 | 7578.21
2009-10-12 02:24 | 59.998 | 3665.3521 | 350 | 352.6444 | 0 | 119 | 10 | 15 | -103 | 7578.54
2009-10-12 02:24 | 59.998 | 3665.0649 | 350 | 352.6444 | 0 | 119.5 | 10 | 15 | -103 | 7578.87
2009-10-12 02:24 | 59.995 | 3666.1333 | 350 | 352.6444 | 0 | 120 | 10 | 15 | -103 | 7579.2
2009-10-12 02:24 | 59.995 | 3666.7346 | 350 | 352.6444 | 0 | 120.5 | 10 | 15 | -103 | 7579.53
2009-10-12 02:24 | 59.993 | 3667.084 | 350 | 352.6444 | 0 | 121 | 10 | 15 | -103 | 7579.86
2009-10-12 02:24 | 59.988 | 3667.3367 | 350 | 354.8957 | 0 | 121.5 | 10 | 15 | -103 | 7580.19
2009-10-12 02:24 | 59.982 | 3667.8533 | 350 | 354.8957 | 0 | 122 | 10 | 15 | -103 | 7580.52
2009-10-12 02:24 | 59.982 | 3668.6909 | 350 | 354.8957 | 0 | 122.5 | 10 | 15 | -103 | 7580.85
2009-10-12 02:24 | 59.982 | 3669.3992 | 350 | 354.8957 | 0 | 123 | 10 | 15 | -103 | 7581.18
2009-10-12 02:24 | 59.984 | 3671.228 | 350 | 354.8957 | 0 | 123.5 | 10 | 15 | -103 | 7581.51
2009-10-12 02:24 | 59.978 | 3670.25 | 350 | 340.4694 | 0 | 124 | 10 | 15 | -103 | 7581.84
2009-10-12 02:24 | 59.978 | 3671.5488 | 350 | 340.4694 | 0 | 124.5 | 10 | 15 | -103 | 7582.17
2009-10-12 02:24 | 59.975 | 3673.2432 | 350 | 340.4694 | 0 | 125 | 10 | 15 | -103 | 7582.5
2009-10-12 02:25 | 59.974 | 3675.8245 | 350 | 340.4694 | 0 | 125.5 | 10 | 15 | -103 | 7582.83
2009-10-12 02:25 | 59.979 | 3676.4182 | 350 | 340.4694 | 0 | 126 | 10 | 15 | -103 | 7583.16
2009-10-12 02:25 | 59.98 | 3674.6375 | 350 | 337.6429 | 0 | 126.5 | 10 | 15 | -103 | 7583.49
2009-10-12 02:25 | 59.98 | 3675.3289 | 350 | 337.6429 | 0 | 127 | 10 | 15 | -103 | 7583.82
2009-10-12 02:25 | 59.984 | 3674.7681 | 350 | 337.6429 | 0 | 127.5 | 10 | 15 | -103 | 7584.15
2009-10-12 02:25 | 59.988 | 3674.3994 | 350 | 337.6429 | 0 | 128 | 10 | 15 | -103 | 7584.48
2009-10-12 02:25 | 59.988 | 3673.0396 | 350 | 337.6429 | 0 | 128.5 | 10 | 15 | -103 | 7584.81
2009-10-12 02:25 | 59.992 | 3672.4417 | 350 | 284.3608 | 0 | 129 | 10 | 15 | -103 | 7585.14
2009-10-12 02:25 | 59.991 | 3671.6802 | 350 | 284.3608 | 0 | 129.5 | 10 | 15 | -103 | 7585.47
2009-10-12 02:25 | 59.991 | 3671.4932 | 350 | 284.3608 | 0 | 130 | 10 | 15 | -103 | 7585.8
2009-10-12 02:25 | 59.993 | 3669.53 | 350 | 284.3608 | 0 | 130.5 | 10 | 15 | -103 | 7586.13
2009-10-12 02:25 | 59.996 | 3670.0278 | 350 | 284.3608 | 0 | 131 | 10 | 15 | -103 | 7586.46
2009-10-12 02:25 | 60.002 | 3671.5781 | 350 | 260.468 | 0 | 131.5 | 10 | 15 | -103 | 7586.79
2009-10-12 02:25 | 60.003 | 3672.6255 | 350 | 260.468 | 0 | 132 | 10 | 15 | -103 | 7587.12
2009-10-12 02:25 | 60.004 | 3673.8186 | 350 | 260.468 | 0 | 132.5 | 10 | 15 | -103 | 7587.45
2009-10-12 02:25 | 60.004 | 3673.2495 | 350 | 260.468 | 0 | 133 | 10 | 15 | -103 | 7587.78
2009-10-12 02:25 | 60.002 | 3673.4963 | 350 | 260.468 | 0 | 133.5 | 10 | 15 | -103 | 7588.11
2009-10-12 02:25 | 60.008 | 3672.418 | 350 | 253.1415 | 0 | 134 | 10 | 15 | -103 | 7588.44
2009-10-12 02:25 | 60.01 | 3672.2168 | 350 | 253.1415 | 0 | 134.5 | 10 | 15 | -103 | 7588.77
2009-10-12 02:26 | 60.01 | 3672.2607 | 350 | 253.1415 | 0 | 135 | 10 | 15 | -103 | 7589.1
2009-10-12 02:26 | 60.011 | 3673.6033 | 350 | 253.1415 | 0 | 135.5 | 10 | 15 | -103 | 7589.43
2009-10-12 02:26 | 60.014 | 3673.5535 | 350 | 253.1415 | 0 | 136 | 10 | 15 | -103 | 7589.76
2009-10-12 02:26 | 60.013 | 3674.5371 | 350 | 251.9299 | 0 | 136.5 | 10 | 15 | -103 | 7590.09
2009-10-12 02:26 | 60.011 | 3673.8125 | 350 | 251.9299 | 0 | 137 | 10 | 15 | -103 | 7590.42
2009-10-12 02:26 | 60.011 | 3672.5632 | 350 | 251.9299 | 0 | 137.5 | 10 | 15 | -103 | 7590.75
2009-10-12 02:26 | 60.022 | 3673.0676 | 350 | 251.9299 | 0 | 138 | 10 | 15 | -103 | 7591.08
2009-10-12 02:26 | 60.017 | 3672.5195 | 350 | 251.9299 | 0 | 138.5 | 10 | 15 | -103 | 7591.41
2009-10-12 02:26 | 60.013 | 3671.25 | 350 | 250.6742 | 0 | 139 | 10 | 15 | -103 | 7591.74
2009-10-12 02:26 | 60.014 | 3672.989 | 350 | 250.6742 | 0 | 139.5 | 10 | 15 | -103 | 7592.07
2009-10-12 02:26 | 60.017 | 3672.9817 | 350 | 250.6742 | 0 | 140 | 10 | 15 | -103 | 7592.4
2009-10-12 02:26 | 60.019 | 3671.9517 | 350 | 250.6742 | 0 | 140.5 | 10 | 15 | -103 | 7592.73
2009-10-12 02:26 | 60.019 | 3671.1931 | 350 | 250.6742 | 0 | 141 | 10 | 15 | -103 | 7593.06
2009-10-12 02:26 | 60.027 | 3671.189 | 350 | 253.6319 | 0 | 141.5 | 10 | 15 | -103 | 7593.39
2009-10-12 02:26 | 60.026 | 3668.6106 | 350 | 253.6319 | 0 | 142 | 10 | 15 | -103 | 7593.72
2009-10-12 02:26 | 60.022 | 3664.4951 | 350 | 253.6319 | 0 | 142.5 | 10 | 15 | -103 | 7594.05
2009-10-12 02:26 | 60.017 | 3666.0618 | 350 | 253.6319 | 0 | 143 | 10 | 15 | -103 | 7594.38
2009-10-12 02:26 | 60.019 | 3666.7874 | 350 | 253.6319 | 0 | 143.5 | 10 | 15 | -103 | 7594.71
2009-10-12 02:26 | 60.019 | 3670.4536 | 350 | 246.9573 | 0 | 144 | 10 | 15 | -103 | 7595.04
2009-10-12 02:26 | 60.021 | 3671.668 | 350 | 246.9573 | 0 | 144.5 | 10 | 15 | -103 | 7595.37
2009-10-12 02:26 | 60.021 | 3672.4932 | 350 | 246.9573 | 0 | 145 | 10 | 15 | -103 | 7595.7
2009-10-12 02:27 | 60.019 | 3672.8574 | 350 | 246.9573 | 0 | 145.5 | 10 | 15 | -103 | 7596.03
2009-10-12 02:27 | 60.022 | 3672.1641 | 350 | 246.9573 | 0 | 146 | 10 | 15 | -103 | 7596.36
2009-10-12 02:27 | 60.031 | 3669.9829 | 350 | 254.5418 | 0 | 146.5 | 10 | 15 | -103 | 7596.69
2009-10-12 02:27 | 60.037 | 3666.4673 | 350 | 254.5418 | 0 | 147 | 10 | 15 | -103 | 7597.02
2009-10-12 02:27 | 60.036 | 3661.5991 | 350 | 254.5418 | 0 | 147.5 | 10 | 15 | -103 | 7597.35
2009-10-12 02:27 | 60.046 | 3660.6724 | 350 | 254.5418 | 0 | 148 | 10 | 15 | -103 | 7597.68
2009-10-12 02:27 | 60.048 | 3649.1904 | 350 | 165.1017 | 0 | 148.5 | 10 | 15 | -103 | 7598.01
2009-10-12 02:27 | 60.043 | 3650.0251 | 350 | 165.1017 | 0 | 149 | 10 | 15 | -103 | 7598.34
2009-10-12 02:27 | 60.041 | 3649.512 | 350 | 165.1017 | 0 | 149.5 | 10 | 15 | -103 | 7598.67
2009-10-12 02:27 | 60.041 | 3654.2944 | 350 | 165.1017 | 0 | 150 | 10 | 15 | -103 | 7599
2009-10-12 02:27 | 60.039 | 3651.8743 | 350 | 165.1017 | 0 | 150.5 | 10 | 15 | -103 | 7599.33
2009-10-12 02:27 | 60.043 | 3651.0593 | 350 | 165.4764 | 0 | 151 | 10 | 15 | -103 | 7599.66
2009-10-12 02:27 | 60.045 | 3648.2363 | 350 | 165.4764 | 0 | 151.5 | 10 | 15 | -103 | 7599.99
2009-10-12 02:27 | 60.041 | 3645.387 | 350 | 165.4764 | 0 | 152 | 10 | 15 | -103 | 7600.32
2009-10-12 02:27 | 60.041 | 3645.4458 | 350 | 165.4764 | 0 | 152.5 | 10 | 15 | -103 | 7600.65
2009-10-12 02:27 | 60.039 | 3640.6821 | 350 | 165.4764 | 0 | 153 | 10 | 15 | -103 | 7600.98
2009-10-12 02:27 | 59.978 | 3659.4648 | 350 | 206.4591 | 0 | 153.5 | 10 | 0 | -103 | 7601.31
2009-10-12 02:27 | 59.836 | 3696.3623 | 350 | 206.4591 | 0 | 154 | 10 | 0 | -103 | 7570
2009-10-12 02:27 | 59.869 | 3734.6726 | 335 | 206.4591 | 0 | 154.5 | 10 | 0 | -103 | 7569
2009-10-12 02:28 | 59.891 | 3737.1567 | 335 | 206.4591 | 0 | 155 | 10 | 0 | -103 | 7570
2009-10-12 02:28 | 59.88 | 3766.113 | 335 | 206.4591 | 0 | 155.5 | 10 | 0 | -103 | 7570
2009-10-12 02:28 | 59.875 | 3766.1938 | 335 | 211.256 | 0 | 156 | 10 | 0 | -103 | 7570
2009-10-12 02:28 | 59.883 | 3769.925 | 335 | 211.256 | 1 | 156.5 | 10 | 0 | -103 | 7570
2009-10-12 02:28 | 59.886 | 3780.6206 | 335 | 211.256 | 1 | 157 | 10 | 0 | -103 | 7570
2009-10-12 02:28 | 59.885 | 3782.4995 | 335 | 211.256 | 1 | 157.5 | 10 | 0 | -103 | 7570
2009-10-12 02:28 | 59.888 | 3784.9619 | 335 | 211.256 | 1 | 158 | 10 | 0 | -103 | 7570
2009-10-12 02:28 | 59.89 | 3784.4189 | 335 | 214.3467 | 1 | 158.5 | 10 | 0 | -103 | 7570
2009-10-12 02:28 | 59.894 | 3788.0723 | 335 | 214.3467 | 1 | 159 | 10 | 0 | -103 | 7570
2009-10-12 02:28 | 59.893 | 3788.8684 | 335 | 214.3467 | 1 | 159.5 | 10 | 0 | -103 | 7570
2009-10-12 02:28 | 59.894 | 3788.4719 | 335 | 214.3467 | 2 | 160 | 10 | 0 | -103 | 7570
2009-10-12 02:28 | 59.891 | 3793.0745 | 335 | 214.3467 | 3 | 160.5 | 10 | 0 | -103 | 7570
2009-10-12 02:28 | 59.885 | 3794.3743 | 335 | 212.1727 | 4 | 161 | 10 | 0 | -103 | 7570
2009-10-12 02:28 | 59.885 | 3800.4275 | 335 | 212.1727 | 5 | 161.5 | 10 | 0 | -103 | 7570
2009-10-12 02:28 | 59.887 | 3799.9592 | 335 | 212.1727 | 6 | 162 | 10 | 0 | -103 | 7570
2009-10-12 02:28 | 59.888 | 3802.925 | 335 | 212.1727 | 7 | 162.5 | 10 | 0 | -103 | 7570
2009-10-12 02:28 | 59.89 | 3802.9509 | 335 | 212.1727 | 8 | 163 | 10 | 0 | -103 | 7570
2009-10-12 02:28 | 59.889 | 3805.4961 | 335 | 215.5982 | 9 | 163.5 | 10 | 0 | -103 | 7570
2009-10-12 02:28 | 59.873 | 3805.6167 | 335 | 215.5982 | 10 | 164 | 10 | 0 | -103 | 7568
2009-10-12 02:28 | 59.857 | 3811.5029 | 335 | 215.5982 | 11 | 164.5 | 10 | 0 | -103 | 7565
2009-10-12 02:28 | 59.852 | 3814.8623 | 335 | 215.5982 | 12 | 165 | 10 | 0 | -103 | 7560
2009-10-12 02:29 | 59.858 | 3825.6426 | 335 | 215.5982 | 13 | 165.5 | 10 | 0 | -103 | 7563
2009-10-12 02:29 | 59.866 | 3826.0532 | 335 | 218.3273 | 14 | 166 | 10 | 0 | -103 | 7564
2009-10-12 02:29 | 59.865 | 3827.5239 | 335 | 218.3273 | 15 | 166.5 | 10 | 0 | -103 | 7566
2009-10-12 02:29 | 59.866 | 3826.7532 | 335 | 218.3273 | 16 | 167 | 10 | 0 | -103 | 7570
2009-10-12 02:29 | 59.871 | 3826.4536 | 335 | 218.3273 | 16 | 167.5 | 10 | 0 | -103 | 7570
2009-10-12 02:29 | 59.879 | 3825.7134 | 335 | 218.3273 | 16 | 168 | 10 | 0 | -103 | 7570
2009-10-12 02:29 | 59.88 | 3822.5054 | 335 | 217.3794 | 16 | 168.5 | 10 | 0 | -103 | 7570
2009-10-12 02:29 | 59.886 | 3819.0811 | 335 | 217.3794 | 16 | 169 | 10 | 0 | -103 | 7570
2009-10-12 02:29 | 59.89 | 3816.8147 | 335 | 217.3794 | 16 | 169.5 | 10 | 0 | -103 | 7569
2009-10-12 02:29 | 59.889 | 3815.0098 | 335 | 217.3794 | 16 | 170 | 10 | 0 | -103 | 7575
2009-10-12 02:29 | 59.893 | 3811.8384 | 335 | 217.3794 | 16 | 170.5 | 10 | 0 | -103 | 7573
2009-10-12 02:29 | 59.903 | 3809.6519 | 335 | 214.8304 | 16 | 171 | 10 | 0 | -103 | 7571
2009-10-12 02:29 | 59.902 | 3805.5933 | 335 | 214.8304 | 16 | 171.5 | 10 | 0 | -103 | 7573
2009-10-12 02:29 | 59.904 | 3804.1885 | 335 | 214.8304 | 16 | 172 | 10 | 0 | -103 | 7575
2009-10-12 02:29 | 59.907 | 3793.9751 | 335 | 214.8304 | 16 | 172.5 | 10 | 0 | -103 | 7577
2009-10-12 02:29 | 59.916 | 3792.1694 | 335 | 214.8304 | 16 | 173 | 10 | 0 | -103 | 7577
2009-10-12 02:29 | 59.916 | 3789.5337 | 335 | 227.6559 | 16 | 173.5 | 10 | 0 | -103 | 7578
2009-10-12 02:29 | 59.918 | 3788.1321 | 335 | 227.6559 | 16 | 174 | 10 | 0 | -103 | 7579
2009-10-12 02:29 | 59.92 | 3783.0283 | 335 | 227.6559 | 16 | 174.5 | 10 | 0 | -103 | 7580
2009-10-12 02:29 | 59.92 | 3781.7012 | 335 | 227.6559 | 16 | 175 | 10 | 0 | -103 | 7581
2009-10-12 02:30 | 59.917 | 3775.6355 | 335 | 227.6559 | 16 | 175.5 | 10 | 0 | -103 | 7585
2009-10-12 02:30 | 59.921 | 3774.6042 | 335 | 225.0181 | 16 | 176 | 10 | 0 | -103 | 7588
2009-10-12 02:30 | 59.923 | 3773.9578 | 335 | 225.0181 | 16 | 176.5 | 10 | 0 | -103 | 7589
2009-10-12 02:30 | 59.925 | 3772.7224 | 335 | 225.0181 | 0 | 177 | 10 | 0 | -103 | 7589
2009-10-12 02:30 | 59.928 | 3769.6296 | 335 | 225.0181 | 0 | 177.5 | 10 | 0 | -103 | 7590
2009-10-12 02:30 | 59.932 | 3768.707 | 335 | 225.0181 | 0 | 178 | 10 | 0 | -103 | 7590
2009-10-12 02:30 | 59.927 | 3767.021 | 335 | 228.3652 | 0 | 178.5 | 10 | 0 | -103 | 7590
2009-10-12 02:30 | 59.931 | 3767.408 | 335 | 228.3652 | 0 | 179 | 10 | 0 | -103 | 7591
2009-10-12 02:30 | 59.929 | 3766.259 | 335 | 228.3652 | 0 | 179.5 | 10 | 0 | -103 | 7591
2009-10-12 02:30 | 59.931 | 3765.6716 | 335 | 228.3652 | 0 | 180 | 10 | 0 | -103 | 7591
2009-10-12 02:30 | 59.937 | 3766.1226 | 335 | 228.3652 | 0 | 180.5 | 10 | 0 | -103 | 7592
2009-10-12 02:30 | 59.945 | 3765.105 | 335 | 234.0753 | 0 | 181 | 10 | 0 | -103 | 7592
2009-10-12 02:30 | 59.949 | 3758.3872 | 335 | 234.0753 | 0 | 181.5 | 10 | 0 | -103 | 7593
2009-10-12 02:30 | 59.942 | 3753.9224 | 335 | 234.0753 | 0 | 182 | 10 | 0 | -103 | 7594
2009-10-12 02:30 | 59.941 | 3746.8887 | 335 | 234.0753 | 0 | 182.5 | 10 | 0 | -103 | 7595
2009-10-12 02:30 | 59.945 | 3747.8755 | 335 | 234.0753 | 0 | 183 | 10 | 0 | -103 | 7655
2009-10-12 02:30 | 59.948 | 3748.6611 | 335 | 228.7982 | 0 | 183.5 | 10 | 0 | -103 | 7656
2009-10-12 02:30 | 59.949 | 3746.7061 | 335 | 228.7982 | 0 | 184 | 10 | 0 | -103 | 7656
2009-10-12 02:30 | 59.951 | 3742.7415 | 335 | 228.7982 | 0 | 184.5 | 10 | 0 | -103 | 7657
2009-10-12 02:30 | 59.953 | 3740.259 | 335 | 228.7982 | 0 | 185 | 10 | 0 | -103 | 7657
2009-10-12 02:31 | 59.951 | 3731.3821 | 335 | 228.7982 | 0 | 185.5 | 10 | 0 | -103 | 7658
2009-10-12 02:31 | 59.952 | 3727.8384 | 335 | 229.467 | 0 | 186 | 10 | 0 | -103 | 7658
2009-10-12 02:31 | 59.952 | 3722.6489 | 335 | 249.3376 | 0 | 186.5 | 10 | 0 | -103 | 7659
2009-10-12 02:31 | 59.952 | 3720.5781 | 335 | 249.3376 | 0 | 187 | 10 | 0 | -103 | 7659
2009-10-12 02:31 | 59.954 | 3718.1418 | 335 | 249.3376 | 0 | 187.5 | 10 | 0 | -103 | 7659
2009-10-12 02:31 | 59.953 | 3715.7527 | 335 | 249.3376 | 0 | 188 | 10 | 0 | -103 | 7660
2009-10-12 02:31 | 59.953 | 3713.4836 | 335 | 249.3376 | 0 | 188.5 | 10 | 0 | -103 | 7660
2009-10-12 02:31 | 59.954 | 3710.8481 | 335 | 258.2782 | 0 | 189 | 10 | 0 | -103 | 7661
2009-10-12 02:31 | 59.954 | 3712.0918 | 335 | 258.2782 | 0 | 189.5 | 10 | 0 | -103 | 7661
2009-10-12 02:31 | 59.957 | 3714.6226 | 335 | 258.2782 | 0 | 190 | 10 | 0 | -103 | 7625.4
2009-10-12 02:31 | 59.956 | 3716.1682 | 335 | 258.2782 | 0 | 190.5 | 10 | 0 | -103 | 7625.73
2009-10-12 02:31 | 59.956 | 3716.4614 | 335 | 258.2782 | 0 | 191 | 10 | 0 | -103 | 7626.06
2009-10-12 02:31 | 59.955 | 3717.759 | 335 | 258.4064 | 0 | 191.5 | 10 | 0 | -103 | 7626.39
2009-10-12 02:31 | 59.961 | 3722.3613 | 335 | 258.4064 | 0 | 192 | 10 | 0 | -103 | 7626.72
2009-10-12 02:31 | 59.962 | 3722.658 | 335 | 258.4064 | 0 | 192.5 | 10 | 0 | -103 | 7627.05
2009-10-12 02:31 | 59.968 | 3722.2666 | 335 | 258.4064 | 0 | 193 | 10 | 0 | -103 | 7627.38
2009-10-12 02:31 | 59.966 | 3721.7866 | 335 | 258.4064 | 0 | 193.5 | 10 | 0 | -103 | 7627.71
2009-10-12 02:31 | 59.968 | 3723.0908 | 335 | 260.5389 | 0 | 194 | 10 | 0 | -103 | 7628.04
2009-10-12 02:31 | 59.97 | 3723.4346 | 335 | 260.5389 | 0 | 194.5 | 10 | 0 | -103 | 7628.37
2009-10-12 02:32 | 59.97 | 3723.8931 | 335 | 260.5389 | 0 | 195 | 10 | 0 | -103 | 7628.7
2009-10-12 02:32 | 59.969 | 3727.1211 | 335 | 260.5389 | 0 | 195.5 | 10 | 0 | -103 | 7629.03
2009-10-12 02:32 | 59.97 | 3728.053 | 335 | 260.5389 | 0 | 196 | 10 | 0 | -103 | 7629.36
2009-10-12 02:32 | 59.971 | 3732.53 | 335 | 257.8821 | 0 | 196.5 | 10 | 0 | -103 | 7629.69
2009-10-12 02:32 | 59.973 | 3733.3271 | 335 | 257.8821 | 0 | 197 | 10 | 0 | -103 | 7630.02
2009-10-12 02:32 | 59.976 | 3736.9075 | 335 | 257.8821 | 0 | 197.5 | 10 | 0 | -103 | 7630.35
2009-10-12 02:32 | 59.978 | 3736.8218 | 335 | 257.8821 | 0 | 198 | 10 | 0 | -103 | 7630.68
2009-10-12 02:32 | 59.976 | 3739.9438 | 335 | 257.8821 | 0 | 198.5 | 10 | 0 | -103 | 7631.01
2009-10-12 02:32 | 59.976 | 3740.877 | 335 | 258.5887 | 0 | 199 | 10 | 0 | -103 | 7631.34
2009-10-12 02:32 | 59.978 | 3745.2336 | 335 | 258.5887 | 0 | 199.5 | 10 | 0 | -103 | 7631.67
2009-10-12 02:32 | 59.98 | 3746.6079 | 335 | 258.5887 | 0 | 200 | 10 | 0 | -103 | 7632
2009-10-12 02:32 | 59.982 | 3750.7163 | 335 | 258.5887 | 0 | 200.5 | 10 | 0 | -103 | 7632.33
2009-10-12 02:32 | 59.98 | 3751.5576 | 335 | 258.5887 | 0 | 201 | 10 | 0 | -103 | 7632.66
2009-10-12 02:32 | 59.979 | 3755.5986 | 335 | 261.9062 | 0 | 201.5 | 10 | 0 | -103 | 7632.99
2009-10-12 02:32 | 59.979 | 3756.4072 | 335 | 261.9062 | 0 | 202 | 10 | 0 | -103 | 7633.32
2009-10-12 02:32 | 59.983 | 3760.4053 | 335 | 261.9062 | 0 | 202.5 | 10 | 0 | -103 | 7633.65
2009-10-12 02:32 | 59.984 | 3760.9822 | 335 | 261.9062 | 0 | 203 | 10 | 0 | -103 | 7633.98
2009-10-12 02:32 | 59.988 | 3762.7373 | 335 | 261.9062 | 0 | 203.5 | 10 | 0 | -103 | 7634.31
2009-10-12 02:32 | 59.987 | 3763.2122 | 335 | 256.7478 | 0 | 204 | 10 | 0 | -103 | 7634.64
2009-10-12 02:32 | 59.987 | 3766.0852 | 335 | 256.7478 | 0 | 204.5 | 10 | 0 | -103 | 7634.97
2009-10-12 02:33 | 59.993 | 3766.4331 | 335 | 256.7478 | 0 | 205 | 10 | 0 | -103 | 7635.3
2009-10-12 02:33 | 59.992 | 3767.7925 | 335 | 256.7478 | 0 | 205.5 | 10 | 0 | -103 | 7635.63
2009-10-12 02:33 | 59.989 | 3768.6335 | 335 | 256.7478 | 0 | 206 | 10 | 0 | -103 | 7635.96
2009-10-12 02:33 | 59.986 | 3772.4446 | 335 | 167.432 | 0 | 206.5 | 10 | 0 | -103 | 7636.29
2009-10-12 02:33 | 59.983 | 3773.6948 | 335 | 167.432 | 0 | 207 | 10 | 0 | -103 | 7636.62
2009-10-12 02:33 | 59.988 | 3775.8408 | 335 | 167.432 | 0 | 207.5 | 10 | 0 | -103 | 7636.95
2009-10-12 02:33 | 59.996 | 3775.3633 | 335 | 167.432 | 0 | 208 | 10 | 0 | -103 | 7637.28
2009-10-12 02:33 | 59.998 | 3775.4917 | 335 | 167.432 | 0 | 208.5 | 10 | 0 | -103 | 7637.61
2009-10-12 02:33 | 60.001 | 3776.4202 | 335 | 164.9734 | 0 | 209 | 10 | 0 | -103 | 7637.94
2009-10-12 02:33 | 59.999 | 3779.6919 | 335 | 164.9734 | 0 | 209.5 | 10 | 0 | -103 | 7638.27
2009-10-12 02:33 | 59.999 | 3781.2559 | 335 | 164.9734 | 0 | 210 | 10 | 0 | -103 | 7638.6
2009-10-12 02:33 | 60.002 | 3783.092 | 335 | 164.9734 | 0 | 210.5 | 10 | 0 | -103 | 7638.93
2009-10-12 02:33 | 60.007 | 3783.8955 | 335 | 164.9734 | 0 | 211 | 10 | 0 | -103 | 7639.26
2009-10-12 02:33 | 60.008 | 3785.7681 | 335 | 157.6281 | 0 | 211.5 | 10 | 0 | -103 | 7639.59
2009-10-12 02:33 | 60.014 | 3785.4626 | 335 | 157.6281 | 0 | 212 | 10 | 0 | -103 | 7639.92
2009-10-12 02:33 | 60.017 | 3786.3042 | 335 | 157.6281 | 0 | 212.5 | 10 | 0 | -103 | 7640.25
2009-10-12 02:33 | 60.021 | 3787.2593 | 335 | 157.6281 | 0 | 213 | 10 | 0 | -103 | 7640.58
2009-10-12 02:33 | 60.017 | 3787.9551 | 335 | 157.6281 | 0 | 213.5 | 10 | 0 | -103 | 7640.91
2009-10-12 02:33 | 60.019 | 3788.0303 | 335 | 155.5317 | 0 | 214 | 10 | 0 | -103 | 7641.24
2009-10-12 02:33 | 60.023 | 3789.2158 | 335 | 155.5317 | 0 | 214.5 | 10 | 0 | -103 | 7641.57
2009-10-12 02:34 | 60.025 | 3787.5366 | 335 | 155.5317 | 0 | 215 | 10 | 0 | -103 | 7641.9
2009-10-12 02:34 | 60.021 | 3786.0767 | 335 | 155.5317 | 0 | 215.5 | 10 | 0 | -103 | 7642.23
2009-10-12 02:34 | 60.024 | 3787.9304 | 335 | 155.5317 | 0 | 216 | 10 | 0 | -103 | 7642.56
2009-10-12 02:34 | 60.024 | 3786.8748 | 335 | 160.4472 | 0 | 216.5 | 10 | 0 | -103 | 7642.89
2009-10-12 02:34 | 60.02 | 3786.5498 | 335 | 160.4472 | 0 | 217 | 10 | 0 | -103 | 7643.22
2009-10-12 02:34 | 60.025 | 3785.0181 | 335 | 160.4472 | 0 | 217.5 | 10 | 0 | -103 | 7643.55
2009-10-12 02:34 | 60.02 | 3785.614 | 335 | 160.4472 | 0 | 218 | 10 | 0 | -103 | 7643.88
2009-10-12 02:34 | 60.02 | 3785.8037 | 335 | 160.4472 | 0 | 218.5 | 10 | 0 | -103 | 7644.21
2009-10-12 02:34 | 60.022 | 3786.8643 | 335 | 163.9586 | 0 | 219 | 10 | 0 | -103 | 7644.54
2009-10-12 02:34 | 60.022 | 3785.2539 | 335 | 163.9586 | 0 | 219.5 | 10 | 0 | -103 | 7644.87
2009-10-12 02:34 | 60.021 | 3785.7261 | 335 | 163.9586 | 0 | 220 | 10 | 0 | -103 | 7645.2
2009-10-12 02:34 | 60.023 | 3785.821 | 335 | 163.9586 | 0 | 220.5 | 10 | 0 | -103 | 7645.53
2009-10-12 02:34 | 60.022 | 3785.7983 | 335 | 163.9586 | 0 | 221 | 10 | 0 | -103 | 7645.86
2009-10-12 02:34 | 60.019 | 3786.9392 | 335 | 166.0724 | 0 | 221.5 | 10 | 0 | -103 | 7646.19
2009-10-12 02:34 | 60.018 | 3787.6274 | 335 | 166.0724 | 0 | 222 | 10 | 0 | -103 | 7646.52
2009-10-12 02:34 | 60.018 | 3789.6733 | 335 | 166.0724 | 0 | 222.5 | 10 | 0 | -103 | 7646.85
2009-10-12 02:34 | 60.019 | 3789.4043 | 335 | 166.0724 | 0 | 223 | 10 | 0 | -103 | 7647.18
2009-10-12 02:34 | 60.019 | 3789.1833 | 335 | 166.0724 | 0 | 223.5 | 10 | 0 | -103 | 7647.51
2009-10-12 02:34 | 60.015 | 3789.3689 | 335 | 163.7666 | 0 | 224 | 10 | 0 | -103 | 7647.84
2009-10-12 02:34 | 60.016 | 3788.6646 | 335 | 163.7666 | 0 | 224.5 | 10 | 0 | -103 | 7648.17
2009-10-12 02:34 | 60.013 | 3788.9329 | 335 | 163.7666 | 0 | 225 | 10 | 0 | -103 | 7648.5
2009-10-12 02:35 | 60.012 | 3790.8052 | 335 | 163.7666 | 0 | 225.5 | 10 | 0 | -103 | 7648.83
2009-10-12 02:35 | 60.01 | 3790.4111 | 335 | 163.7666 | 0 | 226 | 10 | 0 | -103 | 7649.16
2009-10-12 02:35 | 60.007 | 3791.5398 | 335 | 165.1017 | 0 | 226.5 | 10 | 0 | -103 | 7649.49
2009-10-12 02:35 | 60.009 | 3792.9453 | 335 | 165.1017 | 0 | 227 | 10 | 0 | -103 | 7649.82
2009-10-12 02:35 | 60.009 | 3791.4431 | 335 | 165.1017 | 0 | 227.5 | 10 | 0 | -103 | 7650.15
2009-10-12 02:35 | 60.003 | 3791.426 | 335 | 165.1017 | 0 | 228 | 10 | 0 | -103 | 7650.48
2009-10-12 02:35 | 59.999 | 3790.4573 | 335 | 165.1017 | 0 | 228.5 | 10 | 0 | -103 | 7650.81
2009-10-12 02:35 | 59.992 | 3790.2163 | 335 | 165.4764 | 0 | 229 | 10 | 0 | -103 | 7651.14
2009-10-12 02:35 | 59.991 | 3788.457 | 335 | 165.4764 | 0 | 229.5 | 10 | 0 | -103 | 7651.47
2009-10-12 02:35 | 59.992 | 3788.105 | 335 | 165.4764 | 0 | 230 | 10 | 0 | -103 | 7651.8
2009-10-12 02:35 | 59.988 | 3788.1895 | 335 | 165.4764 | 0 | 230.5 | 10 | 0 | -103 | 7652.13
2009-10-12 02:35 | 59.985 | 3788.4973 | 335 | 165.4764 | 0 | 231 | 10 | 0 | -103 | 7652.46
2009-10-12 02:35 | 59.984 | 3788.5708 | 335 | 206.4591 | 0 | 231.5 | 10 | 0 | -103 | 7652.79
2009-10-12 02:35 | 59.984 | 3788.1011 | 335 | 206.4591 | 0 | 232 | 10 | 0 | -103 | 7616
2009-10-12 02:35 | 59.982 | 3786.4529 | 335 | 206.4591 | 0 | 232.5 | 10 | 0 | -103 | 7626
2009-10-12 02:35 | 59.982 | 3787.7324 | 335 | 206.4591 | 0 | 233 | 10 | 0 | -103 | 7632
2009-10-12 02:35 | 59.979 | 3789.2852 | 335 | 206.4591 | 0 | 233.5 | 10 | 0 | -103 | 7632
2009-10-12 02:35 | 59.976 | 3788.2563 | 335 | 211.256 | 0 | 234 | 10 | 0 | -103 | 7632
2009-10-12 02:35 | 59.976 | 3790.4673 | 335 | 211.256 | 1 | 234.5 | 10 | 0 | -103 | 7632
2009-10-12 02:36 | 59.982 | 3790.6646 | 335 | 211.256 | 1 | 235 | 10 | 0 | -103 | 7632
2009-10-12 02:36 | 59.978 | 3789.6738 | 335 | 211.256 | 1 | 235.5 | 10 | 0 | -103 | 7632
2009-10-12 02:36 | 59.974 | 3789.2671 | 335 | 211.256 | 1 | 236 | 10 | 0 | -103 | 7632
2009-10-12 02:36 | 59.976 | 3790.4304 | 335 | 214.3467 | 1 | 236.5 | 10 | 0 | -103 | 7632
2009-10-12 02:36 | 59.977 | 3789.9143 | 335 | 214.3467 | 1 | 237 | 10 | 0 | -103 | 7632
2009-10-12 02:36 | 59.975 | 3787.4421 | 335 | 214.3467 | 1 | 237.5 | 10 | 0 | -103 | 7632
2009-10-12 02:36 | 59.969 | 3788.9629 | 335 | 214.3467 | 2 | 238 | 10 | 0 | -103 | 7632
2009-10-12 02:36 | 59.97 | 3791.877 | 335 | 214.3467 | 3 | 238.5 | 10 | 0 | -103 | 7632
2009-10-12 02:36 | 59.973 | 3792.9106 | 335 | 212.1727 | 4 | 239 | 10 | 0 | -103 | 7632
2009-10-12 02:36 | 59.978 | 3789.125 | 335 | 212.1727 | 5 | 239.5 | 10 | 0 | -103 | 7632
2009-10-12 02:36 | 59.978 | 3788.0796 | 335 | 212.1727 | 6 | 240 | 10 | 0 | -103 | 7632
2009-10-12 02:36 | 59.975 | 3787.135 | 335 | 212.1727 | 7 | 240.5 | 10 | 0 | -103 | 7632
2009-10-12 02:36 | 59.976 | 3787.1643 | 335 | 212.1727 | 8 | 241 | 10 | 0 | -103 | 7632
2009-10-12 02:36 | 59.975 | 3787.4048 | 335 | 215.5982 | 9 | 241.5 | 10 | 0 | -103 | 7632
2009-10-12 02:36 | 59.969 | 3786.4868 | 335 | 215.5982 | 10 | 242 | 10 | 0 | -103 | 7632
2009-10-12 02:36 | 59.966 | 3789.2139 | 335 | 215.5982 | 11 | 242.5 | 10 | 0 | -103 | 7632
2009-10-12 02:36 | 59.966 | 3790.5117 | 335 | 215.5982 | 12 | 243 | 10 | 0 | -103 | 7632
2009-10-12 02:36 | 59.969 | 3792.2183 | 335 | 215.5982 | 13 | 243.5 | 10 | 0 | -103 | 7632
2009-10-12 02:36 | 59.968 | 3790.9595 | 335 | 218.3273 | 14 | 244 | 10 | 0 | -103 | 7632
2009-10-12 02:36 | 59.965 | 3789.0264 | 335 | 218.3273 | 15 | 244.5 | 10 | 0 | -103 | 7632
2009-10-12 02:36 | 59.97 | 3789.1675 | 335 | 218.3273 | 16 | 245 | 10 | 0 | -103 | 7632
2009-10-12 02:37 | 59.972 | 3785.6899 | 335 | 218.3273 | 16 | 245.5 | 10 | 0 | -103 | 7632
2009-10-12 02:37 | 59.967 | 3784.8306 | 335 | 218.3273 | 16 | 246 | 10 | 0 | -103 | 7632
2009-10-12 02:37 | 59.969 | 3784.3203 | 335 | 217.3794 | 16 | 246.5 | 10 | 0 | -103 | 7632
2009-10-12 02:37 | 59.969 | 3782.8086 | 335 | 217.3794 | 16 | 247 | 10 | 0 | -103 | 7632
2009-10-12 02:37 | 59.967 | 3779.3516 | 335 | 217.3794 | 16 | 247.5 | 10 | 0 | -103 | 7631
2009-10-12 02:37 | 59.966 | 3779.0562 | 335 | 217.3794 | 16 | 248 | 10 | 0 | -103 | 7625
2009-10-12 02:37 | 59.965 | 3779.2117 | 335 | 217.3794 | 16 | 248.5 | 10 | 0 | -103 | 7623
2009-10-12 02:37 | 59.967 | 3779.3347 | 335 | 214.8304 | 16 | 249 | 10 | 0 | -103 | 7621
2009-10-12 02:37 | 59.965 | 3775.6467 | 335 | 214.8304 | 16 | 249.5 | 10 | 0 | -103 | 7623
2009-10-12 02:37 | 59.964 | 3776.5967 | 335 | 214.8304 | 16 | 250 | 10 | 0 | -103 | 7625
2009-10-12 02:37 | 59.97 | 3776.0229 | 335 | 214.8304 | 16 | 250.5 | 10 | 0 | -103 | 7627
2009-10-12 02:37 | 59.969 | 3773.1699 | 335 | 214.8304 | 16 | 251 | 10 | 0 | -103 | 7628
2009-10-12 02:37 | 59.968 | 3768.793 | 335 | 227.6559 | 16 | 251.5 | 10 | 0 | -103 | 7628
2009-10-12 02:37 | 59.965 | 3768.5029 | 335 | 227.6559 | 16 | 252 | 10 | 0 | -103 | 7629
2009-10-12 02:37 | 59.97 | 3767.3662 | 335 | 227.6559 | 16 | 252.5 | 10 | 0 | -103 | 7630
2009-10-12 02:37 | 59.968 | 3764.7861 | 335 | 227.6559 | 16 | 253 | 10 | 0 | -103 | 7631
2009-10-12 02:37 | 59.965 | 3759.5918 | 335 | 227.6559 | 16 | 253.5 | 10 | 0 | -103 | 7635
2009-10-12 02:37 | 59.969 | 3761.8938 | 335 | 225.0181 | 16 | 254 | 10 | 0 | -103 | 7638
2009-10-12 02:37 | 59.967 | 3760.5825 | 335 | 225.0181 | 16 | 254.5 | 10 | 0 | -103 | 7639
2009-10-12 02:38 | 59.966 | 3760.1575 | 335 | 225.0181 | 16 | 255 | 10 | 0 | -103 | 7642
2009-10-12 02:38 | 59.979 | 3759.4949 | 335 | 225.0181 | 16 | 255.5 | 10 | 0 | -103 | 7644
2009-10-12 02:38 | 59.983 | 3757.7729 | 335 | 225.0181 | 16 | 256 | 10 | 0 | -103 | 7645
2009-10-12 02:38 | 59.974 | 3753.0874 | 335 | 228.3652 | 16 | 256.5 | 10 | 0 | -103 | 7647
2009-10-12 02:38 | 59.965 | 3751.6367 | 335 | 228.3652 | 16 | 257 | 10 | 0 | -103 | 7648
2009-10-12 02:38 | 59.962 | 3758.2246 | 335 | 228.3652 | 16 | 257.5 | 10 | 0 | -103 | 7649
2009-10-12 02:38 | 59.961 | 3759.2498 | 335 | 228.3652 | 16 | 258 | 10 | 0 | -103 | 7650
2009-10-12 02:38 | 59.961 | 3760.9648 | 335 | 228.3652 | 16 | 258.5 | 10 | 0 | -103 | 7651
2009-10-12 02:38 | 59.963 | 3762.0222 | 335 | 234.0753 | 16 | 259 | 10 | 0 | -103 | 7652
2009-10-12 02:38 | 59.959 | 3763.1001 | 335 | 234.0753 | 16 | 259.5 | 10 | 0 | -103 | 7653
2009-10-12 02:38 | 59.951 | 3763.8582 | 335 | 234.0753 | 16 | 260 | 10 | 0 | -103 | 7654
2009-10-12 02:38 | 59.953 | 3766.1267 | 335 | 234.0753 | 16 | 260.5 | 10 | 0 | -103 | 7655
2009-10-12 02:38 | 59.957 | 3768.3389 | 335 | 234.0753 | 16 | 261 | 10 | 0 | -103 | 7655
2009-10-12 02:38 | 59.956 | 3767.4375 | 335 | 228.7982 | 16 | 261.5 | 10 | 0 | -103 | 7656
2009-10-12 02:38 | 59.963 | 3765.6064 | 335 | 228.7982 | 16 | 262 | 10 | 0 | -103 | 7656
2009-10-12 02:38 | 59.961 | 3761.5703 | 335 | 228.7982 | 16 | 262.5 | 10 | 0 | -103 | 7657
2009-10-12 02:38 | 59.963 | 3761.9199 | 335 | 228.7982 | 16 | 263 | 10 | 0 | -103 | 7657
2009-10-12 02:38 | 59.963 | 3758.522 | 335 | 228.7982 | 16 | 263.5 | 10 | 0 | -103 | 7658
2009-10-12 02:38 | 59.968 | 3752.4287 | 335 | 229.467 | 16 | 264 | 10 | 0 | -103 | 7658
2009-10-12 02:38 | 59.968 | 3753.8296 | 335 | 229.467 | 16 | 264.5 | 10 | 0 | -103 | 7659
2009-10-12 02:38 | 59.97 | 3753.5103 | 335 | 229.467 | 16 | 265 | 10 | 0 | -103 | 7659
2009-10-12 02:39 | 59.973 | 3752.7407 | 335 | 229.467 | 16 | 265.5 | 10 | 0 | -103 | 7659
2009-10-12 02:39 | 59.965 | 3753.1782 | 335 | 229.467 | 16 | 266 | 10 | 0 | -103 | 7660
2009-10-12 02:39 | 59.967 | 3753.2905 | 335 | 228.9802 | 16 | 266.5 | 10 | 0 | -103 | 7660
2009-10-12 02:39 | 59.972 | 3752.8716 | 335 | 228.9802 | 16 | 267 | 10 | 0 | -103 | 7661
2009-10-12 02:39 | 59.976 | 3749.3979 | 335 | 228.9802 | 16 | 267.5 | 10 | 0 | -103 | 7661
2009-10-12 02:39 | 59.969 | 3747.4758 | 335 | 228.9802 | 16 | 268 | 10 | 0 | -103 | 7662
2009-10-12 02:39 | 59.973 | 3741.2852 | 335 | 228.9802 | 16 | 268.5 | 10 | 0 | -103 | 7662
2009-10-12 02:39 | 59.978 | 3746.6509 | 335 | 219.9756 | 16 | 269 | 10 | 0 | -103 | 7663
2009-10-12 02:39 | 59.981 | 3743.3506 | 335 | 219.9756 | 16 | 269.5 | 10 | 0 | -103 | 7663
2009-10-12 02:39 | 59.981 | 3741.6182 | 335 | 219.9756 | 16 | 270 | 10 | 0 | -103 | 7664
2009-10-12 02:39 | 59.982 | 3738.4844 | 335 | 219.9756 | 16 | 270.5 | 10 | 0 | -103 | 7664
2009-10-12 02:39 | 59.984 | 3738.9014 | 335 | 219.9756 | 16 | 271 | 10 | 0 | -103 | 7665
2009-10-12 02:39 | 59.982 | 3737.2732 | 335 | 229.0892 | 16 | 271.5 | 10 | 0 | -103 | 7666
2009-10-12 02:39 | 59.979 | 3736.3083 | 335 | 229.0892 | 16 | 272 | 10 | 0 | -103 | 7666
2009-10-12 02:39 | 59.98 | 3735.4482 | 335 | 229.0892 | 16 | 272.5 | 10 | 0 | -103 | 7667
2009-10-12 02:39 | 59.978 | 3735.6497 | 335 | 229.0892 | 16 | 273 | 10 | 0 | -103 | 7668
2009-10-12 02:39 | 59.98 | 3738.012 | 335 | 229.0892 | 16 | 273.5 | 10 | 0 | -103 | 7668
2009-10-12 02:39 | 59.98 | 3736.7476 | 335 | 229.6633 | 16 | 274 | 10 | 0 | -103 | 7669
2009-10-12 02:39 | 59.978 | 3736.0674 | 335 | 229.6633 | 16 | 274.5 | 10 | 0 | -103 | 7669
2009-10-12 02:40 | 59.972 | 3736.0942 | 335 | 229.6633 | 16 | 275 | 10 | 0 | -103 | 7670
2009-10-12 02:40 | 59.971 | 3738.571 | 335 | 229.6633 | 16 | 275.5 | 10 | 0 | -103 | 7670
2009-10-12 02:40 | 59.974 | 3738.8748 | 335 | 229.6633 | 16 | 276 | 10 | 0 | -103 | 7671
2009-10-12 02:40 | 59.975 | 3738.647 | 335 | 229.2339 | 16 | 276.5 | 10 | 0 | -103 | 7671
2009-10-12 02:40 | 59.972 | 3737.6841 | 335 | 229.2339 | 16 | 277 | 10 | 0 | -103 | 7672
2009-10-12 02:40 | 59.969 | 3737.8921 | 335 | 229.2339 | 16 | 277.5 | 10 | 0 | -103 | 7673
2009-10-12 02:40 | 59.974 | 3740.0168 | 335 | 229.2339 | 16 | 278 | 10 | 0 | -103 | 7673
2009-10-12 02:40 | 59.972 | 3742.0527 | 350 | 229.2339 | 16 | 278.5 | 10 | 0 | -103 | 7673
2009-10-12 02:40 | 59.972 | 3742.4238 | 350 | 231.4099 | 16 | 279 | 10 | 0 | -103 | 7673
2009-10-12 02:40 | 59.977 | 3742.2451 | 350 | 231.4099 | 16 | 279.5 | 10 | 0 | -103 | 7673
2009-10-12 02:40 | 59.978 | 3741.7231 | 350 | 231.4099 | 16 | 280 | 10 | 0 | -103 | 7673
2009-10-12 02:40 | 59.976 | 3740.6292 | 350 | 231.4099 | 16 | 280.5 | 10 | 0 | -103 | 7673
2009-10-12 02:40 | 59.974 | 3739.9644 | 350 | 231.4099 | 16 | 281 | 10 | 0 | -103 | 7673
2009-10-12 02:40 | 59.977 | 3742.8325 | 350 | 218.6223 | 16 | 281.5 | 10 | 0 | -103 | 7673
2009-10-12 02:40 | 59.978 | 3741.2678 | 350 | 218.6223 | 16 | 282 | 10 | 0 | -103 | 7673
2009-10-12 02:40 | 59.979 | 3738.9658 | 350 | 218.6223 | 16 | 282.5 | 10 | 0 | -103 | 7673
2009-10-12 02:40 | 59.977 | 3738.7061 | 350 | 218.6223 | 16 | 283 | 10 | 0 | -103 | 7673
2009-10-12 02:40 | 59.974 | 3739.8596 | 350 | 218.6223 | 16 | 283.5 | 10 | 0 | -103 | 7673
2009-10-12 02:40 | 59.971 | 3738.1016 | 350 | 213.5359 | 16 | 284 | 10 | 0 | -103 | 7673
2009-10-12 02:40 | 59.971 | 3743.5068 | 350 | 213.5359 | 16 | 284.5 | 10 | 0 | -103 | 7673
2009-10-12 02:40 | 59.968 | 3743.4187 | 350 | 213.5359 | 16 | 285 | 10 | 0 | -103 | 7673
2009-10-12 02:41 | 59.966 | 3745.7441 | 350 | 213.5359 | 16 | 285.5 | 10 | 0 | -103 | 7674
2009-10-12 02:41 | 59.971 | 3747.3396 | 350 | 213.5359 | 16 | 286 | 10 | 0 | -103 | 7675
2009-10-12 02:41 | 59.973 | 3749.75 | 350 | 225.6519 | 16 | 286.5 | 10 | 0 | -103 | 7676
2009-10-12 02:41 | 59.969 | 3746.2166 | 350 | 225.6519 | 16 | 287 | 10 | 0 | -103 | 7677
2009-10-12 02:41 | 59.972 | 3743.7451 | 350 | 225.6519 | 16 | 287.5 | 10 | 0 | -103 | 7678
2009-10-12 02:41 | 59.973 | 3743.1489 | 350 | 225.6519 | 16 | 288 | 10 | 0 | -103 | 7679
2009-10-12 02:41 | 59.97 | 3739.4526 | 350 | 225.6519 | 16 | 288.5 | 10 | 0 | -103 | 7680
2009-10-12 02:41 | 59.974 | 3733.376 | 350 | 212.5736 | 16 | 289 | 10 | 0 | -103 | 7681
2009-10-12 02:41 | 59.982 | 3737.5825 | 350 | 212.5736 | 16 | 289.5 | 10 | 0 | -103 | 7682
2009-10-12 02:41 | 59.985 | 3736.2295 | 350 | 212.5736 | 16 | 290 | 10 | 0 | -103 | 7684
2009-10-12 02:41 | 59.985 | 3733.4338 | 350 | 212.5736 | 16 | 290.5 | 10 | 0 | -103 | 7685
2009-10-12 02:41 | 59.989 | 3733.1152 | 350 | 212.5736 | 16 | 291 | 10 | 0 | -103 | 7687
2009-10-12 02:41 | 59.989 | 3729.1802 | 350 | 219.8973 | 16 | 291.5 | 10 | 0 | -103 | 7689
2009-10-12 02:41 | 59.987 | 3725.4587 | 350 | 219.8973 | 16 | 292 | 10 | 0 | -103 | 7690
2009-10-12 02:41 | 59.99 | 3720.1079 | 350 | 219.8973 | 16 | 292.5 | 10 | 0 | -103 | 7692
2009-10-12 02:41 | 59.996 | 3720.9382 | 350 | 219.8973 | 16 | 293 | 10 | 0 | -103 | 7692
2009-10-12 02:41 | 60.001 | 3725.6768 | 350 | 219.8973 | 16 | 293.5 | 10 | 0 | -103 | 7693
2009-10-12 02:41 | 60.004 | 3727.7542 | 350 | 231.1754 | 16 | 294 | 10 | 0 | -103 | 7693
2009-10-12 02:41 | 60.006 | 3727.6833 | 350 | 231.1754 | 16 | 294.5 | 10 | 0 | -103 | 7694
2009-10-12 02:42 | 60.014 | 3727.2314 | 350 | 231.1754 | 16 | 295 | 10 | 0 | -103 | 7694
2009-10-12 02:42 | 60.019 | 3726.4463 | 350 | 231.1754 | 16 | 295.5 | 10 | 0 | -103 | 7695
2009-10-12 02:42 | 60.025 | 3726.0156 | 350 | 231.1754 | 16 | 296 | 10 | 0 | -103 | 7695
2009-10-12 02:42 | 60.026 | 3716.3745 | 350 | 226.6341 | 16 | 296.5 | 10 | 0 | -103 | 7695
2009-10-12 02:42 | 60.029 | 3717.3325 | 350 | 226.6341 | 16 | 297 | 10 | 0 | -103 | 7696
2009-10-12 02:42 | 60.029 | 3717.1421 | 350 | 226.6341 | 16 | 297.5 | 10 | 0 | -103 | 7696
2009-10-12 02:42 | 60.036 | 3715.166 | 350 | 226.6341 | 16 | 298 | 10 | 0 | -103 | 7697
2009-10-12 02:42 | 60.037 | 3710.2834 | 350 | 226.6341 | 16 | 298.5 | 10 | 0 | -103 | 7697
2009-10-12 02:42 | 60.036 | 3710.1577 | 350 | 227.2551 | 16 | 299 | 10 | 0 | -103 | 7697
2009-10-12 02:42 | 60.041 | 3698.5911 | 350 | 227.2551 | 16 | 299.5 | 10 | 0 | -103 | 7698
2009-10-12 02:42 | 60.044 | 3704.5913 | 350 | 227.2551 | 16 | 300 | 10 | 0 | -103 | 7698
2009-10-12 02:42 | 60.043 | 3702.4824 | 350 | 227.2551 | 16 | 300.5 | 10 | 0 | -103 | 7698.33
2009-10-12 02:42 | 60.048 | 3701.3164 | 350 | 227.2551 | 16 | 301 | 10 | 0 | -103 | 7698.66
2009-10-12 02:42 | 60.046 | 3699.5286 | 350 | 229.2902 | 16 | 301.5 | 10 | 0 | -103 | 7698.99
2009-10-12 02:42 | 60.043 | 3699.7261 | 350 | 229.2902 | 16 | 302 | 10 | 0 | -103 | 7699.32
2009-10-12 02:42 | 60.043 | 3690.4773 | 350 | 229.2902 | 16 | 302.5 | 10 | 0 | -103 | 7699.65
2009-10-12 02:42 | 60.043 | 3696.8645 | 350 | 229.2902 | 16 | 303 | 10 | 0 | -103 | 7699.98
2009-10-12 02:42 | 60.043 | 3696.1819 | 350 | 229.2902 | 16 | 303.5 | 10 | 0 | -103 | 7700.31
2009-10-12 02:42 | 60.04 | 3696.5413 | 350 | 221.4614 | 16 | 304 | 10 | 0 | -103 | 7700.64
2009-10-12 02:42 | 60.041 | 3698.686 | 350 | 221.4614 | 16 | 304.5 | 10 | 0 | -103 | 7700.97
2009-10-12 02:42 | 60.039 | 3699.6306 | 350 | 221.4614 | 16 | 305 | 10 | 0 | -103 | 7701.3
2009-10-12 02:43 | 60.036 | 3699.7122 | 350 | 221.4614 | 16 | 305.5 | 10 | 0 | -103 | 7701.63
2009-10-12 02:43 | 60.033 | 3700.1057 | 350 | 221.4614 | 16 | 306 | 10 | 0 | -103 | 7701.96
2009-10-12 02:43 | 60.034 | 3701.1218 | 350 | 241.2744 | 16 | 306.5 | 10 | 0 | -103 | 7702.29
2009-10-12 02:43 | 60.037 | 3701.8652 | 350 | 241.2744 | 16 | 307 | 10 | 0 | -103 | 7702.62
2009-10-12 02:43 | 60.035 | 3701.9978 | 350 | 241.2744 | 16 | 307.5 | 10 | 0 | -103 | 7702.95
2009-10-12 02:43 | 60.033 | 3702.9126 | 350 | 241.2744 | 16 | 308 | 10 | 0 | -103 | 7703.28
2009-10-12 02:43 | 60.036 | 3705.5225 | 350 | 241.2744 | 16 | 308.5 | 10 | 0 | -103 | 7703.61
2009-10-12 02:43 | 60.034 | 3704.9668 | 350 | 243.0719 | 16 | 309 | 10 | 0 | -103 | 7703.94
2009-10-12 02:43 | 60.032 | 3702.7708 | 350 | 243.0719 | 16 | 309.5 | 10 | 0 | -103 | 7704.27
2009-10-12 02:43 | 60.034 | 3703.7063 | 350 | 243.0719 | 16 | 310 | 10 | 0 | -103 | 7704.6
2009-10-12 02:43 | 60.033 | 3705.4353 | 350 | 243.0719 | 16 | 310.5 | 10 | 0 | -103 | 7704.93
2009-10-12 02:43 | 60.035 | 3704.3601 | 350 | 243.0719 | 16 | 311 | 10 | 0 | -103 | 7705.26
2009-10-12 02:43 | 60.035 | 3702.2043 | 350 | 241.6702 | 16 | 311.5 | 10 | 0 | -103 | 7705.59
2009-10-12 02:43 | 60.039 | 3701.9419 | 350 | 241.6702 | 16 | 312 | 10 | 0 | -103 | 7705.92
2009-10-12 02:43 | 60.037 | 3703.3179 | 350 | 241.6702 | 16 | 312.5 | 10 | 0 | -103 | 7706.25
2009-10-12 02:43 | 60.036 | 3702.457 | 350 | 241.6702 | 16 | 313 | 10 | 0 | -103 | 7706.58
2009-10-12 02:43 | 60.034 | 3703.2686 | 350 | 241.6702 | 16 | 313.5 | 10 | 0 | -103 | 7706.91
2009-10-12 02:43 | 60.037 | 3703.8435 | 350 | 228.1493 | 16 | 314 | 10 | 0 | -103 | 7707.24
2009-10-12 02:43 | 60.037 | 3702.5176 | 350 | 228.1493 | 16 | 314.5 | 10 | 0 | -103 | 7707.57
2009-10-12 02:44 | 60.038 | 3702.2795 | 350 | 228.1493 | 16 | 315 | 10 | 0 | -103 | 7707.9
2009-10-12 02:44 | 60.04 | 3692.178 | 350 | 228.1493 | 16 | 315.5 | 10 | 0 | -103 | 7708.23
2009-10-12 02:44 | 60.045 | 3700.2759 | 350 | 228.1493 | 16 | 316 | 10 | 0 | -103 | 7708.56
2009-10-12 02:44 | 60.045 | 3697.7285 | 350 | 235.129 | 16 | 316.5 | 10 | 0 | -103 | 7708.89
2009-10-12 02:44 | 60.043 | 3696.916 | 350 | 235.129 | 16 | 317 | 10 | 0 | -103 | 7709.22
2009-10-12 02:44 | 60.04 | 3697.3459 | 350 | 235.129 | 16 | 317.5 | 10 | 0 | -103 | 7709.55
2009-10-12 02:44 | 60.046 | 3698.4292 | 350 | 235.129 | 16 | 318 | 10 | 0 | -103 | 7709.88
2009-10-12 02:44 | 60.042 | 3693.5837 | 350 | 235.129 | 16 | 318.5 | 10 | 0 | -103 | 7710.21
2009-10-12 02:44 | 60.039 | 3693.2407 | 350 | 246.4331 | 16 | 319 | 10 | 0 | -103 | 7710.54
2009-10-12 02:44 | 60.039 | 3699.3643 | 350 | 246.4331 | 16 | 319.5 | 10 | 0 | -103 | 7710.87
2009-10-12 02:44 | 60.037 | 3701.791 | 350 | 246.4331 | 16 | 320 | 10 | 0 | -103 | 7711.2
2009-10-12 02:44 | 60.034 | 3700.7534 | 350 | 246.4331 | 16 | 320.5 | 10 | 0 | -103 | 7711.53
2009-10-12 02:44 | 60.032 | 3702.1479 | 350 | 246.4331 | 16 | 321 | 10 | 0 | -103 | 7711.86
2009-10-12 02:44 | 60.031 | 3707.521 | 350 | 236.5535 | 16 | 321.5 | 10 | 0 | -103 | 7712.19
2009-10-12 02:44 | 60.027 | 3707.2866 | 350 | 236.5535 | 16 | 322 | 10 | 0 | -103 | 7712.52
2009-10-12 02:44 | 60.031 | 3707.3403 | 350 | 236.5535 | 16 | 322.5 | 10 | 0 | -103 | 7712.85
2009-10-12 02:44 | 60.031 | 3707.9165 | 350 | 236.5535 | 16 | 323 | 10 | 0 | -103 | 7713.18
2009-10-12 02:44 | 60.031 | 3706.8574 | 350 | 236.5535 | 16 | 323.5 | 10 | 0 | -103 | 7713.51
2009-10-12 02:44 | 60.039 | 3707.6152 | 350 | 230.2976 | 16 | 324 | 10 | 0 | -103 | 7713.84
2009-10-12 02:44 | 60.039 | 3703.7461 | 350 | 230.2976 | 16 | 324.5 | 10 | 0 | -103 | 7714.17
2009-10-12 02:44 | 60.037 | 3701.582 | 350 | 230.2976 | 16 | 325 | 10 | 0 | -103 | 7714.5
2009-10-12 02:45 | 60.035 | 3701.2075 | 350 | 230.2976 | 16 | 325.5 | 10 | 0 | -103 | 7714.83
2009-10-12 02:45 | 60.04 | 3702.2122 | 350 | 230.2976 | 16 | 326 | 10 | 0 | -103 | 7715.16
2009-10-12 02:45 | 60.042 | 3700.3975 | 350 | 231.1755 | 16 | 326.5 | 10 | 0 | -103 | 7715.49
2009-10-12 02:45 | 60.036 | 3699.6897 | 350 | 231.1755 | 16 | 327 | 10 | 0 | -103 | 7715.82
2009-10-12 02:45 | 60.04 | 3700.8271 | 350 | 231.1755 | 16 | 327.5 | 10 | 0 | -103 | 7716.15
2009-10-12 02:45 | 60.045 | 3700.6616 | 350 | 231.1755 | 16 | 328 | 10 | 0 | -103 | 7716.48
2009-10-12 02:45 | 60.048 | 3695.6882 | 350 | 231.1755 | 16 | 328.5 | 10 | 0 | -103 | 7716.81
2009-10-12 02:45 | 60.044 | 3695.8186 | 350 | 225.6176 | 16 | 329 | 10 | 0 | -103 | 7717.14
2009-10-12 02:45 | 60.044 | 3694.7991 | 350 | 225.6176 | 16 | 329.5 | 10 | 0 | -103 | 7717.47
2009-10-12 02:45 | 60.044 | 3696.897 | 350 | 225.6176 | 16 | 330 | 10 | 0 | -103 | 7717.8
2009-10-12 02:45 | 60.04 | 3696.0227 | 350 | 225.6176 | 16 | 330.5 | 10 | 0 | -103 | 7718.13
2009-10-12 02:45 | 60.045 | 3698.4243 | 350 | 225.6176 | 16 | 331 | 10 | 0 | -103 | 7718.46
2009-10-12 02:45 | 60.044 | 3700.1768 | 350 | 230.7344 | 16 | 331.5 | 10 | 0 | -103 | 7718.79
2009-10-12 02:45 | 60.039 | 3699.8064 | 350 | 230.7344 | 16 | 332 | 10 | 0 | -103 | 7719.12
2009-10-12 02:45 | 60.042 | 3697.6807 | 350 | 230.7344 | 16 | 332.5 | 10 | 0 | -103 | 7719.45
2009-10-12 02:45 | 60.041 | 3698.5073 | 350 | 230.7344 | 16 | 333 | 10 | 0 | -103 | 7719.78
2009-10-12 02:45 | 60.038 | 3698.4658 | 350 | 230.7344 | 16 | 333.5 | 10 | 0 | -103 | 7720.11
2009-10-12 02:45 | 60.037 | 3699.0771 | 350 | 234.8471 | 16 | 334 | 10 | 0 | -103 | 7720.44
2009-10-12 02:45 | 60.039 | 3701.5918 | 350 | 234.8471 | 16 | 334.5 | 10 | 0 | -103 | 7720.77
2009-10-12 02:46 | 60.04 | 3700.9023 | 350 | 234.8471 | 16 | 335 | 10 | 0 | -103 | 7721.1
2009-10-12 02:46 | 60.039 | 3700.27 | 350 | 234.8471 | 16 | 335.5 | 10 | 0 | -103 | 7721.43
2009-10-12 02:46 | 60.038 | 3701.1394 | 350 | 234.8471 | 16 | 336 | 10 | 0 | -103 | 7721.76
2009-10-12 02:46 | 60.039 | 3700.2644 | 350 | 228.9609 | 16 | 336.5 | 10 | 0 | -103 | 7722.09
2009-10-12 02:46 | 60.037 | 3699.4585 | 350 | 228.9609 | 16 | 337 | 10 | 0 | -103 | 7722.42
2009-10-12 02:46 | 60.037 | 3700.4575 | 350 | 228.9609 | 16 | 337.5 | 10 | 0 | -103 | 7722.75
2009-10-12 02:46 | 60.039 | 3699.5051 | 350 | 228.9609 | 16 | 338 | 10 | 0 | -103 | 7723.08
2009-10-12 02:46 | 60.038 | 3699.2161 | 350 | 228.9609 | 16 | 338.5 | 10 | 0 | -103 | 7723.41
2009-10-12 02:46 | 60.035 | 3699.4004 | 350 | 231.1779 | 16 | 339 | 10 | 0 | -103 | 7723.74
2009-10-12 02:46 | 60.033 | 3702.1731 | 350 | 231.1779 | 16 | 339.5 | 10 | 0 | -103 | 7724.07
2009-10-12 02:46 | 60.03 | 3702.9675 | 350 | 231.1779 | 16 | 340 | 10 | 0 | -103 | 7724.4
2009-10-12 02:46 | 60.032 | 3704.9517 | 350 | 231.1779 | 16 | 340.5 | 10 | 0 | -103 | 7724.73
2009-10-12 02:46 | 60.037 | 3705.7751 | 350 | 231.1779 | 16 | 341 | 10 | 0 | -103 | 7725.06
2009-10-12 02:46 | 60.042 | 3703.7441 | 350 | 236.4893 | 16 | 341.5 | 10 | 0 | -103 | 7725.39
2009-10-12 02:46 | 60.036 | 3701.9812 | 350 | 236.4893 | 16 | 342 | 10 | 0 | -103 | 7725.72
2009-10-12 02:46 | 60.031 | 3700.7471 | 350 | 236.4893 | 16 | 342.5 | 10 | 0 | -103 | 7726.05
2009-10-12 02:46 | 60.031 | 3702.2126 | 350 | 236.4893 | 16 | 343 | 10 | 0 | -103 | 7726.38
2009-10-12 02:46 | 60.034 | 3705.5137 | 350 | 236.4893 | 16 | 343.5 | 10 | 0 | -103 | 7726.71
2009-10-12 02:46 | 60.032 | 3704.4487 | 350 | 245.0389 | 16 | 344 | 10 | 0 | -103 | 7727.04
2009-10-12 02:46 | 60.038 | 3703.6196 | 350 | 245.0389 | 16 | 344.5 | 10 | 0 | -103 | 7727.37
2009-10-12 02:46 | 60.044 | 3702.7954 | 350 | 245.0389 | 16 | 345 | 10 | 0 | -103 | 7727.7
2009-10-12 02:47 | 60.042 | 3697.3804 | 350 | 245.0389 | 16 | 345.5 | 10 | 0 | -103 | 7728.03
2009-10-12 02:47 | 60.04 | 3696.2495 | 350 | 245.0389 | 16 | 346 | 10 | 0 | -103 | 7728.36
2009-10-12 02:47 | 60.04 | 3693.5181 | 350 | 223.6057 | 16 | 346.5 | 10 | 0 | -103 | 7728.69
2009-10-12 02:47 | 60.043 | 3693.5771 | 350 | 223.6057 | 16 | 347 | 10 | 0 | -103 | 7729.02
2009-10-12 02:47 | 60.041 | 3695.1855 | 350 | 223.6057 | 16 | 347.5 | 10 | 0 | -103 | 7729.35
2009-10-12 02:47 | 60.038 | 3693.7861 | 350 | 223.6057 | 16 | 348 | 10 | 0 | -103 | 7729.68
2009-10-12 02:47 | 60.043 | 3694.9263 | 350 | 223.6057 | 16 | 348.5 | 10 | 0 | -103 | 7730.01
2009-10-12 02:47 | 60.042 | 3694.9377 | 350 | 231.1194 | 16 | 349 | 10 | 0 | -103 | 7730.34
2009-10-12 02:47 | 60.036 | 3691.3301 | 350 | 231.1194 | 16 | 349.5 | 10 | 0 | -103 | 7730.67
2009-10-12 02:47 | 60.041 | 3692.6863 | 350 | 231.1194 | 16 | 350 | 10 | 0 | -103 | 7731
2009-10-12 02:47 | 60.042 | 3693.3901 | 350 | 231.1194 | 16 | 350.5 | 10 | 0 | -103 | 7731.33
2009-10-12 02:47 | 60.043 | 3692.3569 | 350 | 231.1194 | 16 | 351 | 10 | 0 | -103 | 7731.66
2009-10-12 02:47 | 60.036 | 3690.8362 | 350 | 237.2066 | 16 | 351.5 | 10 | 0 | -103 | 7731.99
2009-10-12 02:47 | 60.039 | 3692.0422 | 350 | 237.2066 | 16 | 352 | 10 | 0 | -103 | 7732.32
2009-10-12 02:47 | 60.037 | 3694.1172 | 350 | 237.2066 | 16 | 352.5 | 10 | 0 | -103 | 7732.65
2009-10-12 02:47 | 60.035 | 3695.2583 | 350 | 237.2066 | 16 | 353 | 10 | 0 | -103 | 7732.98
2009-10-12 02:47 | 60.035 | 3695.9492 | 350 | 237.2066 | 16 | 353.5 | 10 | 0 | -103 | 7733.31
2009-10-12 02:47 | 60.036 | 3695.4912 | 350 | 240.5164 | 16 | 354 | 10 | 0 | -103 | 7733.64
2009-10-12 02:47 | 60.03 | 3696.4863 | 350 | 240.5164 | 16 | 354.5 | 10 | 0 | -103 | 7733.97
2009-10-12 02:48 | 60.03 | 3697.3357 | 350 | 240.5164 | 16 | 355 | 10 | 0 | -103 | 7734.3
2009-10-12 02:48 | 60.031 | 3699.3569 | 350 | 240.5164 | 16 | 355.5 | 10 | 0 | -103 | 7734.63
2009-10-12 02:48 | 60.032 | 3699.2512 | 350 | 240.5164 | 16 | 356 | 10 | 0 | -103 | 7734.96
2009-10-12 02:48 | 60.031 | 3699.1052 | 350 | 237.5661 | 16 | 356.5 | 10 | 0 | -103 | 7735.29
2009-10-12 02:48 | 60.032 | 3699.1265 | 350 | 237.5661 | 16 | 357 | 10 | 0 | -103 | 7735.62
2009-10-12 02:48 | 60.032 | 3698.136 | 350 | 237.5661 | 16 | 357.5 | 10 | 0 | -103 | 7735.95
2009-10-12 02:48 | 60.037 | 3698.2773 | 350 | 237.5661 | 16 | 358 | 10 | 0 | -103 | 7736.28
2009-10-12 02:48 | 60.04 | 3695.9404 | 350 | 237.5661 | 16 | 358.5 | 10 | 0 | -103 | 7736.61
2009-10-12 02:48 | 60.042 | 3693.7358 | 350 | 231.5814 | 16 | 359 | 10 | 0 | -103 | 7736.94
2009-10-12 02:48 | 60.036 | 3691.7585 | 350 | 231.5814 | 16 | 359.5 | 10 | 0 | -103 | 7737.27
2009-10-12 02:48 | 60.041 | 3691.9189 | 350 | 231.5814 | 16 | 360 | 10 | 0 | -103 | 7737.6
2009-10-12 02:48 | 60.04 | 3691.5815 | 350 | 231.5814 | 16 | 360.5 | 10 | 0 | -103 | 7737.93
2009-10-12 02:48 | 60.036 | 3692.3735 | 350 | 231.5814 | 16 | 361 | 10 | 0 | -103 | 7738.26
2009-10-12 02:48 | 60.038 | 3694.7102 | 350 | 235.8508 | 16 | 361.5 | 10 | 0 | -103 | 7738.59
2009-10-12 02:48 | 60.041 | 3694.3313 | 350 | 235.8508 | 16 | 362 | 10 | 0 | -103 | 7738.92
2009-10-12 02:48 | 60.04 | 3693.6172 | 350 | 235.8508 | 16 | 362.5 | 10 | 0 | -103 | 7739.25
2009-10-12 02:48 | 60.033 | 3694.324 | 350 | 235.8508 | 16 | 363 | 10 | 0 | -103 | 7739.58
2009-10-12 02:48 | 60.034 | 3694.6604 | 350 | 235.8508 | 16 | 363.5 | 10 | 0 | -103 | 7739.91
2009-10-12 02:48 | 60.04 | 3693.7476 | 350 | 233.56 | 16 | 364 | 10 | 0 | -103 | 7740.24
2009-10-12 02:48 | 60.041 | 3691.4453 | 350 | 233.56 | 16 | 364.5 | 10 | 0 | -103 | 7740.57
2009-10-12 02:49 | 60.037 | 3691.0117 | 350 | 233.56 | 16 | 365 | 10 | 0 | -103 | 7740.9
2009-10-12 02:49 | 60.036 | 3693.0767 | 350 | 233.56 | 16 | 365.5 | 10 | 0 | -103 | 7741.23
2009-10-12 02:49 | 60.038 | 3693.7271 | 350 | 233.56 | 16 | 366 | 10 | 0 | -103 | 7741.56
2009-10-12 02:49 | 60.039 | 3692.6406 | 350 | 219.01 | 16 | 366.5 | 10 | 0 | -103 | 7741.89
2009-10-12 02:49 | 60.034 | 3688.1594 | 350 | 219.01 | 16 | 367 | 10 | 0 | -103 | 7742.22
2009-10-12 02:49 | 60.033 | 3688.2085 | 350 | 219.01 | 16 | 367.5 | 10 | 0 | -103 | 7742.55
2009-10-12 02:49 | 60.034 | 3690.0918 | 350 | 219.01 | 16 | 368 | 10 | 0 | -103 | 7742.88
2009-10-12 02:49 | 60.029 | 3693.3208 | 350 | 219.01 | 16 | 368.5 | 10 | 0 | -103 | 7743.21
2009-10-12 02:49 | 60.031 | 3694.5933 | 350 | 205.3389 | 16 | 369 | 10 | 0 | -103 | 7743.54
2009-10-12 02:49 | 60.03 | 3694.6089 | 350 | 205.3389 | 16 | 369.5 | 10 | 0 | -103 | 7743.87
2009-10-12 02:49 | 60.026 | 3693.4116 | 350 | 205.3389 | 16 | 370 | 10 | 0 | -103 | 7744.2
2009-10-12 02:49 | 60.022 | 3696.0259 | 350 | 205.3389 | 16 | 370.5 | 10 | 0 | -103 | 7744.53
2009-10-12 02:49 | 60.024 | 3698.0122 | 350 | 205.3389 | 16 | 371 | 10 | 0 | -103 | 7744.86
2009-10-12 02:49 | 60.023 | 3699.4143 | 350 | 236.2854 | 16 | 371.5 | 10 | 0 | -103 | 7745.19
2009-10-12 02:49 | 60.021 | 3698.9351 | 350 | 236.2854 | 16 | 372 | 10 | 0 | -103 | 7745.52
2009-10-12 02:49 | 60.023 | 3700.5442 | 350 | 236.2854 | 16 | 372.5 | 10 | 0 | -103 | 7745.85
2009-10-12 02:49 | 60.026 | 3700.4858 | 350 | 236.2854 | 16 | 373 | 10 | 0 | -103 | 7746.18
2009-10-12 02:49 | 60.026 | 3697.9607 | 350 | 236.2854 | 16 | 373.5 | 10 | 0 | -103 | 7746.51
2009-10-12 02:49 | 60.024 | 3699.9138 | 350 | 223.0157 | 16 | 374 | 10 | 0 | -103 | 7746.84
2009-10-12 02:49 | 60.024 | 3701.3013 | 350 | 223.0157 | 16 | 374.5 | 10 | 0 | -103 | 7747.17
2009-10-12 02:50 | 60.023 | 3701.4502 | 350 | 223.0157 | 16 | 375 | 10 | 0 | -103 | 7747.5
2009-10-12 02:50 | 60.023 | 3701.0938 | 350 | 223.0157 | 16 | 375.5 | 10 | 0 | -103 | 7747.83
2009-10-12 02:50 | 60.026 | 3701.7017 | 350 | 223.0157 | 16 | 376 | 10 | 0 | -103 | 7748.16
2009-10-12 02:50 | 60.029 | 3701.9648 | 350 | 223.0157 | 16 | 376.5 | 10 | 0 | -103 | 7748.49
2009-10-12 02:50 | 60.024 | 3700.2688 | 350 | 223.0157 | 16 | 377 | 10 | 0 | -103 | 7748.82
2009-10-12 02:50 | 60.021 | 3701.0898 | 350 | 223.0157 | 16 | 377.5 | 10 | 0 | -103 | 7749.15
2009-10-12 02:50 | 60.025 | 3701.2681 | 350 | 223.0157 | 16 | 378 | 10 | 0 | -103 | 7749.48
2009-10-12 02:50 | 60.025 | 3700.5874 | 350 | 223.0157 | 16 | 378.5 | 10 | 0 | -103 | 7749.81
2009-10-12 02:50 | 60.026 | 3700.5317 | 350 | 223.0157 | 16 | 379 | 10 | 0 | -103 | 7750.14
2009-10-12 02:50 | 60.024 | 3700.2954 | 350 | 223.0157 | 16 | 379.5 | 10 | 0 | -103 | 7750.47
2009-10-12 02:50 | 60.023 | 3700.2773 | 350 | 223.0157 | 16 | 380 | 10 | 0 | -103 | 7750.8
2009-10-12 02:50 | 60.026 | 3700.8628 | 350 | 223.0157 | 16 | 380.5 | 10 | 0 | -103 | 7751.13
2009-10-12 02:50 | 60.02 | 3700.2603 | 350 | 223.0157 | 16 | 381 | 10 | 0 | -103 | 7751.46
2009-10-12 02:50 | 60.02 | 3699.9255 | 350 | 223.0157 | 16 | 381.5 | 10 | 0 | -103 | 7751.79
2009-10-12 02:50 | 60.015 | 3700.9648 | 350 | 223.0157 | 16 | 382 | 10 | 0 | -103 | 7752.12
2009-10-12 02:50 | 60.016 | 3703.5161 | 350 | 223.0157 | 16 | 382.5 | 10 | 0 | -103 | 7752.45
2009-10-12 02:50 | 60.015 | 3703.8237 | 350 | 223.0157 | 16 | 383 | 10 | 0 | -103 | 7752.78
2009-10-12 02:50 | 60.015 | 3703.6895 | 350 | 223.0157 | 16 | 383.5 | 10 | 0 | -103 | 7753.11
2009-10-12 02:50 | 60.017 | 3703.0034 | 350 | 223.0157 | 16 | 384 | 10 | 0 | -103 | 7753.44
2009-10-12 02:50 | 60.012 | 3702.9995 | 350 | 223.0157 | 16 | 384.5 | 10 | 0 | -103 | 7753.77
2009-10-12 02:50 | 60.008 | 3703.1667 | 350 | 223.0157 | 16 | 385 | 10 | 0 | -103 | 7754.1
2009-10-12 02:51 | 60.002 | 3703.6157 | 350 | 223.0157 | 16 | 385.5 | 10 | 0 | -103 | 7754.43
2009-10-12 02:51 | 59.999 | 3703.7754 | 350 | 223.0157 | 16 | 386 | 10 | 0 | -103 | 7754.76
2009-10-12 02:51 | 60.002 | 3701.5337 | 350 | 223.0157 | 16 | 386.5 | 10 | 0 | -103 | 7755.09
2009-10-12 02:51 | 60.004 | 3700.6167 | 350 | 223.0157 | 16 | 387 | 10 | 0 | -103 | 7755.42
2009-10-12 02:51 | 60.001 | 3700.6252 | 350 | 223.0157 | 16 | 387.5 | 10 | 0 | -103 | 7755.75
2009-10-12 02:51 | 59.993 | 3701.3889 | 350 | 223.0157 | 16 | 388 | 10 | 0 | -103 | 7756.08
2009-10-12 02:51 | 59.992 | 3700.6714 | 350 | 223.0157 | 16 | 388.5 | 10 | 0 | -103 | 7756.41
2009-10-12 02:51 | 59.987 | 3700.8264 | 350 | 223.0157 | 16 | 389 | 10 | 0 | -103 | 7756.74
2009-10-12 02:51 | 59.985 | 3700.7 | 350 | 223.0157 | 16 | 389.5 | 10 | 0 | -103 | 7757.07
2009-10-12 02:51 | 59.986 | 3699.8538 | 350 | 223.0157 | 16 | 390 | 10 | 0 | -103 | 7757.4
2009-10-12 02:51 | 59.984 | 3700.3423 | 350 | 223.0157 | 16 | 390.5 | 10 | 0 | -103 | 7757.73
2009-10-12 02:51 | 59.98 | 3700.7698 | 350 | 223.0157 | 16 | 391 | 10 | 0 | -103 | 7758.06
2009-10-12 02:51 | 59.977 | 3701.6252 | 350 | 223.0157 | 16 | 391.5 | 10 | 0 | -103 | 7758.39
2009-10-12 02:51 | 59.976 | 3703.1658 | 350 | 223.0157 | 16 | 392 | 10 | 0 | -103 | 7758.72
2009-10-12 02:51 | 59.972 | 3704.7847 | 350 | 223.0157 | 16 | 392.5 | 10 | 0 | -103 | 7759.05
2009-10-12 02:51 | 59.977 | 3705.8105 | 350 | 223.0157 | 16 | 393 | 10 | 0 | -103 | 7759.38
2009-10-12 02:51 | 59.975 | 3706.688 | 350 | 223.0157 | 16 | 393.5 | 10 | 0 | -103 | 7759.71
2009-10-12 02:51 | 59.971 | 3706.543 | 350 | 223.0157 | 16 | 394 | 10 | 0 | -103 | 7760.04
2009-10-12 02:51 | 59.971 | 3707.0266 | 350 | 223.0157 | 16 | 394.5 | 10 | 0 | -103 | 7760.37
2009-10-12 02:52 | 59.979 | 3710.1182 | 350 | 223.0157 | 16 | 395 | 10 | 0 | -103 | 7760.7
2009-10-12 02:52 | 59.98 | 3708.7007 | 350 | 223.0157 | 16 | 395.5 | 10 | 0 | -103 | 7761.03
2009-10-12 02:52 | 59.982 | 3708.0181 | 350 | 223.0157 | 16 | 396 | 10 | 0 | -103 | 7761.36
2009-10-12 02:52 | 59.982 | 3706.3425 | 350 | 223.0157 | 16 | 396.5 | 10 | 0 | -103 | 7761.69
2009-10-12 02:52 | 59.981 | 3706.1255 | 350 | 223.0157 | 16 | 397 | 10 | 0 | -103 | 7762.02
2009-10-12 02:52 | 59.979 | 3706.1187 | 350 | 223.0157 | 16 | 397.5 | 10 | 0 | -103 | 7762.35
2009-10-12 02:52 | 59.976 | 3706.1904 | 350 | 223.0157 | 16 | 398 | 10 | 0 | -103 | 7762.68
2009-10-12 02:52 | 59.978 | 3709.4089 | 350 | 223.0157 | 16 | 398.5 | 10 | 0 | -103 | 7763.01
2009-10-12 02:52 | 59.976 | 3708.9714 | 350 | 223.0157 | 16 | 399 | 10 | 0 | -103 | 7763.34
2009-10-12 02:52 | 59.978 | 3708.0708 | 350 | 223.0157 | 16 | 399.5 | 10 | 0 | -103 | 7763.67
2009-10-12 02:52 | 59.971 | 3707.24 | 350 | 223.0157 | 16 | 400 | 10 | 0 | -103 | 7764
2009-10-12 02:52 | 59.97 | 3709.9612 | 350 | 223.0157 | 16 | 400.5 | 10 | 0 | -103 | 7764.33
2009-10-12 02:52 | 59.971 | 3711.75 | 350 | 223.0157 | 16 | 401 | 10 | 0 | -103 | 7764.66
2009-10-12 02:52 | 59.99 | 3710.6953 | 350 | 223.0157 | 16 | 401.5 | 10 | 0 | -103 | 7764.99
2009-10-12 02:52 | 59.999 | 3707.8667 | 350 | 223.0157 | 16 | 402 | 10 | 0 | -103 | 7765.32
2009-10-12 02:52 | 59.999 | 3705.6392 | 350 | 223.0157 | 16 | 402.5 | 10 | 0 | -103 | 7765.65
2009-10-12 02:52 | 59.999 | 3703.7869 | 350 | 223.0157 | 16 | 403 | 10 | 0 | -103 | 7765.98
2009-10-12 02:52 | 60.003 | 3702.0706 | 350 | 223.0157 | 16 | 403.5 | 10 | 0 | -103 | 7766.31
2009-10-12 02:52 | 60.005 | 3699.51 | 350 | 223.0157 | 16 | 404 | 10 | 0 | -103 | 7766.64
2009-10-12 02:52 | 60.01 | 3698.1367 | 350 | 223.0157 | 16 | 404.5 | 10 | 0 | -103 | 7766.97
2009-10-12 02:52 | 60.02 | 3697.8821 | 350 | 223.0157 | 16 | 405 | 10 | 0 | -103 | 7767.3
2009-10-12 02:53 | 60.022 | 3698.6045 | 350 | 223.0157 | 16 | 405.5 | 10 | 0 | -103 | 7767.63
2009-10-12 02:53 | 60.025 | 3697.8684 | 350 | 223.0157 | 16 | 406 | 10 | 0 | -103 | 7767.96
2009-10-12 02:53 | 60.025 | 3693.9121 | 350 | 223.0157 | 16 | 406.5 | 10 | 0 | -103 | 7768.29
2009-10-12 02:53 | 60.023 | 3693.4177 | 350 | 223.0157 | 16 | 407 | 10 | 0 | -103 | 7768.62
2009-10-12 02:53 | 60.029 | 3688.021 | 350 | 223.0157 | 16 | 407.5 | 10 | 0 | -103 | 7768.95
2009-10-12 02:53 | 60.029 | 3689.1431 | 350 | 223.0157 | 16 | 408 | 10 | 0 | -103 | 7769.28
2009-10-12 02:53 | 60.028 | 3687.8779 | 350 | 223.0157 | 16 | 408.5 | 10 | 0 | -103 | 7769.61
2009-10-12 02:53 | 60.031 | 3687.0264 | 350 | 223.0157 | 16 | 409 | 10 | 0 | -103 | 7769.94
2009-10-12 02:53 | 60.032 | 3685.2756 | 350 | 223.0157 | 16 | 409.5 | 10 | 0 | -103 | 7770.27
2009-10-12 02:53 | 60.033 | 3685.5762 | 350 | 223.0157 | 16 | 410 | 10 | 0 | -103 | 7770.6
2009-10-12 02:53 | 60.03 | 3685.9849 | 350 | 223.0157 | 16 | 410.5 | 10 | 0 | -103 | 7770.93
2009-10-12 02:53 | 60.021 | 3687.1589 | 350 | 223.0157 | 16 | 411 | 10 | 0 | -103 | 7771.26
2009-10-12 02:53 | 60.019 | 3688.9971 | 350 | 223.0157 | 16 | 411.5 | 10 | 0 | -103 | 7771.59
2009-10-12 02:53 | 60.017 | 3690.4258 | 350 | 223.0157 | 16 | 412 | 10 | 0 | -103 | 7771.92
2009-10-12 02:53 | 60.017 | 3692.7153 | 350 | 223.0157 | 16 | 412.5 | 10 | 0 | -103 | 7772.25
2009-10-12 02:53 | 60.015 | 3692.5776 | 350 | 223.0157 | 16 | 413 | 10 | 0 | -103 | 7772.58
2009-10-12 02:53 | 60.015 | 3693.1731 | 350 | 223.0157 | 16 | 413.5 | 10 | 0 | -103 | 7772.91
2009-10-12 02:53 | 60.009 | 3693.2488 | 350 | 223.0157 | 16 | 414 | 10 | 0 | -103 | 7773.24
2009-10-12 02:53 | 60.008 | 3695.1243 | 350 | 223.0157 | 16 | 414.5 | 10 | 0 | -103 | 7773.57
2009-10-12 02:54 | 60.005 | 3694.6807 | 350 | 223.0157 | 16 | 415 | 10 | 0 | -103 | 7773.9
2009-10-12 02:54 | 60.005 | 3694.1987 | 350 | 223.0157 | 16 | 415.5 | 10 | 0 | -103 | 7774.23
2009-10-12 02:54 | 59.999 | 3693.7495 | 350 | 223.0157 | 16 | 416 | 10 | 0 | -103 | 7774.56
2009-10-12 02:54 | 59.997 | 3692.8062 | 350 | 223.0157 | 16 | 416.5 | 10 | 0 | -103 | 7774.89
2009-10-12 02:54 | 60 | 3691.1499 | 350 | 223.0157 | 16 | 417 | 10 | 0 | -103 | 7775.22
2009-10-12 02:54 | 59.998 | 3691.0769 | 350 | 223.0157 | 16 | 417.5 | 10 | 0 | -103 | 7775.55
2009-10-12 02:54 | 59.994 | 3690.5876 | 350 | 223.0157 | 16 | 418 | 10 | 0 | -103 | 7775.88
2009-10-12 02:54 | 59.992 | 3688.4827 | 350 | 223.0157 | 16 | 418.5 | 10 | 0 | -103 | 7776.21
2009-10-12 02:54 | 59.988 | 3689.4453 | 350 | 223.0157 | 16 | 419 | 10 | 0 | -103 | 7776.54
2009-10-12 02:54 | 59.985 | 3689.5249 | 350 | 223.0157 | 16 | 419.5 | 10 | 0 | -103 | 7776.87
2009-10-12 02:54 | 59.988 | 3689.7356 | 350 | 223.0157 | 16 | 420 | 10 | 0 | -103 | 7777.2
2009-10-12 02:54 | 59.988 | 3688.2402 | 350 | 223.0157 | 16 | 420.5 | 10 | 0 | -103 | 7777.53
2009-10-12 02:54 | 59.983 | 3687.4937 | 350 | 223.0157 | 16 | 421 | 10 | 0 | -103 | 7777.86
2009-10-12 02:54 | 59.983 | 3686.7073 | 350 | 223.0157 | 16 | 421.5 | 10 | 0 | -103 | 7778.19
2009-10-12 02:54 | 59.986 | 3685.6597 | 350 | 223.0157 | 16 | 422 | 10 | 0 | -103 | 7778.52
2009-10-12 02:54 | 59.987 | 3684.3335 | 350 | 223.0157 | 16 | 422.5 | 10 | 0 | -103 | 7778.85
2009-10-12 02:54 | 59.986 | 3683.9109 | 350 | 223.0157 | 16 | 423 | 10 | 0 | -103 | 7779.18
2009-10-12 02:54 | 59.985 | 3684.2083 | 350 | 223.0157 | 16 | 423.5 | 10 | 0 | -103 | 7779.51
2009-10-12 02:54 | 59.983 | 3683.811 | 350 | 223.0157 | 16 | 424 | 10 | 0 | -103 | 7779.84
2009-10-12 02:54 | 59.982 | 3684.2578 | 350 | 223.0157 | 16 | 424.5 | 10 | 0 | -103 | 7780.17
2009-10-12 02:54 | 59.98 | 3684.8843 | 350 | 223.0157 | 16 | 425 | 10 | 0 | -103 | 7780.5
2009-10-12 02:55 | 59.978 | 3685.6543 | 350 | 223.0157 | 16 | 425.5 | 10 | 0 | -103 | 7780.83
2009-10-12 02:55 | 59.975 | 3685.0869 | 350 | 223.0157 | 16 | 426 | 10 | 0 | -103 | 7781.16
2009-10-12 02:55 | 59.973 | 3685.196 | 350 | 223.0157 | 16 | 426.5 | 10 | 0 | -103 | 7781.49
2009-10-12 02:55 | 59.976 | 3687.4124 | 350 | 223.0157 | 16 | 427 | 10 | 0 | -103 | 7781.82
2009-10-12 02:55 | 59.976 | 3688.5986 | 350 | 223.0157 | 16 | 427.5 | 10 | 0 | -103 | 7782.15
2009-10-12 02:55 | 59.982 | 3687.8477 | 350 | 223.0157 | 16 | 428 | 10 | 0 | -103 | 7782.48
2009-10-12 02:55 | 59.979 | 3685.7822 | 350 | 223.0157 | 16 | 428.5 | 10 | 0 | -103 | 7782.81
2009-10-12 02:55 | 59.977 | 3684.8901 | 350 | 223.0157 | 16 | 429 | 10 | 0 | -103 | 7783.14
2009-10-12 02:55 | 59.977 | 3684.5493 | 350 | 223.0157 | 16 | 429.5 | 10 | 0 | -103 | 7783.47
2009-10-12 02:55 | 59.978 | 3684.0933 | 350 | 223.0157 | 16 | 430 | 10 | 0 | -103 | 7783.8
2009-10-12 02:55 | 59.978 | 3682.8142 | 350 | 223.0157 | 16 | 430.5 | 10 | 0 | -103 | 7784.13
2009-10-12 02:55 | 59.983 | 3682.3176 | 350 | 223.0157 | 16 | 431 | 10 | 0 | -103 | 7784.46
2009-10-12 02:55 | 59.981 | 3682.6475 | 350 | 223.0157 | 16 | 431.5 | 10 | 0 | -103 | 7784.79
2009-10-12 02:55 | 59.978 | 3682.8555 | 350 | 223.0157 | 16 | 432 | 10 | 0 | -103 | 7785.12
2009-10-12 02:55 | 59.979 | 3684.0518 | 350 | 223.0157 | 16 | 432.5 | 10 | 0 | -103 | 7785.45
2009-10-12 02:55 | 59.979 | 3684.3184 | 350 | 223.0157 | 16 | 433 | 10 | 0 | -103 | 7785.78
2009-10-12 02:55 | 59.983 | 3686.6294 | 350 | 223.0157 | 16 | 433.5 | 10 | 0 | -103 | 7786.11
2009-10-12 02:55 | 59.99 | 3685.2864 | 350 | 223.0157 | 16 | 434 | 10 | 0 | -103 | 7786.44
2009-10-12 02:55 | 59.992 | 3682.416 | 350 | 223.0157 | 16 | 434.5 | 10 | 0 | -103 | 7786.77
2009-10-12 02:55 | 59.99 | 3681.4026 | 350 | 223.0157 | 16 | 435 | 10 | 0 | -103 | 7787.1
2009-10-12 02:56 | 59.988 | 3679.4358 | 350 | 223.0157 | 16 | 435.5 | 10 | 0 | -103 | 7787.43
2009-10-12 02:56 | 59.99 | 3671.7612 | 350 | 223.0157 | 16 | 436 | 10 | 0 | -103 | 7787.76
2009-10-12 02:56 | 59.993 | 3670.1594 | 350 | 223.0157 | 16 | 436.5 | 10 | 0 | -103 | 7788.09
2009-10-12 02:56 | 59.993 | 3679.0005 | 350 | 223.0157 | 16 | 437 | 10 | 0 | -103 | 7788.42
2009-10-12 02:56 | 59.994 | 3681.7988 | 350 | 223.0157 | 16 | 437.5 | 10 | 0 | -103 | 7788.75
2009-10-12 02:56 | 59.993 | 3682.7004 | 350 | 223.0157 | 16 | 438 | 10 | 0 | -103 | 7789.08
2009-10-12 02:56 | 59.989 | 3685.0303 | 350 | 223.0157 | 16 | 438.5 | 10 | 0 | -103 | 7789.41
2009-10-12 02:56 | 59.986 | 3684.8784 | 350 | 223.0157 | 16 | 439 | 10 | 0 | -103 | 7789.74
2009-10-12 02:56 | 59.985 | 3684.478 | 350 | 223.0157 | 16 | 439.5 | 10 | 0 | -103 | 7790.07
2009-10-12 02:56 | 59.987 | 3685.5837 | 350 | 223.0157 | 16 | 440 | 10 | 0 | -103 | 7790.4
2009-10-12 02:56 | 59.986 | 3684.5867 | 350 | 223.0157 | 16 | 440.5 | 10 | 0 | -103 | 7790.73
2009-10-12 02:56 | 59.985 | 3684.9761 | 350 | 223.0157 | 16 | 441 | 10 | 0 | -103 | 7791.06
2009-10-12 02:56 | 59.982 | 3684.8721 | 350 | 223.0157 | 16 | 441.5 | 10 | 0 | -103 | 7791.39
2009-10-12 02:56 | 59.982 | 3684.2446 | 350 | 223.0157 | 16 | 442 | 10 | 0 | -103 | 7791.72
2009-10-12 02:56 | 59.987 | 3685.5891 | 350 | 223.0157 | 16 | 442.5 | 10 | 0 | -103 | 7792.05
2009-10-12 02:56 | 59.997 | 3683.7358 | 350 | 223.0157 | 16 | 443 | 10 | 0 | -103 | 7792.38
2009-10-12 02:56 | 60 | 3682.2341 | 350 | 223.0157 | 16 | 443.5 | 10 | 0 | -103 | 7792.71
2009-10-12 02:56 | 60.003 | 3682.1377 | 350 | 223.0157 | 16 | 444 | 10 | 0 | -103 | 7793.04
2009-10-12 02:56 | 60.003 | 3681.689 | 350 | 223.0157 | 16 | 444.5 | 10 | 0 | -103 | 7793.37
2009-10-12 02:56 | 60.003 | 3681.4585 | 350 | 223.0157 | 16 | 445 | 10 | 0 | -103 | 7793.7
2009-10-12 02:57 | 60.002 | 3681.0129 | 350 | 223.0157 | 16 | 445.5 | 10 | 0 | -103 | 7794.03
2009-10-12 02:57 | 60.004 | 3680.167 | 350 | 223.0157 | 16 | 446 | 10 | 0 | -103 | 7794.36
2009-10-12 02:57 | 60.005 | 3679.4292 | 350 | 223.0157 | 16 | 446.5 | 10 | 0 | -103 | 7794.69
2009-10-12 02:57 | 60.009 | 3679.6692 | 350 | 223.0157 | 16 | 447 | 10 | 0 | -103 | 7795.02
2009-10-12 02:57 | 60.012 | 3678.2673 | 350 | 223.0157 | 16 | 447.5 | 10 | 0 | -103 | 7795.35
2009-10-12 02:57 | 60.021 | 3676.7961 | 350 | 223.0157 | 16 | 448 | 10 | 0 | -103 | 7795.68
2009-10-12 02:57 | 60.022 | 3674.7976 | 350 | 223.0157 | 16 | 448.5 | 10 | 0 | -103 | 7796.01
2009-10-12 02:57 | 60.02 | 3673.906 | 350 | 223.0157 | 16 | 449 | 10 | 0 | -103 | 7796.34
2009-10-12 02:57 | 60.018 | 3670.5098 | 350 | 223.0157 | 16 | 449.5 | 10 | 0 | -103 | 7796.67
2009-10-12 02:57 | 60.02 | 3673.6479 | 350 | 223.0157 | 16 | 450 | 10 | 0 | -103 | 7797
2009-10-12 02:57 | 60.02 | 3675.8647
2009-10-12 02:57 | 60.018 | 3676.6758
2009-10-12 02:57 | 60.019 | 3676.437
2009-10-12 02:57 | 60.018 | 3677.1848
2009-10-12 02:57 | 60.017 | 3678.8284
2009-10-12 02:57 | 60.016 | 3679.2888
2009-10-12 02:57 | 60.016 | 3679.2756
2009-10-12 02:57 | 60.014 | 3678.5986
2009-10-12 02:57 | 60.014 | 3678.2505
2009-10-12 02:58 | 60.013 | 3678.5894
2009-10-12 02:58 | 60.015 | 3675.6978
2009-10-12 02:58 | 60.016 | 3674.6694
2009-10-12 02:58 | 60.019 | 3674.4019
2009-10-12 02:58 | 60.021 | 3674.5461
2009-10-12 02:58 | 60.02 | 3671.9136
2009-10-12 02:58 | 60.024 | 3671.9819
2009-10-12 02:58 | 60.026 | 3670.821
2009-10-12 02:58 | 60.026 | 3671.0596
2009-10-12 02:58 | 60.022 | 3673.7937
2009-10-12 02:58 | 60.022 | 3674.0095
2009-10-12 02:58 | 60.024 | 3675.2842
2009-10-12 02:58 | 60.029 | 3676.0513
2009-10-12 02:58 | 60.028 | 3672.5835
2009-10-12 02:58 | 60.032 | 3671.3428
2009-10-12 02:58 | 60.035 | 3668.6538
2009-10-12 02:58 | 60.028 | 3668.7671
2009-10-12 02:58 | 60.021 | 3667.3218
2009-10-12 02:58 | 60.024 | 3657.1641
2009-10-12 02:58 | 60.025 | 3668.6375
2009-10-12 02:58 | 60.022 | 3669.3088
2009-10-12 02:59 | 60.023 | 3670.7354
2009-10-12 02:59 | 60.02 | 3671.332
2009-10-12 02:59 | 60.02 | 3672.6831
2009-10-12 02:59 | 60.02 | 3673.8325
2009-10-12 02:59 | 60.017 | 3675.6406
2009-10-12 02:59 | 60.012 | 3675.9707
2009-10-12 02:59 | 60.01 | 3678.3137
2009-10-12 02:59 | 60.01 | 3679.3928
2009-10-12 02:59 | 60.01 | 3679.7915
2009-10-12 02:59 | 60.012 | 3679.5967
2009-10-12 02:59 | 60.012 | 3680.1104
2009-10-12 02:59 | 60.014 | 3679.0615
2009-10-12 02:59 | 60.013 | 3679.5869
2009-10-12 02:59 | 60.011 | 3679.6367
2009-10-12 02:59 | 60.01 | 3678.4177
2009-10-12 02:59 | 60.01 | 3679.3831
2009-10-12 02:59 | 60.011 | 3679.9324
2009-10-12 02:59 | 60.016 | 3679.1382
2009-10-12 02:59 | 60.018 | 3678.4985
2009-10-12 03:00 | 60.019 | 3678.4556
2009-10-12 03:00 | 60.019 | 3677.4463
2009-10-12 03:00 | 60.02 | 3677.4314
2009-10-12 03:00 | 60.018 | 3677.3154
2009-10-12 03:00 | 60.016 | 3678.1511
2009-10-12 03:00 | 60.016 | 3678.8735
2009-10-12 03:00 | 60.023 | 3680.7708
2009-10-12 03:00 | 60.022 | 3680.353
2009-10-12 03:00 | 60.015 | 3679.1665
2009-10-12 03:00 | 60.016 | 3680.6724
2009-10-12 03:00 | 60.017 | 3682.7297
2009-10-12 03:00 | 60.01 | 3682.7136
2009-10-12 03:00 | 60.004 | 3682.0103
2009-10-12 03:00 | 59.995 | 3682.4834
2009-10-12 03:00 | 59.982 | 3685.3064
2009-10-12 03:00 | 59.974 | 3684.6426
2009-10-12 03:00 | 59.97 | 3687.5271
2009-10-12 03:00 | 59.968 | 3692.2874
2009-10-12 03:00 | 59.968 | 3692.9663
2009-10-12 03:00 | 59.972 | 3693.7932
2009-10-12 03:00 | 59.966 | 3694.9736
2009-10-12 03:01 | 59.964 | 3698.502
2009-10-12 03:01 | 59.966 | 3698.6169
2009-10-12 03:01 | 59.963 | 3699.8501
2009-10-12 03:01 | 59.965 | 3702.6448
2009-10-12 03:01 | 59.968 | 3702.218
2009-10-12 03:01 | 59.97 | 3704.0234
2009-10-12 03:01 | 59.97 | 3702.9883
2009-10-12 03:01 | 59.972 | 3703.8137
2009-10-12 03:01 | 59.976 | 3705.625
2009-10-12 03:01 | 59.975 | 3704.2935
2009-10-12 03:01 | 59.977 | 3701.9438
2009-10-12 03:01 | 59.976 | 3703.1421
2009-10-12 03:01 | 59.974 | 3705.3757
2009-10-12 03:01 | 59.974 | 3705.6624
2009-10-12 03:01 | 59.974 | 3706.7764
2009-10-12 03:01 | 59.977 | 3707.5139
2009-10-12 03:01 | 59.979 | 3706.446
2009-10-12 03:01 | 59.983 | 3706.335
2009-10-12 03:01 | 59.985 | 3705.9431
2009-10-12 03:02 | 59.98 | 3704.1272
2009-10-12 03:02 | 59.979 | 3705.9744
2009-10-12 03:02 | 59.987 | 3705.9675
2009-10-12 03:02 | 59.986 | 3704.6831
2009-10-12 03:02 | 59.98 | 3703.9133
2009-10-12 03:02 | 59.982 | 3704.9883
2009-10-12 03:02 | 59.985 | 3705.0498
2009-10-12 03:02 | 59.987 | 3703.7407
2009-10-12 03:02 | 59.992 | 3701.8311
2009-10-12 03:02 | 59.996 | 3700.0698
2009-10-12 03:02 | 59.997 | 3701.3081
2009-10-12 03:02 | 59.997 | 3700.9128
2009-10-12 03:02 | 59.997 | 3700.541
2009-10-12 03:02 | 59.996 | 3700.8582
2009-10-12 03:02 | 59.996 | 3700.5486
2009-10-12 03:02 | 59.998 | 3700.2239
2009-10-12 03:02 | 60.009 | 3699.5
2009-10-12 03:02 | 60.01 | 3697.96
2009-10-12 03:02 | 60.005 | 3699.4087
2009-10-12 03:02 | 60.004 | 3700.7383
2009-10-12 03:02 | 60.003 | 3701.1099
2009-10-12 03:03 | 60.001 | 3699.9976
2009-10-12 03:03 | 60.004 | 3700.2202
2009-10-12 03:03 | 60.007 | 3702.5542
2009-10-12 03:03 | 60.008 | 3702.2759
2009-10-12 03:03 | 60.008 | 3701.9229
2009-10-12 03:03 | 60.006 | 3702.9431
2009-10-12 03:03 | 60.006 | 3703.9604
2009-10-12 03:03 | 60 | 3703.8193
2009-10-12 03:03 | 59.999 | 3704.3457
2009-10-12 03:03 | 60 | 3705.3291
2009-10-12 03:03 | 60.004 | 3704.4048
2009-10-12 03:03 | 60.013 | 3703.6753
2009-10-12 03:03 | 60.015 | 3702.6692
2009-10-12 03:03 | 60.012 | 3703.0166
2009-10-12 03:03 | 60.009 | 3703.2974
2009-10-12 03:03 | 60.008 | 3705.1887
2009-10-12 03:03 | 60.011 | 3704.646
2009-10-12 03:03 | 60.013 | 3704.0513
2009-10-12 03:03 | 60.016 | 3704.2551
2009-10-12 03:04 | 60.018 | 3703.7075
2009-10-12 03:04 | 60.019 | 3704.5239
2009-10-12 03:04 | 60.013 | 3704.1392
2009-10-12 03:04 | 60.011 | 3705.4294
2009-10-12 03:04 | 60.009 | 3705.9419
2009-10-12 03:04 | 60.008 | 3705.634
2009-10-12 03:04 | 60.011 | 3705.7485
2009-10-12 03:04 | 60.015 | 3706.9453
2009-10-12 03:04 | 60.021 | 3706.6299
2009-10-12 03:04 | 60.018 | 3703.8948
2009-10-12 03:04 | 60.019 | 3704.2239
2009-10-12 03:04 | 60.019 | 3704.6484
2009-10-12 03:04 | 60.022 | 3704.7954
2009-10-12 03:04 | 60.025 | 3702.7642
2009-10-12 03:04 | 60.03 | 3702.0083
2009-10-12 03:04 | 60.027 | 3701.063
2009-10-12 03:04 | 60.021 | 3700.3401
2009-10-12 03:04 | 60.023 | 3701.5676
2009-10-12 03:04 | 60.02 | 3702.9587
2009-10-12 03:04 | 60.024 | 3703.6211
2009-10-12 03:05 | 60.022 | 3703.374
2009-10-12 03:05 | 60.022 | 3703.9307
2009-10-12 03:05 | 60.025 | 3704.9473
2009-10-12 03:05 | 60.023 | 3703.5413
2009-10-12 03:05 | 60.02 | 3703.1602
2009-10-12 03:05 | 60.018 | 3704.3765
2009-10-12 03:05 | 60.008 | 3705.4412
2009-10-12 03:05 | 60.012 | 3710.072
2009-10-12 03:05 | 60.019 | 3707.9707
2009-10-12 03:05 | 60.019 | 3707.6094
2009-10-12 03:05 | 60.016 | 3708.8311
2009-10-12 03:05 | 60.015 | 3709.8135
2009-10-12 03:05 | 60.014 | 3709.8169
2009-10-12 03:05 | 60.016 | 3709.0938
2009-10-12 03:05 | 60.019 | 3709.6416
2009-10-12 03:05 | 60.016 | 3709.9331
2009-10-12 03:05 | 60.014 | 3710.6768
2009-10-12 03:05 | 60.018 | 3709.3545
2009-10-12 03:05 | 60.023 | 3707.696
2009-10-12 03:05 | 60.024 | 3707.1201
2009-10-12 03:06 | 60.026 | 3706.99
2009-10-12 03:06 | 60.024 | 3704.1851
2009-10-12 03:06 | 60.02 | 3704.4058
2009-10-12 03:06 | 60.019 | 3706.5674
2009-10-12 03:06 | 60.025 | 3705.5159
2009-10-12 03:06 | 60.028 | 3704.4285
2009-10-12 03:06 | 60.031 | 3704.7734
2009-10-12 03:06 | 60.029 | 3702.6855
2009-10-12 03:06 | 60.026 | 3702.093
2009-10-12 03:06 | 60.029 | 3703.6755
2009-10-12 03:06 | 60.033 | 3701.5195
2009-10-12 03:06 | 60.03 | 3698.2217
2009-10-12 03:06 | 60.016 | 3698.0088
2009-10-12 03:06 | 60.019 | 3703.1924
2009-10-12 03:06 | 60.028 | 3703.8147
2009-10-12 03:06 | 60.021 | 3699.9561
2009-10-12 03:06 | 60.015 | 3700.8157
2009-10-12 03:06 | 60.012 | 3706.9434
2009-10-12 03:06 | 60.014 | 3708.5273
2009-10-12 03:06 | 60.013 | 3707.6475
2009-10-12 03:06 | 60.016 | 3706.9912
2009-10-12 03:07 | 60.016 | 3705.5845
2009-10-12 03:07 | 60.013 | 3705.3979
2009-10-12 03:07 | 60.007 | 3709.144
2009-10-12 03:07 | 59.994 | 3708.9895
2009-10-12 03:07 | 59.993 | 3706.1926
2009-10-12 03:07 | 59.993 | 3707.3037
2009-10-12 03:07 | 59.994 | 3706.7603
2009-10-12 03:07 | 59.994 | 3706.9211
2009-10-12 03:07 | 59.993 | 3706.8879
2009-10-12 03:07 | 59.988 | 3704.9336
2009-10-12 03:07 | 59.985 | 3706.481
2009-10-12 03:07 | 59.982 | 3707.0713
2009-10-12 03:07 | 59.98 | 3707.4785
2009-10-12 03:07 | 59.981 | 3708.2458
2009-10-12 03:07 | 59.982 | 3710.4194
2009-10-12 03:07 | 59.98 | 3710.1338
2009-10-12 03:07 | 59.98 | 3710.0239
2009-10-12 03:07 | 59.98 | 3709.1919
2009-10-12 03:07 | 59.983 | 3709.3994
2009-10-12 03:08 | 59.981 | 3707.9114
2009-10-12 03:08 | 59.981 | 3707.6382
2009-10-12 03:08 | 59.981 | 3709.689
2009-10-12 03:08 | 59.981 | 3706.541
2009-10-12 03:08 | 59.98 | 3711.2563
2009-10-12 03:08 | 59.978 | 3712.3032
2009-10-12 03:08 | 59.979 | 3712.0122
2009-10-12 03:08 | 59.978 | 3712.0928
2009-10-12 03:08 | 59.976 | 3713.9917
2009-10-12 03:08 | 59.975 | 3715.0835
2009-10-12 03:08 | 59.975 | 3715.3228
2009-10-12 03:08 | 59.979 | 3714.7173
2009-10-12 03:08 | 59.975 | 3715.1614
2009-10-12 03:08 | 59.976 | 3713.9963
2009-10-12 03:08 | 59.977 | 3714.0627
2009-10-12 03:08 | 59.975 | 3715.6311
2009-10-12 03:08 | 59.979 | 3715.6885
2009-10-12 03:08 | 59.98 | 3715.7246
2009-10-12 03:08 | 59.978 | 3714.8481
2009-10-12 03:08 | 59.979 | 3713.3584
2009-10-12 03:08 | 59.983 | 3712.2747
2009-10-12 03:09 | 59.987 | 3712.1526
2009-10-12 03:09 | 59.984 | 3710.0503
2009-10-12 03:09 | 59.98 | 3710.4719
2009-10-12 03:09 | 59.98 | 3710.6235
2009-10-12 03:09 | 59.979 | 3710.1997
2009-10-12 03:09 | 59.975 | 3710.4746
2009-10-12 03:09 | 59.979 | 3710.803
2009-10-12 03:09 | 59.983 | 3709.2859
2009-10-12 03:09 | 59.983 | 3709.5251
2009-10-12 03:09 | 59.99 | 3708.3711
2009-10-12 03:09 | 59.987 | 3706.512
2009-10-12 03:09 | 59.976 | 3707.4905
2009-10-12 03:09 | 59.979 | 3709.894
2009-10-12 03:09 | 59.983 | 3712.3035
2009-10-12 03:09 | 59.979 | 3711.6272
2009-10-12 03:09 | 59.978 | 3712.0762
2009-10-12 03:09 | 59.975 | 3712.9985
2009-10-12 03:09 | 59.989 | 3713.5103
2009-10-12 03:09 | 59.999 | 3715.4429
2009-10-12 03:10 | 59.989 | 3712.0918
2009-10-12 03:10 | 59.986 | 3714.8936
2009-10-12 03:10 | 59.983 | 3714.9531
2009-10-12 03:10 | 59.982 | 3716.3083
2009-10-12 03:10 | 59.99 | 3715.4385
2009-10-12 03:10 | 59.995 | 3714.7141
2009-10-12 03:10 | 59.99 | 3715.0676
2009-10-12 03:10 | 59.989 | 3715.7913
2009-10-12 03:10 | 59.996 | 3716.2847
2009-10-12 03:10 | 60 | 3714.4604
2009-10-12 03:10 | 60.004 | 3711.7085
2009-10-12 03:10 | 60.004 | 3712.8506
2009-10-12 03:10 | 59.999 | 3713.3616
2009-10-12 03:10 | 59.998 | 3718.2925
2009-10-12 03:10 | 59.996 | 3719.0791
2009-10-12 03:10 | 60.001 | 3717.8152
2009-10-12 03:10 | 60.001 | 3717.8887
2009-10-12 03:10 | 60.003 | 3718.1953
2009-10-12 03:10 | 60.004 | 3719.0212
2009-10-12 03:10 | 60.004 | 3719.8975
2009-10-12 03:10 | 60.006 | 3719.2993
2009-10-12 03:11 | 60.003 | 3719.5273
2009-10-12 03:11 | 60.006 | 3719.731
2009-10-12 03:11 | 60.009 | 3718.5796
2009-10-12 03:11 | 60.01 | 3718.9761
2009-10-12 03:11 | 60.009 | 3720.0337
2009-10-12 03:11 | 60.015 | 3720.6089
2009-10-12 03:11 | 60.014 | 3721.2388
2009-10-12 03:11 | 60.009 | 3720.3804
2009-10-12 03:11 | 60.008 | 3720.8071
2009-10-12 03:11 | 60.01 | 3721.2722
2009-10-12 03:11 | 60.009 | 3721.2446
2009-10-12 03:11 | 60.013 | 3721.5938
2009-10-12 03:11 | 60.014 | 3721.999
2009-10-12 03:11 | 60.012 | 3721.646
2009-10-12 03:11 | 60.01 | 3720.8596
2009-10-12 03:11 | 60.007 | 3721.6453
2009-10-12 03:11 | 60.003 | 3725.0703
2009-10-12 03:11 | 60 | 3724.656
2009-10-12 03:11 | 59.998 | 3724.6606
2009-10-12 03:11 | 59.999 | 3723.696
2009-10-12 03:12 | 60.002 | 3723.4053
2009-10-12 03:12 | 60.003 | 3721.8789
2009-10-12 03:12 | 59.999 | 3722.9065
2009-10-12 03:12 | 60.001 | 3724.1421
2009-10-12 03:12 | 59.995 | 3723.2012
2009-10-12 03:12 | 59.987 | 3723.6389
2009-10-12 03:12 | 59.988 | 3724.6543
2009-10-12 03:12 | 59.99 | 3725.3608
2009-10-12 03:12 | 59.992 | 3725.0464
2009-10-12 03:12 | 59.992 | 3723.6926

## Entry Data
Balancing Authority Name: | My BA
Balancing Authority Frequency Response Obligation (FRO from FRS Form 1) | -80
Note: See "Instruction" tab for more detailed instructions.
Step 1. | Copy and Paste Event Data into the appropriate cells of the "Data" worksheet.
Maintain date and time format of mm/dd/yy hh:mm:ss.
Step 2. | Determine Time of T(0) and edit formula in cell "C8" to reference the correct row of the "Data" worksheet. | 40098.1023
T(0) is the first change in frequency of about 0.010 Hz (10 mHz) which should be the first scan of frequency data of the event.
Step 3. | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1063
Step 4. | Enter MW output of generator or load that caused event (+ for gen loss, - for load loss) | 633 | MW
(Value from NERC Event List. If multiple units, enter total MW loss.)
If MW loss value is not known, enter a default 1000 MW.
Step 5. | Hit the big blue button to copy your data for pasting into FRS Form 1 "BA Event Data" worksheet.
Step 6. | Paste data into "FRS Form 1" in the appropriate row on the "BA Event Data" worksheet.
Step 7. | Save this workbook using the following file name format:MyBA_yymmdd_hhmm_FRS_Form2.xlsm
| 2009-10-12 02:27 | Date yymmdd
| 40098.1023 | Time hh:ss of T(0)
Where "MyBA" = your BA mnemonic
Note on C8: Cell "C8": Observe the first change in frequency that identifies the beginning of the event. Look in column "B" of the "Data" worksheet. Select and edit the formula in this cell ("=Data!Axxx") to reference that row number in the "Data" sheet of this first change in frequency where xxx is that row number.
Note on C11: Cell "C11": Similar to identifying the end of a DCS event but only looking at frequency, observe frequency following the beginning of the event. When actual frequency recovers to 60.00 Hz or to the pre-event frequency, edit the formula in this cell to reference that row number in the "Data" worksheet that this occurs. ("=Data!Axxx")
Copy Form 2 Data for Pasting into Form 1

## IPFR (hidden)
IPFR = Interconnection Primary Frequency Response

## Evaluation
scan rate | 2 | seconds |  |  | Date: | 2009-10-12 02:27 |  |  | Balancing Authority | My BA | [10 empty] | A Point | 40098.1023 |  |  |  |  | A Point | 40098.1023 | [13 empty] | Non-Conforming Load sign convention | + | (Data is positive for Load then enter "+" else "-" | [11 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27
[5 empty] | Time of T(0) | 40098.1023 |  |  | Grid Nominal Frequency | 60 | Hz | [9 empty] | FPointA | 60.039 | 40098.1023 |  |  |  | FPointA | 60.039 | 40098.1023 | [26 empty] | Time of T(0) | 40098.1023 | [12 empty] | Time of T(0) | 40098.1023 | [12 empty] | Time of T(0) | 40098.1023 | [12 empty] | Time of T(0) | 40098.1023 | [12 empty] | Time of T(0) | 40098.1023
[5 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1063 |  |  | Capacity @ Droop for Minimum Performance | 2400 | MW | [9 empty] | A Value | 60.0417 |  |  |  |  | A Value | 60.0417 | [27 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1063 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1063 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1063 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1063 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1063
[5 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0417 | Hz |  | Droop Setting | 5% | 3 | Hz | [8 empty] | C Value | 59.836 | #N/A |  |  |  | C Value | 59.836 | #N/A | [26 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0417 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0417 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0417 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0417 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0417 | Hz
[5 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+52)] | 59.8887 | Hz |  | Deadband Setting | 0 | Hz | [9 empty] | Delta FCA | -0.20575 |  |  |  |  | Delta FC | [28 empty] | Value B Post-Perturbation Average Frequency [T(+12 to T(+24)] | 59.8823 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+18 to T(+30)] | 59.8844 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+40)] | 59.8892 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+18 to T(+52)] | 59.8879 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+52)] | 59.8887 | Hz
[5 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15304 | Hz |  | Hz Span | 3 | Hz | [9 empty] | FR C | -307.6528 | MW/0.1 Hz | [32 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15946 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15732 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15257 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15381 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15304 | Hz
[5 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3647.0459 | MW |  | Frequency Response Obligation (FRO) | -80 | MW/0.1 Hz | [9 empty] | Slope A-C dF/dT | #N/A | Hz/second |  |  |  |  | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | [18 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3647.0459 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3647.0459 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3647.0459 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3647.0459 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3647.0459 | MW
[5 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+52)] | 3787.775 | MW | [13 empty] | C Value Maximum Resource Loss | 633 | [5 empty] | 12 to 24 sec | 12 to 24 sec | 18 to 30 sec | 18 to 30 sec | 20 to 40 sec | 20 to 40 sec | 18 to 52 sec | 18 to 52 sec | 20 to 52 sec | 20 to 52 sec | [18 empty] | Value B Post-Perturbation Average Interchange MW [T(+12 to T(+24)] | 3766.6891 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+18 to T(+30)] | 3778.5405 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+40)] | 3783.7721 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+18 to T(+52)] | 3786.576 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+52)] | 3787.775 | MW
[5 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 140.7291 | MW | [13 empty] | Secondary C Value | No | n/a | Time |  |  | B Frequency Value | 59.8823 |  | 59.8844 |  | 59.8887 |  | 59.8879 |  | 59.8887 | [19 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 119.6432 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 131.4946 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 136.7263 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 139.5302 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 140.7291 | MW
[5 empty] | Initial Performance Ramp Magnitude Adjustment | -12.5915 | MW | [19 empty] | Delta FB | -0.15946 | -397.4363 | -0.15732 | -402.6343 | -0.15304 | -415.1637 | -0.15381 | -411.9588 | -0.15304 | -413.8616 | [18 empty] | Net Total Adjustments | -53.7506 | MW | [11 empty] | Net Total Adjustments | -53.9069 | MW | [11 empty] | Net Total Adjustments | -54.5143 | MW | [11 empty] | Net Total Adjustments | -52.6641 | MW | [11 empty] | Net Total Adjustments | -52.5288 | MW
[5 empty] | EPFR Pre-Perturbation Average | -33.4 | MW | [19 empty] | Slope B dF/dT | -0.0079732 |  | -0.0078661 |  | -0.0076522 |  | -0.0076903 |  | -0.0076522 | [19 empty] | EPFR for FRO Pre-Perturbation Average | -33.4 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -33.4 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -33.4 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -33.4 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -33.4 | MW
[5 empty] | EPFR Post-Perturbation Average | 89.0352 | MW | [19 empty] | RatioB-C | 77.5032 |  | 76.4617 |  | 74.3829 |  | 74.753 |  | 74.3829 | [19 empty] | EPFR for FRO Post-Perturbation Average | 94.1711 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 92.4569 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 88.6541 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 89.6444 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 89.0352 | MW
[5 empty] | EPFR Delta | 122.4352 | MW |  | TC (frequency response filter constant) | 0.35 | Time Constant for delayed delivery of PFR during Sustained Measure | [15 empty] | Sustainability Index | -0.017185 |  | -0.019328 |  | -0.023605 |  | -0.022844 |  | -0.023605 | [19 empty] | EPFR for FRO Delta | 127.5711 | MW | [11 empty] | EPFR for FRO Delta | 125.8569 | MW | [11 empty] | EPFR for FRO Delta | 122.0541 | MW | [11 empty] | EPFR for FRO Delta | 123.0443 | MW | [11 empty] | EPFR for FRO Delta | 122.4352 | MW
[21 empty] | Tzero | 40098.1023 | [33 empty] | EPFR for FRO Adjusted | 73.8205 | MW | [11 empty] | EPFR for FRO Adjusted | 71.95 | MW | [11 empty] | EPFR for FRO Adjusted | 67.5397 | MW | [11 empty] | EPFR for FRO Adjusted | 70.3803 | MW | [11 empty] | EPFR for FRO Adjusted | 69.9064 | MW
[21 empty] | FT+4 | 59.836 | [33 empty] | Pre JOU Dynamic Schedules MW | 350 |  |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 350 |  |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 350 | MW |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 350 | MW |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 350 | MW |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz
[9 empty] | Low Hz | Delta Hz Event | [10 empty] | FT+10 | 59.891 | [33 empty] | Pre Non-Conforming Load MW | -165.4296 |  |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | -165.4296 |  |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | -165.4296 | MW |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | -165.4296 | MW |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | -165.4296 | MW |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz
[9 empty] | 3764.1974 | Actual Interchange MW Average during frequency recovery period | [10 empty] | FT+20 | 59.883 | [33 empty] | Pre Pumped Hydro MW | 0 |  |  |  | EPFR for Bias Setting Pre-Perturbation Average | -43.0025 | MW | [6 empty] | Pre Pumped Hydro MW | 0 |  |  |  | EPFR for Bias Setting Pre-Perturbation Average | -43.0025 | MW | [6 empty] | Pre Pumped Hydro MW | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | -43.0025 | MW | [6 empty] | Pre Pumped Hydro MW | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | -43.0025 | MW | [6 empty] | Pre Pumped Hydro MW | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | -43.0025 | MW
[9 empty] | 3776.1733 | Target Interchange MW Average during frequency recovery period | [10 empty] | FT+60 | 59.89 | [33 empty] | Pre Ramping Units MW | 151.8125 |  |  |  | EPFR for Bias Setting Post-Perturbation Average | 121.2453 | MW | [6 empty] | Pre Ramping Units MW | 151.8125 |  |  |  | EPFR for Bias Setting Post-Perturbation Average | 119.0383 | MW | [6 empty] | Pre Ramping Units MW | 151.8125 | MW |  |  | EPFR for Bias Setting Post-Perturbation Average | 114.1422 | MW | [6 empty] | Pre Ramping Units MW | 151.8125 | MW |  |  | EPFR for Bias Setting Post-Perturbation Average | 115.4171 | MW | [6 empty] | Pre Ramping Units MW | 151.8125 | MW |  |  | EPFR for Bias Setting Post-Perturbation Average | 114.6328 | MW
|  |  | EPFR = Expected Primary Frequency Response |  | EPFR(Final) | 109.8437 | MW |  | 3728.9001 | Interchange Average Ramp MW during frequency recovery period | [8 empty] | Interconnection Evaluation | [36 empty] | Pre Transferred Frequency Response MW | -4.175 |  |  |  | EPFR for Bias Setting Delta | 164.2478 | MW | [6 empty] | Pre Transferred Frequency Response MW | -4.175 |  |  |  | EPFR for Bias Setting Delta | 162.0407 | MW | [6 empty] | Pre Transferred Frequency Response MW | -4.175 | MW |  |  | EPFR for Bias Setting Delta | 157.1446 | MW | [6 empty] | Pre Transferred Frequency Response MW | -4.175 | MW |  |  | EPFR for Bias Setting Delta | 158.4196 | MW | [6 empty] | Pre Transferred Frequency Response MW | -4.175 | MW |  |  | EPFR for Bias Setting Delta | 157.6353 | MW
[5 empty] | MW Response in right direction for frequency delta | Yes |  |  | 3645.4458 | Actual MW @ T(-4) | [45 empty] | Pre Contingent BA Lost Generation MW | 15 |  |  |  | Primary Frequency Response Delivery of Bias | 72.84% | [7 empty] | Pre Contingent BA Lost Generation MW | 15 |  |  |  | Primary Frequency Response Delivery of Bias | 81.15% | [7 empty] | Pre Contingent BA Lost Generation MW | 15 | MW |  |  | Primary Frequency Response Delivery of Bias | 87.01% | [7 empty] | Pre Contingent BA Lost Generation MW | 15 | MW |  |  | Primary Frequency Response Delivery of Bias | 88.08% | [7 empty] | Pre Contingent BA Lost Generation MW | 15 | MW |  |  | Primary Frequency Response Delivery of Bias | 89.28%
[9 empty] | 101.4817 | Starting and Ending Difference in Interchange MW during frequency recovery period (indicates ramp direction during recovery period) | [45 empty] | Sum of Pre Perturbation Adjustments | 347.2079 | [12 empty] | Sum of Pre Perturbation Adjustments | 347.2079 | [12 empty] | Sum of Pre Perturbation Adjustments | 347.2079 | MW | [11 empty] | Sum of Pre Perturbation Adjustments | 347.2079 | MW | [11 empty] | Sum of Pre Perturbation Adjustments | 347.2079 | MW
[9 empty] | 0:06 | Event Duration (h:mm:ss)
[9 empty] | No | Target MW Average minus MW @ T(-4) less than zero | [10 empty] | B Value Average Resource Loss | 633 | [33 empty] | Post JOU Dynamic Schedules MW | 335 |  |  |  | Pre-Perturbation BA Load | 7600.1963 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 335 |  |  |  | Pre-Perturbation BA Load | 7600.1963 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 335 | MW |  |  | Pre-Perturbation BA Load | 7600.1963 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 335 | MW |  |  | Pre-Perturbation BA Load | 7600.1963 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 335 | MW |  |  | Pre-Perturbation BA Load | 7600.1963 | MW
[9 empty] | 130.7275 | Interchange Target Relative Average Change - MW (Low Frequency Event) | [10 empty] | B Value Average LaaR Loss | 0 | [33 empty] | Post Non-Conforming Load MW | -209.8855 |  |  |  | Post-Perturbation BA Load | 7570 | MW | [6 empty] | Post Non-Conforming Load MW | -211.256 |  |  |  | Post-Perturbation BA Load | 7570 | MW | [6 empty] | Post Non-Conforming Load MW | -212.6609 | MW |  |  | Post-Perturbation BA Load | 7570 | MW | [6 empty] | Post Non-Conforming Load MW | -212.6617 | MW |  |  | Post-Perturbation BA Load | 7570 | MW | [6 empty] | Post Non-Conforming Load MW | -212.7443 | MW |  |  | Post-Perturbation BA Load | 7570 | MW
[9 empty] | 118.7516 | Interchange Actual Relative Average Change - MW (Low Frequency Event) | [10 empty] | B Value Average Net Loss | 633 | [33 empty] | Post Pumped Hydro MW | 0.42857 |  |  |  | Pre to Post Perturbation BA Load Change | -30.1963 | MW | [6 empty] | Post Pumped Hydro MW | 0.85714 |  |  |  | Pre to Post Perturbation BA Load Change | -30.1963 | MW | [6 empty] | Post Pumped Hydro MW | 1.0909 | MW |  |  | Pre to Post Perturbation BA Load Change | -30.1963 | MW | [6 empty] | Post Pumped Hydro MW | 2 | MW |  |  | Pre to Post Perturbation BA Load Change | -30.1963 | MW | [6 empty] | Post Pumped Hydro MW | 2.1176 | MW |  |  | Pre to Post Perturbation BA Load Change | -30.1963 | MW
[9 empty] | No | Interchange Actual Average minus MW @ T(-4) less than zero | [45 empty] | Post Ramping Units MW | 156.1429 |  |  |  | Load Dampening Frequency Response | -18.9361 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 157.1429 |  |  |  | Load Dampening Frequency Response | -19.194 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 158.1818 | MW |  |  | Load Dampening Frequency Response | -19.792 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 159 | MW |  |  | Load Dampening Frequency Response | -19.6328 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 159.1765 | MW |  |  | Load Dampening Frequency Response | -19.7304 | MW/0.1 Hz
[9 empty] | Yes | Interchange Average MW minus MW @ T(-4) greater than zero | [13 empty] | Interconnection Bias Total | [31 empty] | Post Transferred Frequency Response MW | 11.7714 |  |  |  | Load Dampening % of Total BA Frequency Response | 25.24% | [7 empty] | Post Transferred Frequency Response MW | 11.5571 |  |  |  | Load Dampening % of Total BA Frequency Response | 22.96% | [7 empty] | Post Transferred Frequency Response MW | 11.0818 | MW |  |  | Load Dampening % of Total BA Frequency Response | 22.09% | [7 empty] | Post Transferred Frequency Response MW | 11.2055 | MW |  |  | Load Dampening % of Total BA Frequency Response | 21.64% | [7 empty] | Post Transferred Frequency Response MW | 11.1294 | MW |  |  | Load Dampening % of Total BA Frequency Response | 21.46%
[9 empty] | Yes | Interchange Target MW Average minus MW @ T(-4) greater than zero | [13 empty] | EI | ERCOT | WECC | [29 empty] | Post Contingent BA Lost Generation MW | 0 | [12 empty] | Post Contingent BA Lost Generation MW | 0 | [12 empty] | Post Contingent BA Lost Generation MW | 0 | MW | [11 empty] | Post Contingent BA Lost Generation MW | 0 | MW | [11 empty] | Post Contingent BA Lost Generation MW | 0 | MW
[9 empty] | 29.2458 | Interchange Target Relative Average Change - MW (High Frequency Event) | [10 empty] | Interconnection Bias Setting | -660 |  | -6349 | -660 | -2024 | [29 empty] | Sum of Post Perturbation Adjustments | 293.4573 | [12 empty] | Sum of Post Perturbation Adjustments | 293.3011 | [12 empty] | Sum of Post Perturbation Adjustments | 292.6936 | MW | [11 empty] | Sum of Post Perturbation Adjustments | 294.5439 | MW | [11 empty] | Sum of Post Perturbation Adjustments | 294.6792 | MW
[9 empty] | 17.2699 | Interchange Actual Relative Average Change - MW (High Frequency Event) | [10 empty] | IPFR as a % of Bias Setting | 0% | [33 empty] | Net Total Adjustments MW | -53.7506 | [12 empty] | Net Total Adjustments MW | -53.9069 | [12 empty] | Net Total Adjustments MW | -54.5143 | MW | [11 empty] | Net Total Adjustments MW | -52.6641 | MW | [11 empty] | Net Total Adjustments MW | -52.5288 | MW
[9 empty] | Up | Ramp Direction during frequency recovery period | [10 empty] | Interconnection Total Energy | 37446 | 60.07%
[21 empty] | Interconnection Peak Energy | 62339 |  |  |  |  | Frequency and Interconnection Frequency Response @ different Average periods of B | [11 empty] | Frequency, Actual Interchange, Adjustment Data, Bias and Load used in the evaluation | [12 empty] | 12 to 24 second Average Period Evaluation | [13 empty] | 18 to 30 second Average Period Evaluation | [13 empty] | 20 to 40 second Average Period Evaluation | [13 empty] | 18 to 52 second Average Period Evaluation | [13 empty] | 20 to 52 second Average Period Evaluation
[5 empty] | Initial Response P.U. Performance | 1.2812 | P.U. |  | 0.90839 | P.U. Sustianed Response P.U. Performance | [45 empty] | Initial P.U. Performance for FRO | 0.93786 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.0448 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.1202 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.134 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.1494 | P.U.
[56 empty] | Initial P.U. Performance Adjusted for FRO | 1.3592 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 1.4731 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 1.5669 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 1.562 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 1.5785 | P.U.
[9 empty] | Initial | [6 empty] | Generator | Generator | Generator | Generator | Generator | Generator | Generator | LaaR | Total | Interconnection | FR B | [15 empty] | JOU | Non- |  |  | Transferred | Contingent | [7 empty] | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected
[7 empty] | FRO |  | Measure |  |  | Average | Average |  | Average | Trip | Trip | Trip | Trip | Trip | Trip | Trip | Trip | Generation | Primary | 20 to 52 sec |  | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Expected |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net
[7 empty] | (EPFR) | (TC) | Final |  |  | Output | Target |  | Ramp | MW | MW | MW | MW | MW | MW | MW | MW | Trip | Frequency | Average |  | 12 to 24 sec | 12 to 24 sec | 18 to 30 sec | 18 to 30 sec | 20 to 40 sec | 20 to 40 sec | 18 to 52 sec | 18 to 52 sec | 20 to 52 sec | 20 to 52 sec |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Primary |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual
|  |  |  | Value B |  |  | Expected | Delayed | Expected |  | Recovery | During | During | Recovery | During | [8 empty] | MW | Response | MW |  | Average | Average | Average | Average | Average | Average | Average | Average | Average | Average |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | Freq Response |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange
|  |  |  | 20 to 52 sec |  |  | Primary | Delivery | Primary | Average | Period | Recovery | Recovery | Period | Recovery | [12 empty] | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW
|  | Frequency | Interchange | Average | Average |  | Frequency | Frequency | Frequency | Ramp | Target | Period | Period | Ramp | Period
| T | Hz | MW | Frequency | MW |  | Response | Response | Response | MW/scan | MW | MW | MW | MW | MW | 633 | [8 empty] | MW/0.1 Hz
0
T-72 sec | 40098.1015 | 60.027 | 3671.189 |  |  |  | -21.6003 | -7.5601 | [15 empty] | 0 |  |  | T-72 sec | [10 empty] | T-72 sec | 40098.1015 | 60.027 | 3671.189 | 350 | -253.6319 | 0 | 141.5 | 10 | 15 | -103 | 7593.39 | -21.6003 | T-72 sec | 40098.1015 | [12 empty] | T-72 sec | 40098.1015 | [12 empty] | T-72 sec | 40098.1015 | [12 empty] | T-72 sec | 40098.1015 | [12 empty] | T-72 sec | 40098.1015
T-70 sec | 40098.1015 | 60.027 | 3671.189 |  |  |  | -21.6003 | -12.4742 | [15 empty] | 0 |  |  | T-70 sec | [10 empty] | T-70 sec | 40098.1015 | 60.027 | 3671.189 | 350 | -253.6319 | 0 | 141.5 | 10 | 15 | -103 | 7593.39 | -21.6003 | T-70 sec | 40098.1015 | [12 empty] | T-70 sec | 40098.1015 | [12 empty] | T-70 sec | 40098.1015 | [12 empty] | T-70 sec | 40098.1015 | [12 empty] | T-70 sec | 40098.1015
T-68 sec | 40098.1015 | 60.026 | 3668.6106 |  |  |  | -20.8008 | -15.3885 | [15 empty] | 0 |  |  | T-68 sec | [10 empty] | T-68 sec | 40098.1015 | 60.026 | 3668.6106 | 350 | -253.6319 | 0 | 142 | 10 | 15 | -103 | 7593.72 | -20.8008 | T-68 sec | 40098.1015 | [12 empty] | T-68 sec | 40098.1015 | [12 empty] | T-68 sec | 40098.1015 | [12 empty] | T-68 sec | 40098.1015 | [12 empty] | T-68 sec | 40098.1015
T-66 sec | 40098.1016 | 60.022 | 3664.4951 |  |  |  | -17.5995 | -16.1623 | [15 empty] | 0 |  |  | T-66 sec | [10 empty] | T-66 sec | 40098.1016 | 60.022 | 3664.4951 | 350 | -253.6319 | 0 | 142.5 | 10 | 15 | -103 | 7594.05 | -17.5995 | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016
T-64 sec | 40098.1016 | 60.022 | 3664.4951 |  |  |  | -17.5995 | -16.6653 | [15 empty] | 0 |  |  | T-64 sec | [10 empty] | T-64 sec | 40098.1016 | 60.022 | 3664.4951 | 350 | -253.6319 | 0 | 142.5 | 10 | 15 | -103 | 7594.05 | -17.5995 | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016
T-62 sec | 40098.1016 | 60.017 | 3666.0618 |  |  |  | -13.5986 | -15.592 | [15 empty] | 0 |  |  | T-62 sec | [10 empty] | T-62 sec | 40098.1016 | 60.017 | 3666.0618 | 350 | -253.6319 | 0 | 143 | 10 | 15 | -103 | 7594.38 | -13.5986 | T-62 sec | 40098.1016 | [12 empty] | T-62 sec | 40098.1016 | [12 empty] | T-62 sec | 40098.1016 | [12 empty] | T-62 sec | 40098.1016 | [12 empty] | T-62 sec | 40098.1016
T-60 sec | 40098.1016 | 60.019 | 3666.7874 |  |  |  | -15.2008 | -15.4551 |  | -0.30972 | 3666.7874 | [12 empty] | 0 |  |  | T-60 sec | [10 empty] | T-60 sec | 40098.1016 | 60.019 | 3666.7874 | 350 | -253.6319 | 0 | 143.5 | 10 | 15 | -103 | 7594.71 | -15.2008 | T-60 sec | 40098.1016 | [12 empty] | T-60 sec | 40098.1016 | [12 empty] | T-60 sec | 40098.1016 | [12 empty] | T-60 sec | 40098.1016 | [12 empty] | T-60 sec | 40098.1016
T-58 sec | 40098.1017 | 60.019 | 3666.7874 |  |  |  | -15.2008 | -15.3661 |  | -0.30972 | 3666.5666 | [12 empty] | 0 |  |  | T-58 sec | [10 empty] | T-58 sec | 40098.1017 | 60.019 | 3666.7874 | 350 | -253.6319 | 0 | 143.5 | 10 | 15 | -103 | 7594.71 | -15.2008 | T-58 sec | 40098.1017 | [12 empty] | T-58 sec | 40098.1017 | [12 empty] | T-58 sec | 40098.1017 | [12 empty] | T-58 sec | 40098.1017 | [12 empty] | T-58 sec | 40098.1017
T-56 sec | 40098.1017 | 60.019 | 3670.4536 |  |  |  | -15.2008 | -15.3082 |  | -0.30972 | 3666.3148 | [12 empty] | 0 |  |  | T-56 sec | [10 empty] | T-56 sec | 40098.1017 | 60.019 | 3670.4536 | 350 | -246.9573 | 0 | 144 | 10 | 15 | -103 | 7595.04 | -15.2008 | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017
T-54 sec | 40098.1017 | 60.021 | 3671.668 |  |  |  | -16.7999 | -15.8303 |  | -0.30972 | 3665.483 | [12 empty] | 0 |  |  | T-54 sec | [10 empty] | T-54 sec | 40098.1017 | 60.021 | 3671.668 | 350 | -246.9573 | 0 | 144.5 | 10 | 15 | -103 | 7595.37 | -16.7999 | T-54 sec | 40098.1017 | [12 empty] | T-54 sec | 40098.1017 | [12 empty] | T-54 sec | 40098.1017 | [12 empty] | T-54 sec | 40098.1017 | [12 empty] | T-54 sec | 40098.1017
T-52 sec | 40098.1017 | 60.021 | 3671.668 |  |  |  | -16.7999 | -16.1697 |  | -0.30972 | 3664.8339 | [12 empty] | 0 |  |  | T-52 sec | [10 empty] | T-52 sec | 40098.1017 | 60.021 | 3671.668 | 350 | -246.9573 | 0 | 144.5 | 10 | 15 | -103 | 7595.37 | -16.7999 | T-52 sec | 40098.1017 | [12 empty] | T-52 sec | 40098.1017 | [12 empty] | T-52 sec | 40098.1017 | [12 empty] | T-52 sec | 40098.1017 | [12 empty] | T-52 sec | 40098.1017
T-50 sec | 40098.1017 | 60.021 | 3672.4932 |  |  |  | -16.7999 | -16.3903 |  | -0.30972 | 3664.3036 | [12 empty] | 0 |  |  | T-50 sec | [10 empty] | T-50 sec | 40098.1017 | 60.021 | 3672.4932 | 350 | -246.9573 | 0 | 145 | 10 | 15 | -103 | 7595.7 | -16.7999 | T-50 sec | 40098.1017 | [12 empty] | T-50 sec | 40098.1017 | [12 empty] | T-50 sec | 40098.1017 | [12 empty] | T-50 sec | 40098.1017 | [12 empty] | T-50 sec | 40098.1017
T-48 sec | 40098.1018 | 60.019 | 3672.8574 |  |  |  | -15.2008 | -15.974 |  | -0.30972 | 3664.4102 | [12 empty] | 0 |  |  | T-48 sec | [10 empty] | T-48 sec | 40098.1018 | 60.019 | 3672.8574 | 350 | -246.9573 | 0 | 145.5 | 10 | 15 | -103 | 7596.03 | -15.2008 | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018
T-46 sec | 40098.1018 | 60.019 | 3672.8574 |  |  |  | -15.2008 | -15.7034 |  | -0.30972 | 3664.3711 | [12 empty] | 0 |  |  | T-46 sec | [10 empty] | T-46 sec | 40098.1018 | 60.019 | 3672.8574 | 350 | -246.9573 | 0 | 145.5 | 10 | 15 | -103 | 7596.03 | -15.2008 | T-46 sec | 40098.1018 | [12 empty] | T-46 sec | 40098.1018 | [12 empty] | T-46 sec | 40098.1018 | [12 empty] | T-46 sec | 40098.1018 | [12 empty] | T-46 sec | 40098.1018
T-44 sec | 40098.1018 | 60.022 | 3672.1641 |  |  |  | -17.5995 | -16.367 |  | -0.30972 | 3663.3977 | [12 empty] | 0 |  |  | T-44 sec | [10 empty] | T-44 sec | 40098.1018 | 60.022 | 3672.1641 | 350 | -246.9573 | 0 | 146 | 10 | 15 | -103 | 7596.36 | -17.5995 | T-44 sec | 40098.1018 | [12 empty] | T-44 sec | 40098.1018 | [12 empty] | T-44 sec | 40098.1018 | [12 empty] | T-44 sec | 40098.1018 | [12 empty] | T-44 sec | 40098.1018
T-42 sec | 40098.1018 | 60.031 | 3669.9829 |  |  |  | -24.7986 | -19.3181 |  | -0.30972 | 3660.1369 | [12 empty] | 0 |  |  | T-42 sec | [10 empty] | T-42 sec | 40098.1018 | 60.031 | 3669.9829 | 350 | -254.5418 | 0 | 146.5 | 10 | 15 | -103 | 7596.69 | -24.7986 | T-42 sec | 40098.1018 | [12 empty] | T-42 sec | 40098.1018 | [12 empty] | T-42 sec | 40098.1018 | [12 empty] | T-42 sec | 40098.1018 | [12 empty] | T-42 sec | 40098.1018
T-40 sec | 40098.1019 | 60.031 | 3669.9829 |  |  |  | -24.7986 | -21.2362 |  | -0.30972 | 3657.909 | [12 empty] | 0 |  |  | T-40 sec | [10 empty] | T-40 sec | 40098.1019 | 60.031 | 3669.9829 | 350 | -254.5418 | 0 | 146.5 | 10 | 15 | -103 | 7596.69 | -24.7986 | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019
T-38 sec | 40098.1019 | 60.037 | 3666.4673 |  |  |  | -29.599 | -24.1632 |  | -0.30972 | 3654.6723 | [12 empty] | 0 |  |  | T-38 sec | [10 empty] | T-38 sec | 40098.1019 | 60.037 | 3666.4673 | 350 | -254.5418 | 0 | 147 | 10 | 15 | -103 | 7597.02 | -29.599 | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019
T-36 sec | 40098.1019 | 60.036 | 3661.5991 |  |  |  | -28.7994 | -25.7859 |  | -0.30972 | 3652.7399 | [12 empty] | 0 |  |  | T-36 sec | [10 empty] | T-36 sec | 40098.1019 | 60.036 | 3661.5991 | 350 | -254.5418 | 0 | 147.5 | 10 | 15 | -103 | 7597.35 | -28.7994 | T-36 sec | 40098.1019 | [12 empty] | T-36 sec | 40098.1019 | [12 empty] | T-36 sec | 40098.1019 | [12 empty] | T-36 sec | 40098.1019 | [12 empty] | T-36 sec | 40098.1019
T-34 sec | 40098.1019 | 60.036 | 3661.5991 |  |  |  | -28.7994 | -26.8406 |  | -0.30972 | 3651.3755 | [12 empty] | 0 |  |  | T-34 sec | [10 empty] | T-34 sec | 40098.1019 | 60.036 | 3661.5991 | 350 | -254.5418 | 0 | 147.5 | 10 | 15 | -103 | 7597.35 | -28.7994 | T-34 sec | 40098.1019 | [12 empty] | T-34 sec | 40098.1019 | [12 empty] | T-34 sec | 40098.1019 | [12 empty] | T-34 sec | 40098.1019 | [12 empty] | T-34 sec | 40098.1019
T-32 sec | 40098.102 | 60.046 | 3660.6724 |  |  |  | -36.8011 | -30.3268 |  | -0.30972 | 3647.5796 | [12 empty] | 0 |  |  | T-32 sec | [10 empty] | T-32 sec | 40098.102 | 60.046 | 3660.6724 | 350 | -254.5418 | 0 | 148 | 10 | 15 | -103 | 7597.68 | -36.8011 | T-32 sec | 40098.102 | [12 empty] | T-32 sec | 40098.102 | [12 empty] | T-32 sec | 40098.102 | [12 empty] | T-32 sec | 40098.102 | [12 empty] | T-32 sec | 40098.102
T-30 sec | 40098.102 | 60.048 | 3649.1904 |  |  |  | -38.4003 | -33.1525 |  | -0.30972 | 3644.4442 | [12 empty] | 0 |  |  | T-30 sec | [10 empty] | T-30 sec | 40098.102 | 60.048 | 3649.1904 | 350 | -165.1017 | 0 | 148.5 | 10 | 15 | -103 | 7598.01 | -38.4003 | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102
T-28 sec | 40098.102 | 60.048 | 3649.1904 |  |  |  | -38.4003 | -34.9892 |  | -0.30972 | 3642.2977 | [12 empty] | 0 |  |  | T-28 sec | [10 empty] | T-28 sec | 40098.102 | 60.048 | 3649.1904 | 350 | -165.1017 | 0 | 148.5 | 10 | 15 | -103 | 7598.01 | -38.4003 | T-28 sec | 40098.102 | [12 empty] | T-28 sec | 40098.102 | [12 empty] | T-28 sec | 40098.102 | [12 empty] | T-28 sec | 40098.102 | [12 empty] | T-28 sec | 40098.102
T-26 sec | 40098.102 | 60.043 | 3650.0251 |  |  |  | -34.3994 | -34.7828 |  | -0.30972 | 3642.1945 | [12 empty] | 0 |  |  | T-26 sec | [10 empty] | T-26 sec | 40098.102 | 60.043 | 3650.0251 | 350 | -165.1017 | 0 | 149 | 10 | 15 | -103 | 7598.34 | -34.3994 | T-26 sec | 40098.102 | [12 empty] | T-26 sec | 40098.102 | [12 empty] | T-26 sec | 40098.102 | [12 empty] | T-26 sec | 40098.102 | [12 empty] | T-26 sec | 40098.102
T-24 sec | 40098.102 | 60.041 | 3649.512 |  |  |  | -32.8003 | -34.0889 |  | -0.30972 | 3642.5786 | [12 empty] | 0 |  |  | T-24 sec | [10 empty] | T-24 sec | 40098.102 | 60.041 | 3649.512 | 350 | -165.1017 | 0 | 149.5 | 10 | 15 | -103 | 7598.67 | -32.8003 | T-24 sec | 40098.102 | [12 empty] | T-24 sec | 40098.102 | [12 empty] | T-24 sec | 40098.102 | [12 empty] | T-24 sec | 40098.102 | [12 empty] | T-24 sec | 40098.102
T-22 sec | 40098.1021 | 60.041 | 3649.512 |  |  |  | -32.8003 | -33.6379 |  | -0.30972 | 3642.7199 | [12 empty] | 0 |  |  | T-22 sec | [10 empty] | T-22 sec | 40098.1021 | 60.041 | 3649.512 | 350 | -165.1017 | 0 | 149.5 | 10 | 15 | -103 | 7598.67 | -32.8003 | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021
T-20 sec | 40098.1021 | 60.041 | 3654.2944 |  |  |  | -32.8003 | -33.3447 |  | -0.30972 | 3642.7034 | [12 empty] | 0 |  |  | T-20 sec | [10 empty] | T-20 sec | 40098.1021 | 60.041 | 3654.2944 | 350 | -165.1017 | 0 | 150 | 10 | 15 | -103 | 7599 | -32.8003 | T-20 sec | 40098.1021 | [12 empty] | T-20 sec | 40098.1021 | [12 empty] | T-20 sec | 40098.1021 | [12 empty] | T-20 sec | 40098.1021 | [12 empty] | T-20 sec | 40098.1021
T-18 sec | 40098.1021 | 60.039 | 3651.8743 |  |  |  | -31.2012 | -32.5945 |  | -0.30972 | 3643.1439 | [12 empty] | 0 |  |  | T-18 sec | [10 empty] | T-18 sec | 40098.1021 | 60.039 | 3651.8743 | 350 | -165.1017 | 0 | 150.5 | 10 | 15 | -103 | 7599.33 | -31.2012 | T-18 sec | 40098.1021 | [12 empty] | T-18 sec | 40098.1021 | [12 empty] | T-18 sec | 40098.1021 | [12 empty] | T-18 sec | 40098.1021 | [12 empty] | T-18 sec | 40098.1021
T-16 sec | 40098.1021 | 60.039 | 3651.8743 | 60.0417 | 3647.0459 |  | -31.2012 | -32.1068 |  | -0.30972 | 3643.3218 | [12 empty] | 0 |  |  | T-16 sec | 60.0417 | [9 empty] | T-16 sec | 40098.1021 | 60.039 | 3651.8743 | 350 | -165.1017 | 0 | 150.5 | 10 | 15 | -103 | 7599.33 | -31.2012 | T-16 sec | 40098.1021 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-16 sec | 40098.1021 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-16 sec | 40098.1021 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-16 sec | 40098.1021 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-16 sec | 40098.1021 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4
T-14 sec | 40098.1022 | 60.043 | 3651.0593 | 60.0417 | 3647.0459 |  | -34.3994 | -32.9092 |  | -0.30972 | 3642.2097 | [12 empty] | 0 |  |  | T-14 sec | 60.0417 | [9 empty] | T-14 sec | 40098.1022 | 60.043 | 3651.0593 | 350 | -165.4764 | 0 | 151 | 10 | 15 | -103 | 7599.66 | -34.3994 | T-14 sec | 40098.1022 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-14 sec | 40098.1022 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-14 sec | 40098.1022 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-14 sec | 40098.1022 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-14 sec | 40098.1022 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4
T-12 sec | 40098.1022 | 60.045 | 3648.2363 | 60.0417 | 3647.0459 |  | -35.9985 | -33.9905 |  | -0.30972 | 3640.8187 | [12 empty] | 0 |  |  | T-12 sec | 60.0417 | [9 empty] | T-12 sec | 40098.1022 | 60.045 | 3648.2363 | 350 | -165.4764 | 0 | 151.5 | 10 | 15 | -103 | 7599.99 | -35.9985 | T-12 sec | 40098.1022 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-12 sec | 40098.1022 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-12 sec | 40098.1022 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-12 sec | 40098.1022 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-12 sec | 40098.1022 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4
T-10 sec | 40098.1022 | 60.045 | 3648.2363 | 60.0417 | 3647.0459 |  | -35.9985 | -34.6933 |  | -0.30972 | 3639.8062 | [12 empty] | 0 |  |  | T-10 sec | 60.0417 | [9 empty] | T-10 sec | 40098.1022 | 60.045 | 3648.2363 | 350 | -165.4764 | 0 | 151.5 | 10 | 15 | -103 | 7599.99 | -35.9985 | T-10 sec | 40098.1022 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-10 sec | 40098.1022 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-10 sec | 40098.1022 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-10 sec | 40098.1022 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-10 sec | 40098.1022 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4
T-08 sec | 40098.1022 | 60.041 | 3645.387 | 60.0417 | 3647.0459 |  | -32.8003 | -34.0308 |  | -0.30972 | 3640.159 | [12 empty] | 0 |  |  | T-08 sec | 60.0417 | [9 empty] | T-08 sec | 40098.1022 | 60.041 | 3645.387 | 350 | -165.4764 | 0 | 152 | 10 | 15 | -103 | 7600.32 | -32.8003 | T-08 sec | 40098.1022 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-08 sec | 40098.1022 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-08 sec | 40098.1022 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-08 sec | 40098.1022 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-08 sec | 40098.1022 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4
T-06 sec | 40098.1023 | 60.041 | 3645.4458 | 60.0417 | 3647.0459 |  | -32.8003 | -33.6001 |  | -0.30972 | 3640.28 | [12 empty] | 0 |  |  | T-06 sec | 60.0417 | [9 empty] | T-06 sec | 40098.1023 | 60.041 | 3645.4458 | 350 | -165.4764 | 0 | 152.5 | 10 | 15 | -103 | 7600.65 | -32.8003 | T-06 sec | 40098.1023 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-06 sec | 40098.1023 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-06 sec | 40098.1023 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-06 sec | 40098.1023 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-06 sec | 40098.1023 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4
T-04 sec | 40098.1023 | 60.041 | 3645.4458 | 60.0417 | 3647.0459 |  | -32.8003 | -33.3202 |  | -0.30972 | 3640.2502 | [12 empty] | 0 |  |  | T-04 sec | 60.0417 | [9 empty] | T-04 sec | 40098.1023 | 60.041 | 3645.4458 | 350 | -165.4764 | 0 | 152.5 | 10 | 15 | -103 | 7600.65 | -32.8003 | T-04 sec | 40098.1023 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-04 sec | 40098.1023 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-04 sec | 40098.1023 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-04 sec | 40098.1023 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-04 sec | 40098.1023 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4
T-02 sec | 40098.1023 | 60.039 | 3640.6821 | 60.0417 | 3647.0459 |  | -31.2012 | -32.5785 |  | -0.30972 | 3640.6821 | [12 empty] | 0 |  |  | T-02 sec | 60.0417 | [9 empty] | T-02 sec | 40098.1023 | 60.039 | 3640.6821 | 350 | -165.4764 | 0 | 153 | 10 | 15 | -103 | 7600.98 | -31.2012 | T-02 sec | 40098.1023 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-02 sec | 40098.1023 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-02 sec | 40098.1023 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-02 sec | 40098.1023 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4 |  | T-02 sec | 40098.1023 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | 10 | 15 | -103 | 7600.1963 | -33.4
T+0 sec | 40098.1023 | 59.978 | 3659.4648 |  |  |  | 17.5995 | -15.0162 |  | 0 | 3658.2444 |  |  |  |  | 633 | [7 empty] | 633 | -992.9519 |  | T+0 sec | [10 empty] | T+0 sec | 40098.1023 | 59.978 | 3659.4648 | 350 | -206.4591 | 0 | 153.5 | 10 | 0 | -103 | 7601.31 | 17.5995 | T+0 sec | 40098.1023 | [12 empty] | T+0 sec | 40098.1023 | [12 empty] | T+0 sec | 40098.1023 | [12 empty] | T+0 sec | 40098.1023 | [12 empty] | T+0 sec | 40098.1023
T+02 sec | 40098.1023 | 59.978 | 3659.4648 |  |  |  | 17.5995 | -3.6007 |  | 0.59346 | 3670.2534 | 3659.4648 | 3664.2489 | 3678.4562 | 3678.4562 | 633 | [7 empty] | 633 | -992.9519 |  | T+02 sec | [10 empty] | T+02 sec | 40098.1023 | 59.978 | 3659.4648 | 350 | -206.4591 | 0 | 153.5 | 10 | 0 | -103 | 7601.31 | 17.5995 | T+02 sec | 40098.1023 | [12 empty] | T+02 sec | 40098.1023 | [12 empty] | T+02 sec | 40098.1023 | [12 empty] | T+02 sec | 40098.1023 | [12 empty] | T+02 sec | 40098.1023
T+04 sec | 40098.1024 | 59.836 | 3696.3623 |  |  |  | 131.2012 | 43.5799 |  | 0.59346 | 3718.0275 | 3671.764 | 3682.1751 | 3679.0497 | 3678.753 | 633 | [7 empty] | 633 | -307.6528 |  | T+04 sec | [10 empty] | T+04 sec | 40098.1024 | 59.836 | 3696.3623 | 350 | -206.4591 | 0 | 154 | 10 | 0 | -103 | 7570 | 131.2012 | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024
T+06 sec | 40098.1024 | 59.836 | 3696.3623 |  |  |  | 131.2012 | 74.2474 |  | 0.59346 | 3749.2884 | 3677.9136 | 3698.9534 | 3679.6432 | 3679.0497 | 633 | [6 empty] | 0 | 633 | -307.6528 |  | T+06 sec | [10 empty] | T+06 sec | 40098.1024 | 59.836 | 3696.3623 | 350 | -206.4591 | 0 | 154 | 10 | 0 | -103 | 7570 | 131.2012 | T+06 sec | 40098.1024 | [12 empty] | T+06 sec | 40098.1024 | [12 empty] | T+06 sec | 40098.1024 | [12 empty] | T+06 sec | 40098.1024 | [12 empty] | T+06 sec | 40098.1024
T+08 sec | 40098.1024 | 59.869 | 3734.6726 |  |  |  | 104.8004 | 84.9409 |  | 0.59346 | 3760.5754 | 3689.2654 | 3711.2778 | 3680.2366 | 3679.3464 | 633 | [6 empty] | 0 | 633 | -366.4245 |  | T+08 sec | [10 empty] | T+08 sec | 40098.1024 | 59.869 | 3734.6726 | 335 | -206.4591 | 0 | 154.5 | 10 | 0 | -103 | 7569 | 104.8004 | T+08 sec | 40098.1024 | [12 empty] | T+08 sec | 40098.1024 | [12 empty] | T+08 sec | 40098.1024 | [12 empty] | T+08 sec | 40098.1024 | [12 empty] | T+08 sec | 40098.1024
T+10 sec | 40098.1024 | 59.891 | 3737.1567 |  |  |  | 87.2009 | 85.7319 |  | 0.59346 | 3761.9599 | 3697.2473 | 3719.7248 | 3680.8301 | 3679.6432 | 633 | [6 empty] | 0 | 633 | -419.8974 |  | T+10 sec | [10 empty] | T+10 sec | 40098.1024 | 59.891 | 3737.1567 | 335 | -206.4591 | 0 | 155 | 10 | 0 | -103 | 7570 | 87.2009 | T+10 sec | 40098.1024 | [12 empty] | T+10 sec | 40098.1024 | [12 empty] | T+10 sec | 40098.1024 | [12 empty] | T+10 sec | 40098.1024 | [12 empty] | T+10 sec | 40098.1024
T+12 sec | 40098.1025 | 59.891 | 3737.1567 |  |  |  | 87.2009 | 86.2461 |  | 0.59346 | 3763.0675 | 3702.9486 | 3725.9166 | 3681.4235 | 3679.9399 | 633 | [6 empty] | 0 | 633 | -419.8974 |  | T+12 sec | 59.8823 | -397.4363 | [8 empty] | T+12 sec | 40098.1025 | 59.891 | 3737.1567 | 335 | -206.4591 | 0 | 155 | 10 | 0 | -103 | 7570 | 87.2009 | T+12 sec | 40098.1025 | 59.8823 | 3766.6891 | 335 | -209.8855 | 0.42857 | 156.1429 | 10 | 0 | -103 | 7570 | 94.1711 | 3720.8664 | T+12 sec | 40098.1025 | [12 empty] | T+12 sec | 40098.1025 | [12 empty] | T+12 sec | 40098.1025 | [12 empty] | T+12 sec | 40098.1025
T+14 sec | 40098.1025 | 59.88 | 3766.113 |  |  |  | 95.9991 | 89.6597 |  | 0.59346 | 3767.0745 | 3710.8442 | 3731.0614 | 3682.017 | 3680.2366 | 633 | [6 empty] | 0 | 633 | -391.3474 |  | T+14 sec | 59.8823 | -397.4363 | [8 empty] | T+14 sec | 40098.1025 | 59.88 | 3766.113 | 335 | -206.4591 | 0 | 155.5 | 10 | 0 | -103 | 7570 | 95.9991 | T+14 sec | 40098.1025 | 59.8823 | 3766.6891 | 335 | -209.8855 | 0.42857 | 156.1429 | 10 | 0 | -103 | 7570 | 94.1711 | 3720.8664 | T+14 sec | 40098.1025 | [12 empty] | T+14 sec | 40098.1025 | [12 empty] | T+14 sec | 40098.1025 | [12 empty] | T+14 sec | 40098.1025
T+16 sec | 40098.1025 | 59.875 | 3766.1938 |  |  |  | 100 | 93.2788 |  | 0.59346 | 3771.2871 | 3716.9941 | 3735.5309 | 3682.6104 | 3680.5333 | 633 | [6 empty] | 0 | 633 | -379.6103 |  | T+16 sec | 59.8823 | -397.4363 | [8 empty] | T+16 sec | 40098.1025 | 59.875 | 3766.1938 | 335 | -211.256 | 0 | 156 | 10 | 0 | -103 | 7570 | 100 | T+16 sec | 40098.1025 | 59.8823 | 3766.6891 | 335 | -209.8855 | 0.42857 | 156.1429 | 10 | 0 | -103 | 7570 | 94.1711 | 3720.8664 | T+16 sec | 40098.1025 | [12 empty] | T+16 sec | 40098.1025 | [12 empty] | T+16 sec | 40098.1025 | [12 empty] | T+16 sec | 40098.1025
T+18 sec | 40098.1025 | 59.875 | 3766.1938 |  |  |  | 100 | 95.6312 |  | 0.59346 | 3774.233 | 3721.9141 | 3739.4011 | 3683.2039 | 3680.8301 | 633 | [6 empty] | 0 | 633 | -379.6103 |  | T+18 sec | 59.8823 | -397.4363 | 59.8844 | -402.6343 |  |  | 59.8879 | -411.9588 |  |  | T+18 sec | 40098.1025 | 59.875 | 3766.1938 | 335 | -211.256 | 0 | 156 | 10 | 0 | -103 | 7570 | 100 | T+18 sec | 40098.1025 | 59.8823 | 3766.6891 | 335 | -209.8855 | 0.42857 | 156.1429 | 10 | 0 | -103 | 7570 | 94.1711 | 3720.8664 | T+18 sec | 40098.1025 | 59.8844 | 3778.5405 | 335 | -211.256 | 0.85714 | 157.1429 | 10 | 0 | -103 | 7570 | 92.4569 | 3718.9959 | T+18 sec | 40098.1025 | [12 empty] | T+18 sec | 40098.1025 | 59.8879 | 3786.576 | 335 | -212.6617 | 2 | 159 | 10 | 0 | -103 | 7570 | 89.6444 | 3717.4261 | T+18 sec | 40098.1025
T+20 sec | 40098.1026 | 59.883 | 3769.925 | 59.8887 | 3787.775 |  | 93.6005 | 94.9204 | 3756.8895 | 0.59346 | 3774.1157 | 3726.2787 | 3742.557 | 3683.7974 | 3681.1268 | 633 | [6 empty] | 0 | 633 | -398.7388 | -413.8616 | T+20 sec | 59.8823 | -397.4363 | 59.8844 | -402.6343 | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+20 sec | 40098.1026 | 59.883 | 3769.925 | 335 | -211.256 | 1 | 156.5 | 10 | 0 | -103 | 7570 | 93.6005 | T+20 sec | 40098.1026 | 59.8823 | 3766.6891 | 335 | -209.8855 | 0.42857 | 156.1429 | 10 | 0 | -103 | 7570 | 94.1711 | 3720.8664 | T+20 sec | 40098.1026 | 59.8844 | 3778.5405 | 335 | -211.256 | 0.85714 | 157.1429 | 10 | 0 | -103 | 7570 | 92.4569 | 3718.9959 | T+20 sec | 40098.1026 | 59.8892 | 3783.7721 | 335 | -212.6609 | 1.0909 | 158.1818 | 10 | 0 | -103 | 7570 | 88.6541 | 3714.5856 | T+20 sec | 40098.1026 | 59.8879 | 3786.576 | 335 | -212.6617 | 2 | 159 | 10 | 0 | -103 | 7570 | 89.6444 | 3717.4261 | T+20 sec | 40098.1026 | 59.8887 | 3787.775 | 335 | -212.7443 | 2.1176 | 159.1765 | 10 | 0 | -103 | 7570 | 89.0352 | 3716.9523
T+22 sec | 40098.1026 | 59.886 | 3780.6206 | 59.8887 | 3787.775 |  | 91.1987 | 93.6178 | 3756.8895 | 0.59346 | 3773.4065 | 3730.8072 | 3745.1278 | 3684.3908 | 3681.4235 | 633 | [6 empty] | 0 | 633 | -406.4248 | -413.8616 | T+22 sec | 59.8823 | -397.4363 | 59.8844 | -402.6343 | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+22 sec | 40098.1026 | 59.886 | 3780.6206 | 335 | -211.256 | 1 | 157 | 10 | 0 | -103 | 7570 | 91.1987 | T+22 sec | 40098.1026 | 59.8823 | 3766.6891 | 335 | -209.8855 | 0.42857 | 156.1429 | 10 | 0 | -103 | 7570 | 94.1711 | 3720.8664 | T+22 sec | 40098.1026 | 59.8844 | 3778.5405 | 335 | -211.256 | 0.85714 | 157.1429 | 10 | 0 | -103 | 7570 | 92.4569 | 3718.9959 | T+22 sec | 40098.1026 | 59.8892 | 3783.7721 | 335 | -212.6609 | 1.0909 | 158.1818 | 10 | 0 | -103 | 7570 | 88.6541 | 3714.5856 | T+22 sec | 40098.1026 | 59.8879 | 3786.576 | 335 | -212.6617 | 2 | 159 | 10 | 0 | -103 | 7570 | 89.6444 | 3717.4261 | T+22 sec | 40098.1026 | 59.8887 | 3787.775 | 335 | -212.7443 | 2.1176 | 159.1765 | 10 | 0 | -103 | 7570 | 89.0352 | 3716.9523
T+24 sec | 40098.1026 | 59.886 | 3780.6206 | 59.8887 | 3787.775 |  | 91.1987 | 92.7712 | 3756.8895 | 0.59346 | 3773.1533 | 3734.639 | 3747.2836 | 3684.9843 | 3681.7203 | 633 | [6 empty] | 0 | 633 | -406.4248 | -413.8616 | T+24 sec | 59.8823 | -397.4363 | 59.8844 | -402.6343 | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+24 sec | 40098.1026 | 59.886 | 3780.6206 | 335 | -211.256 | 1 | 157 | 10 | 0 | -103 | 7570 | 91.1987 | T+24 sec | 40098.1026 | 59.8823 | 3766.6891 | 335 | -209.8855 | 0.42857 | 156.1429 | 10 | 0 | -103 | 7570 | 94.1711 | 3720.8664 | T+24 sec | 40098.1026 | 59.8844 | 3778.5405 | 335 | -211.256 | 0.85714 | 157.1429 | 10 | 0 | -103 | 7570 | 92.4569 | 3718.9959 | T+24 sec | 40098.1026 | 59.8892 | 3783.7721 | 335 | -212.6609 | 1.0909 | 158.1818 | 10 | 0 | -103 | 7570 | 88.6541 | 3714.5856 | T+24 sec | 40098.1026 | 59.8879 | 3786.576 | 335 | -212.6617 | 2 | 159 | 10 | 0 | -103 | 7570 | 89.6444 | 3717.4261 | T+24 sec | 40098.1026 | 59.8887 | 3787.775 | 335 | -212.7443 | 2.1176 | 159.1765 | 10 | 0 | -103 | 7570 | 89.0352 | 3716.9523
T+26 sec | 40098.1026 | 59.885 | 3782.4995 | 59.8887 | 3787.775 |  | 92.0013 | 92.5017 | 3756.8895 | 0.59346 | 3773.4773 | 3738.0576 | 3749.1546 | 3685.5777 | 3682.017 | 633 | [6 empty] | 0 | 633 | -403.8235 | -413.8616 | T+26 sec |  |  | 59.8844 | -402.6343 | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+26 sec | 40098.1026 | 59.885 | 3782.4995 | 335 | -211.256 | 1 | 157.5 | 10 | 0 | -103 | 7570 | 92.0013 | T+26 sec | 40098.1026 | [12 empty] | T+26 sec | 40098.1026 | 59.8844 | 3778.5405 | 335 | -211.256 | 0.85714 | 157.1429 | 10 | 0 | -103 | 7570 | 92.4569 | 3718.9959 | T+26 sec | 40098.1026 | 59.8892 | 3783.7721 | 335 | -212.6609 | 1.0909 | 158.1818 | 10 | 0 | -103 | 7570 | 88.6541 | 3714.5856 | T+26 sec | 40098.1026 | 59.8879 | 3786.576 | 335 | -212.6617 | 2 | 159 | 10 | 0 | -103 | 7570 | 89.6444 | 3717.4261 | T+26 sec | 40098.1026 | 59.8887 | 3787.775 | 335 | -212.7443 | 2.1176 | 159.1765 | 10 | 0 | -103 | 7570 | 89.0352 | 3716.9523
T+28 sec | 40098.1027 | 59.888 | 3784.9619 | 59.8887 | 3787.775 |  | 89.5996 | 91.486 | 3756.8895 | 0.59346 | 3773.055 | 3741.1846 | 3750.7479 | 3686.1712 | 3682.3137 | 633 | [6 empty] | 0 | 633 | -411.7087 | -413.8616 | T+28 sec |  |  | 59.8844 | -402.6343 | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+28 sec | 40098.1027 | 59.888 | 3784.9619 | 335 | -211.256 | 1 | 158 | 10 | 0 | -103 | 7570 | 89.5996 | T+28 sec | 40098.1027 | [12 empty] | T+28 sec | 40098.1027 | 59.8844 | 3778.5405 | 335 | -211.256 | 0.85714 | 157.1429 | 10 | 0 | -103 | 7570 | 92.4569 | 3718.9959 | T+28 sec | 40098.1027 | 59.8892 | 3783.7721 | 335 | -212.6609 | 1.0909 | 158.1818 | 10 | 0 | -103 | 7570 | 88.6541 | 3714.5856 | T+28 sec | 40098.1027 | 59.8879 | 3786.576 | 335 | -212.6617 | 2 | 159 | 10 | 0 | -103 | 7570 | 89.6444 | 3717.4261 | T+28 sec | 40098.1027 | 59.8887 | 3787.775 | 335 | -212.7443 | 2.1176 | 159.1765 | 10 | 0 | -103 | 7570 | 89.0352 | 3716.9523
T+30 sec | 40098.1027 | 59.888 | 3784.9619 | 59.8887 | 3787.775 |  | 89.5996 | 90.8258 | 3756.8895 | 0.59346 | 3772.9882 | 3743.9207 | 3752.1379 | 3686.7646 | 3682.6104 | 633 | [6 empty] | 0 | 633 | -411.7087 | -413.8616 | T+30 sec |  |  | 59.8844 | -402.6343 | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+30 sec | 40098.1027 | 59.888 | 3784.9619 | 335 | -211.256 | 1 | 158 | 10 | 0 | -103 | 7570 | 89.5996 | T+30 sec | 40098.1027 | [12 empty] | T+30 sec | 40098.1027 | 59.8844 | 3778.5405 | 335 | -211.256 | 0.85714 | 157.1429 | 10 | 0 | -103 | 7570 | 92.4569 | 3718.9959 | T+30 sec | 40098.1027 | 59.8892 | 3783.7721 | 335 | -212.6609 | 1.0909 | 158.1818 | 10 | 0 | -103 | 7570 | 88.6541 | 3714.5856 | T+30 sec | 40098.1027 | 59.8879 | 3786.576 | 335 | -212.6617 | 2 | 159 | 10 | 0 | -103 | 7570 | 89.6444 | 3717.4261 | T+30 sec | 40098.1027 | 59.8887 | 3787.775 | 335 | -212.7443 | 2.1176 | 159.1765 | 10 | 0 | -103 | 7570 | 89.0352 | 3716.9523
T+32 sec | 40098.1027 | 59.89 | 3784.4189 | 59.8887 | 3787.775 |  | 88.0005 | 89.8369 | 3756.8895 | 0.59346 | 3772.5929 | 3746.3029 | 3753.3412 | 3687.3581 | 3682.9072 | 633 | [6 empty] | 0 | 633 | -417.1319 | -413.8616 | T+32 sec |  |  |  |  | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+32 sec | 40098.1027 | 59.89 | 3784.4189 | 335 | -214.3467 | 1 | 158.5 | 10 | 0 | -103 | 7570 | 88.0005 | T+32 sec | 40098.1027 | [12 empty] | T+32 sec | 40098.1027 | [12 empty] | T+32 sec | 40098.1027 | 59.8892 | 3783.7721 | 335 | -212.6609 | 1.0909 | 158.1818 | 10 | 0 | -103 | 7570 | 88.6541 | 3714.5856 | T+32 sec | 40098.1027 | 59.8879 | 3786.576 | 335 | -212.6617 | 2 | 159 | 10 | 0 | -103 | 7570 | 89.6444 | 3717.4261 | T+32 sec | 40098.1027 | 59.8887 | 3787.775 | 335 | -212.7443 | 2.1176 | 159.1765 | 10 | 0 | -103 | 7570 | 89.0352 | 3716.9523
T+34 sec | 40098.1027 | 59.894 | 3788.0723 | 59.8887 | 3787.775 |  | 84.7992 | 88.0737 | 3756.8895 | 0.59346 | 3771.4231 | 3748.6234 | 3754.3457 | 3687.9516 | 3683.2039 | 633 | [6 empty] | 0 | 633 | -428.4294 | -413.8616 | T+34 sec |  |  |  |  | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+34 sec | 40098.1027 | 59.894 | 3788.0723 | 335 | -214.3467 | 1 | 159 | 10 | 0 | -103 | 7570 | 84.7992 | T+34 sec | 40098.1027 | [12 empty] | T+34 sec | 40098.1027 | [12 empty] | T+34 sec | 40098.1027 | 59.8892 | 3783.7721 | 335 | -212.6609 | 1.0909 | 158.1818 | 10 | 0 | -103 | 7570 | 88.6541 | 3714.5856 | T+34 sec | 40098.1027 | 59.8879 | 3786.576 | 335 | -212.6617 | 2 | 159 | 10 | 0 | -103 | 7570 | 89.6444 | 3717.4261 | T+34 sec | 40098.1027 | 59.8887 | 3787.775 | 335 | -212.7443 | 2.1176 | 159.1765 | 10 | 0 | -103 | 7570 | 89.0352 | 3716.9523
T+36 sec | 40098.1027 | 59.894 | 3788.0723 | 59.8887 | 3787.775 |  | 84.7992 | 86.9276 | 3756.8895 | 0.59346 | 3770.8705 | 3750.6997 | 3755.2154 | 3688.545 | 3683.5006 | 633 | [6 empty] | 0 | 633 | -428.4294 | -413.8616 | T+36 sec |  |  |  |  | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+36 sec | 40098.1027 | 59.894 | 3788.0723 | 335 | -214.3467 | 1 | 159 | 10 | 0 | -103 | 7570 | 84.7992 | T+36 sec | 40098.1027 | [12 empty] | T+36 sec | 40098.1027 | [12 empty] | T+36 sec | 40098.1027 | 59.8892 | 3783.7721 | 335 | -212.6609 | 1.0909 | 158.1818 | 10 | 0 | -103 | 7570 | 88.6541 | 3714.5856 | T+36 sec | 40098.1027 | 59.8879 | 3786.576 | 335 | -212.6617 | 2 | 159 | 10 | 0 | -103 | 7570 | 89.6444 | 3717.4261 | T+36 sec | 40098.1027 | 59.8887 | 3787.775 | 335 | -212.7443 | 2.1176 | 159.1765 | 10 | 0 | -103 | 7570 | 89.0352 | 3716.9523
T+38 sec | 40098.1028 | 59.893 | 3788.8684 | 59.8887 | 3787.775 |  | 85.5988 | 86.4625 | 3756.8895 | 0.59346 | 3770.9988 | 3752.6081 | 3756.0046 | 3689.1385 | 3683.7974 | 633 | [6 empty] | 0 | 633 | -425.5508 | -413.8616 | T+38 sec |  |  |  |  | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+38 sec | 40098.1028 | 59.893 | 3788.8684 | 335 | -214.3467 | 1 | 159.5 | 10 | 0 | -103 | 7570 | 85.5988 | T+38 sec | 40098.1028 | [12 empty] | T+38 sec | 40098.1028 | [12 empty] | T+38 sec | 40098.1028 | 59.8892 | 3783.7721 | 335 | -212.6609 | 1.0909 | 158.1818 | 10 | 0 | -103 | 7570 | 88.6541 | 3714.5856 | T+38 sec | 40098.1028 | 59.8879 | 3786.576 | 335 | -212.6617 | 2 | 159 | 10 | 0 | -103 | 7570 | 89.6444 | 3717.4261 | T+38 sec | 40098.1028 | 59.8887 | 3787.775 | 335 | -212.7443 | 2.1176 | 159.1765 | 10 | 0 | -103 | 7570 | 89.0352 | 3716.9523
T+40 sec | 40098.1028 | 59.894 | 3788.4719 | 59.8887 | 3787.775 |  | 84.7992 | 85.8804 | 3756.8895 | 0.59346 | 3771.0101 | 3754.3159 | 3756.7192 | 3689.7319 | 3684.0941 | 633 | [6 empty] | 0 | 633 | -428.4294 | -413.8616 | T+40 sec |  |  |  |  | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+40 sec | 40098.1028 | 59.894 | 3788.4719 | 335 | -214.3467 | 2 | 160 | 10 | 0 | -103 | 7570 | 84.7992 | T+40 sec | 40098.1028 | [12 empty] | T+40 sec | 40098.1028 | [12 empty] | T+40 sec | 40098.1028 | 59.8892 | 3783.7721 | 335 | -212.6609 | 1.0909 | 158.1818 | 10 | 0 | -103 | 7570 | 88.6541 | 3714.5856 | T+40 sec | 40098.1028 | 59.8879 | 3786.576 | 335 | -212.6617 | 2 | 159 | 10 | 0 | -103 | 7570 | 89.6444 | 3717.4261 | T+40 sec | 40098.1028 | 59.8887 | 3787.775 | 335 | -212.7443 | 2.1176 | 159.1765 | 10 | 0 | -103 | 7570 | 89.0352 | 3716.9523
T+42 sec | 40098.1028 | 59.894 | 3788.4719 | 59.8887 | 3787.775 |  | 84.7992 | 85.502 | 3756.8895 | 0.59346 | 3771.2252 | 3755.8685 | 3757.3785 | 3690.3254 | 3684.3908 | 633 | [6 empty] | 0 | 633 | -428.4294 | -413.8616 | T+42 sec | [6 empty] | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+42 sec | 40098.1028 | 59.894 | 3788.4719 | 335 | -214.3467 | 2 | 160 | 10 | 0 | -103 | 7570 | 84.7992 | T+42 sec | 40098.1028 | [12 empty] | T+42 sec | 40098.1028 | [12 empty] | T+42 sec | 40098.1028 | [12 empty] | T+42 sec | 40098.1028 | 59.8879 | 3786.576 | 335 | -212.6617 | 2 | 159 | 10 | 0 | -103 | 7570 | 89.6444 | 3717.4261 | T+42 sec | 40098.1028 | 59.8887 | 3787.775 | 335 | -212.7443 | 2.1176 | 159.1765 | 10 | 0 | -103 | 7570 | 89.0352 | 3716.9523
T+44 sec | 40098.1028 | 59.891 | 3793.0745 | 59.8887 | 3787.775 |  | 87.2009 | 86.0966 | 3756.8895 | 0.59346 | 3772.4133 | 3757.4861 | 3758.0322 | 3690.9188 | 3684.6875 | 633 | [6 empty] | 0 | 633 | -419.8974 | -413.8616 | T+44 sec | [6 empty] | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+44 sec | 40098.1028 | 59.891 | 3793.0745 | 335 | -214.3467 | 3 | 160.5 | 10 | 0 | -103 | 7570 | 87.2009 | T+44 sec | 40098.1028 | [12 empty] | T+44 sec | 40098.1028 | [12 empty] | T+44 sec | 40098.1028 | [12 empty] | T+44 sec | 40098.1028 | 59.8879 | 3786.576 | 335 | -212.6617 | 2 | 159 | 10 | 0 | -103 | 7570 | 89.6444 | 3717.4261 | T+44 sec | 40098.1028 | 59.8887 | 3787.775 | 335 | -212.7443 | 2.1176 | 159.1765 | 10 | 0 | -103 | 7570 | 89.0352 | 3716.9523
T+46 sec | 40098.1029 | 59.885 | 3794.3743 | 59.8887 | 3787.775 |  | 92.0013 | 88.1633 | 3756.8895 | 0.59346 | 3775.0734 | 3759.0231 | 3758.7423 | 3691.5123 | 3684.9843 | 633 | [6 empty] | 0 | 633 | -403.8235 | -413.8616 | T+46 sec | [6 empty] | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+46 sec | 40098.1029 | 59.885 | 3794.3743 | 335 | -212.1727 | 4 | 161 | 10 | 0 | -103 | 7570 | 92.0013 | T+46 sec | 40098.1029 | [12 empty] | T+46 sec | 40098.1029 | [12 empty] | T+46 sec | 40098.1029 | [12 empty] | T+46 sec | 40098.1029 | 59.8879 | 3786.576 | 335 | -212.6617 | 2 | 159 | 10 | 0 | -103 | 7570 | 89.6444 | 3717.4261 | T+46 sec | 40098.1029 | 59.8887 | 3787.775 | 335 | -212.7443 | 2.1176 | 159.1765 | 10 | 0 | -103 | 7570 | 89.0352 | 3716.9523
T+48 sec | 40098.1029 | 59.885 | 3794.3743 | 59.8887 | 3787.775 |  | 92.0013 | 89.5066 | 3756.8895 | 0.59346 | 3777.0102 | 3760.4372 | 3759.473 | 3692.1057 | 3685.281 | 633 | [6 empty] | 0 | 633 | -403.8235 | -413.8616 | T+48 sec | [6 empty] | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+48 sec | 40098.1029 | 59.885 | 3794.3743 | 335 | -212.1727 | 4 | 161 | 10 | 0 | -103 | 7570 | 92.0013 | T+48 sec | 40098.1029 | [12 empty] | T+48 sec | 40098.1029 | [12 empty] | T+48 sec | 40098.1029 | [12 empty] | T+48 sec | 40098.1029 | 59.8879 | 3786.576 | 335 | -212.6617 | 2 | 159 | 10 | 0 | -103 | 7570 | 89.6444 | 3717.4261 | T+48 sec | 40098.1029 | 59.8887 | 3787.775 | 335 | -212.7443 | 2.1176 | 159.1765 | 10 | 0 | -103 | 7570 | 89.0352 | 3716.9523
T+50 sec | 40098.1029 | 59.885 | 3800.4275 | 59.8887 | 3787.775 |  | 92.0013 | 90.3798 | 3756.8895 | 0.59346 | 3778.4768 | 3761.9753 | 3760.2039 | 3692.6992 | 3685.5777 | 633 | [6 empty] | 0 | 633 | -403.8235 | -413.8616 | T+50 sec | [6 empty] | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+50 sec | 40098.1029 | 59.885 | 3800.4275 | 335 | -212.1727 | 5 | 161.5 | 10 | 0 | -103 | 7570 | 92.0013 | T+50 sec | 40098.1029 | [12 empty] | T+50 sec | 40098.1029 | [12 empty] | T+50 sec | 40098.1029 | [12 empty] | T+50 sec | 40098.1029 | 59.8879 | 3786.576 | 335 | -212.6617 | 2 | 159 | 10 | 0 | -103 | 7570 | 89.6444 | 3717.4261 | T+50 sec | 40098.1029 | 59.8887 | 3787.775 | 335 | -212.7443 | 2.1176 | 159.1765 | 10 | 0 | -103 | 7570 | 89.0352 | 3716.9523
T+52 sec | 40098.1029 | 59.887 | 3799.9592 | 59.8887 | 3787.775 |  | 90.3992 | 90.3865 | 3756.8895 | 0.59346 | 3779.0771 | 3763.3821 | 3760.9029 | 3693.2927 | 3685.8745 | 633 | [6 empty] | 0 | 633 | -409.0497 | -413.8616 | T+52 sec | [6 empty] | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+52 sec | 40098.1029 | 59.887 | 3799.9592 | 335 | -212.1727 | 6 | 162 | 10 | 0 | -103 | 7570 | 90.3992 | T+52 sec | 40098.1029 | [12 empty] | T+52 sec | 40098.1029 | [12 empty] | T+52 sec | 40098.1029 | [12 empty] | T+52 sec | 40098.1029 | 59.8879 | 3786.576 | 335 | -212.6617 | 2 | 159 | 10 | 0 | -103 | 7570 | 89.6444 | 3717.4261 | T+52 sec | 40098.1029 | 59.8887 | 3787.775 | 335 | -212.7443 | 2.1176 | 159.1765 | 10 | 0 | -103 | 7570 | 89.0352 | 3716.9523
T+54 sec | 40098.103 | 59.887 | 3799.9592 |  |  |  | 90.3992 | 90.391 |  | 0.59346 | 3779.6749 | 3764.6884 | 3761.5733 | 3693.8861 | 3686.1712 | 633 | [6 empty] | 0 | 633 | -409.0497 |  | T+54 sec | [10 empty] | T+54 sec | 40098.103 | 59.887 | 3799.9592 | 335 | -212.1727 | 6 | 162 | 10 | 0 | -103 | 7570 | 90.3992 | T+54 sec | 40098.103 | [12 empty] | T+54 sec | 40098.103 | [12 empty] | T+54 sec | 40098.103 | [12 empty] | T+54 sec | 40098.103 | [12 empty] | T+54 sec | 40098.103
T+56 sec | 40098.103 | 59.888 | 3802.925 |  |  |  | 89.5996 | 90.114 |  | 0.59346 | 3779.9914 | 3766.0069 | 3762.2084 | 3694.4796 | 3686.4679 | 633 | [6 empty] | 0 | 633 | -411.7087 |  | T+56 sec | [10 empty] | T+56 sec | 40098.103 | 59.888 | 3802.925 | 335 | -212.1727 | 7 | 162.5 | 10 | 0 | -103 | 7570 | 89.5996 | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103
T+58 sec | 40098.103 | 59.89 | 3802.9509 |  |  |  | 88.0005 | 89.3743 |  | 0.59346 | 3779.8452 | 3767.2384 | 3762.7963 | 3695.073 | 3686.7646 | 633 | [6 empty] | 0 | 633 | -417.1319 |  | T+58 sec | [10 empty] | T+58 sec | 40098.103 | 59.89 | 3802.9509 | 335 | -212.1727 | 8 | 163 | 10 | 0 | -103 | 7570 | 88.0005 | T+58 sec | 40098.103 | [12 empty] | T+58 sec | 40098.103 | [12 empty] | T+58 sec | 40098.103 | [12 empty] | T+58 sec | 40098.103 | [12 empty] | T+58 sec | 40098.103
T+60 sec | 40098.103 | 59.89 | 3802.9509 |  |  |  | 88.0005 | 88.8934 |  | 0.59346 | 3779.9578 | 3768.3904 | 3763.3499 | 3695.6665 | 3687.0614 | 633 | [6 empty] | 0 | 633 | -417.1319 |  | T+60 sec | [10 empty] | T+60 sec | 40098.103 | 59.89 | 3802.9509 | 335 | -212.1727 | 8 | 163 | 10 | 0 | -103 | 7570 | 88.0005 | T+60 sec | 40098.103 | [12 empty] | T+60 sec | 40098.103 | [12 empty] | T+60 sec | 40098.103 | [12 empty] | T+60 sec | 40098.103 | [12 empty] | T+60 sec | 40098.103
T+62 sec | 40098.103 | 59.889 | 3805.4961 |  |  |  | 88.8 | 88.8608 |  | 0.59346 | 3780.5186 | 3769.5499 | 3763.8864 | 3696.2599 | 3687.3581 | 633 | [6 empty] | 0 | 633 | -414.4026 |  | T+62 sec | [10 empty] | T+62 sec | 40098.103 | 59.889 | 3805.4961 | 335 | -215.5982 | 9 | 163.5 | 10 | 0 | -103 | 7570 | 88.8 | T+62 sec | 40098.103 | [12 empty] | T+62 sec | 40098.103 | [12 empty] | T+62 sec | 40098.103 | [12 empty] | T+62 sec | 40098.103 | [12 empty] | T+62 sec | 40098.103
T+64 sec | 40098.1031 | 59.873 | 3805.6167 |  |  |  | 101.5991 | 93.3192 |  | 0.59346 | 3785.5704 | 3770.6429 | 3764.5435 | 3696.8534 | 3687.6548 | 633 | [6 empty] | 0 | 633 | -375.1137 |  | T+64 sec | [10 empty] | T+64 sec | 40098.1031 | 59.873 | 3805.6167 | 335 | -215.5982 | 10 | 164 | 10 | 0 | -103 | 7568 | 101.5991 | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031
T+66 sec | 40098.1031 | 59.873 | 3805.6167 |  |  |  | 101.5991 | 96.2172 |  | 0.59346 | 3789.0619 | 3771.6715 | 3765.2647 | 3697.4469 | 3687.9516 | 633 | [6 empty] | 0 | 633 | -375.1137 |  | T+66 sec | [10 empty] | T+66 sec | 40098.1031 | 59.873 | 3805.6167 | 335 | -215.5982 | 10 | 164 | 10 | 0 | -103 | 7568 | 101.5991 | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031
T+68 sec | 40098.1031 | 59.857 | 3811.5029 |  |  |  | 114.4012 | 102.5816 |  | 0.59346 | 3796.0198 | 3772.8096 | 3766.1434 | 3698.0403 | 3688.2483 | 633 | [6 empty] | 0 | 633 | -342.6224 |  | T+68 sec | [10 empty] | T+68 sec | 40098.1031 | 59.857 | 3811.5029 | 335 | -215.5982 | 11 | 164.5 | 10 | 0 | -103 | 7565 | 114.4012 | T+68 sec | 40098.1031 | [12 empty] | T+68 sec | 40098.1031 | [12 empty] | T+68 sec | 40098.1031 | [12 empty] | T+68 sec | 40098.1031 | [12 empty] | T+68 sec | 40098.1031
T+70 sec | 40098.1031 | 59.852 | 3814.8623 |  |  |  | 118.399 | 108.1177 |  | 0.59346 | 3802.1493 | 3773.9777 | 3767.1435 | 3698.6338 | 3688.545 | 633 | [6 empty] | 0 | 633 | -333.599 |  | T+70 sec | [10 empty] | T+70 sec | 40098.1031 | 59.852 | 3814.8623 | 335 | -215.5982 | 12 | 165 | 10 | 0 | -103 | 7560 | 118.399 | T+70 sec | 40098.1031 | [12 empty] | T+70 sec | 40098.1031 | [12 empty] | T+70 sec | 40098.1031 | [12 empty] | T+70 sec | 40098.1031 | [12 empty] | T+70 sec | 40098.1031
T+72 sec | 40098.1032 | 59.852 | 3814.8623 |  |  |  | 118.399 | 111.7162 |  | 0.59346 | 3806.3413 | 3775.0827 | 3768.2029 | 3699.2272 | 3688.8417 | 633 | [6 empty] | 0 | 633 | -333.599 |  | T+72 sec | [10 empty] | T+72 sec | 40098.1032 | 59.852 | 3814.8623 | 335 | -215.5982 | 12 | 165 | 10 | 0 | -103 | 7560 | 118.399 | T+72 sec | 40098.1032 | [12 empty] | T+72 sec | 40098.1032 | [12 empty] | T+72 sec | 40098.1032 | [12 empty] | T+72 sec | 40098.1032 | [12 empty] | T+72 sec | 40098.1032
T+74 sec | 40098.1032 | 59.858 | 3825.6426 |  |  |  | 113.5986 | 112.375 |  | 0.59346 | 3807.5936 | 3776.4132 | 3769.2395 | 3699.8207 | 3689.1385 | 633 | [6 empty] | 0 | 633 | -344.4931 |  | T+74 sec | [10 empty] | T+74 sec | 40098.1032 | 59.858 | 3825.6426 | 335 | -215.5982 | 13 | 165.5 | 10 | 0 | -103 | 7563 | 113.5986 | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032
T+76 sec | 40098.1032 | 59.866 | 3826.0532 |  |  |  | 107.1991 | 110.5635 |  | 0.59346 | 3806.3755 | 3777.686 | 3770.1917 | 3700.4141 | 3689.4352 | 633 | [6 empty] | 0 | 633 | -360.1731 |  | T+76 sec | [10 empty] | T+76 sec | 40098.1032 | 59.866 | 3826.0532 | 335 | -218.3273 | 14 | 166 | 10 | 0 | -103 | 7564 | 107.1991 | T+76 sec | 40098.1032 | [12 empty] | T+76 sec | 40098.1032 | [12 empty] | T+76 sec | 40098.1032 | [12 empty] | T+76 sec | 40098.1032 | [12 empty] | T+76 sec | 40098.1032
T+78 sec | 40098.1032 | 59.866 | 3826.0532 |  |  |  | 107.1991 | 109.3859 |  | 0.59346 | 3805.7914 | 3778.8952 | 3771.0817 | 3701.0076 | 3689.7319 | 633 | [6 empty] | 0 | 633 | -360.1731 |  | T+78 sec | [10 empty] | T+78 sec | 40098.1032 | 59.866 | 3826.0532 | 335 | -218.3273 | 14 | 166 | 10 | 0 | -103 | 7564 | 107.1991 | T+78 sec | 40098.1032 | [12 empty] | T+78 sec | 40098.1032 | [12 empty] | T+78 sec | 40098.1032 | [12 empty] | T+78 sec | 40098.1032 | [12 empty] | T+78 sec | 40098.1032
T+80 sec | 40098.1033 | 59.865 | 3827.5239 |  |  |  | 107.9987 | 108.9004 |  | 0.59346 | 3805.8993 | 3780.0813 | 3771.9309 | 3701.6011 | 3690.0287 | 633 | [6 empty] | 0 | 633 | -358.1364 |  | T+80 sec | [10 empty] | T+80 sec | 40098.1033 | 59.865 | 3827.5239 | 335 | -218.3273 | 15 | 166.5 | 10 | 0 | -103 | 7566 | 107.9987 | T+80 sec | 40098.1033 | [12 empty] | T+80 sec | 40098.1033 | [12 empty] | T+80 sec | 40098.1033 | [12 empty] | T+80 sec | 40098.1033 | [12 empty] | T+80 sec | 40098.1033
| 40098.1033 | 59.866 | 3826.7532 |  |  |  | 107.1991 | 108.3049 |  | 0.59346 | 3805.8973 | 3781.1925 | 3772.7397 | 3702.1945 | 3690.3254 | 633 | [6 empty] | 0 | 633 | -360.1731 | [13 empty] | 40098.1033 | 59.866 | 3826.7532 | 335 | -218.3273 | 16 | 167 | 10 | 0 | -103 | 7570 | 107.1991
| 40098.1033 | 59.866 | 3826.7532 |  |  |  | 107.1991 | 107.9179 |  | 0.59346 | 3806.1037 | 3782.2521 | 3773.5156 | 3702.788 | 3690.6221 | 633 | [6 empty] | 0 | 633 | -360.1731 | [13 empty] | 40098.1033 | 59.866 | 3826.7532 | 335 | -218.3273 | 16 | 167 | 10 | 0 | -103 | 7570 | 107.1991
| 40098.1033 | 59.871 | 3826.4536 |  |  |  | 103.2013 | 106.2671 |  | 0.59346 | 3805.0464 | 3783.2566 | 3774.2322 | 3703.3814 | 3690.9188 | 633 | [6 empty] | 0 | 633 | -370.714 | [13 empty] | 40098.1033 | 59.871 | 3826.4536 | 335 | -218.3273 | 16 | 167.5 | 10 | 0 | -103 | 7570 | 103.2013
| 40098.1033 | 59.879 | 3825.7134 |  |  |  | 96.7987 | 102.9532 |  | 0.59346 | 3802.3259 | 3784.2001 | 3774.8565 | 3703.9749 | 3691.2156 | 633 | [6 empty] | 0 | 633 | -388.9441 | [13 empty] | 40098.1033 | 59.879 | 3825.7134 | 335 | -218.3273 | 16 | 168 | 10 | 0 | -103 | 7570 | 96.7987
| 40098.1034 | 59.879 | 3825.7134 |  |  |  | 96.7987 | 100.7991 |  | 0.59346 | 3800.7653 | 3785.1026 | 3775.4197 | 3704.5683 | 3691.5123 | 633 | [6 empty] | 0 | 633 | -388.9441 | [13 empty] | 40098.1034 | 59.879 | 3825.7134 | 335 | -218.3273 | 16 | 168 | 10 | 0 | -103 | 7570 | 96.7987
| 40098.1034 | 59.88 | 3822.5054 |  |  |  | 95.9991 | 99.1191 |  | 0.59346 | 3799.6788 | 3785.8984 | 3775.9359 | 3705.1618 | 3691.809 | 633 | [6 empty] | 0 | 633 | -391.3474 | [13 empty] | 40098.1034 | 59.88 | 3822.5054 | 335 | -217.3794 | 16 | 168.5 | 10 | 0 | -103 | 7570 | 95.9991
| 40098.1034 | 59.886 | 3819.0811 |  |  |  | 91.1987 | 96.347 |  | 0.59346 | 3797.5001 | 3786.5897 | 3776.3851 | 3705.7553 | 3692.1057 | 633 | [6 empty] | 0 | 633 | -406.4248 | [13 empty] | 40098.1034 | 59.886 | 3819.0811 | 335 | -217.3794 | 16 | 169 | 10 | 0 | -103 | 7570 | 91.1987
| 40098.1034 | 59.886 | 3819.0811 |  |  |  | 91.1987 | 94.5451 |  | 0.59346 | 3796.2917 | 3787.2528 | 3776.7914 | 3706.3487 | 3692.4025 | 633 | [6 empty] | 0 | 633 | -406.4248 | [13 empty] | 40098.1034 | 59.886 | 3819.0811 | 335 | -217.3794 | 16 | 169 | 10 | 0 | -103 | 7570 | 91.1987
| 40098.1035 | 59.89 | 3816.8147 |  |  |  | 88.0005 | 92.2545 |  | 0.59346 | 3794.5945 | 3787.844 | 3777.1474 | 3706.9422 | 3692.6992 | 633 | [6 empty] | 0 | 633 | -417.1319 | [13 empty] | 40098.1035 | 59.89 | 3816.8147 | 335 | -217.3794 | 16 | 169.5 | 10 | 0 | -103 | 7569 | 88.0005
| 40098.1035 | 59.889 | 3815.0098 |  |  |  | 88.8 | 91.0454 |  | 0.59346 | 3793.9789 | 3788.3767 | 3777.4775 | 3707.5356 | 3692.9959 | 633 | [6 empty] | 0 | 633 | -414.4026 | [13 empty] | 40098.1035 | 59.889 | 3815.0098 | 335 | -217.3794 | 16 | 170 | 10 | 0 | -103 | 7575 | 88.8
| 40098.1035 | 59.889 | 3815.0098 |  |  |  | 88.8 | 90.2595 |  | 0.59346 | 3793.7865 | 3788.8889 | 3777.7911 | 3708.1291 | 3693.2927 | 633 | [6 empty] | 0 | 633 | -414.4026 | [13 empty] | 40098.1035 | 59.889 | 3815.0098 | 335 | -217.3794 | 16 | 170 | 10 | 0 | -103 | 7575 | 88.8
| 40098.1035 | 59.893 | 3811.8384 |  |  |  | 85.5988 | 88.6283 |  | 0.59346 | 3792.7487 | 3789.3219 | 3778.0733 | 3708.7225 | 3693.5894 | 633 | [6 empty] | 0 | 633 | -425.5508 | [13 empty] | 40098.1035 | 59.893 | 3811.8384 | 335 | -217.3794 | 16 | 170.5 | 10 | 0 | -103 | 7573 | 85.5988
| 40098.1036 | 59.903 | 3809.6519 |  |  |  | 77.6001 | 84.7684 |  | 0.59346 | 3789.4823 | 3789.6984 | 3778.2846 | 3709.316 | 3693.8861 | 633 | [6 empty] | 0 | 633 | -456.216 | [13 empty] | 40098.1036 | 59.903 | 3809.6519 | 335 | -214.8304 | 16 | 171 | 10 | 0 | -103 | 7571 | 77.6001
| 40098.1036 | 59.903 | 3809.6519 |  |  |  | 77.6001 | 82.2595 |  | 0.59346 | 3787.5668 | 3790.0611 | 3778.4534 | 3709.9094 | 3694.1828 | 633 | [6 empty] | 0 | 633 | -456.216 | [13 empty] | 40098.1036 | 59.903 | 3809.6519 | 335 | -214.8304 | 16 | 171 | 10 | 0 | -103 | 7571 | 77.6001
| 40098.1036 | 59.902 | 3805.5933 |  |  |  | 78.3997 | 80.9086 |  | 0.59346 | 3786.8093 | 3790.3385 | 3778.6026 | 3710.5029 | 3694.4796 | 633 | [6 empty] | 0 | 633 | -452.9532 | [13 empty] | 40098.1036 | 59.902 | 3805.5933 | 335 | -214.8304 | 16 | 171.5 | 10 | 0 | -103 | 7573 | 78.3997
| 40098.1036 | 59.904 | 3804.1885 |  |  |  | 76.8005 | 79.4707 |  | 0.59346 | 3785.965 | 3790.5815 | 3778.7317 | 3711.0964 | 3694.7763 | 633 | [6 empty] | 0 | 633 | -459.526 | [13 empty] | 40098.1036 | 59.904 | 3804.1885 | 335 | -214.8304 | 16 | 172 | 10 | 0 | -103 | 7575 | 76.8005
| 40098.1036 | 59.904 | 3804.1885 |  |  |  | 76.8005 | 78.5362 |  | 0.59346 | 3785.6238 | 3790.8161 | 3778.8506 | 3711.6898 | 3695.073 | 633 | [6 empty] | 0 | 633 | -459.526 | [13 empty] | 40098.1036 | 59.904 | 3804.1885 | 335 | -214.8304 | 16 | 172 | 10 | 0 | -103 | 7575 | 76.8005
| 40098.1037 | 59.907 | 3793.9751 |  |  |  | 74.3988 | 77.0881 |  | 0.59346 | 3784.7692 | 3790.8696 | 3778.9509 | 3712.2833 | 3695.3698 | 633 | [6 empty] | 0 | 633 | -469.7642 | [13 empty] | 40098.1037 | 59.907 | 3793.9751 | 335 | -214.8304 | 16 | 172.5 | 10 | 0 | -103 | 7577 | 74.3988
| 40098.1037 | 59.916 | 3792.1694 |  |  |  | 67.1997 | 73.6272 |  | 0.59346 | 3781.9017 | 3790.8913 | 3779.0001 | 3712.8767 | 3695.6665 | 633 | [6 empty] | 0 | 633 | -503.3814 | [13 empty] | 40098.1037 | 59.916 | 3792.1694 | 335 | -214.8304 | 16 | 173 | 10 | 0 | -103 | 7577 | 67.1997
| 40098.1037 | 59.916 | 3792.1694 |  |  |  | 67.1997 | 71.3776 |  | 0.59346 | 3780.2456 | 3790.9122 | 3779.0205 | 3713.4702 | 3695.9632 | 633 | [6 empty] | 0 | 633 | -503.3814 | [13 empty] | 40098.1037 | 59.916 | 3792.1694 | 335 | -214.8304 | 16 | 173 | 10 | 0 | -103 | 7577 | 67.1997
| 40098.1037 | 59.916 | 3789.5337 |  |  |  | 67.1997 | 69.9153 |  | 0.59346 | 3779.3768 | 3790.89 | 3779.0262 | 3714.0636 | 3696.2599 | 633 | [6 empty] | 0 | 633 | -503.3814 | [13 empty] | 40098.1037 | 59.916 | 3789.5337 | 335 | -227.6559 | 16 | 173.5 | 10 | 0 | -103 | 7578 | 67.1997
| 40098.1038 | 59.918 | 3788.1321 |  |  |  | 65.6006 | 68.4052 |  | 0.59346 | 3778.4601 | 3790.8462 | 3779.0173 | 3714.6571 | 3696.5567 | 633 | [6 empty] | 0 | 633 | -511.5123 | [13 empty] | 40098.1038 | 59.918 | 3788.1321 | 335 | -227.6559 | 16 | 174 | 10 | 0 | -103 | 7579 | 65.6006
| 40098.1038 | 59.918 | 3788.1321 |  |  |  | 65.6006 | 67.4236 |  | 0.59346 | 3778.072 | 3790.8038 | 3779.0025 | 3715.2506 | 3696.8534 | 633 | [6 empty] | 0 | 633 | -511.5123 | [13 empty] | 40098.1038 | 59.918 | 3788.1321 | 335 | -227.6559 | 16 | 174 | 10 | 0 | -103 | 7579 | 65.6006
| 40098.1038 | 59.92 | 3783.0283 |  |  |  | 64.0015 | 66.2258 |  | 0.59346 | 3777.4677 | 3790.6842 | 3778.9789 | 3715.844 | 3697.1501 | 633 | [6 empty] | 0 | 633 | -519.9102 | [13 empty] | 40098.1038 | 59.92 | 3783.0283 | 335 | -227.6559 | 16 | 174.5 | 10 | 0 | -103 | 7580 | 64.0015
| 40098.1038 | 59.92 | 3781.7012 |  |  |  | 64.0015 | 65.4473 |  | 0.59346 | 3777.2826 | 3790.5481 | 3778.9532 | 3716.4375 | 3697.4469 | 633 | [6 empty] | 0 | 633 | -519.9102 | [13 empty] | 40098.1038 | 59.92 | 3781.7012 | 335 | -227.6559 | 16 | 175 | 10 | 0 | -103 | 7581 | 64.0015
| 40098.1039 | 59.92 | 3781.7012 |  |  |  | 64.0015 | 64.9413 |  | 0.59346 | 3777.37 | 3790.4161 | 3778.9295 | 3717.0309 | 3697.7436 | 633 | [6 empty] | 0 | 633 | -519.9102 | [13 empty] | 40098.1039 | 59.92 | 3781.7012 | 335 | -227.6559 | 16 | 175 | 10 | 0 | -103 | 7581 | 64.0015
| 40098.1039 | 59.917 | 3775.6355 |  |  |  | 66.4001 | 65.4519 |  | 0.59346 | 3778.4741 | 3790.1987 | 3778.9228 | 3717.6244 | 3698.0403 | 633 | [6 empty] | 0 | 633 | -507.4143 | [13 empty] | 40098.1039 | 59.917 | 3775.6355 | 335 | -227.6559 | 16 | 175.5 | 10 | 0 | -103 | 7585 | 66.4001
| 40098.1039 | 59.921 | 3774.6042 |  |  |  | 63.1989 | 64.6633 |  | 0.59346 | 3778.279 | 3789.9727 | 3778.9135 | 3718.2178 | 3698.337 | 633 | [6 empty] | 0 | 633 | -524.23 | [13 empty] | 40098.1039 | 59.921 | 3774.6042 | 335 | -225.0181 | 16 | 176 | 10 | 0 | -103 | 7588 | 63.1989
| 40098.1039 | 59.921 | 3774.6042 |  |  |  | 63.1989 | 64.1508 |  | 0.59346 | 3778.3599 | 3789.7531 | 3778.9056 | 3718.8113 | 3698.6338 | 633 | [6 empty] | 0 | 633 | -524.23 | [13 empty] | 40098.1039 | 59.921 | 3774.6042 | 335 | -225.0181 | 16 | 176 | 10 | 0 | -103 | 7588 | 63.1989
| 40098.1039 | 59.923 | 3773.9578 |  |  |  | 61.5997 | 63.2579 |  | 0.59346 | 3778.0605 | 3789.5307 | 3778.8937 | 3719.4048 | 3698.9305 | 633 | [6 empty] | 0 | 633 | -533.0543 | [13 empty] | 40098.1039 | 59.923 | 3773.9578 | 335 | -225.0181 | 16 | 176.5 | 10 | 0 | -103 | 7589 | 61.5997
| 40098.104 | 59.925 | 3772.7224 |  |  |  | 60.0006 | 62.1178 |  | 0.59346 | 3777.5139 | 3789.2972 | 3778.8745 | 3719.9982 | 3699.2272 | 633 | [6 empty] | 0 | 633 | -542.1808 | [13 empty] | 40098.104 | 59.925 | 3772.7224 | 335 | -225.0181 | 0 | 177 | 10 | 0 | -103 | 7589 | 60.0006
| 40098.104 | 59.925 | 3772.7224 |  |  |  | 60.0006 | 61.3768 |  | 0.59346 | 3777.3663 | 3789.0702 | 3778.8539 | 3720.5917 | 3699.524 | 633 | [6 empty] | 0 | 633 | -542.1808 | [13 empty] | 40098.104 | 59.925 | 3772.7224 | 335 | -225.0181 | 0 | 177 | 10 | 0 | -103 | 7589 | 60.0006
| 40098.104 | 59.928 | 3769.6296 |  |  |  | 57.5989 | 60.0545 |  | 0.59346 | 3776.6375 | 3788.8075 | 3778.8239 | 3721.1851 | 3699.8207 | 633 | [6 empty] | 0 | 633 | -556.4906 | [13 empty] | 40098.104 | 59.928 | 3769.6296 | 335 | -225.0181 | 0 | 177.5 | 10 | 0 | -103 | 7590 | 57.5989
| 40098.104 | 59.932 | 3768.707 |  |  |  | 54.4006 | 58.0757 |  | 0.59346 | 3775.2521 | 3788.5394 | 3778.7763 | 3721.7786 | 3700.1174 | 633 | [6 empty] | 0 | 633 | -576.7614 | [13 empty] | 40098.104 | 59.932 | 3768.707 | 335 | -225.0181 | 0 | 178 | 10 | 0 | -103 | 7590 | 54.4006
| 40098.1041 | 59.932 | 3768.707 |  |  |  | 54.4006 | 56.7894 |  | 0.59346 | 3774.5593 | 3788.2785 | 3778.7208 | 3722.372 | 3700.4141 | 633 | [6 empty] | 0 | 633 | -576.7614 | [13 empty] | 40098.1041 | 59.932 | 3768.707 | 335 | -225.0181 | 0 | 178 | 10 | 0 | -103 | 7590 | 54.4006
| 40098.1041 | 59.927 | 3767.021 |  |  |  | 58.4015 | 57.3536 |  | 0.59346 | 3775.717 | 3788.0024 | 3778.6818 | 3722.9655 | 3700.7109 | 633 | [6 empty] | 0 | 633 | -551.6253 | [13 empty] | 40098.1041 | 59.927 | 3767.021 | 335 | -228.3652 | 0 | 178.5 | 10 | 0 | -103 | 7590 | 58.4015
| 40098.1041 | 59.931 | 3767.408 |  |  |  | 55.2002 | 56.5999 |  | 0.59346 | 3775.5567 | 3787.7384 | 3778.6417 | 3723.559 | 3701.0076 | 633 | [6 empty] | 0 | 633 | -571.5565 | [13 empty] | 40098.1041 | 59.931 | 3767.408 | 335 | -228.3652 | 0 | 179 | 10 | 0 | -103 | 7591 | 55.2002
| 40098.1041 | 59.931 | 3767.408 |  |  |  | 55.2002 | 56.11 |  | 0.59346 | 3775.6603 | 3787.481 | 3778.604 | 3724.1524 | 3701.3043 | 633 | [6 empty] | 0 | 633 | -571.5565 | [13 empty] | 40098.1041 | 59.931 | 3767.408 | 335 | -228.3652 | 0 | 179 | 10 | 0 | -103 | 7591 | 55.2002
| 40098.1042 | 59.929 | 3766.259 |  |  |  | 56.7993 | 56.3513 |  | 0.59346 | 3776.495 | 3787.2158 | 3778.5776 | 3724.7459 | 3701.6011 | 633 | [6 empty] | 0 | 633 | -561.4236 | [13 empty] | 40098.1042 | 59.929 | 3766.259 | 335 | -228.3652 | 0 | 179.5 | 10 | 0 | -103 | 7591 | 56.7993
| 40098.1042 | 59.931 | 3765.6716 |  |  |  | 55.2002 | 55.9484 |  | 0.59346 | 3776.6856 | 3786.9498 | 3778.5543 | 3725.3393 | 3701.8978 | 633 | [6 empty] | 0 | 633 | -571.5565 | [13 empty] | 40098.1042 | 59.931 | 3765.6716 | 335 | -228.3652 | 0 | 180 | 10 | 0 | -103 | 7591 | 55.2002
| 40098.1042 | 59.931 | 3765.6716 |  |  |  | 55.2002 | 55.6865 |  | 0.59346 | 3777.0172 | 3786.6903 | 3778.5355 | 3725.9328 | 3702.1945 | 633 | [6 empty] | 0 | 633 | -571.5565 | [13 empty] | 40098.1042 | 59.931 | 3765.6716 | 335 | -228.3652 | 0 | 180 | 10 | 0 | -103 | 7591 | 55.2002
| 40098.1042 | 59.937 | 3766.1226 |  |  |  | 50.3998 | 53.8362 |  | 0.59346 | 3775.7603 | 3786.4425 | 3778.5021 | 3726.5262 | 3702.4912 | 633 | [6 empty] | 0 | 633 | -604.2978 | [13 empty] | 40098.1042 | 59.937 | 3766.1226 | 335 | -228.3652 | 0 | 180.5 | 10 | 0 | -103 | 7592 | 50.3998
| 40098.1042 | 59.945 | 3765.105 |  |  |  | 44.0002 | 50.3936 |  | 0.59346 | 3772.9111 | 3786.1885 | 3778.4355 | 3727.1197 | 3702.788 | 633 | [6 empty] | 0 | 633 | -654.2618 | [13 empty] | 40098.1042 | 59.945 | 3765.105 | 335 | -234.0753 | 0 | 181 | 10 | 0 | -103 | 7592 | 44.0002
| 40098.1043 | 59.945 | 3765.105 |  |  |  | 44.0002 | 48.1559 |  | 0.59346 | 3771.2669 | 3785.9404 | 3778.3512 | 3727.7132 | 3703.0847 | 633 | [6 empty] | 0 | 633 | -654.2618 | [13 empty] | 40098.1043 | 59.945 | 3765.105 | 335 | -234.0753 | 0 | 181 | 10 | 0 | -103 | 7592 | 44.0002
| 40098.1043 | 59.949 | 3758.3872 |  |  |  | 40.799 | 45.581 |  | 0.59346 | 3769.2854 | 3785.6201 | 3778.2458 | 3728.3066 | 3703.3814 | 633 | [6 empty] | 0 | 633 | -682.4898 | [13 empty] | 40098.1043 | 59.949 | 3758.3872 | 335 | -234.0753 | 0 | 181.5 | 10 | 0 | -103 | 7593 | 40.799
| 40098.1043 | 59.942 | 3753.9224 |  |  |  | 46.3989 | 45.8673 |  | 0.59346 | 3770.1652 | 3785.2557 | 3778.1529 | 3728.9001 | 3703.6782 | 633 | [6 empty] | 0 | 633 | -634.5953 | [13 empty] | 40098.1043 | 59.942 | 3753.9224 | 335 | -234.0753 | 0 | 182 | 10 | 0 | -103 | 7594 | 46.3989
| 40098.1043 | 59.942 | 3753.9224 |  |  |  | 46.3989 | 46.0533 |  | 0.59346 | 3770.9447 | 3784.8997 | 3778.071 | 3729.4935 | 3703.9749 | 633 | [6 empty] | 0 | 633 | -634.5953 | [13 empty] | 40098.1043 | 59.942 | 3753.9224 | 335 | -234.0753 | 0 | 182 | 10 | 0 | -103 | 7594 | 46.3989
| 40098.1044 | 59.941 | 3746.8887 |  |  |  | 47.1985 | 46.4541 |  | 0.59346 | 3771.939 | 3784.4726 | 3778.0021 | 3730.087 | 3704.2716 | 633 | [6 empty] | 0 | 633 | -628.2999 | [13 empty] | 40098.1044 | 59.941 | 3746.8887 | 335 | -234.0753 | 0 | 182.5 | 10 | 0 | -103 | 7595 | 47.1985
| 40098.1044 | 59.945 | 3747.8755 |  |  |  | 44.0002 | 45.5953 |  | 0.59346 | 3771.6736 | 3784.0659 | 3777.9318 | 3730.6804 | 3704.5683 | 633 | [6 empty] | 0 | 633 | -654.2618 | [13 empty] | 40098.1044 | 59.945 | 3747.8755 | 335 | -234.0753 | 0 | 183 | 10 | 0 | -103 | 7655 | 44.0002
| 40098.1044 | 59.945 | 3747.8755 |  |  |  | 44.0002 | 45.037 |  | 0.59346 | 3771.7088 | 3783.6682 | 3777.8634 | 3731.2739 | 3704.8651 | 633 | [6 empty] | 0 | 633 | -654.2618 | [13 empty] | 40098.1044 | 59.945 | 3747.8755 | 335 | -234.0753 | 0 | 183 | 10 | 0 | -103 | 7655 | 44.0002
| 40098.1044 | 59.948 | 3748.6611 |  |  |  | 41.5985 | 43.8335 |  | 0.59346 | 3771.0987 | 3783.2877 | 3777.7899 | 3731.8673 | 3705.1618 | 633 | [6 empty] | 0 | 633 | -675.2137 | [13 empty] | 40098.1044 | 59.948 | 3748.6611 | 335 | -228.7982 | 0 | 183.5 | 10 | 0 | -103 | 7656 | 41.5985
| 40098.1045 | 59.949 | 3746.7061 |  |  |  | 40.799 | 42.7714 |  | 0.59346 | 3770.6301 | 3782.8944 | 3777.7129 | 3732.4608 | 3705.4585 | 633 | [6 empty] | 0 | 633 | -682.4898 | [13 empty] | 40098.1045 | 59.949 | 3746.7061 | 335 | -228.7982 | 0 | 184 | 10 | 0 | -103 | 7656 | 40.799
| 40098.1045 | 59.949 | 3746.7061 |  |  |  | 40.799 | 42.0811 |  | 0.59346 | 3770.5332 | 3782.5094 | 3777.6365 | 3733.0543 | 3705.7553 | 633 | [6 empty] | 0 | 633 | -682.4898 | [13 empty] | 40098.1045 | 59.949 | 3746.7061 | 335 | -228.7982 | 0 | 184 | 10 | 0 | -103 | 7656 | 40.799
| 40098.1045 | 59.951 | 3742.7415 |  |  |  | 39.1998 | 41.0726 |  | 0.59346 | 3770.1182 | 3782.0908 | 3777.5574 | 3733.6477 | 3706.052 | 633 | [6 empty] | 0 | 633 | -697.5227 | [13 empty] | 40098.1045 | 59.951 | 3742.7415 | 335 | -228.7982 | 0 | 184.5 | 10 | 0 | -103 | 7657 | 39.1998
| 40098.1045 | 59.953 | 3740.259 |  |  |  | 37.6007 | 39.8575 |  | 0.59346 | 3769.4965 | 3781.655 | 3777.4734 | 3734.2412 | 3706.3487 | 633 | [6 empty] | 0 | 633 | -713.2327 | [13 empty] | 40098.1045 | 59.953 | 3740.259 | 335 | -228.7982 | 0 | 185 | 10 | 0 | -103 | 7657 | 37.6007
| 40098.1045 | 59.953 | 3740.259 |  |  |  | 37.6007 | 39.0676 |  | 0.59346 | 3769.3001 | 3781.2283 | 3777.3891 | 3734.8346 | 3706.6454 | 633 | [6 empty] | 0 | 633 | -713.2327 | [13 empty] | 40098.1045 | 59.953 | 3740.259 | 335 | -228.7982 | 0 | 185 | 10 | 0 | -103 | 7657 | 37.6007
| 40098.1046 | 59.951 | 3731.3821 |  |  |  | 39.1998 | 39.1139 |  | 0.59346 | 3769.9398 | 3780.7196 | 3777.3131 | 3735.4281 | 3706.9422 | 633 | [6 empty] | 0 | 633 | -697.5227 | [13 empty] | 40098.1046 | 59.951 | 3731.3821 | 335 | -228.7982 | 0 | 185.5 | 10 | 0 | -103 | 7658 | 39.1998
| 40098.1046 | 59.952 | 3727.8384 |  |  |  | 38.4003 | 38.8641 |  | 0.59346 | 3770.2835 | 3780.1855 | 3777.2421 | 3736.0215 | 3707.2389 | 633 | [6 empty] | 0 | 633 | -705.2902 | [13 empty] | 40098.1046 | 59.952 | 3727.8384 | 335 | -229.467 | 0 | 186 | 10 | 0 | -103 | 7658 | 38.4003
| 40098.1046 | 59.952 | 3727.8384 |  |  |  | 38.4003 | 38.7018 |  | 0.59346 | 3770.7146 | 3779.662 | 3777.1768 | 3736.615 | 3707.5356 | 633 | [6 empty] | 0 | 633 | -705.2902 | [13 empty] | 40098.1046 | 59.952 | 3727.8384 | 335 | -229.467 | 0 | 186 | 10 | 0 | -103 | 7658 | 38.4003
| 40098.1046 | 59.952 | 3722.6489 |  |  |  | 38.4003 | 38.5962 |  | 0.59346 | 3771.2026 | 3779.0975 | 3777.1177 | 3737.2085 | 3707.8324 | 633 | [6 empty] | 0 | 633 | -705.2902 | [13 empty] | 40098.1046 | 59.952 | 3722.6489 | 335 | -249.3376 | 0 | 186.5 | 10 | 0 | -103 | 7659 | 38.4003
| 40098.1047 | 59.952 | 3720.5781 |  |  |  | 38.4003 | 38.5277 |  | 0.59346 | 3771.7274 | 3778.5238 | 3777.0648 | 3737.8019 | 3708.1291 | 633 | [6 empty] | 0 | 633 | -705.2902 | [13 empty] | 40098.1047 | 59.952 | 3720.5781 | 335 | -249.3376 | 0 | 187 | 10 | 0 | -103 | 7659 | 38.4003
| 40098.1047 | 59.952 | 3720.5781 |  |  |  | 38.4003 | 38.4831 |  | 0.59346 | 3772.2763 | 3777.9612 | 3777.0183 | 3738.3954 | 3708.4258 | 633 | [6 empty] | 0 | 633 | -705.2902 | [13 empty] | 40098.1047 | 59.952 | 3720.5781 | 335 | -249.3376 | 0 | 187 | 10 | 0 | -103 | 7659 | 38.4003
| 40098.1047 | 59.954 | 3718.1418 |  |  |  | 36.8011 | 37.8944 |  | 0.59346 | 3772.2811 | 3777.386 | 3776.9728 | 3738.9888 | 3708.7225 | 633 | [6 empty] | 0 | 633 | -721.3561 | [13 empty] | 40098.1047 | 59.954 | 3718.1418 | 335 | -249.3376 | 0 | 187.5 | 10 | 0 | -103 | 7659 | 36.8011
| 40098.1047 | 59.953 | 3715.7527 |  |  |  | 37.6007 | 37.7916 |  | 0.59346 | 3772.7717 | 3776.7991 | 3776.9328 | 3739.5823 | 3709.0193 | 633 | [6 empty] | 0 | 633 | -713.2327 | [13 empty] | 40098.1047 | 59.953 | 3715.7527 | 335 | -249.3376 | 0 | 188 | 10 | 0 | -103 | 7660 | 37.6007
| 40098.1048 | 59.953 | 3715.7527 |  |  |  | 37.6007 | 37.7248 |  | 0.59346 | 3773.2984 | 3776.2231 | 3776.8985 | 3740.1757 | 3709.316 | 633 | [6 empty] | 0 | 633 | -713.2327 | [13 empty] | 40098.1048 | 59.953 | 3715.7527 | 335 | -249.3376 | 0 | 188 | 10 | 0 | -103 | 7660 | 37.6007
| 40098.1048 | 59.953 | 3713.4836 |  |  |  | 37.6007 | 37.6814 |  | 0.59346 | 3773.8484 | 3775.6368 | 3776.87 | 3740.7692 | 3709.6127 | 633 | [6 empty] | 0 | 633 | -713.2327 | [13 empty] | 40098.1048 | 59.953 | 3713.4836 | 335 | -249.3376 | 0 | 188.5 | 10 | 0 | -103 | 7660 | 37.6007
| 40098.1048 | 59.954 | 3710.8481 |  |  |  | 36.8011 | 37.3733 |  | 0.59346 | 3774.1338 | 3775.0369 | 3776.8447 | 3741.3627 | 3709.9094 | 633 | [6 empty] | 0 | 633 | -721.3561 | [13 empty] | 40098.1048 | 59.954 | 3710.8481 | 335 | -258.2782 | 0 | 189 | 10 | 0 | -103 | 7661 | 36.8011
| 40098.1048 | 59.954 | 3710.8481 |  |  |  | 36.8011 | 37.173 |  | 0.59346 | 3774.527 | 3774.448 | 3776.8234 | 3741.9561 | 3710.2062 | 633 | [6 empty] | 0 | 633 | -721.3561 | [13 empty] | 40098.1048 | 59.954 | 3710.8481 | 335 | -258.2782 | 0 | 189 | 10 | 0 | -103 | 7661 | 36.8011
| 40098.1048 | 59.954 | 3712.0918 |  |  |  | 36.8011 | 37.0429 |  | 0.59346 | 3774.9903 | 3773.8811 | 3776.8067 | 3742.5496 | 3710.5029 | 633 | [6 empty] | 0 | 633 | -721.3561 | [13 empty] | 40098.1048 | 59.954 | 3712.0918 | 335 | -258.2782 | 0 | 189.5 | 10 | 0 | -103 | 7661 | 36.8011
| 40098.1049 | 59.957 | 3714.6226 |  |  |  | 34.3994 | 36.1177 |  | 0.59346 | 3774.6585 | 3773.3473 | 3776.7874 | 3743.143 | 3710.7996 | 633 | [6 empty] | 0 | 633 | -746.9095 | [13 empty] | 40098.1049 | 59.957 | 3714.6226 | 335 | -258.2782 | 0 | 190 | 10 | 0 | -103 | 7625.4 | 34.3994
| 40098.1049 | 59.957 | 3714.6226 |  |  |  | 34.3994 | 35.5163 |  | 0.59346 | 3774.6506 | 3772.8229 | 3776.7683 | 3743.7365 | 3711.0964 | 633 | [6 empty] | 0 | 633 | -746.9095 | [13 empty] | 40098.1049 | 59.957 | 3714.6226 | 335 | -258.2782 | 0 | 190 | 10 | 0 | -103 | 7625.4 | 34.3994
| 40098.1049 | 59.956 | 3716.1682 |  |  |  | 35.199 | 35.4052 |  | 0.59346 | 3775.133 | 3772.3216 | 3776.7538 | 3744.3299 | 3711.3931 | 633 | [6 empty] | 0 | 633 | -738.2038 | [13 empty] | 40098.1049 | 59.956 | 3716.1682 | 335 | -258.2782 | 0 | 190.5 | 10 | 0 | -103 | 7625.73 | 35.199
| 40098.1049 | 59.956 | 3716.4614 |  |  |  | 35.199 | 35.333 |  | 0.59346 | 3775.6543 | 3771.8316 | 3776.7442 | 3744.9234 | 3711.6898 | 633 | [6 empty] | 0 | 633 | -738.2038 | [13 empty] | 40098.1049 | 59.956 | 3716.4614 | 335 | -258.2782 | 0 | 191 | 10 | 0 | -103 | 7626.06 | 35.199
| 40098.105 | 59.956 | 3716.4614 |  |  |  | 35.199 | 35.2861 |  | 0.59346 | 3776.2008 | 3771.3501 | 3776.7395 | 3745.5169 | 3711.9865 | 633 | [6 empty] | 0 | 633 | -738.2038 | [13 empty] | 40098.105 | 59.956 | 3716.4614 | 335 | -258.2782 | 0 | 191 | 10 | 0 | -103 | 7626.06 | 35.199
| 40098.105 | 59.955 | 3717.759 |  |  |  | 35.9985 | 35.5355 |  | 0.59346 | 3777.0436 | 3770.8881 | 3776.7421 | 3746.1103 | 3712.2833 | 633 | [6 empty] | 0 | 633 | -729.6988 | [13 empty] | 40098.105 | 59.955 | 3717.759 | 335 | -258.4064 | 0 | 191.5 | 10 | 0 | -103 | 7626.39 | 35.9985
| 40098.105 | 59.961 | 3722.3613 |  |  |  | 31.2012 | 34.0185 |  | 0.59346 | 3776.1201 | 3770.4733 | 3776.7368 | 3746.7038 | 3712.58 | 633 | [6 empty] | 0 | 633 | -783.8872 | [13 empty] | 40098.105 | 59.961 | 3722.3613 | 335 | -258.4064 | 0 | 192 | 10 | 0 | -103 | 7626.72 | 31.2012
| 40098.105 | 59.961 | 3722.3613 |  |  |  | 31.2012 | 33.0324 |  | 0.59346 | 3775.7275 | 3770.0656 | 3776.7282 | 3747.2972 | 3712.8767 | 633 | [6 empty] | 0 | 633 | -783.8872 | [13 empty] | 40098.105 | 59.961 | 3722.3613 | 335 | -258.4064 | 0 | 192 | 10 | 0 | -103 | 7626.72 | 31.2012
| 40098.1051 | 59.962 | 3722.658 |  |  |  | 30.3986 | 32.1106 |  | 0.59346 | 3775.3991 | 3769.6672 | 3776.717 | 3747.8907 | 3713.1735 | 633 | [6 empty] | 0 | 633 | -793.7488 | [13 empty] | 40098.1051 | 59.962 | 3722.658 | 335 | -258.4064 | 0 | 192.5 | 10 | 0 | -103 | 7627.05 | 30.3986
| 40098.1051 | 59.968 | 3722.2666 |  |  |  | 25.6012 | 29.8323 |  | 0.59346 | 3773.7143 | 3769.2722 | 3776.692 | 3748.4841 | 3713.4702 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1051 | 59.968 | 3722.2666 | 335 | -258.4064 | 0 | 193 | 10 | 0 | -103 | 7627.38 | 25.6012
| 40098.1051 | 59.968 | 3722.2666 |  |  |  | 25.6012 | 28.3514 |  | 0.59346 | 3772.8268 | 3768.8838 | 3776.6601 | 3749.0776 | 3713.7669 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1051 | 59.968 | 3722.2666 | 335 | -258.4064 | 0 | 193 | 10 | 0 | -103 | 7627.38 | 25.6012
| 40098.1051 | 59.966 | 3721.7866 |  |  |  | 27.2003 | 27.9485 |  | 0.59346 | 3773.0174 | 3768.4977 | 3776.6302 | 3749.671 | 3714.0636 | 633 | [6 empty] | 0 | 633 | -835.6397 | [13 empty] | 40098.1051 | 59.966 | 3721.7866 | 335 | -258.4064 | 0 | 193.5 | 10 | 0 | -103 | 7627.71 | 27.2003
| 40098.1052 | 59.968 | 3723.0908 |  |  |  | 25.6012 | 27.127 |  | 0.59346 | 3772.7893 | 3768.1285 | 3776.599 | 3750.2645 | 3714.3604 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1052 | 59.968 | 3723.0908 | 335 | -260.5389 | 0 | 194 | 10 | 0 | -103 | 7628.04 | 25.6012
| 40098.1052 | 59.968 | 3723.0908 |  |  |  | 25.6012 | 26.5929 |  | 0.59346 | 3772.8488 | 3767.7653 | 3776.5687 | 3750.858 | 3714.6571 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1052 | 59.968 | 3723.0908 | 335 | -260.5389 | 0 | 194 | 10 | 0 | -103 | 7628.04 | 25.6012
| 40098.1052 | 59.97 | 3723.4346 |  |  |  | 23.999 | 25.6851 |  | 0.59346 | 3772.5343 | 3767.4107 | 3776.5365 | 3751.4514 | 3714.9538 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1052 | 59.97 | 3723.4346 | 335 | -260.5389 | 0 | 194.5 | 10 | 0 | -103 | 7628.37 | 23.999
| 40098.1052 | 59.97 | 3723.8931 |  |  |  | 23.999 | 25.095 |  | 0.59346 | 3772.5377 | 3767.0653 | 3776.5047 | 3752.0449 | 3715.2506 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1052 | 59.97 | 3723.8931 | 335 | -260.5389 | 0 | 195 | 10 | 0 | -103 | 7628.7 | 23.999
| 40098.1052 | 59.97 | 3723.8931 |  |  |  | 23.999 | 24.7114 |  | 0.59346 | 3772.7476 | 3766.7254 | 3776.4752 | 3752.6383 | 3715.5473 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1052 | 59.97 | 3723.8931 | 335 | -260.5389 | 0 | 195 | 10 | 0 | -103 | 7628.7 | 23.999
| 40098.1053 | 59.969 | 3727.1211 |  |  |  | 24.7986 | 24.7419 |  | 0.59346 | 3773.3715 | 3766.416 | 3776.4509 | 3753.2318 | 3715.844 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1053 | 59.969 | 3727.1211 | 335 | -260.5389 | 0 | 195.5 | 10 | 0 | -103 | 7629.03 | 24.7986
| 40098.1053 | 59.97 | 3728.053 |  |  |  | 23.999 | 24.4819 |  | 0.59346 | 3773.705 | 3766.1186 | 3776.4296 | 3753.8252 | 3716.1407 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1053 | 59.97 | 3728.053 | 335 | -260.5389 | 0 | 196 | 10 | 0 | -103 | 7629.36 | 23.999
| 40098.1053 | 59.97 | 3728.053 |  |  |  | 23.999 | 24.3129 |  | 0.59346 | 3774.1294 | 3765.8258 | 3776.4119 | 3754.4187 | 3716.4375 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1053 | 59.97 | 3728.053 | 335 | -260.5389 | 0 | 196 | 10 | 0 | -103 | 7629.36 | 23.999
| 40098.1053 | 59.971 | 3732.53 |  |  |  | 23.1995 | 23.9232 |  | 0.59346 | 3774.3332 | 3765.5716 | 3776.3961 | 3755.0122 | 3716.7342 | 633 | [6 empty] | 0 | 633 | -894.7087 | [13 empty] | 40098.1053 | 59.971 | 3732.53 | 335 | -257.8821 | 0 | 196.5 | 10 | 0 | -103 | 7629.69 | 23.1995
| 40098.1054 | 59.973 | 3733.3271 |  |  |  | 21.6003 | 23.1102 |  | 0.59346 | 3774.1137 | 3765.3273 | 3776.3788 | 3755.6056 | 3717.0309 | 633 | [6 empty] | 0 | 633 | -920.7222 | [13 empty] | 40098.1054 | 59.973 | 3733.3271 | 335 | -257.8821 | 0 | 197 | 10 | 0 | -103 | 7630.02 | 21.6003
| 40098.1054 | 59.973 | 3733.3271 |  |  |  | 21.6003 | 22.5817 |  | 0.59346 | 3774.1787 | 3765.0867 | 3776.3622 | 3756.1991 | 3717.3277 | 633 | [6 empty] | 0 | 633 | -920.7222 | [13 empty] | 40098.1054 | 59.973 | 3733.3271 | 335 | -257.8821 | 0 | 197 | 10 | 0 | -103 | 7630.02 | 21.6003
| 40098.1054 | 59.976 | 3736.9075 |  |  |  | 19.1986 | 21.3976 |  | 0.59346 | 3773.588 | 3764.8764 | 3776.3415 | 3756.7925 | 3717.6244 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.1054 | 59.976 | 3736.9075 | 335 | -257.8821 | 0 | 197.5 | 10 | 0 | -103 | 7630.35 | 19.1986
| 40098.1054 | 59.978 | 3736.8218 |  |  |  | 17.5995 | 20.0683 |  | 0.59346 | 3772.8521 | 3764.6686 | 3776.3157 | 3757.386 | 3717.9211 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1054 | 59.978 | 3736.8218 | 335 | -257.8821 | 0 | 198 | 10 | 0 | -103 | 7630.68 | 17.5995
| 40098.1055 | 59.978 | 3736.8218 |  |  |  | 17.5995 | 19.2042 |  | 0.59346 | 3772.5815 | 3764.4639 | 3776.2882 | 3757.9794 | 3718.2178 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1055 | 59.978 | 3736.8218 | 335 | -257.8821 | 0 | 198 | 10 | 0 | -103 | 7630.68 | 17.5995
| 40098.1055 | 59.976 | 3739.9438 |  |  |  | 19.1986 | 19.2022 |  | 0.59346 | 3773.173 | 3764.2849 | 3776.2655 | 3758.5729 | 3718.5146 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.1055 | 59.976 | 3739.9438 | 335 | -257.8821 | 0 | 198.5 | 10 | 0 | -103 | 7631.01 | 19.1986
| 40098.1055 | 59.976 | 3740.877 |  |  |  | 19.1986 | 19.201 |  | 0.59346 | 3773.7652 | 3764.1153 | 3776.2474 | 3759.1664 | 3718.8113 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.1055 | 59.976 | 3740.877 | 335 | -258.5887 | 0 | 199 | 10 | 0 | -103 | 7631.34 | 19.1986
| 40098.1055 | 59.976 | 3740.877 |  |  |  | 19.1986 | 19.2001 |  | 0.59346 | 3774.3578 | 3763.9481 | 3776.2338 | 3759.7598 | 3719.108 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.1055 | 59.976 | 3740.877 | 335 | -258.5887 | 0 | 199 | 10 | 0 | -103 | 7631.34 | 19.1986
| 40098.1055 | 59.978 | 3745.2336 |  |  |  | 17.5995 | 18.6399 |  | 0.59346 | 3774.391 | 3763.8144 | 3776.2206 | 3760.3533 | 3719.4048 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1055 | 59.978 | 3745.2336 | 335 | -258.5887 | 0 | 199.5 | 10 | 0 | -103 | 7631.67 | 17.5995
| 40098.1056 | 59.98 | 3746.6079 |  |  |  | 16.0004 | 17.7161 |  | 0.59346 | 3774.0607 | 3763.6924 | 3776.2053 | 3760.9467 | 3719.7015 | 633 | [6 empty] | 0 | 633 | -1025.0944 | [13 empty] | 40098.1056 | 59.98 | 3746.6079 | 335 | -258.5887 | 0 | 200 | 10 | 0 | -103 | 7632 | 16.0004
| 40098.1056 | 59.98 | 3746.6079 |  |  |  | 16.0004 | 17.1156 |  | 0.59346 | 3774.0536 | 3763.5721 | 3776.1901 | 3761.5402 | 3719.9982 | 633 | [6 empty] | 0 | 633 | -1025.0944 | [13 empty] | 40098.1056 | 59.98 | 3746.6079 | 335 | -258.5887 | 0 | 200 | 10 | 0 | -103 | 7632 | 16.0004
| 40098.1056 | 59.982 | 3750.7163 |  |  |  | 14.4012 | 16.1656 |  | 0.59346 | 3773.6971 | 3763.4822 | 3776.1727 | 3762.1336 | 3720.2949 | 633 | [6 empty] | 0 | 633 | -1059.3874 | [13 empty] | 40098.1056 | 59.982 | 3750.7163 | 335 | -258.5887 | 0 | 200.5 | 10 | 0 | -103 | 7632.33 | 14.4012
| 40098.1056 | 59.98 | 3751.5576 |  |  |  | 16.0004 | 16.1077 |  | 0.59346 | 3774.2327 | 3763.3993 | 3776.1592 | 3762.7271 | 3720.5917 | 633 | [6 empty] | 0 | 633 | -1025.0944 | [13 empty] | 40098.1056 | 59.98 | 3751.5576 | 335 | -258.5887 | 0 | 201 | 10 | 0 | -103 | 7632.66 | 16.0004
| 40098.1057 | 59.98 | 3751.5576 |  |  |  | 16.0004 | 16.0702 |  | 0.59346 | 3774.7886 | 3763.3177 | 3776.1498 | 3763.3206 | 3720.8884 | 633 | [6 empty] | 0 | 633 | -1025.0944 | [13 empty] | 40098.1057 | 59.98 | 3751.5576 | 335 | -258.5887 | 0 | 201 | 10 | 0 | -103 | 7632.66 | 16.0004
| 40098.1057 | 59.979 | 3755.5986 |  |  |  | 16.7999 | 16.3256 |  | 0.59346 | 3775.6374 | 3763.2648 | 3776.1463 | 3763.914 | 3721.1851 | 633 | [6 empty] | 0 | 633 | -1008.7671 | [13 empty] | 40098.1057 | 59.979 | 3755.5986 | 335 | -261.9062 | 0 | 201.5 | 10 | 0 | -103 | 7632.99 | 16.7999
| 40098.1057 | 59.979 | 3756.4072 |  |  |  | 16.7999 | 16.4916 |  | 0.59346 | 3776.3969 | 3763.2182 | 3776.148 | 3764.5075 | 3721.4819 | 633 | [6 empty] | 0 | 633 | -1008.7671 | [13 empty] | 40098.1057 | 59.979 | 3756.4072 | 335 | -261.9062 | 0 | 202 | 10 | 0 | -103 | 7633.32 | 16.7999
| 40098.1057 | 59.979 | 3756.4072 |  |  |  | 16.7999 | 16.5995 |  | 0.59346 | 3777.0983 | 3763.1721 | 3776.1544 | 3765.1009 | 3721.7786 | 633 | [6 empty] | 0 | 633 | -1008.7671 | [13 empty] | 40098.1057 | 59.979 | 3756.4072 | 335 | -261.9062 | 0 | 202 | 10 | 0 | -103 | 7633.32 | 16.7999
| 40098.1058 | 59.983 | 3760.4053 |  |  |  | 13.5986 | 15.5492 |  | 0.59346 | 3776.6414 | 3763.1536 | 3776.1577 | 3765.6944 | 3722.0753 | 633 | [6 empty] | 0 | 633 | -1077.479 | [13 empty] | 40098.1058 | 59.983 | 3760.4053 | 335 | -261.9062 | 0 | 202.5 | 10 | 0 | -103 | 7633.65 | 13.5986
| 40098.1058 | 59.984 | 3760.9822 |  |  |  | 12.7991 | 14.5867 |  | 0.59346 | 3776.2723 | 3763.1391 | 3776.1584 | 3766.2878 | 3722.372 | 633 | [6 empty] | 0 | 633 | -1096.1268 | [13 empty] | 40098.1058 | 59.984 | 3760.9822 | 335 | -261.9062 | 0 | 203 | 10 | 0 | -103 | 7633.98 | 12.7991
| 40098.1058 | 59.984 | 3760.9822 |  |  |  | 12.7991 | 13.961 |  | 0.59346 | 3776.2402 | 3763.1248 | 3776.159 | 3766.8813 | 3722.6688 | 633 | [6 empty] | 0 | 633 | -1096.1268 | [13 empty] | 40098.1058 | 59.984 | 3760.9822 | 335 | -261.9062 | 0 | 203 | 10 | 0 | -103 | 7633.98 | 12.7991
| 40098.1058 | 59.988 | 3762.7373 |  |  |  | 9.6008 | 12.4349 |  | 0.59346 | 3775.3075 | 3763.1223 | 3776.1534 | 3767.4747 | 3722.9655 | 633 | [6 empty] | 0 | 633 | -1177.6527 | [13 empty] | 40098.1058 | 59.988 | 3762.7373 | 335 | -261.9062 | 0 | 203.5 | 10 | 0 | -103 | 7634.31 | 9.6008
| 40098.1058 | 59.987 | 3763.2122 |  |  |  | 10.4004 | 11.7228 |  | 0.59346 | 3775.1889 | 3763.1229 | 3776.1471 | 3768.0682 | 3723.2622 | 633 | [6 empty] | 0 | 633 | -1156.155 | [13 empty] | 40098.1058 | 59.987 | 3763.2122 | 335 | -256.7478 | 0 | 204 | 10 | 0 | -103 | 7634.64 | 10.4004
| 40098.1059 | 59.987 | 3763.2122 |  |  |  | 10.4004 | 11.26 |  | 0.59346 | 3775.3195 | 3763.1234 | 3776.1417 | 3768.6617 | 3723.559 | 633 | [6 empty] | 0 | 633 | -1156.155 | [13 empty] | 40098.1059 | 59.987 | 3763.2122 | 335 | -256.7478 | 0 | 204 | 10 | 0 | -103 | 7634.64 | 10.4004
| 40098.1059 | 59.987 | 3766.0852 |  |  |  | 10.4004 | 10.9591 |  | 0.59346 | 3775.6121 | 3763.1425 | 3776.1383 | 3769.2551 | 3723.8557 | 633 | [6 empty] | 0 | 633 | -1156.155 | [13 empty] | 40098.1059 | 59.987 | 3766.0852 | 335 | -256.7478 | 0 | 204.5 | 10 | 0 | -103 | 7634.97 | 10.4004
| 40098.1059 | 59.993 | 3766.4331 |  |  |  | 5.6 | 9.0834 |  | 0.59346 | 3774.3299 | 3763.1636 | 3776.1267 | 3769.8486 | 3724.1524 | 633 | [6 empty] | 0 | 633 | -1298.4636 | [13 empty] | 40098.1059 | 59.993 | 3766.4331 | 335 | -256.7478 | 0 | 205 | 10 | 0 | -103 | 7635.3 | 5.6
| 40098.1059 | 59.993 | 3766.4331 |  |  |  | 5.6 | 7.8642 |  | 0.59346 | 3773.7041 | 3763.1845 | 3776.1112 | 3770.442 | 3724.4491 | 633 | [6 empty] | 0 | 633 | -1298.4636 | [13 empty] | 40098.1059 | 59.993 | 3766.4331 | 335 | -256.7478 | 0 | 205 | 10 | 0 | -103 | 7635.3 | 5.6
| 40098.106 | 59.992 | 3767.7925 |  |  |  | 6.3995 | 7.3516 |  | 0.59346 | 3773.7849 | 3763.2136 | 3776.0965 | 3771.0355 | 3724.7459 | 633 | [6 empty] | 0 | 633 | -1272.3778 | [13 empty] | 40098.106 | 59.992 | 3767.7925 | 335 | -256.7478 | 0 | 205.5 | 10 | 0 | -103 | 7635.63 | 6.3995
| 40098.106 | 59.989 | 3768.6335 |  |  |  | 8.8013 | 7.859 |  | 0.59346 | 3774.8858 | 3763.2477 | 3776.0889 | 3771.6289 | 3725.0426 | 633 | [6 empty] | 0 | 633 | -1199.9649 | [13 empty] | 40098.106 | 59.989 | 3768.6335 | 335 | -256.7478 | 0 | 206 | 10 | 0 | -103 | 7635.96 | 8.8013
| 40098.106 | 59.989 | 3768.6335 |  |  |  | 8.8013 | 8.1888 |  | 0.59346 | 3775.809 | 3763.2814 | 3776.0872 | 3772.2224 | 3725.3393 | 633 | [6 empty] | 0 | 633 | -1199.9649 | [13 empty] | 40098.106 | 59.989 | 3768.6335 | 335 | -256.7478 | 0 | 206 | 10 | 0 | -103 | 7635.96 | 8.8013
| 40098.106 | 59.986 | 3772.4446 |  |  |  | 11.2 | 9.2427 |  | 0.59346 | 3777.4564 | 3763.3383 | 3776.0957 | 3772.8159 | 3725.6361 | 633 | [6 empty] | 0 | 633 | -1135.4282 | [13 empty] | 40098.106 | 59.986 | 3772.4446 | 335 | -167.432 | 0 | 206.5 | 10 | 0 | -103 | 7636.29 | 11.2
| 40098.1061 | 59.983 | 3773.6948 |  |  |  | 13.5986 | 10.7673 |  | 0.59346 | 3779.5744 | 3763.4022 | 3776.1171 | 3773.4093 | 3725.9328 | 633 | [6 empty] | 0 | 633 | -1077.479 | [13 empty] | 40098.1061 | 59.983 | 3773.6948 | 335 | -167.432 | 0 | 207 | 10 | 0 | -103 | 7636.62 | 13.5986
| 40098.1061 | 59.983 | 3773.6948 |  |  |  | 13.5986 | 11.7582 |  | 0.59346 | 3781.1589 | 3763.4654 | 3776.1481 | 3774.0028 | 3726.2295 | 633 | [6 empty] | 0 | 633 | -1077.479 | [13 empty] | 40098.1061 | 59.983 | 3773.6948 | 335 | -167.432 | 0 | 207 | 10 | 0 | -103 | 7636.62 | 13.5986
| 40098.1061 | 59.988 | 3775.8408 |  |  |  | 9.6008 | 11.0032 |  | 0.59346 | 3780.9972 | 3763.5408 | 3776.1776 | 3774.5962 | 3726.5262 | 633 | [6 empty] | 0 | 633 | -1177.6527 | [13 empty] | 40098.1061 | 59.988 | 3775.8408 | 335 | -167.432 | 0 | 207.5 | 10 | 0 | -103 | 7636.95 | 9.6008
| 40098.1061 | 59.996 | 3775.3633 |  |  |  | 3.2013 | 8.2725 |  | 0.59346 | 3778.86 | 3763.6125 | 3776.1939 | 3775.1897 | 3726.823 | 633 | [6 empty] | 0 | 633 | -1383.559 | [13 empty] | 40098.1061 | 59.996 | 3775.3633 | 335 | -167.432 | 0 | 208 | 10 | 0 | -103 | 7637.28 | 3.2013
| 40098.1061 | 59.996 | 3775.3633 |  |  |  | 3.2013 | 6.4976 |  | 0.59346 | 3777.6786 | 3763.6833 | 3776.2028 | 3775.7831 | 3727.1197 | 633 | [6 empty] | 0 | 633 | -1383.559 | [13 empty] | 40098.1061 | 59.996 | 3775.3633 | 335 | -167.432 | 0 | 208 | 10 | 0 | -103 | 7637.28 | 3.2013
| 40098.1062 | 59.998 | 3775.4917 |  |  |  | 1.5991 | 4.7831 |  | 0.59346 | 3776.5576 | 3763.754 | 3776.205 | 3776.3766 | 3727.4164 | 633 | [6 empty] | 0 | 633 | -1446.895 | [13 empty] | 40098.1062 | 59.998 | 3775.4917 | 335 | -167.432 | 0 | 208.5 | 10 | 0 | -103 | 7637.61 | 1.5991
| 40098.1062 | 60.001 | 3776.4202 |  |  |  | -0.79956 | 2.8292 |  | 0.59346 | 3775.1971 | 3763.8294 | 3776.199 | 3776.9701 | 3727.7132 | 633 | [6 empty] | 0 | 633 | -1553.355 | [13 empty] | 40098.1062 | 60.001 | 3776.4202 | 335 | -164.9734 | 0 | 209 | 10 | 0 | -103 | 7637.94 | -0.79956
| 40098.1062 | 60.001 | 3776.4202 |  |  |  | -0.79956 | 1.5591 |  | 0.59346 | 3774.5205 | 3763.9039 | 3776.189 | 3777.5635 | 3728.0099 | 633 | [6 empty] | 0 | 633 | -1553.355 | [13 empty] | 40098.1062 | 60.001 | 3776.4202 | 335 | -164.9734 | 0 | 209 | 10 | 0 | -103 | 7637.94 | -0.79956
| 40098.1062 | 59.999 | 3779.6919 |  |  |  | 0.79956 | 1.2933 |  | 0.59346 | 3774.8481 | 3763.9967 | 3776.1811 | 3778.157 | 3728.3066 | 633 | [6 empty] | 0 | 633 | -1480.7224 | [13 empty] | 40098.1062 | 59.999 | 3779.6919 | 335 | -164.9734 | 0 | 209.5 | 10 | 0 | -103 | 7638.27 | 0.79956
| 40098.1063 | 59.999 | 3781.2559 |  |  |  | 0.79956 | 1.1205 |  | 0.59346 | 3775.2688 | 3764.0977 | 3776.1758 | 3778.7504 | 3728.6033 | 633 | [6 empty] | 0 | 633 | -1480.7224 | [13 empty] | 40098.1063 | 59.999 | 3781.2559 | 335 | -164.9734 | 0 | 210 | 10 | 0 | -103 | 7638.6 | 0.79956
| 40098.1063 | 59.999 | 3781.2559 |  |  |  | 0.79956 | 1.0082 |  | 0.59346 | 3775.7499 | 3764.1974 | 3776.1733 | 3779.3439 | 3728.9001 | 633 | [6 empty] | 0 | 633 | -1480.7224 | [13 empty] | 40098.1063 | 59.999 | 3781.2559 | 335 | -164.9734 | 0 | 210 | 10 | 0 | -103 | 7638.6 | 0.79956
| 40098.1063 | 60.002 | 3783.092 |  |  |  | -1.5991 | 0.095608 |  | 0 | 3774.8373 | 3764.3066 | 3776.1656 | 3779.3439 | 3729.1933 | 633 | [6 empty] | 0 | 633 | -1592.4107 | [13 empty] | 40098.1063 | 60.002 | 3783.092 | 335 | -164.9734 | 0 | 210.5 | 10 | 0 | -103 | 7638.93 | -1.5991
| 40098.1063 | 60.007 | 3783.8955 |  |  |  | -5.6 | -1.8978 |  | 0 | 3772.8439 | 3764.4192 | 3776.1465 | 3779.3439 | 3729.4832 | 633 | [6 empty] | 0 | 633 | -1821.5835 | [13 empty] | 40098.1063 | 60.007 | 3783.8955 | 335 | -164.9734 | 0 | 211 | 10 | 0 | -103 | 7639.26 | -5.6
| 40098.1064 | 60.007 | 3783.8955 |  |  |  | -5.6 | -3.1936 |  | 0 | 3771.5481 | 3764.5305 | 3776.1202 | 3779.3439 | 3729.7698 | 633 | [6 empty] | 0 | 633 | -1821.5835 | [13 empty] | 40098.1064 | 60.007 | 3783.8955 | 335 | -164.9734 | 0 | 211 | 10 | 0 | -103 | 7639.26 | -5.6
| 40098.1064 | 60.008 | 3785.7681 |  |  |  | -6.3995 | -4.3157 |  | 0 | 3770.4261 | 3764.6512 | 3776.0879 | 3779.3439 | 3730.0531 | 633 | [6 empty] | 0 | 633 | -1875.5259 | [13 empty] | 40098.1064 | 60.008 | 3785.7681 | 335 | -157.6281 | 0 | 211.5 | 10 | 0 | -103 | 7639.59 | -6.3995
| 40098.1064 | 60.014 | 3785.4626 |  |  |  | -11.2 | -6.7252 |  | 0 | 3768.0166 | 3764.7688 | 3776.0423 | 3779.3439 | 3730.3331 | 633 | [6 empty] | 0 | 633 | -2281.0798 | [13 empty] | 40098.1064 | 60.014 | 3785.4626 | 335 | -157.6281 | 0 | 212 | 10 | 0 | -103 | 7639.92 | -11.2
| 40098.1064 | 60.014 | 3785.4626 |  |  |  | -11.2 | -8.2913 |  | 0 | 3766.4504 | 3764.885 | 3775.9884 | 3779.3439 | 3730.61 | 633 | [6 empty] | 0 | 633 | -2281.0798 | [13 empty] | 40098.1064 | 60.014 | 3785.4626 | 335 | -157.6281 | 0 | 212 | 10 | 0 | -103 | 7639.92 | -11.2
| 40098.1064 | 60.017 | 3786.3042 |  |  |  | -13.5986 | -10.1489 |  | 0 | 3764.5928 | 3765.0047 | 3775.9247 | 3779.3439 | 3730.8838 | 633 | [6 empty] | 0 | 633 | -2557.4039 | [13 empty] | 40098.1064 | 60.017 | 3786.3042 | 335 | -157.6281 | 0 | 212.5 | 10 | 0 | -103 | 7640.25 | -13.5986
| 40098.1065 | 60.021 | 3787.2593 |  |  |  | -16.7999 | -12.4768 |  | 0 | 3762.265 | 3765.1283 | 3775.8489 | 3779.3439 | 3731.1545 | 633 | [6 empty] | 0 | 633 | -3050.5957 | [13 empty] | 40098.1065 | 60.021 | 3787.2593 | 335 | -157.6281 | 0 | 213 | 10 | 0 | -103 | 7640.58 | -16.7999
| 40098.1065 | 60.021 | 3787.2593 |  |  |  | -16.7999 | -13.9899 |  | 0 | 3760.7519 | 3765.2506 | 3775.7654 | 3779.3439 | 3731.4223 | 633 | [6 empty] | 0 | 633 | -3050.5957 | [13 empty] | 40098.1065 | 60.021 | 3787.2593 | 335 | -157.6281 | 0 | 213 | 10 | 0 | -103 | 7640.58 | -16.7999
| 40098.1065 | 60.017 | 3787.9551 |  |  |  | -13.5986 | -13.8529 |  | 0 | 3760.8888 | 3765.3753 | 3775.6837 | 3779.3439 | 3731.687 | 633 | [6 empty] | 0 | 633 | -2557.4039 | [13 empty] | 40098.1065 | 60.017 | 3787.9551 | 335 | -157.6281 | 0 | 213.5 | 10 | 0 | -103 | 7640.91 | -13.5986
| 40098.1065 | 60.019 | 3788.0303 |  |  |  | -15.2008 | -14.3247 |  | 0 | 3760.417 | 3765.4991 | 3775.6003 | 3779.3439 | 3731.9489 | 633 | [6 empty] | 0 | 633 | -2782.5464 | [13 empty] | 40098.1065 | 60.019 | 3788.0303 | 335 | -155.5317 | 0 | 214 | 10 | 0 | -103 | 7641.24 | -15.2008
| 40098.1066 | 60.019 | 3788.0303 |  |  |  | -15.2008 | -14.6313 |  | 0 | 3760.1104 | 3765.6216 | 3775.5161 | 3779.3439 | 3732.2079 | 633 | [6 empty] | 0 | 633 | -2782.5464 | [13 empty] | 40098.1066 | 60.019 | 3788.0303 | 335 | -155.5317 | 0 | 214 | 10 | 0 | -103 | 7641.24 | -15.2008
| 40098.1066 | 60.023 | 3789.2158 |  |  |  | -18.399 | -15.95 |  | 0 | 3758.7917 | 3765.7491 | 3775.4257 | 3779.3439 | 3732.464 | 633 | [6 empty] | 0 | 633 | -3375.794 | [13 empty] | 40098.1066 | 60.023 | 3789.2158 | 335 | -155.5317 | 0 | 214.5 | 10 | 0 | -103 | 7641.57 | -18.399
| 40098.1066 | 60.025 | 3787.5366 |  |  |  | -20.0012 | -17.3679 |  | 0 | 3757.3738 | 3765.8663 | 3775.3286 | 3779.3439 | 3732.7174 | 633 | [6 empty] | 0 | 633 | -3779.4591 | [13 empty] | 40098.1066 | 60.025 | 3787.5366 | 335 | -155.5317 | 0 | 215 | 10 | 0 | -103 | 7641.9 | -20.0012
| 40098.1066 | 60.025 | 3787.5366 |  |  |  | -20.0012 | -18.2896 |  | 0 | 3756.4521 | 3765.9821 | 3775.2277 | 3779.3439 | 3732.9681 | 633 | [6 empty] | 0 | 633 | -3779.4591 | [13 empty] | 40098.1066 | 60.025 | 3787.5366 | 335 | -155.5317 | 0 | 215 | 10 | 0 | -103 | 7641.9 | -20.0012
| 40098.1067 | 60.021 | 3786.0767 |  |  |  | -16.7999 | -17.7682 |  | 0 | 3756.9735 | 3766.089 | 3775.1306 | 3779.3439 | 3733.2161 | 633 | [6 empty] | 0 | 633 | -3050.5957 | [13 empty] | 40098.1067 | 60.021 | 3786.0767 | 335 | -155.5317 | 0 | 215.5 | 10 | 0 | -103 | 7642.23 | -16.7999
| 40098.1067 | 60.024 | 3787.9304 |  |  |  | -19.1986 | -18.2688 |  | 0 | 3756.4729 | 3766.2046 | 3775.0319 | 3779.3439 | 3733.4615 | 633 | [6 empty] | 0 | 633 | -3565.8569 | [13 empty] | 40098.1067 | 60.024 | 3787.9304 | 335 | -155.5317 | 0 | 216 | 10 | 0 | -103 | 7642.56 | -19.1986
| 40098.1067 | 60.024 | 3787.9304 |  |  |  | -19.1986 | -18.5943 |  | 0 | 3756.1475 | 3766.3189 | 3774.9325 | 3779.3439 | 3733.7042 | 633 | [6 empty] | 0 | 633 | -3565.8569 | [13 empty] | 40098.1067 | 60.024 | 3787.9304 | 335 | -155.5317 | 0 | 216 | 10 | 0 | -103 | 7642.56 | -19.1986
| 40098.1067 | 60.024 | 3786.8748 |  |  |  | -19.1986 | -18.8058 |  | 0 | 3755.936 | 3766.4266 | 3774.833 | 3779.3439 | 3733.9444 | 633 | [6 empty] | 0 | 633 | -3565.8569 | [13 empty] | 40098.1067 | 60.024 | 3786.8748 | 335 | -160.4472 | 0 | 216.5 | 10 | 0 | -103 | 7642.89 | -19.1986
| 40098.1067 | 60.02 | 3786.5498 |  |  |  | -16.0004 | -17.8239 |  | 0 | 3756.9178 | 3766.5314 | 3774.7397 | 3779.3439 | 3734.1821 | 633 | [6 empty] | 0 | 633 | -2910.4122 | [13 empty] | 40098.1067 | 60.02 | 3786.5498 | 335 | -160.4472 | 0 | 217 | 10 | 0 | -103 | 7643.22 | -16.0004
| 40098.1068 | 60.02 | 3786.5498 |  |  |  | -16.0004 | -17.1857 |  | 0 | 3757.5561 | 3766.6351 | 3774.6507 | 3779.3439 | 3734.4174 | 633 | [6 empty] | 0 | 633 | -2910.4122 | [13 empty] | 40098.1068 | 60.02 | 3786.5498 | 335 | -160.4472 | 0 | 217 | 10 | 0 | -103 | 7643.22 | -16.0004
| 40098.1068 | 60.025 | 3785.0181 |  |  |  | -20.0012 | -18.1711 |  | 0 | 3756.5706 | 3766.7298 | 3774.5575 | 3779.3439 | 3734.6501 | 633 | [6 empty] | 0 | 633 | -3779.4591 | [13 empty] | 40098.1068 | 60.025 | 3785.0181 | 335 | -160.4472 | 0 | 217.5 | 10 | 0 | -103 | 7643.55 | -20.0012
| 40098.1068 | 60.02 | 3785.614 |  |  |  | -16.0004 | -17.4113 |  | 0 | 3757.3304 | 3766.8267 | 3774.4691 | 3779.3439 | 3734.8805 | 633 | [6 empty] | 0 | 633 | -2910.4122 | [13 empty] | 40098.1068 | 60.02 | 3785.614 | 335 | -160.4472 | 0 | 218 | 10 | 0 | -103 | 7643.88 | -16.0004
| 40098.1068 | 60.02 | 3785.614 |  |  |  | -16.0004 | -16.9175 |  | 0 | 3757.8242 | 3766.9225 | 3774.3842 | 3779.3439 | 3735.1085 | 633 | [6 empty] | 0 | 633 | -2910.4122 | [13 empty] | 40098.1068 | 60.02 | 3785.614 | 335 | -160.4472 | 0 | 218 | 10 | 0 | -103 | 7643.88 | -16.0004
| 40098.1069 | 60.02 | 3785.8037 |  |  |  | -16.0004 | -16.5965 |  | 0 | 3758.1452 | 3767.0184 | 3774.3018 | 3779.3439 | 3735.3342 | 633 | [6 empty] | 0 | 633 | -2910.4122 | [13 empty] | 40098.1069 | 60.02 | 3785.8037 | 335 | -160.4472 | 0 | 218.5 | 10 | 0 | -103 | 7644.21 | -16.0004
| 40098.1069 | 60.022 | 3786.8643 |  |  |  | -17.5995 | -16.9475 |  | 0 | 3757.7942 | 3767.1186 | 3774.2184 | 3779.3439 | 3735.5576 | 633 | [6 empty] | 0 | 633 | -3204.9667 | [13 empty] | 40098.1069 | 60.022 | 3786.8643 | 335 | -163.9586 | 0 | 219 | 10 | 0 | -103 | 7644.54 | -17.5995
| 40098.1069 | 60.022 | 3786.8643 |  |  |  | -17.5995 | -17.1757 |  | 0 | 3757.566 | 3767.2178 | 3774.1347 | 3779.3439 | 3735.7788 | 633 | [6 empty] | 0 | 633 | -3204.9667 | [13 empty] | 40098.1069 | 60.022 | 3786.8643 | 335 | -163.9586 | 0 | 219 | 10 | 0 | -103 | 7644.54 | -17.5995
| 40098.1069 | 60.022 | 3785.2539 |  |  |  | -17.5995 | -17.324 |  | 0 | 3757.4177 | 3767.308 | 3774.0512 | 3779.3439 | 3735.9977 | 633 | [6 empty] | 0 | 633 | -3204.9667 | [13 empty] | 40098.1069 | 60.022 | 3785.2539 | 335 | -163.9586 | 0 | 219.5 | 10 | 0 | -103 | 7644.87 | -17.5995
| 40098.107 | 60.021 | 3785.7261 |  |  |  | -16.7999 | -17.1406 |  | 0 | 3757.6011 | 3767.3997 | 3773.9693 | 3779.3439 | 3736.2144 | 633 | [6 empty] | 0 | 633 | -3050.5957 | [13 empty] | 40098.107 | 60.021 | 3785.7261 | 335 | -163.9586 | 0 | 220 | 10 | 0 | -103 | 7645.2 | -16.7999
| 40098.107 | 60.021 | 3785.7261 |  |  |  | -16.7999 | -17.0214 |  | 0 | 3757.7204 | 3767.4904 | 3773.8889 | 3779.3439 | 3736.429 | 633 | [6 empty] | 0 | 633 | -3050.5957 | [13 empty] | 40098.107 | 60.021 | 3785.7261 | 335 | -163.9586 | 0 | 220 | 10 | 0 | -103 | 7645.2 | -16.7999
| 40098.107 | 60.023 | 3785.821 |  |  |  | -18.399 | -17.5036 |  | 0 | 3757.2382 | 3767.5807 | 3773.8069 | 3779.3439 | 3736.6414 | 633 | [6 empty] | 0 | 633 | -3375.794 | [13 empty] | 40098.107 | 60.023 | 3785.821 | 335 | -163.9586 | 0 | 220.5 | 10 | 0 | -103 | 7645.53 | -18.399
| 40098.107 | 60.022 | 3785.7983 |  |  |  | -17.5995 | -17.5371 |  | 0 | 3757.2046 | 3767.67 | 3773.7255 | 3779.3439 | 3736.8518 | 633 | [6 empty] | 0 | 633 | -3204.9667 | [13 empty] | 40098.107 | 60.022 | 3785.7983 | 335 | -163.9586 | 0 | 221 | 10 | 0 | -103 | 7645.86 | -17.5995
| 40098.107 | 60.022 | 3785.7983 |  |  |  | -17.5995 | -17.559 |  | 0 | 3757.1828 | 3767.7584 | 3773.6448 | 3779.3439 | 3737.0601 | 633 | [6 empty] | 0 | 633 | -3204.9667 | [13 empty] | 40098.107 | 60.022 | 3785.7983 | 335 | -163.9586 | 0 | 221 | 10 | 0 | -103 | 7645.86 | -17.5995
| 40098.1071 | 60.019 | 3786.9392 |  |  |  | -15.2008 | -16.7336 |  | 0 | 3758.0081 | 3767.8515 | 3773.5689 | 3779.3439 | 3737.2664 | 633 | [6 empty] | 0 | 633 | -2782.5464 | [13 empty] | 40098.1071 | 60.019 | 3786.9392 | 335 | -166.0724 | 0 | 221.5 | 10 | 0 | -103 | 7646.19 | -15.2008
| 40098.1071 | 60.018 | 3787.6274 |  |  |  | -14.4012 | -15.9173 |  | 0 | 3758.8245 | 3767.9471 | 3773.4976 | 3779.3439 | 3737.4706 | 633 | [6 empty] | 0 | 633 | -2665.443 | [13 empty] | 40098.1071 | 60.018 | 3787.6274 | 335 | -166.0724 | 0 | 222 | 10 | 0 | -103 | 7646.52 | -14.4012
| 40098.1071 | 60.018 | 3787.6274 |  |  |  | -14.4012 | -15.3867 |  | 0 | 3759.3551 | 3768.0417 | 3773.4296 | 3779.3439 | 3737.6729 | 633 | [6 empty] | 0 | 633 | -2665.443 | [13 empty] | 40098.1071 | 60.018 | 3787.6274 | 335 | -166.0724 | 0 | 222 | 10 | 0 | -103 | 7646.52 | -14.4012
| 40098.1071 | 60.018 | 3789.6733 |  |  |  | -14.4012 | -15.0418 |  | 0 | 3759.7 | 3768.1452 | 3773.364 | 3779.3439 | 3737.8732 | 633 | [6 empty] | 0 | 633 | -2665.443 | [13 empty] | 40098.1071 | 60.018 | 3789.6733 | 335 | -166.0724 | 0 | 222.5 | 10 | 0 | -103 | 7646.85 | -14.4012
| 40098.1072 | 60.019 | 3789.4043 |  |  |  | -15.2008 | -15.0974 |  | 0 | 3759.6443 | 3768.2464 | 3773.2986 | 3779.3439 | 3738.0717 | 633 | [6 empty] | 0 | 633 | -2782.5464 | [13 empty] | 40098.1072 | 60.019 | 3789.4043 | 335 | -166.0724 | 0 | 223 | 10 | 0 | -103 | 7647.18 | -15.2008
| 40098.1072 | 60.019 | 3789.4043 |  |  |  | -15.2008 | -15.1336 |  | 0 | 3759.6081 | 3768.3467 | 3773.2337 | 3779.3439 | 3738.2682 | 633 | [6 empty] | 0 | 633 | -2782.5464 | [13 empty] | 40098.1072 | 60.019 | 3789.4043 | 335 | -166.0724 | 0 | 223 | 10 | 0 | -103 | 7647.18 | -15.2008
| 40098.1072 | 60.019 | 3789.1833 |  |  |  | -15.2008 | -15.1571 |  | 0 | 3759.5846 | 3768.445 | 3773.1694 | 3779.3439 | 3738.4629 | 633 | [6 empty] | 0 | 633 | -2782.5464 | [13 empty] | 40098.1072 | 60.019 | 3789.1833 | 335 | -166.0724 | 0 | 223.5 | 10 | 0 | -103 | 7647.51 | -15.2008
| 40098.1072 | 60.015 | 3789.3689 |  |  |  | -11.9995 | -14.052 |  | 0 | 3760.6898 | 3768.5432 | 3773.1108 | 3779.3439 | 3738.6557 | 633 | [6 empty] | 0 | 633 | -2366.3052 | [13 empty] | 40098.1072 | 60.015 | 3789.3689 | 335 | -163.7666 | 0 | 224 | 10 | 0 | -103 | 7647.84 | -11.9995
| 40098.1073 | 60.015 | 3789.3689 |  |  |  | -11.9995 | -13.3336 |  | 0 | 3761.4081 | 3768.6405 | 3773.0561 | 3779.3439 | 3738.8467 | 633 | [6 empty] | 0 | 633 | -2366.3052 | [13 empty] | 40098.1073 | 60.015 | 3789.3689 | 335 | -163.7666 | 0 | 224 | 10 | 0 | -103 | 7647.84 | -11.9995
| 40098.1073 | 60.016 | 3788.6646 |  |  |  | -12.7991 | -13.1465 |  | 0 | 3761.5952 | 3768.7337 | 3773.0028 | 3779.3439 | 3739.036 | 633 | [6 empty] | 0 | 633 | -2458.1461 | [13 empty] | 40098.1073 | 60.016 | 3788.6646 | 335 | -163.7666 | 0 | 224.5 | 10 | 0 | -103 | 7648.17 | -12.7991
| 40098.1073 | 60.013 | 3788.9329 |  |  |  | -10.4004 | -12.1854 |  | 0 | 3762.5564 | 3768.8272 | 3772.9544 | 3779.3439 | 3739.2234 | 633 | [6 empty] | 0 | 633 | -2201.78 | [13 empty] | 40098.1073 | 60.013 | 3788.9329 | 335 | -163.7666 | 0 | 225 | 10 | 0 | -103 | 7648.5 | -10.4004
| 40098.1073 | 60.013 | 3788.9329 |  |  |  | -10.4004 | -11.5606 |  | 0 | 3763.1811 | 3768.9198 | 3772.9094 | 3779.3439 | 3739.4092 | 633 | [6 empty] | 0 | 633 | -2201.78 | [13 empty] | 40098.1073 | 60.013 | 3788.9329 | 335 | -163.7666 | 0 | 225 | 10 | 0 | -103 | 7648.5 | -10.4004
| 40098.1073 | 60.012 | 3790.8052 |  |  |  | -9.6008 | -10.8747 |  | 0 | 3763.867 | 3769.0202 | 3772.8679 | 3779.3439 | 3739.5932 | 633 | [6 empty] | 0 | 633 | -2127.8086 | [13 empty] | 40098.1073 | 60.012 | 3790.8052 | 335 | -163.7666 | 0 | 225.5 | 10 | 0 | -103 | 7648.83 | -9.6008
| 40098.1074 | 60.01 | 3790.4111 |  |  |  | -7.9987 | -9.8681 |  | 0 | 3764.8737 | 3769.1179 | 3772.8314 | 3779.3439 | 3739.7756 | 633 | [6 empty] | 0 | 633 | -1993.5983 | [13 empty] | 40098.1074 | 60.01 | 3790.4111 | 335 | -163.7666 | 0 | 226 | 10 | 0 | -103 | 7649.16 | -7.9987
| 40098.1074 | 60.01 | 3790.4111 |  |  |  | -7.9987 | -9.2138 |  | 0 | 3765.528 | 3769.2147 | 3772.7982 | 3779.3439 | 3739.9562 | 633 | [6 empty] | 0 | 633 | -1993.5983 | [13 empty] | 40098.1074 | 60.01 | 3790.4111 | 335 | -163.7666 | 0 | 226 | 10 | 0 | -103 | 7649.16 | -7.9987
| 40098.1074 | 60.007 | 3791.5398 |  |  |  | -5.6 | -7.949 |  | 0 | 3766.7928 | 3769.3157 | 3772.771 | 3779.3439 | 3740.1353 | 633 | [6 empty] | 0 | 633 | -1821.5835 | [13 empty] | 40098.1074 | 60.007 | 3791.5398 | 335 | -165.1017 | 0 | 226.5 | 10 | 0 | -103 | 7649.49 | -5.6
| 40098.1074 | 60.009 | 3792.9453 |  |  |  | -7.1991 | -7.6865 |  | 0 | 3767.0552 | 3769.4221 | 3772.7453 | 3779.3439 | 3740.3127 | 633 | [6 empty] | 0 | 633 | -1932.7605 | [13 empty] | 40098.1074 | 60.009 | 3792.9453 | 335 | -165.1017 | 0 | 227 | 10 | 0 | -103 | 7649.82 | -7.1991
| 40098.1075 | 60.009 | 3792.9453 |  |  |  | -7.1991 | -7.5159 |  | 0 | 3767.2258 | 3769.5276 | 3772.7205 | 3779.3439 | 3740.4885 | 633 | [6 empty] | 0 | 633 | -1932.7605 | [13 empty] | 40098.1075 | 60.009 | 3792.9453 | 335 | -165.1017 | 0 | 227 | 10 | 0 | -103 | 7649.82 | -7.1991
| 40098.1075 | 60.009 | 3791.4431 |  |  |  | -7.1991 | -7.405 |  | 0 | 3767.3367 | 3769.6255 | 3772.6965 | 3779.3439 | 3740.6627 | 633 | [6 empty] | 0 | 633 | -1932.7605 | [13 empty] | 40098.1075 | 60.009 | 3791.4431 | 335 | -165.1017 | 0 | 227.5 | 10 | 0 | -103 | 7650.15 | -7.1991
| 40098.1075 | 60.003 | 3791.426 |  |  |  | -2.3987 | -5.6528 |  | 0 | 3769.0889 | 3769.7224 | 3772.6805 | 3779.3439 | 3740.8354 | 633 | [6 empty] | 0 | 633 | -1633.4808 | [13 empty] | 40098.1075 | 60.003 | 3791.426 | 335 | -165.1017 | 0 | 228 | 10 | 0 | -103 | 7650.48 | -2.3987
| 40098.1075 | 60.003 | 3791.426 |  |  |  | -2.3987 | -4.5139 |  | 0 | 3770.2279 | 3769.8184 | 3772.6696 | 3779.3439 | 3741.0066 | 633 | [6 empty] | 0 | 633 | -1633.4808 | [13 empty] | 40098.1075 | 60.003 | 3791.426 | 335 | -165.1017 | 0 | 228 | 10 | 0 | -103 | 7650.48 | -2.3987
| 40098.1076 | 59.999 | 3790.4573 |  |  |  | 0.79956 | -2.6542 |  | 0 | 3772.0876 | 3769.9093 | 3772.667 | 3779.3439 | 3741.1762 | 633 | [6 empty] | 0 | 633 | -1480.7224 | [13 empty] | 40098.1076 | 59.999 | 3790.4573 | 335 | -165.1017 | 0 | 228.5 | 10 | 0 | -103 | 7650.81 | 0.79956
| 40098.1076 | 59.992 | 3790.2163 |  |  |  | 6.3995 | 0.51463 |  | 0 | 3775.2564 | 3769.9984 | 3772.6784 | 3779.3439 | 3741.3444 | 633 | [6 empty] | 0 | 633 | -1272.3778 | [13 empty] | 40098.1076 | 59.992 | 3790.2163 | 335 | -165.4764 | 0 | 229 | 10 | 0 | -103 | 7651.14 | 6.3995
| 40098.1076 | 59.992 | 3790.2163 |  |  |  | 6.3995 | 2.5743 |  | 0 | 3777.3161 | 3770.0867 | 3772.6986 | 3779.3439 | 3741.511 | 633 | [6 empty] | 0 | 633 | -1272.3778 | [13 empty] | 40098.1076 | 59.992 | 3790.2163 | 335 | -165.4764 | 0 | 229 | 10 | 0 | -103 | 7651.14 | 6.3995
| 40098.1076 | 59.991 | 3788.457 |  |  |  | 7.1991 | 4.193 |  | 0 | 3778.9347 | 3770.1665 | 3772.7258 | 3779.3439 | 3741.6762 | 633 | [6 empty] | 0 | 633 | -1247.3195 | [13 empty] | 40098.1076 | 59.991 | 3788.457 | 335 | -165.4764 | 0 | 229.5 | 10 | 0 | -103 | 7651.47 | 7.1991
| 40098.1077 | 59.992 | 3788.105 |  |  |  | 6.3995 | 4.9653 |  | 0 | 3779.707 | 3770.2442 | 3772.756 | 3779.3439 | 3741.84 | 633 | [6 empty] | 0 | 633 | -1272.3778 | [13 empty] | 40098.1077 | 59.992 | 3788.105 | 335 | -165.4764 | 0 | 230 | 10 | 0 | -103 | 7651.8 | 6.3995
| 40098.1077 | 59.992 | 3788.105 |  |  |  | 6.3995 | 5.4673 |  | 0 | 3780.209 | 3770.3212 | 3772.7881 | 3779.3439 | 3742.0024 | 633 | [6 empty] | 0 | 633 | -1272.3778 | [13 empty] | 40098.1077 | 59.992 | 3788.105 | 335 | -165.4764 | 0 | 230 | 10 | 0 | -103 | 7651.8 | 6.3995
| 40098.1077 | 59.988 | 3788.1895 |  |  |  | 9.6008 | 6.914 |  | 0 | 3781.6558 | 3770.3979 | 3772.8262 | 3779.3439 | 3742.1633 | 633 | [6 empty] | 0 | 633 | -1177.6527 | [13 empty] | 40098.1077 | 59.988 | 3788.1895 | 335 | -165.4764 | 0 | 230.5 | 10 | 0 | -103 | 7652.13 | 9.6008
| 40098.1077 | 59.985 | 3788.4973 |  |  |  | 11.9995 | 8.6939 |  | 0 | 3783.4357 | 3770.4752 | 3772.8715 | 3779.3439 | 3742.3229 | 633 | [6 empty] | 0 | 633 | -1115.4314 | [13 empty] | 40098.1077 | 59.985 | 3788.4973 | 335 | -165.4764 | 0 | 231 | 10 | 0 | -103 | 7652.46 | 11.9995
| 40098.1077 | 59.985 | 3788.4973 |  |  |  | 11.9995 | 9.8509 |  | 0 | 3784.5926 | 3770.5519 | 3772.9214 | 3779.3439 | 3742.4811 | 633 | [6 empty] | 0 | 633 | -1115.4314 | [13 empty] | 40098.1077 | 59.985 | 3788.4973 | 335 | -165.4764 | 0 | 231 | 10 | 0 | -103 | 7652.46 | 11.9995
| 40098.1078 | 59.984 | 3788.5708 |  |  |  | 12.7991 | 10.8828 |  | 0 | 3785.6245 | 3770.6282 | 3772.9752 | 3779.3439 | 3742.638 | 633 | [6 empty] | 0 | 633 | -1096.1268 | [13 empty] | 40098.1078 | 59.984 | 3788.5708 | 335 | -206.4591 | 0 | 231.5 | 10 | 0 | -103 | 7652.79 | 12.7991
| 40098.1078 | 59.984 | 3788.1011 |  |  |  | 12.7991 | 11.5535 |  | 0 | 3786.2952 | 3770.702 | 3773.0314 | 3779.3439 | 3742.7935 | 633 | [6 empty] | 0 | 633 | -1096.1268 | [13 empty] | 40098.1078 | 59.984 | 3788.1011 | 335 | -206.4591 | 0 | 232 | 10 | 0 | -103 | 7616 | 12.7991
| 40098.1078 | 59.984 | 3788.1011 |  |  |  | 12.7991 | 11.9894 |  | 0 | 3786.7312 | 3770.7751 | 3773.089 | 3779.3439 | 3742.9477 | 633 | [6 empty] | 0 | 633 | -1096.1268 | [13 empty] | 40098.1078 | 59.984 | 3788.1011 | 335 | -206.4591 | 0 | 232 | 10 | 0 | -103 | 7616 | 12.7991
| 40098.1078 | 59.982 | 3786.4529 |  |  |  | 14.4012 | 12.8336 |  | 0 | 3787.5753 | 3770.8407 | 3773.1496 | 3779.3439 | 3743.1006 | 633 | [6 empty] | 0 | 633 | -1059.3874 | [13 empty] | 40098.1078 | 59.982 | 3786.4529 | 335 | -206.4591 | 0 | 232.5 | 10 | 0 | -103 | 7626 | 14.4012
| 40098.1079 | 59.982 | 3787.7324 |  |  |  | 14.4012 | 13.3823 |  | 0 | 3788.124 | 3770.9111 | 3773.212 | 3779.3439 | 3743.2523 | 633 | [6 empty] | 0 | 633 | -1059.3874 | [13 empty] | 40098.1079 | 59.982 | 3787.7324 | 335 | -206.4591 | 0 | 233 | 10 | 0 | -103 | 7632 | 14.4012
| 40098.1079 | 59.982 | 3787.7324 |  |  |  | 14.4012 | 13.7389 |  | 0 | 3788.4806 | 3770.9809 | 3773.2753 | 3779.3439 | 3743.4027 | 633 | [6 empty] | 0 | 633 | -1059.3874 | [13 empty] | 40098.1079 | 59.982 | 3787.7324 | 335 | -206.4591 | 0 | 233 | 10 | 0 | -103 | 7632 | 14.4012
| 40098.1079 | 59.979 | 3789.2852 |  |  |  | 16.7999 | 14.8103 |  | 0 | 3789.552 | 3771.0565 | 3773.3426 | 3779.3439 | 3743.5518 | 633 | [6 empty] | 0 | 633 | -1008.7671 | [13 empty] | 40098.1079 | 59.979 | 3789.2852 | 335 | -206.4591 | 0 | 233.5 | 10 | 0 | -103 | 7632 | 16.7999
| 40098.1079 | 59.976 | 3788.2563 |  |  |  | 19.1986 | 16.3462 |  | 0 | 3791.0879 | 3771.1273 | 3773.4156 | 3779.3439 | 3743.6997 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.1079 | 59.976 | 3788.2563 | 335 | -211.256 | 0 | 234 | 10 | 0 | -103 | 7632 | 19.1986
| 40098.108 | 59.976 | 3788.2563 |  |  |  | 19.1986 | 17.3445 |  | 0 | 3792.0863 | 3771.1975 | 3773.4921 | 3779.3439 | 3743.8464 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.108 | 59.976 | 3788.2563 | 335 | -211.256 | 0 | 234 | 10 | 0 | -103 | 7632 | 19.1986
| 40098.108 | 59.976 | 3790.4673 |  |  |  | 19.1986 | 17.9935 |  | 0 | 3792.7352 | 3771.2761 | 3773.5707 | 3779.3439 | 3743.9919 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.108 | 59.976 | 3790.4673 | 335 | -211.256 | 1 | 234.5 | 10 | 0 | -103 | 7632 | 19.1986
| 40098.108 | 59.982 | 3790.6646 |  |  |  | 14.4012 | 16.7362 |  | 0 | 3791.4779 | 3771.3549 | 3773.6435 | 3779.3439 | 3744.1362 | 633 | [6 empty] | 0 | 633 | -1059.3874 | [13 empty] | 40098.108 | 59.982 | 3790.6646 | 335 | -211.256 | 1 | 235 | 10 | 0 | -103 | 7632 | 14.4012
| 40098.108 | 59.982 | 3790.6646 |  |  |  | 14.4012 | 15.919 |  | 0 | 3790.6607 | 3771.4331 | 3773.7124 | 3779.3439 | 3744.2793 | 633 | [6 empty] | 0 | 633 | -1059.3874 | [13 empty] | 40098.108 | 59.982 | 3790.6646 | 335 | -211.256 | 1 | 235 | 10 | 0 | -103 | 7632 | 14.4012
| 40098.108 | 59.978 | 3789.6738 |  |  |  | 17.5995 | 16.5071 |  | 0 | 3791.2489 | 3771.5067 | 3773.7831 | 3779.3439 | 3744.4212 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.108 | 59.978 | 3789.6738 | 335 | -211.256 | 1 | 235.5 | 10 | 0 | -103 | 7632 | 17.5995
| 40098.1081 | 59.974 | 3789.2671 |  |  |  | 20.8008 | 18.0099 |  | 0 | 3792.7517 | 3771.578 | 3773.8593 | 3779.3439 | 3744.5621 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.1081 | 59.974 | 3789.2671 | 335 | -211.256 | 1 | 236 | 10 | 0 | -103 | 7632 | 20.8008
| 40098.1081 | 59.974 | 3789.2671 |  |  |  | 20.8008 | 18.9867 |  | 0 | 3793.7285 | 3771.6488 | 3773.9387 | 3779.3439 | 3744.7017 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.1081 | 59.974 | 3789.2671 | 335 | -211.256 | 1 | 236 | 10 | 0 | -103 | 7632 | 20.8008
| 40098.1081 | 59.976 | 3790.4304 |  |  |  | 19.1986 | 19.0609 |  | 0 | 3793.8026 | 3771.7236 | 3774.0179 | 3779.3439 | 3744.8403 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.1081 | 59.976 | 3790.4304 | 335 | -214.3467 | 1 | 236.5 | 10 | 0 | -103 | 7632 | 19.1986
| 40098.1081 | 59.977 | 3789.9143 |  |  |  | 18.399 | 18.8292 |  | 0 | 3793.571 | 3771.7958 | 3774.0955 | 3779.3439 | 3744.9778 | 633 | [6 empty] | 0 | 633 | -977.6248 | [13 empty] | 40098.1081 | 59.977 | 3789.9143 | 335 | -214.3467 | 1 | 237 | 10 | 0 | -103 | 7632 | 18.399
| 40098.1082 | 59.977 | 3789.9143 |  |  |  | 18.399 | 18.6787 |  | 0 | 3793.4204 | 3771.8674 | 3774.1718 | 3779.3439 | 3745.1141 | 633 | [6 empty] | 0 | 633 | -977.6248 | [13 empty] | 40098.1082 | 59.977 | 3789.9143 | 335 | -214.3467 | 1 | 237 | 10 | 0 | -103 | 7632 | 18.399
| 40098.1082 | 59.975 | 3787.4421 |  |  |  | 20.0012 | 19.1416 |  | 0 | 3793.8833 | 3771.9287 | 3774.2495 | 3779.3439 | 3745.2494 | 633 | [6 empty] | 0 | 633 | -948.2936 | [13 empty] | 40098.1082 | 59.975 | 3787.4421 | 335 | -214.3467 | 1 | 237.5 | 10 | 0 | -103 | 7632 | 20.0012
| 40098.1082 | 59.969 | 3788.9629 |  |  |  | 24.7986 | 21.1215 |  | 0 | 3795.8633 | 3771.9955 | 3774.3342 | 3779.3439 | 3745.3837 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1082 | 59.969 | 3788.9629 | 335 | -214.3467 | 2 | 238 | 10 | 0 | -103 | 7632 | 24.7986
| 40098.1082 | 59.969 | 3788.9629 |  |  |  | 24.7986 | 22.4085 |  | 0 | 3797.1502 | 3772.0618 | 3774.4233 | 3779.3439 | 3745.5169 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1082 | 59.969 | 3788.9629 | 335 | -214.3467 | 2 | 238 | 10 | 0 | -103 | 7632 | 24.7986
| 40098.1083 | 59.97 | 3791.877 |  |  |  | 23.999 | 22.9652 |  | 0 | 3797.7069 | 3772.1389 | 3774.5139 | 3779.3439 | 3745.649 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1083 | 59.97 | 3791.877 | 335 | -214.3467 | 3 | 238.5 | 10 | 0 | -103 | 7632 | 23.999
| 40098.1083 | 59.973 | 3792.9106 |  |  |  | 21.6003 | 22.4875 |  | 0 | 3797.2292 | 3772.2194 | 3774.602 | 3779.3439 | 3745.7801 | 633 | [6 empty] | 0 | 633 | -920.7222 | [13 empty] | 40098.1083 | 59.973 | 3792.9106 | 335 | -212.1727 | 4 | 239 | 10 | 0 | -103 | 7632 | 21.6003
| 40098.1083 | 59.973 | 3792.9106 |  |  |  | 21.6003 | 22.177 |  | 0 | 3796.9187 | 3772.2993 | 3774.6881 | 3779.3439 | 3745.9102 | 633 | [6 empty] | 0 | 633 | -920.7222 | [13 empty] | 40098.1083 | 59.973 | 3792.9106 | 335 | -212.1727 | 4 | 239 | 10 | 0 | -103 | 7632 | 21.6003
| 40098.1083 | 59.978 | 3789.125 |  |  |  | 17.5995 | 20.5749 |  | 0 | 3795.3166 | 3772.364 | 3774.7675 | 3779.3439 | 3746.0393 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1083 | 59.978 | 3789.125 | 335 | -212.1727 | 5 | 239.5 | 10 | 0 | -103 | 7632 | 17.5995
| 40098.1083 | 59.978 | 3788.0796 |  |  |  | 17.5995 | 19.5335 |  | 0 | 3794.2752 | 3772.4242 | 3774.8422 | 3779.3439 | 3746.1674 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1083 | 59.978 | 3788.0796 | 335 | -212.1727 | 6 | 240 | 10 | 0 | -103 | 7632 | 17.5995
| 40098.1084 | 59.978 | 3788.0796 |  |  |  | 17.5995 | 18.8566 |  | 0 | 3793.5983 | 3772.484 | 3774.9138 | 3779.3439 | 3746.2945 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1084 | 59.978 | 3788.0796 | 335 | -212.1727 | 6 | 240 | 10 | 0 | -103 | 7632 | 17.5995
| 40098.1084 | 59.975 | 3787.135 |  |  |  | 20.0012 | 19.2572 |  | 0 | 3793.9989 | 3772.5397 | 3774.9864 | 3779.3439 | 3746.4206 | 633 | [6 empty] | 0 | 633 | -948.2936 | [13 empty] | 40098.1084 | 59.975 | 3787.135 | 335 | -212.1727 | 7 | 240.5 | 10 | 0 | -103 | 7632 | 20.0012
| 40098.1084 | 59.976 | 3787.1643 |  |  |  | 19.1986 | 19.2367 |  | 0 | 3793.9784 | 3772.5951 | 3775.0583 | 3779.3439 | 3746.5458 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.1084 | 59.976 | 3787.1643 | 335 | -212.1727 | 8 | 241 | 10 | 0 | -103 | 7632 | 19.1986
| 40098.1084 | 59.976 | 3787.1643 |  |  |  | 19.1986 | 19.2234 |  | 0 | 3793.9651 | 3772.65 | 3775.1297 | 3779.3439 | 3746.67 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.1084 | 59.976 | 3787.1643 | 335 | -212.1727 | 8 | 241 | 10 | 0 | -103 | 7632 | 19.1986
| 40098.1085 | 59.975 | 3787.4048 |  |  |  | 20.0012 | 19.4956 |  | 0 | 3794.2374 | 3772.7055 | 3775.2015 | 3779.3439 | 3746.7933 | 633 | [6 empty] | 0 | 633 | -948.2936 | [13 empty] | 40098.1085 | 59.975 | 3787.4048 | 335 | -215.5982 | 9 | 241.5 | 10 | 0 | -103 | 7632 | 20.0012
| 40098.1085 | 59.969 | 3786.4868 |  |  |  | 24.7986 | 21.3517 |  | 0 | 3796.0934 | 3772.7571 | 3775.2797 | 3779.3439 | 3746.9157 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1085 | 59.969 | 3786.4868 | 335 | -215.5982 | 10 | 242 | 10 | 0 | -103 | 7632 | 24.7986
| 40098.1085 | 59.969 | 3786.4868 |  |  |  | 24.7986 | 22.5581 |  | 0 | 3797.2998 | 3772.8084 | 3775.3619 | 3779.3439 | 3747.0372 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1085 | 59.969 | 3786.4868 | 335 | -215.5982 | 10 | 242 | 10 | 0 | -103 | 7632 | 24.7986
| 40098.1085 | 59.966 | 3789.2139 |  |  |  | 27.2003 | 24.1829 |  | 0 | 3798.9246 | 3772.8693 | 3775.4495 | 3779.3439 | 3747.1577 | 633 | [6 empty] | 0 | 633 | -835.6397 | [13 empty] | 40098.1085 | 59.966 | 3789.2139 | 335 | -215.5982 | 11 | 242.5 | 10 | 0 | -103 | 7632 | 27.2003
| 40098.1086 | 59.966 | 3790.5117 |  |  |  | 27.2003 | 25.239 |  | 0 | 3799.9807 | 3772.9347 | 3775.5404 | 3779.3439 | 3747.2774 | 633 | [6 empty] | 0 | 633 | -835.6397 | [13 empty] | 40098.1086 | 59.966 | 3790.5117 | 335 | -215.5982 | 12 | 243 | 10 | 0 | -103 | 7632 | 27.2003
| 40098.1086 | 59.966 | 3790.5117 |  |  |  | 27.2003 | 25.9254 |  | 0 | 3800.6672 | 3772.9995 | 3775.6331 | 3779.3439 | 3747.3961 | 633 | [6 empty] | 0 | 633 | -835.6397 | [13 empty] | 40098.1086 | 59.966 | 3790.5117 | 335 | -215.5982 | 12 | 243 | 10 | 0 | -103 | 7632 | 27.2003
| 40098.1086 | 59.969 | 3792.2183 |  |  |  | 24.7986 | 25.531 |  | 0 | 3800.2728 | 3773.0702 | 3775.7237 | 3779.3439 | 3747.514 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1086 | 59.969 | 3792.2183 | 335 | -215.5982 | 13 | 243.5 | 10 | 0 | -103 | 7632 | 24.7986
| 40098.1086 | 59.968 | 3790.9595 |  |  |  | 25.6012 | 25.5556 |  | 0 | 3800.2973 | 3773.1357 | 3775.8137 | 3779.3439 | 3747.631 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1086 | 59.968 | 3790.9595 | 335 | -218.3273 | 14 | 244 | 10 | 0 | -103 | 7632 | 25.6012
| 40098.1086 | 59.968 | 3790.9595 |  |  |  | 25.6012 | 25.5716 |  | 0 | 3800.3133 | 3773.2008 | 3775.9031 | 3779.3439 | 3747.7472 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1086 | 59.968 | 3790.9595 | 335 | -218.3273 | 14 | 244 | 10 | 0 | -103 | 7632 | 25.6012
| 40098.1087 | 59.965 | 3789.0264 |  |  |  | 27.9999 | 26.4215 |  | 0 | 3801.1632 | 3773.2583 | 3775.995 | 3779.3439 | 3747.8625 | 633 | [6 empty] | 0 | 633 | -824.7578 | [13 empty] | 40098.1087 | 59.965 | 3789.0264 | 335 | -218.3273 | 15 | 244.5 | 10 | 0 | -103 | 7632 | 27.9999
| 40098.1087 | 59.97 | 3789.1675 |  |  |  | 23.999 | 25.5736 |  | 0 | 3800.3153 | 3773.316 | 3776.0831 | 3779.3439 | 3747.977 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1087 | 59.97 | 3789.1675 | 335 | -218.3273 | 16 | 245 | 10 | 0 | -103 | 7632 | 23.999
| 40098.1087 | 59.97 | 3789.1675 |  |  |  | 23.999 | 25.0225 |  | 0 | 3799.7642 | 3773.3732 | 3776.1686 | 3779.3439 | 3748.0906 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1087 | 59.97 | 3789.1675 | 335 | -218.3273 | 16 | 245 | 10 | 0 | -103 | 7632 | 23.999
| 40098.1087 | 59.972 | 3785.6899 |  |  |  | 22.3999 | 24.1046 |  | 0 | 3798.8463 | 3773.4175 | 3776.2501 | 3779.3439 | 3748.2035 | 633 | [6 empty] | 0 | 633 | -907.5291 | [13 empty] | 40098.1087 | 59.972 | 3785.6899 | 335 | -218.3273 | 16 | 245.5 | 10 | 0 | -103 | 7632 | 22.3999
| 40098.1088 | 59.967 | 3784.8306 |  |  |  | 26.4008 | 24.9083 |  | 0 | 3799.65 | 3773.4584 | 3776.334 | 3779.3439 | 3748.3155 | 633 | [6 empty] | 0 | 633 | -846.8125 | [13 empty] | 40098.1088 | 59.967 | 3784.8306 | 335 | -218.3273 | 16 | 246 | 10 | 0 | -103 | 7632 | 26.4008
| 40098.1088 | 59.967 | 3784.8306 |  |  |  | 26.4008 | 25.4306 |  | 0 | 3800.1724 | 3773.499 | 3776.4191 | 3779.3439 | 3748.4267 | 633 | [6 empty] | 0 | 633 | -846.8125 | [13 empty] | 40098.1088 | 59.967 | 3784.8306 | 335 | -218.3273 | 16 | 246 | 10 | 0 | -103 | 7632 | 26.4008
| 40098.1088 | 59.969 | 3784.3203 |  |  |  | 24.7986 | 25.2094 |  | 0 | 3799.9511 | 3773.5375 | 3776.5029 | 3779.3439 | 3748.5371 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1088 | 59.969 | 3784.3203 | 335 | -217.3794 | 16 | 246.5 | 10 | 0 | -103 | 7632 | 24.7986
| 40098.1088 | 59.969 | 3782.8086 |  |  |  | 24.7986 | 25.0656 |  | 0 | 3799.8074 | 3773.5704 | 3776.5855 | 3779.3439 | 3748.6468 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1088 | 59.969 | 3782.8086 | 335 | -217.3794 | 16 | 247 | 10 | 0 | -103 | 7632 | 24.7986
| 40098.1089 | 59.969 | 3782.8086 |  |  |  | 24.7986 | 24.9722 |  | 0 | 3799.7139 | 3773.6031 | 3776.6673 | 3779.3439 | 3748.7556 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1089 | 59.969 | 3782.8086 | 335 | -217.3794 | 16 | 247 | 10 | 0 | -103 | 7632 | 24.7986
| 40098.1089 | 59.967 | 3779.3516 |  |  |  | 26.4008 | 25.4722 |  | 0 | 3800.2139 | 3773.6233 | 3776.7502 | 3779.3439 | 3748.8637 | 633 | [6 empty] | 0 | 633 | -846.8125 | [13 empty] | 40098.1089 | 59.967 | 3779.3516 | 335 | -217.3794 | 16 | 247.5 | 10 | 0 | -103 | 7631 | 26.4008
| 40098.1089 | 59.966 | 3779.0562 |  |  |  | 27.2003 | 26.077 |  | 0 | 3800.8188 | 3773.6424 | 3776.8346 | 3779.3439 | 3748.971 | 633 | [6 empty] | 0 | 633 | -835.6397 | [13 empty] | 40098.1089 | 59.966 | 3779.0562 | 335 | -217.3794 | 16 | 248 | 10 | 0 | -103 | 7625 | 27.2003
| 40098.1089 | 59.966 | 3779.0562 |  |  |  | 27.2003 | 26.4702 |  | 0 | 3801.2119 | 3773.6613 | 3776.9198 | 3779.3439 | 3749.0776 | 633 | [6 empty] | 0 | 633 | -835.6397 | [13 empty] | 40098.1089 | 59.966 | 3779.0562 | 335 | -217.3794 | 16 | 248 | 10 | 0 | -103 | 7625 | 27.2003
| 40098.1089 | 59.965 | 3779.2117 |  |  |  | 27.9999 | 27.0056 |  | 0 | 3801.7473 | 3773.6806 | 3777.0064 | 3779.3439 | 3749.1834 | 633 | [6 empty] | 0 | 633 | -824.7578 | [13 empty] | 40098.1089 | 59.965 | 3779.2117 | 335 | -217.3794 | 16 | 248.5 | 10 | 0 | -103 | 7623 | 27.9999
| 40098.109 | 59.967 | 3779.3347 |  |  |  | 26.4008 | 26.7939 |  | 0 | 3801.5356 | 3773.7003 | 3777.0915 | 3779.3439 | 3749.2885 | 633 | [6 empty] | 0 | 633 | -846.8125 | [13 empty] | 40098.109 | 59.967 | 3779.3347 | 335 | -214.8304 | 16 | 249 | 10 | 0 | -103 | 7621 | 26.4008
| 40098.109 | 59.967 | 3779.3347 |  |  |  | 26.4008 | 26.6563 |  | 0 | 3801.398 | 3773.7198 | 3777.1756 | 3779.3439 | 3749.3929 | 633 | [6 empty] | 0 | 633 | -846.8125 | [13 empty] | 40098.109 | 59.967 | 3779.3347 | 335 | -214.8304 | 16 | 249 | 10 | 0 | -103 | 7621 | 26.4008
| 40098.109 | 59.965 | 3775.6467 |  |  |  | 27.9999 | 27.1265 |  | 0 | 3801.8683 | 3773.7264 | 3777.2608 | 3779.3439 | 3749.4965 | 633 | [6 empty] | 0 | 633 | -824.7578 | [13 empty] | 40098.109 | 59.965 | 3775.6467 | 335 | -214.8304 | 16 | 249.5 | 10 | 0 | -103 | 7623 | 27.9999
| 40098.109 | 59.964 | 3776.5967 |  |  |  | 28.7994 | 27.7121 |  | 0 | 3802.4538 | 3773.7363 | 3777.3474 | 3779.3439 | 3749.5994 | 633 | [6 empty] | 0 | 633 | -814.1557 | [13 empty] | 40098.109 | 59.964 | 3776.5967 | 335 | -214.8304 | 16 | 250 | 10 | 0 | -103 | 7625 | 28.7994
| 40098.1091 | 59.964 | 3776.5967 |  |  |  | 28.7994 | 28.0926 |  | 0 | 3802.8344 | 3773.7461 | 3777.4346 | 3779.3439 | 3749.7016 | 633 | [6 empty] | 0 | 633 | -814.1557 | [13 empty] | 40098.1091 | 59.964 | 3776.5967 | 335 | -214.8304 | 16 | 250 | 10 | 0 | -103 | 7625 | 28.7994
| 40098.1091 | 59.97 | 3776.0229 |  |  |  | 23.999 | 26.6599 |  | 0 | 3801.4016 | 3773.7538 | 3777.5164 | 3779.3439 | 3749.8032 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1091 | 59.97 | 3776.0229 | 335 | -214.8304 | 16 | 250.5 | 10 | 0 | -103 | 7627 | 23.999
| 40098.1091 | 59.969 | 3773.1699 |  |  |  | 24.7986 | 26.0084 |  | 0 | 3800.7502 | 3773.7518 | 3777.5955 | 3779.3439 | 3749.904 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1091 | 59.969 | 3773.1699 | 335 | -214.8304 | 16 | 251 | 10 | 0 | -103 | 7628 | 24.7986
| 40098.1091 | 59.969 | 3773.1699 |  |  |  | 24.7986 | 25.585 |  | 0 | 3800.3267 | 3773.7499 | 3777.6725 | 3779.3439 | 3750.0041 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1091 | 59.969 | 3773.1699 | 335 | -214.8304 | 16 | 251 | 10 | 0 | -103 | 7628 | 24.7986
| 40098.1092 | 59.968 | 3768.793 |  |  |  | 25.6012 | 25.5907 |  | 0 | 3800.3324 | 3773.7331 | 3777.7491 | 3779.3439 | 3750.1036 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1092 | 59.968 | 3768.793 | 335 | -227.6559 | 16 | 251.5 | 10 | 0 | -103 | 7628 | 25.6012
| 40098.1092 | 59.965 | 3768.5029 |  |  |  | 27.9999 | 26.4339 |  | 0 | 3801.1756 | 3773.7155 | 3777.8279 | 3779.3439 | 3750.2024 | 633 | [6 empty] | 0 | 633 | -824.7578 | [13 empty] | 40098.1092 | 59.965 | 3768.5029 | 335 | -227.6559 | 16 | 252 | 10 | 0 | -103 | 7629 | 27.9999
| 40098.1092 | 59.965 | 3768.5029 |  |  |  | 27.9999 | 26.982 |  | 0 | 3801.7237 | 3773.698 | 3777.9081 | 3779.3439 | 3750.3005 | 633 | [6 empty] | 0 | 633 | -824.7578 | [13 empty] | 40098.1092 | 59.965 | 3768.5029 | 335 | -227.6559 | 16 | 252 | 10 | 0 | -103 | 7629 | 27.9999
| 40098.1092 | 59.97 | 3767.3662 |  |  |  | 23.999 | 25.9379 |  | 0 | 3800.6797 | 3773.6768 | 3777.9843 | 3779.3439 | 3750.3979 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1092 | 59.97 | 3767.3662 | 335 | -227.6559 | 16 | 252.5 | 10 | 0 | -103 | 7630 | 23.999
| 40098.1092 | 59.968 | 3764.7861 |  |  |  | 25.6012 | 25.8201 |  | 0 | 3800.5618 | 3773.6472 | 3778.0596 | 3779.3439 | 3750.4947 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1092 | 59.968 | 3764.7861 | 335 | -227.6559 | 16 | 253 | 10 | 0 | -103 | 7631 | 25.6012
| 40098.1093 | 59.968 | 3764.7861 |  |  |  | 25.6012 | 25.7435 |  | 0 | 3800.4852 | 3773.6178 | 3778.1341 | 3779.3439 | 3750.5909 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1093 | 59.968 | 3764.7861 | 335 | -227.6559 | 16 | 253 | 10 | 0 | -103 | 7631 | 25.6012
| 40098.1093 | 59.965 | 3759.5918 |  |  |  | 27.9999 | 26.5332 |  | 0 | 3801.275 | 3773.5713 | 3778.2107 | 3779.3439 | 3750.6864 | 633 | [6 empty] | 0 | 633 | -824.7578 | [13 empty] | 40098.1093 | 59.965 | 3759.5918 | 335 | -227.6559 | 16 | 253.5 | 10 | 0 | -103 | 7635 | 27.9999
| 40098.1093 | 59.969 | 3761.8938 |  |  |  | 24.7986 | 25.9261 |  | 0 | 3800.6678 | 3773.5328 | 3778.2848 | 3779.3439 | 3750.7813 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1093 | 59.969 | 3761.8938 | 335 | -225.0181 | 16 | 254 | 10 | 0 | -103 | 7638 | 24.7986
| 40098.1093 | 59.969 | 3761.8938 |  |  |  | 24.7986 | 25.5315 |  | 0 | 3800.2732 | 3773.4945 | 3778.3571 | 3779.3439 | 3750.8756 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1093 | 59.969 | 3761.8938 | 335 | -225.0181 | 16 | 254 | 10 | 0 | -103 | 7638 | 24.7986
| 40098.1094 | 59.967 | 3760.5825 |  |  |  | 26.4008 | 25.8357 |  | 0 | 3800.5775 | 3773.4522 | 3778.43 | 3779.3439 | 3750.9692 | 633 | [6 empty] | 0 | 633 | -846.8125 | [13 empty] | 40098.1094 | 59.967 | 3760.5825 | 335 | -225.0181 | 16 | 254.5 | 10 | 0 | -103 | 7639 | 26.4008
| 40098.1094 | 59.966 | 3760.1575 |  |  |  | 27.2003 | 26.3133 |  | 0 | 3801.0551 | 3773.4087 | 3778.5039 | 3779.3439 | 3751.0623 | 633 | [6 empty] | 0 | 633 | -835.6397 | [13 empty] | 40098.1094 | 59.966 | 3760.1575 | 335 | -225.0181 | 16 | 255 | 10 | 0 | -103 | 7642 | 27.2003
| 40098.1094 | 59.966 | 3760.1575 |  |  |  | 27.2003 | 26.6238 |  | 0 | 3801.3655 | 3773.3656 | 3778.5784 | 3779.3439 | 3751.1547 | 633 | [6 empty] | 0 | 633 | -835.6397 | [13 empty] | 40098.1094 | 59.966 | 3760.1575 | 335 | -225.0181 | 16 | 255 | 10 | 0 | -103 | 7642 | 27.2003
| 40098.1094 | 59.979 | 3759.4949 |  |  |  | 16.7999 | 23.1854 |  | 0 | 3797.9272 | 3773.3205 | 3778.6412 | 3779.3439 | 3751.2465 | 633 | [6 empty] | 0 | 633 | -1008.7671 | [13 empty] | 40098.1094 | 59.979 | 3759.4949 | 335 | -225.0181 | 16 | 255.5 | 10 | 0 | -103 | 7644 | 16.7999
| 40098.1095 | 59.983 | 3757.7729 |  |  |  | 13.5986 | 19.83 |  | 0 | 3794.5718 | 3773.2702 | 3778.6928 | 3779.3439 | 3751.3377 | 633 | [6 empty] | 0 | 633 | -1077.479 | [13 empty] | 40098.1095 | 59.983 | 3757.7729 | 335 | -225.0181 | 16 | 256 | 10 | 0 | -103 | 7645 | 13.5986
| 40098.1095 | 59.983 | 3757.7729 |  |  |  | 13.5986 | 17.6491 |  | 0 | 3792.3908 | 3773.2202 | 3778.737 | 3779.3439 | 3751.4284 | 633 | [6 empty] | 0 | 633 | -1077.479 | [13 empty] | 40098.1095 | 59.983 | 3757.7729 | 335 | -225.0181 | 16 | 256 | 10 | 0 | -103 | 7645 | 13.5986
| 40098.1095 | 59.974 | 3753.0874 |  |  |  | 20.8008 | 18.7522 |  | 0 | 3793.4939 | 3773.1555 | 3778.7844 | 3779.3439 | 3751.5184 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.1095 | 59.974 | 3753.0874 | 335 | -228.3652 | 16 | 256.5 | 10 | 0 | -103 | 7647 | 20.8008
| 40098.1095 | 59.965 | 3751.6367 |  |  |  | 27.9999 | 21.9889 |  | 0 | 3796.7306 | 3773.0865 | 3778.8419 | 3779.3439 | 3751.6079 | 633 | [6 empty] | 0 | 633 | -824.7578 | [13 empty] | 40098.1095 | 59.965 | 3751.6367 | 335 | -228.3652 | 16 | 257 | 10 | 0 | -103 | 7648 | 27.9999
| 40098.1095 | 59.965 | 3751.6367 |  |  |  | 27.9999 | 24.0927 |  | 0 | 3798.8345 | 3773.018 | 3778.9058 | 3779.3439 | 3751.6968 | 633 | [6 empty] | 0 | 633 | -824.7578 | [13 empty] | 40098.1095 | 59.965 | 3751.6367 | 335 | -228.3652 | 16 | 257 | 10 | 0 | -103 | 7648 | 27.9999
| 40098.1096 | 59.962 | 3758.2246 |  |  |  | 30.3986 | 26.2998 |  | 0 | 3801.0415 | 3772.9709 | 3778.9763 | 3779.3439 | 3751.7851 | 633 | [6 empty] | 0 | 633 | -793.7488 | [13 empty] | 40098.1096 | 59.962 | 3758.2246 | 335 | -228.3652 | 16 | 257.5 | 10 | 0 | -103 | 7649 | 30.3986
| 40098.1096 | 59.961 | 3759.2498 |  |  |  | 31.2012 | 28.0153 |  | 0 | 3802.757 | 3772.9273 | 3779.0518 | 3779.3439 | 3751.8729 | 633 | [6 empty] | 0 | 633 | -783.8872 | [13 empty] | 40098.1096 | 59.961 | 3759.2498 | 335 | -228.3652 | 16 | 258 | 10 | 0 | -103 | 7650 | 31.2012
| 40098.1096 | 59.961 | 3759.2498 |  |  |  | 31.2012 | 29.1303 |  | 0 | 3803.8721 | 3772.884 | 3779.1303 | 3779.3439 | 3751.9601 | 633 | [6 empty] | 0 | 633 | -783.8872 | [13 empty] | 40098.1096 | 59.961 | 3759.2498 | 335 | -228.3652 | 16 | 258 | 10 | 0 | -103 | 7650 | 31.2012
| 40098.1096 | 59.961 | 3760.9648 |  |  |  | 31.2012 | 29.8551 |  | 0 | 3804.5969 | 3772.8464 | 3779.2107 | 3779.3439 | 3752.0468 | 633 | [6 empty] | 0 | 633 | -783.8872 | [13 empty] | 40098.1096 | 59.961 | 3760.9648 | 335 | -228.3652 | 16 | 258.5 | 10 | 0 | -103 | 7651 | 31.2012
| 40098.1097 | 59.963 | 3762.0222 |  |  |  | 29.599 | 29.7655 |  | 0 | 3804.5072 | 3772.8124 | 3779.2902 | 3779.3439 | 3752.1329 | 633 | [6 empty] | 0 | 633 | -803.8228 | [13 empty] | 40098.1097 | 59.963 | 3762.0222 | 335 | -234.0753 | 16 | 259 | 10 | 0 | -103 | 7652 | 29.599
| 40098.1097 | 59.963 | 3762.0222 |  |  |  | 29.599 | 29.7072 |  | 0 | 3804.4489 | 3772.7786 | 3779.3691 | 3779.3439 | 3752.2184 | 633 | [6 empty] | 0 | 633 | -803.8228 | [13 empty] | 40098.1097 | 59.963 | 3762.0222 | 335 | -234.0753 | 16 | 259 | 10 | 0 | -103 | 7652 | 29.599
| 40098.1097 | 59.959 | 3763.1001 |  |  |  | 32.8003 | 30.7898 |  | 0 | 3805.5315 | 3772.7483 | 3779.4508 | 3779.3439 | 3752.3035 | 633 | [6 empty] | 0 | 633 | -764.9517 | [13 empty] | 40098.1097 | 59.959 | 3763.1001 | 335 | -234.0753 | 16 | 259.5 | 10 | 0 | -103 | 7653 | 32.8003
| 40098.1097 | 59.951 | 3763.8582 |  |  |  | 39.1998 | 33.7333 |  | 0 | 3808.475 | 3772.7206 | 3779.5413 | 3779.3439 | 3752.388 | 633 | [6 empty] | 0 | 633 | -697.5227 | [13 empty] | 40098.1097 | 59.951 | 3763.8582 | 335 | -234.0753 | 16 | 260 | 10 | 0 | -103 | 7654 | 39.1998
| 40098.1098 | 59.951 | 3763.8582 |  |  |  | 39.1998 | 35.6466 |  | 0 | 3810.3883 | 3772.6931 | 3779.6371 | 3779.3439 | 3752.4719 | 633 | [6 empty] | 0 | 633 | -697.5227 | [13 empty] | 40098.1098 | 59.951 | 3763.8582 | 335 | -234.0753 | 16 | 260 | 10 | 0 | -103 | 7654 | 39.1998
| 40098.1098 | 59.953 | 3766.1267 |  |  |  | 37.6007 | 36.3305 |  | 0 | 3811.0723 | 3772.6728 | 3779.7344 | 3779.3439 | 3752.5554 | 633 | [6 empty] | 0 | 633 | -713.2327 | [13 empty] | 40098.1098 | 59.953 | 3766.1267 | 335 | -234.0753 | 16 | 260.5 | 10 | 0 | -103 | 7655 | 37.6007
| 40098.1098 | 59.957 | 3768.3389 |  |  |  | 34.3994 | 35.6546 |  | 0 | 3810.3964 | 3772.6594 | 3779.829 | 3779.3439 | 3752.6383 | 633 | [6 empty] | 0 | 633 | -746.9095 | [13 empty] | 40098.1098 | 59.957 | 3768.3389 | 335 | -234.0753 | 16 | 261 | 10 | 0 | -103 | 7655 | 34.3994
| 40098.1098 | 59.957 | 3768.3389 |  |  |  | 34.3994 | 35.2153 |  | 0 | 3809.957 | 3772.6461 | 3779.9217 | 3779.3439 | 3752.7208 | 633 | [6 empty] | 0 | 633 | -746.9095 | [13 empty] | 40098.1098 | 59.957 | 3768.3389 | 335 | -234.0753 | 16 | 261 | 10 | 0 | -103 | 7655 | 34.3994
| 40098.1098 | 59.956 | 3767.4375 |  |  |  | 35.199 | 35.2096 |  | 0 | 3809.9513 | 3772.6301 | 3780.0138 | 3779.3439 | 3752.8027 | 633 | [6 empty] | 0 | 633 | -738.2038 | [13 empty] | 40098.1098 | 59.956 | 3767.4375 | 335 | -228.7982 | 16 | 261.5 | 10 | 0 | -103 | 7656 | 35.199
| 40098.1099 | 59.963 | 3765.6064 |  |  |  | 29.599 | 33.2459 |  | 0 | 3807.9876 | 3772.6086 | 3780.0994 | 3779.3439 | 3752.8841 | 633 | [6 empty] | 0 | 633 | -803.8228 | [13 empty] | 40098.1099 | 59.963 | 3765.6064 | 335 | -228.7982 | 16 | 262 | 10 | 0 | -103 | 7656 | 29.599
| 40098.1099 | 59.963 | 3765.6064 |  |  |  | 29.599 | 31.9695 |  | 0 | 3806.7112 | 3772.5873 | 3780.1805 | 3779.3439 | 3752.965 | 633 | [6 empty] | 0 | 633 | -803.8228 | [13 empty] | 40098.1099 | 59.963 | 3765.6064 | 335 | -228.7982 | 16 | 262 | 10 | 0 | -103 | 7656 | 29.599
| 40098.1099 | 59.961 | 3761.5703 |  |  |  | 31.2012 | 31.7006 |  | 0 | 3806.4423 | 3772.5538 | 3780.2603 | 3779.3439 | 3753.0454 | 633 | [6 empty] | 0 | 633 | -783.8872 | [13 empty] | 40098.1099 | 59.961 | 3761.5703 | 335 | -228.7982 | 16 | 262.5 | 10 | 0 | -103 | 7657 | 31.2012
| 40098.1099 | 59.963 | 3761.9199 |  |  |  | 29.599 | 30.965 |  | 0 | 3805.7068 | 3772.5216 | 3780.3374 | 3779.3439 | 3753.1254 | 633 | [6 empty] | 0 | 633 | -803.8228 | [13 empty] | 40098.1099 | 59.963 | 3761.9199 | 335 | -228.7982 | 16 | 263 | 10 | 0 | -103 | 7657 | 29.599
| 40098.11 | 59.963 | 3761.9199 |  |  |  | 29.599 | 30.4869 |  | 0 | 3805.2286 | 3772.4896 | 3780.4126 | 3779.3439 | 3753.2048 | 633 | [6 empty] | 0 | 633 | -803.8228 | [13 empty] | 40098.11 | 59.963 | 3761.9199 | 335 | -228.7982 | 16 | 263 | 10 | 0 | -103 | 7657 | 29.599
| 40098.11 | 59.963 | 3758.522 |  |  |  | 29.599 | 30.1761 |  | 0 | 3804.9179 | 3772.4475 | 3780.4865 | 3779.3439 | 3753.2838 | 633 | [6 empty] | 0 | 633 | -803.8228 | [13 empty] | 40098.11 | 59.963 | 3758.522 | 335 | -228.7982 | 16 | 263.5 | 10 | 0 | -103 | 7658 | 29.599
| 40098.11 | 59.968 | 3752.4287 |  |  |  | 25.6012 | 28.5749 |  | 0 | 3803.3166 | 3772.3874 | 3780.555 | 3779.3439 | 3753.3623 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.11 | 59.968 | 3752.4287 | 335 | -229.467 | 16 | 264 | 10 | 0 | -103 | 7658 | 25.6012
| 40098.11 | 59.968 | 3752.4287 |  |  |  | 25.6012 | 27.5341 |  | 0 | 3802.2758 | 3772.3276 | 3780.62 | 3779.3439 | 3753.4403 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.11 | 59.968 | 3752.4287 | 335 | -229.467 | 16 | 264 | 10 | 0 | -103 | 7658 | 25.6012
| 40098.1101 | 59.968 | 3753.8296 |  |  |  | 25.6012 | 26.8576 |  | 0 | 3801.5993 | 3772.2724 | 3780.6827 | 3779.3439 | 3753.5179 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1101 | 59.968 | 3753.8296 | 335 | -229.467 | 16 | 264.5 | 10 | 0 | -103 | 7659 | 25.6012
| 40098.1101 | 59.97 | 3753.5103 |  |  |  | 23.999 | 25.8571 |  | 0 | 3800.5988 | 3772.2166 | 3780.7419 | 3779.3439 | 3753.5949 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1101 | 59.97 | 3753.5103 | 335 | -229.467 | 16 | 265 | 10 | 0 | -103 | 7659 | 23.999
| 40098.1101 | 59.97 | 3753.5103 |  |  |  | 23.999 | 25.2068 |  | 0 | 3799.9485 | 3772.161 | 3780.7989 | 3779.3439 | 3753.6716 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1101 | 59.97 | 3753.5103 | 335 | -229.467 | 16 | 265 | 10 | 0 | -103 | 7659 | 23.999
| 40098.1101 | 59.973 | 3752.7407 |  |  |  | 21.6003 | 23.9445 |  | 0 | 3798.6863 | 3772.1036 | 3780.8519 | 3779.3439 | 3753.7478 | 633 | [6 empty] | 0 | 633 | -920.7222 | [13 empty] | 40098.1101 | 59.973 | 3752.7407 | 335 | -229.467 | 16 | 265.5 | 10 | 0 | -103 | 7659 | 21.6003
| 40098.1102 | 59.965 | 3753.1782 |  |  |  | 27.9999 | 25.3639 |  | 0 | 3800.1056 | 3772.0478 | 3780.9087 | 3779.3439 | 3753.8235 | 633 | [6 empty] | 0 | 633 | -824.7578 | [13 empty] | 40098.1102 | 59.965 | 3753.1782 | 335 | -229.467 | 16 | 266 | 10 | 0 | -103 | 7660 | 27.9999
| 40098.1102 | 59.965 | 3753.1782 |  |  |  | 27.9999 | 26.2865 |  | 0 | 3801.0282 | 3771.9923 | 3780.9678 | 3779.3439 | 3753.8988 | 633 | [6 empty] | 0 | 633 | -824.7578 | [13 empty] | 40098.1102 | 59.965 | 3753.1782 | 335 | -229.467 | 16 | 266 | 10 | 0 | -103 | 7660 | 27.9999
| 40098.1102 | 59.967 | 3753.2905 |  |  |  | 26.4008 | 26.3265 |  | 0 | 3801.0682 | 3771.9374 | 3781.0268 | 3779.3439 | 3753.9736 | 633 | [6 empty] | 0 | 633 | -846.8125 | [13 empty] | 40098.1102 | 59.967 | 3753.2905 | 335 | -228.9802 | 16 | 266.5 | 10 | 0 | -103 | 7660 | 26.4008
| 40098.1102 | 59.972 | 3752.8716 |  |  |  | 22.3999 | 24.9522 |  | 0 | 3799.6939 | 3771.8817 | 3781.0814 | 3779.3439 | 3754.048 | 633 | [6 empty] | 0 | 633 | -907.5291 | [13 empty] | 40098.1102 | 59.972 | 3752.8716 | 335 | -228.9802 | 16 | 267 | 10 | 0 | -103 | 7661 | 22.3999
| 40098.1102 | 59.972 | 3752.8716 |  |  |  | 22.3999 | 24.0589 |  | 0 | 3798.8006 | 3771.8262 | 3781.133 | 3779.3439 | 3754.122 | 633 | [6 empty] | 0 | 633 | -907.5291 | [13 empty] | 40098.1102 | 59.972 | 3752.8716 | 335 | -228.9802 | 16 | 267 | 10 | 0 | -103 | 7661 | 22.3999
| 40098.1103 | 59.976 | 3749.3979 |  |  |  | 19.1986 | 22.3578 |  | 0 | 3797.0995 | 3771.7611 | 3781.1794 | 3779.3439 | 3754.1955 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.1103 | 59.976 | 3749.3979 | 335 | -228.9802 | 16 | 267.5 | 10 | 0 | -103 | 7661 | 19.1986
| 40098.1103 | 59.969 | 3747.4758 |  |  |  | 24.7986 | 23.2121 |  | 0 | 3797.9538 | 3771.6907 | 3781.2281 | 3779.3439 | 3754.2686 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1103 | 59.969 | 3747.4758 | 335 | -228.9802 | 16 | 268 | 10 | 0 | -103 | 7662 | 24.7986
| 40098.1103 | 59.969 | 3747.4758 |  |  |  | 24.7986 | 23.7673 |  | 0 | 3798.5091 | 3771.6207 | 3781.278 | 3779.3439 | 3754.3413 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1103 | 59.969 | 3747.4758 | 335 | -228.9802 | 16 | 268 | 10 | 0 | -103 | 7662 | 24.7986
| 40098.1103 | 59.973 | 3741.2852 |  |  |  | 21.6003 | 23.0089 |  | 0 | 3797.7506 | 3771.5333 | 3781.3255 | 3779.3439 | 3754.4136 | 633 | [6 empty] | 0 | 633 | -920.7222 | [13 empty] | 40098.1103 | 59.973 | 3741.2852 | 335 | -228.9802 | 16 | 268.5 | 10 | 0 | -103 | 7662 | 21.6003
| 40098.1104 | 59.978 | 3746.6509 |  |  |  | 17.5995 | 21.1156 |  | 0 | 3795.8573 | 3771.4617 | 3781.3672 | 3779.3439 | 3754.4854 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1104 | 59.978 | 3746.6509 | 335 | -219.9756 | 16 | 269 | 10 | 0 | -103 | 7663 | 17.5995
| 40098.1104 | 59.978 | 3746.6509 |  |  |  | 17.5995 | 19.885 |  | 0 | 3794.6267 | 3771.3907 | 3781.4052 | 3779.3439 | 3754.5568 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1104 | 59.978 | 3746.6509 | 335 | -219.9756 | 16 | 269 | 10 | 0 | -103 | 7663 | 17.5995
| 40098.1104 | 59.981 | 3743.3506 |  |  |  | 15.2008 | 18.2455 |  | 0 | 3792.9872 | 3771.3105 | 3781.4383 | 3779.3439 | 3754.6279 | 633 | [6 empty] | 0 | 633 | -1041.9588 | [13 empty] | 40098.1104 | 59.981 | 3743.3506 | 335 | -219.9756 | 16 | 269.5 | 10 | 0 | -103 | 7663 | 15.2008
| 40098.1104 | 59.981 | 3741.6182 |  |  |  | 15.2008 | 17.1799 |  | 0 | 3791.9216 | 3771.226 | 3781.4682 | 3779.3439 | 3754.6985 | 633 | [6 empty] | 0 | 633 | -1041.9588 | [13 empty] | 40098.1104 | 59.981 | 3741.6182 | 335 | -219.9756 | 16 | 270 | 10 | 0 | -103 | 7664 | 15.2008
| 40098.1105 | 59.981 | 3741.6182 |  |  |  | 15.2008 | 16.4872 |  | 0 | 3791.2289 | 3771.1418 | 3781.4959 | 3779.3439 | 3754.7687 | 633 | [6 empty] | 0 | 633 | -1041.9588 | [13 empty] | 40098.1105 | 59.981 | 3741.6182 | 335 | -219.9756 | 16 | 270 | 10 | 0 | -103 | 7664 | 15.2008
| 40098.1105 | 59.982 | 3738.4844 |  |  |  | 14.4012 | 15.7571 |  | 0 | 3790.4988 | 3771.0493 | 3781.5214 | 3779.3439 | 3754.8385 | 633 | [6 empty] | 0 | 633 | -1059.3874 | [13 empty] | 40098.1105 | 59.982 | 3738.4844 | 335 | -219.9756 | 16 | 270.5 | 10 | 0 | -103 | 7664 | 14.4012
| 40098.1105 | 59.984 | 3738.9014 |  |  |  | 12.7991 | 14.7218 |  | 0 | 3789.4635 | 3770.9585 | 3781.5439 | 3779.3439 | 3754.9079 | 633 | [6 empty] | 0 | 633 | -1096.1268 | [13 empty] | 40098.1105 | 59.984 | 3738.9014 | 335 | -219.9756 | 16 | 271 | 10 | 0 | -103 | 7665 | 12.7991
| 40098.1105 | 59.984 | 3738.9014 |  |  |  | 12.7991 | 14.0488 |  | 0 | 3788.7906 | 3770.8682 | 3781.5643 | 3779.3439 | 3754.977 | 633 | [6 empty] | 0 | 633 | -1096.1268 | [13 empty] | 40098.1105 | 59.984 | 3738.9014 | 335 | -219.9756 | 16 | 271 | 10 | 0 | -103 | 7665 | 12.7991
| 40098.1105 | 59.982 | 3737.2732 |  |  |  | 14.4012 | 14.1722 |  | 0 | 3788.9139 | 3770.7738 | 3781.5849 | 3779.3439 | 3755.0456 | 633 | [6 empty] | 0 | 633 | -1059.3874 | [13 empty] | 40098.1105 | 59.982 | 3737.2732 | 335 | -229.0892 | 16 | 271.5 | 10 | 0 | -103 | 7666 | 14.4012
| 40098.1106 | 59.979 | 3736.3083 |  |  |  | 16.7999 | 15.0919 |  | 0 | 3789.8336 | 3770.6773 | 3781.608 | 3779.3439 | 3755.1138 | 633 | [6 empty] | 0 | 633 | -1008.7671 | [13 empty] | 40098.1106 | 59.979 | 3736.3083 | 335 | -229.0892 | 16 | 272 | 10 | 0 | -103 | 7666 | 16.7999
| 40098.1106 | 59.979 | 3736.3083 |  |  |  | 16.7999 | 15.6897 |  | 0 | 3790.4314 | 3770.5813 | 3781.6327 | 3779.3439 | 3755.1817 | 633 | [6 empty] | 0 | 633 | -1008.7671 | [13 empty] | 40098.1106 | 59.979 | 3736.3083 | 335 | -229.0892 | 16 | 272 | 10 | 0 | -103 | 7666 | 16.7999
| 40098.1106 | 59.98 | 3735.4482 |  |  |  | 16.0004 | 15.7984 |  | 0 | 3790.5402 | 3770.4834 | 3781.6575 | 3779.3439 | 3755.2492 | 633 | [6 empty] | 0 | 633 | -1025.0944 | [13 empty] | 40098.1106 | 59.98 | 3735.4482 | 335 | -229.0892 | 16 | 272.5 | 10 | 0 | -103 | 7667 | 16.0004
| 40098.1106 | 59.978 | 3735.6497 |  |  |  | 17.5995 | 16.4288 |  | 0 | 3791.1705 | 3770.3867 | 3781.6839 | 3779.3439 | 3755.3163 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1106 | 59.978 | 3735.6497 | 335 | -229.0892 | 16 | 273 | 10 | 0 | -103 | 7668 | 17.5995
| 40098.1107 | 59.978 | 3735.6497 |  |  |  | 17.5995 | 16.8385 |  | 0 | 3791.5803 | 3770.2904 | 3781.7113 | 3779.3439 | 3755.3831 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1107 | 59.978 | 3735.6497 | 335 | -229.0892 | 16 | 273 | 10 | 0 | -103 | 7668 | 17.5995
| 40098.1107 | 59.98 | 3738.012 |  |  |  | 16.0004 | 16.5452 |  | 0 | 3791.2869 | 3770.2013 | 3781.7378 | 3779.3439 | 3755.4494 | 633 | [6 empty] | 0 | 633 | -1025.0944 | [13 empty] | 40098.1107 | 59.98 | 3738.012 | 335 | -229.0892 | 16 | 273.5 | 10 | 0 | -103 | 7668 | 16.0004
| 40098.1107 | 59.98 | 3736.7476 |  |  |  | 16.0004 | 16.3545 |  | 0 | 3791.0962 | 3770.1091 | 3781.7635 | 3779.3439 | 3755.5154 | 633 | [6 empty] | 0 | 633 | -1025.0944 | [13 empty] | 40098.1107 | 59.98 | 3736.7476 | 335 | -229.6633 | 16 | 274 | 10 | 0 | -103 | 7669 | 16.0004
| 40098.1107 | 59.98 | 3736.7476 |  |  |  | 16.0004 | 16.2306 |  | 0 | 3790.9723 | 3770.0175 | 3781.7888 | 3779.3439 | 3755.5811 | 633 | [6 empty] | 0 | 633 | -1025.0944 | [13 empty] | 40098.1107 | 59.98 | 3736.7476 | 335 | -229.6633 | 16 | 274 | 10 | 0 | -103 | 7669 | 16.0004
| 40098.1108 | 59.978 | 3736.0674 |  |  |  | 17.5995 | 16.7097 |  | 0 | 3791.4514 | 3769.9245 | 3781.8153 | 3779.3439 | 3755.6464 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1108 | 59.978 | 3736.0674 | 335 | -229.6633 | 16 | 274.5 | 10 | 0 | -103 | 7669 | 17.5995
| 40098.1108 | 59.972 | 3736.0942 |  |  |  | 22.3999 | 18.7013 |  | 0 | 3793.443 | 3769.832 | 3781.8471 | 3779.3439 | 3755.7113 | 633 | [6 empty] | 0 | 633 | -907.5291 | [13 empty] | 40098.1108 | 59.972 | 3736.0942 | 335 | -229.6633 | 16 | 275 | 10 | 0 | -103 | 7670 | 22.3999
| 40098.1108 | 59.972 | 3736.0942 |  |  |  | 22.3999 | 19.9958 |  | 0 | 3794.7375 | 3769.7401 | 3781.8822 | 3779.3439 | 3755.7759 | 633 | [6 empty] | 0 | 633 | -907.5291 | [13 empty] | 40098.1108 | 59.972 | 3736.0942 | 335 | -229.6633 | 16 | 275 | 10 | 0 | -103 | 7670 | 22.3999
| 40098.1108 | 59.971 | 3738.571 |  |  |  | 23.1995 | 21.1171 |  | 0 | 3795.8588 | 3769.6554 | 3781.9202 | 3779.3439 | 3755.8401 | 633 | [6 empty] | 0 | 633 | -894.7087 | [13 empty] | 40098.1108 | 59.971 | 3738.571 | 335 | -229.6633 | 16 | 275.5 | 10 | 0 | -103 | 7670 | 23.1995
| 40098.1108 | 59.974 | 3738.8748 |  |  |  | 20.8008 | 21.0064 |  | 0 | 3795.7481 | 3769.572 | 3781.9577 | 3779.3439 | 3755.904 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.1108 | 59.974 | 3738.8748 | 335 | -229.6633 | 16 | 276 | 10 | 0 | -103 | 7671 | 20.8008
| 40098.1109 | 59.974 | 3738.8748 |  |  |  | 20.8008 | 20.9344 |  | 0 | 3795.6762 | 3769.489 | 3781.9947 | 3779.3439 | 3755.9675 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.1109 | 59.974 | 3738.8748 | 335 | -229.6633 | 16 | 276 | 10 | 0 | -103 | 7671 | 20.8008
| 40098.1109 | 59.975 | 3738.647 |  |  |  | 20.0012 | 20.6078 |  | 0 | 3795.3495 | 3769.4059 | 3782.0307 | 3779.3439 | 3756.0307 | 633 | [6 empty] | 0 | 633 | -948.2936 | [13 empty] | 40098.1109 | 59.975 | 3738.647 | 335 | -229.2339 | 16 | 276.5 | 10 | 0 | -103 | 7671 | 20.0012
| 40098.1109 | 59.972 | 3737.6841 |  |  |  | 22.3999 | 21.235 |  | 0 | 3795.9768 | 3769.3206 | 3782.0682 | 3779.3439 | 3756.0935 | 633 | [6 empty] | 0 | 633 | -907.5291 | [13 empty] | 40098.1109 | 59.972 | 3737.6841 | 335 | -229.2339 | 16 | 277 | 10 | 0 | -103 | 7672 | 22.3999
| 40098.1109 | 59.972 | 3737.6841 |  |  |  | 22.3999 | 21.6427 |  | 0 | 3796.3845 | 3769.2358 | 3782.1066 | 3779.3439 | 3756.156 | 633 | [6 empty] | 0 | 633 | -907.5291 | [13 empty] | 40098.1109 | 59.972 | 3737.6841 | 335 | -229.2339 | 16 | 277 | 10 | 0 | -103 | 7672 | 22.3999
| 40098.111 | 59.969 | 3737.8921 |  |  |  | 24.7986 | 22.7473 |  | 0 | 3797.489 | 3769.152 | 3782.1477 | 3779.3439 | 3756.2182 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.111 | 59.969 | 3737.8921 | 335 | -229.2339 | 16 | 277.5 | 10 | 0 | -103 | 7673 | 24.7986
| 40098.111 | 59.974 | 3740.0168 |  |  |  | 20.8008 | 22.066 |  | 0 | 3796.8077 | 3769.0743 | 3782.1868 | 3779.3439 | 3756.28 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.111 | 59.974 | 3740.0168 | 335 | -229.2339 | 16 | 278 | 10 | 0 | -103 | 7673 | 20.8008
| 40098.111 | 59.974 | 3740.0168 |  |  |  | 20.8008 | 21.6232 |  | 0 | 3796.3649 | 3768.997 | 3782.2245 | 3779.3439 | 3756.3415 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.111 | 59.974 | 3740.0168 | 335 | -229.2339 | 16 | 278 | 10 | 0 | -103 | 7673 | 20.8008
| 40098.111 | 59.972 | 3742.0527 |  |  |  | 22.3999 | 21.895 |  | 0 | 3796.6368 | 3768.9255 | 3782.2628 | 3779.3439 | 3756.4027 | 633 | [6 empty] | 0 | 633 | -907.5291 | [13 empty] | 40098.111 | 59.972 | 3742.0527 | 350 | -229.2339 | 16 | 278.5 | 10 | 0 | -103 | 7673 | 22.3999
| 40098.1111 | 59.972 | 3742.4238 |  |  |  | 22.3999 | 22.0717 |  | 0 | 3796.8135 | 3768.8554 | 3782.3013 | 3779.3439 | 3756.4635 | 633 | [6 empty] | 0 | 633 | -907.5291 | [13 empty] | 40098.1111 | 59.972 | 3742.4238 | 350 | -231.4099 | 16 | 279 | 10 | 0 | -103 | 7673 | 22.3999
| 40098.1111 | 59.972 | 3742.4238 |  |  |  | 22.3999 | 22.1866 |  | 0 | 3796.9283 | 3768.7857 | 3782.3399 | 3779.3439 | 3756.5241 | 633 | [6 empty] | 0 | 633 | -907.5291 | [13 empty] | 40098.1111 | 59.972 | 3742.4238 | 350 | -231.4099 | 16 | 279 | 10 | 0 | -103 | 7673 | 22.3999
| 40098.1111 | 59.977 | 3742.2451 |  |  |  | 18.399 | 20.861 |  | 0 | 3795.6027 | 3768.7158 | 3782.3748 | 3779.3439 | 3756.5843 | 633 | [6 empty] | 0 | 633 | -977.6248 | [13 empty] | 40098.1111 | 59.977 | 3742.2451 | 350 | -231.4099 | 16 | 279.5 | 10 | 0 | -103 | 7673 | 18.399
| 40098.1111 | 59.978 | 3741.7231 |  |  |  | 17.5995 | 19.7194 |  | 0 | 3794.4612 | 3768.645 | 3782.4065 | 3779.3439 | 3756.6442 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1111 | 59.978 | 3741.7231 | 350 | -231.4099 | 16 | 280 | 10 | 0 | -103 | 7673 | 17.5995
| 40098.1111 | 59.978 | 3741.7231 |  |  |  | 17.5995 | 18.9775 |  | 0 | 3793.7192 | 3768.5745 | 3782.4361 | 3779.3439 | 3756.7037 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1111 | 59.978 | 3741.7231 | 350 | -231.4099 | 16 | 280 | 10 | 0 | -103 | 7673 | 17.5995
| 40098.1112 | 59.976 | 3740.6292 |  |  |  | 19.1986 | 19.0549 |  | 0 | 3793.7966 | 3768.5016 | 3782.4658 | 3779.3439 | 3756.763 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.1112 | 59.976 | 3740.6292 | 350 | -231.4099 | 16 | 280.5 | 10 | 0 | -103 | 7673 | 19.1986
| 40098.1112 | 59.974 | 3739.9644 |  |  |  | 20.8008 | 19.6659 |  | 0 | 3794.4077 | 3768.4272 | 3782.4969 | 3779.3439 | 3756.822 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.1112 | 59.974 | 3739.9644 | 350 | -231.4099 | 16 | 281 | 10 | 0 | -103 | 7673 | 20.8008
| 40098.1112 | 59.974 | 3739.9644 |  |  |  | 20.8008 | 20.0631 |  | 0 | 3794.8049 | 3768.3533 | 3782.5288 | 3779.3439 | 3756.8806 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.1112 | 59.974 | 3739.9644 | 350 | -231.4099 | 16 | 281 | 10 | 0 | -103 | 7673 | 20.8008
| 40098.1112 | 59.977 | 3742.8325 |  |  |  | 18.399 | 19.4807 |  | 0 | 3794.2224 | 3768.2872 | 3782.5591 | 3779.3439 | 3756.939 | 633 | [6 empty] | 0 | 633 | -977.6248 | [13 empty] | 40098.1112 | 59.977 | 3742.8325 | 350 | -218.6223 | 16 | 281.5 | 10 | 0 | -103 | 7673 | 18.399
| 40098.1113 | 59.978 | 3741.2678 |  |  |  | 17.5995 | 18.8223 |  | 0 | 3793.564 | 3768.2174 | 3782.5876 | 3779.3439 | 3756.997 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1113 | 59.978 | 3741.2678 | 350 | -218.6223 | 16 | 282 | 10 | 0 | -103 | 7673 | 17.5995
| 40098.1113 | 59.978 | 3741.2678 |  |  |  | 17.5995 | 18.3943 |  | 0 | 3793.136 | 3768.1479 | 3782.6147 | 3779.3439 | 3757.0548 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1113 | 59.978 | 3741.2678 | 350 | -218.6223 | 16 | 282 | 10 | 0 | -103 | 7673 | 17.5995
| 40098.1113 | 59.979 | 3738.9658 |  |  |  | 16.7999 | 17.8363 |  | 0 | 3792.578 | 3768.0729 | 3782.6404 | 3779.3439 | 3757.1122 | 633 | [6 empty] | 0 | 633 | -1008.7671 | [13 empty] | 40098.1113 | 59.979 | 3738.9658 | 350 | -218.6223 | 16 | 282.5 | 10 | 0 | -103 | 7673 | 16.7999
| 40098.1113 | 59.977 | 3738.7061 |  |  |  | 18.399 | 18.0332 |  | 0 | 3792.775 | 3767.9976 | 3782.6663 | 3779.3439 | 3757.1693 | 633 | [6 empty] | 0 | 633 | -977.6248 | [13 empty] | 40098.1113 | 59.977 | 3738.7061 | 350 | -218.6223 | 16 | 283 | 10 | 0 | -103 | 7673 | 18.399
| 40098.1114 | 59.977 | 3738.7061 |  |  |  | 18.399 | 18.1613 |  | 0 | 3792.903 | 3767.9227 | 3782.6925 | 3779.3439 | 3757.2262 | 633 | [6 empty] | 0 | 633 | -977.6248 | [13 empty] | 40098.1114 | 59.977 | 3738.7061 | 350 | -218.6223 | 16 | 283 | 10 | 0 | -103 | 7673 | 18.399
| 40098.1114 | 59.974 | 3739.8596 |  |  |  | 20.8008 | 19.0851 |  | 0 | 3793.8268 | 3767.8511 | 3782.7209 | 3779.3439 | 3757.2828 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.1114 | 59.974 | 3739.8596 | 350 | -218.6223 | 16 | 283.5 | 10 | 0 | -103 | 7673 | 20.8008
| 40098.1114 | 59.971 | 3738.1016 |  |  |  | 23.1995 | 20.5251 |  | 0 | 3795.2669 | 3767.7754 | 3782.7528 | 3779.3439 | 3757.3391 | 633 | [6 empty] | 0 | 633 | -894.7087 | [13 empty] | 40098.1114 | 59.971 | 3738.1016 | 350 | -213.5359 | 16 | 284 | 10 | 0 | -103 | 7673 | 23.1995
| 40098.1114 | 59.971 | 3738.1016 |  |  |  | 23.1995 | 21.4611 |  | 0 | 3796.2029 | 3767.7001 | 3782.787 | 3779.3439 | 3757.395 | 633 | [6 empty] | 0 | 633 | -894.7087 | [13 empty] | 40098.1114 | 59.971 | 3738.1016 | 350 | -213.5359 | 16 | 284 | 10 | 0 | -103 | 7673 | 23.1995
| 40098.1114 | 59.971 | 3743.5068 |  |  |  | 23.1995 | 22.0696 |  | 0 | 3796.8113 | 3767.6388 | 3782.8225 | 3779.3439 | 3757.4508 | 633 | [6 empty] | 0 | 633 | -894.7087 | [13 empty] | 40098.1114 | 59.971 | 3743.5068 | 350 | -213.5359 | 16 | 284.5 | 10 | 0 | -103 | 7673 | 23.1995
| 40098.1115 | 59.968 | 3743.4187 |  |  |  | 25.6012 | 23.3056 |  | 0 | 3798.0474 | 3767.5777 | 3782.8609 | 3779.3439 | 3757.5062 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1115 | 59.968 | 3743.4187 | 350 | -213.5359 | 16 | 285 | 10 | 0 | -103 | 7673 | 25.6012
| 40098.1115 | 59.968 | 3743.4187 |  |  |  | 25.6012 | 24.1091 |  | 0 | 3798.8508 | 3767.5168 | 3782.9012 | 3779.3439 | 3757.5613 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1115 | 59.968 | 3743.4187 | 350 | -213.5359 | 16 | 285 | 10 | 0 | -103 | 7673 | 25.6012
| 40098.1115 | 59.966 | 3745.7441 |  |  |  | 27.2003 | 25.191 |  | 0 | 3799.9327 | 3767.4621 | 3782.944 | 3779.3439 | 3757.6162 | 633 | [6 empty] | 0 | 633 | -835.6397 | [13 empty] | 40098.1115 | 59.966 | 3745.7441 | 350 | -213.5359 | 16 | 285.5 | 10 | 0 | -103 | 7674 | 27.2003
| 40098.1115 | 59.971 | 3747.3396 |  |  |  | 23.1995 | 24.494 |  | 0 | 3799.2357 | 3767.4117 | 3782.9848 | 3779.3439 | 3757.6708 | 633 | [6 empty] | 0 | 633 | -894.7087 | [13 empty] | 40098.1115 | 59.971 | 3747.3396 | 350 | -213.5359 | 16 | 286 | 10 | 0 | -103 | 7675 | 23.1995
| 40098.1116 | 59.971 | 3747.3396 |  |  |  | 23.1995 | 24.0409 |  | 0 | 3798.7826 | 3767.3615 | 3783.0243 | 3779.3439 | 3757.7251 | 633 | [6 empty] | 0 | 633 | -894.7087 | [13 empty] | 40098.1116 | 59.971 | 3747.3396 | 350 | -213.5359 | 16 | 286 | 10 | 0 | -103 | 7675 | 23.1995
| 40098.1116 | 59.973 | 3749.75 |  |  |  | 21.6003 | 23.1867 |  | 0 | 3797.9284 | 3767.3176 | 3783.0615 | 3779.3439 | 3757.7791 | 633 | [6 empty] | 0 | 633 | -920.7222 | [13 empty] | 40098.1116 | 59.973 | 3749.75 | 350 | -225.6519 | 16 | 286.5 | 10 | 0 | -103 | 7676 | 21.6003
| 40098.1116 | 59.969 | 3746.2166 |  |  |  | 24.7986 | 23.7509 |  | 0 | 3798.4926 | 3767.2651 | 3783.0999 | 3779.3439 | 3757.8329 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1116 | 59.969 | 3746.2166 | 350 | -225.6519 | 16 | 287 | 10 | 0 | -103 | 7677 | 24.7986
| 40098.1116 | 59.969 | 3746.2166 |  |  |  | 24.7986 | 24.1176 |  | 0 | 3798.8593 | 3767.2129 | 3783.139 | 3779.3439 | 3757.8864 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1116 | 59.969 | 3746.2166 | 350 | -225.6519 | 16 | 287 | 10 | 0 | -103 | 7677 | 24.7986
| 40098.1117 | 59.972 | 3743.7451 |  |  |  | 22.3999 | 23.5164 |  | 0 | 3798.2581 | 3767.1548 | 3783.1764 | 3779.3439 | 3757.9397 | 633 | [6 empty] | 0 | 633 | -907.5291 | [13 empty] | 40098.1117 | 59.972 | 3743.7451 | 350 | -225.6519 | 16 | 287.5 | 10 | 0 | -103 | 7678 | 22.3999
| 40098.1117 | 59.973 | 3743.1489 |  |  |  | 21.6003 | 22.8458 |  | 0 | 3797.5875 | 3767.0955 | 3783.212 | 3779.3439 | 3757.9927 | 633 | [6 empty] | 0 | 633 | -920.7222 | [13 empty] | 40098.1117 | 59.973 | 3743.1489 | 350 | -225.6519 | 16 | 288 | 10 | 0 | -103 | 7679 | 21.6003
| 40098.1117 | 59.973 | 3743.1489 |  |  |  | 21.6003 | 22.4099 |  | 0 | 3797.1516 | 3767.0365 | 3783.2463 | 3779.3439 | 3758.0454 | 633 | [6 empty] | 0 | 633 | -920.7222 | [13 empty] | 40098.1117 | 59.973 | 3743.1489 | 350 | -225.6519 | 16 | 288 | 10 | 0 | -103 | 7679 | 21.6003
| 40098.1117 | 59.97 | 3739.4526 |  |  |  | 23.999 | 22.9661 |  | 0 | 3797.7078 | 3766.9687 | 3783.2819 | 3779.3439 | 3758.0978 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1117 | 59.97 | 3739.4526 | 350 | -225.6519 | 16 | 288.5 | 10 | 0 | -103 | 7680 | 23.999
| 40098.1117 | 59.974 | 3733.376 |  |  |  | 20.8008 | 22.2082 |  | 0 | 3796.95 | 3766.8864 | 3783.3154 | 3779.3439 | 3758.15 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.1117 | 59.974 | 3733.376 | 350 | -212.5736 | 16 | 289 | 10 | 0 | -103 | 7681 | 20.8008
| 40098.1118 | 59.974 | 3733.376 |  |  |  | 20.8008 | 21.7156 |  | 0 | 3796.4574 | 3766.8045 | 3783.3475 | 3779.3439 | 3758.202 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.1118 | 59.974 | 3733.376 | 350 | -212.5736 | 16 | 289 | 10 | 0 | -103 | 7681 | 20.8008
| 40098.1118 | 59.982 | 3737.5825 |  |  |  | 14.4012 | 19.1556 |  | 0 | 3793.8973 | 3766.7332 | 3783.3732 | 3779.3439 | 3758.2537 | 633 | [6 empty] | 0 | 633 | -1059.3874 | [13 empty] | 40098.1118 | 59.982 | 3737.5825 | 350 | -212.5736 | 16 | 289.5 | 10 | 0 | -103 | 7682 | 14.4012
| 40098.1118 | 59.985 | 3736.2295 |  |  |  | 11.9995 | 16.651 |  | 0 | 3791.3927 | 3766.659 | 3783.3927 | 3779.3439 | 3758.3051 | 633 | [6 empty] | 0 | 633 | -1115.4314 | [13 empty] | 40098.1118 | 59.985 | 3736.2295 | 350 | -212.5736 | 16 | 290 | 10 | 0 | -103 | 7684 | 11.9995
| 40098.1118 | 59.985 | 3736.2295 |  |  |  | 11.9995 | 15.023 |  | 0 | 3789.7647 | 3766.5851 | 3783.4082 | 3779.3439 | 3758.3563 | 633 | [6 empty] | 0 | 633 | -1115.4314 | [13 empty] | 40098.1118 | 59.985 | 3736.2295 | 350 | -212.5736 | 16 | 290 | 10 | 0 | -103 | 7684 | 11.9995
| 40098.1119 | 59.985 | 3733.4338 |  |  |  | 11.9995 | 13.9647 |  | 0 | 3788.7065 | 3766.5049 | 3783.421 | 3779.3439 | 3758.4072 | 633 | [6 empty] | 0 | 633 | -1115.4314 | [13 empty] | 40098.1119 | 59.985 | 3733.4338 | 350 | -212.5736 | 16 | 290.5 | 10 | 0 | -103 | 7685 | 11.9995
| 40098.1119 | 59.989 | 3733.1152 |  |  |  | 8.8013 | 12.1575 |  | 0 | 3786.8993 | 3766.4242 | 3783.4294 | 3779.3439 | 3758.4579 | 633 | [6 empty] | 0 | 633 | -1199.9649 | [13 empty] | 40098.1119 | 59.989 | 3733.1152 | 350 | -212.5736 | 16 | 291 | 10 | 0 | -103 | 7687 | 8.8013
| 40098.1119 | 59.989 | 3733.1152 |  |  |  | 8.8013 | 10.9828 |  | 0 | 3785.7246 | 3766.3439 | 3783.435 | 3779.3439 | 3758.5084 | 633 | [6 empty] | 0 | 633 | -1199.9649 | [13 empty] | 40098.1119 | 59.989 | 3733.1152 | 350 | -212.5736 | 16 | 291 | 10 | 0 | -103 | 7687 | 8.8013
| 40098.1119 | 59.989 | 3729.1802 |  |  |  | 8.8013 | 10.2193 |  | 0 | 3784.961 | 3766.2546 | 3783.4386 | 3779.3439 | 3758.5586 | 633 | [6 empty] | 0 | 633 | -1199.9649 | [13 empty] | 40098.1119 | 59.989 | 3729.1802 | 350 | -219.8973 | 16 | 291.5 | 10 | 0 | -103 | 7689 | 8.8013
| 40098.112 | 59.987 | 3725.4587 |  |  |  | 10.4004 | 10.2827 |  | 0 | 3785.0244 | 3766.1568 | 3783.4424 | 3779.3439 | 3758.6086 | 633 | [6 empty] | 0 | 633 | -1156.155 | [13 empty] | 40098.112 | 59.987 | 3725.4587 | 350 | -219.8973 | 16 | 292 | 10 | 0 | -103 | 7690 | 10.4004
| 40098.112 | 59.987 | 3725.4587 |  |  |  | 10.4004 | 10.3239 |  | 0 | 3785.0656 | 3766.0594 | 3783.4463 | 3779.3439 | 3758.6583 | 633 | [6 empty] | 0 | 633 | -1156.155 | [13 empty] | 40098.112 | 59.987 | 3725.4587 | 350 | -219.8973 | 16 | 292 | 10 | 0 | -103 | 7690 | 10.4004
| 40098.112 | 59.99 | 3720.1079 |  |  |  | 7.9987 | 9.51 |  | 0 | 3784.2518 | 3765.9497 | 3783.4482 | 3779.3439 | 3758.7078 | 633 | [6 empty] | 0 | 633 | -1223.2292 | [13 empty] | 40098.112 | 59.99 | 3720.1079 | 350 | -219.8973 | 16 | 292.5 | 10 | 0 | -103 | 7692 | 7.9987
| 40098.112 | 59.996 | 3720.9382 |  |  |  | 3.2013 | 7.302 |  | 0 | 3782.0437 | 3765.8426 | 3783.4449 | 3779.3439 | 3758.757 | 633 | [6 empty] | 0 | 633 | -1383.559 | [13 empty] | 40098.112 | 59.996 | 3720.9382 | 350 | -219.8973 | 16 | 293 | 10 | 0 | -103 | 7692 | 3.2013
| 40098.112 | 59.996 | 3720.9382 |  |  |  | 3.2013 | 5.8667 |  | 0 | 3780.6085 | 3765.7359 | 3783.4382 | 3779.3439 | 3758.806 | 633 | [6 empty] | 0 | 633 | -1383.559 | [13 empty] | 40098.112 | 59.996 | 3720.9382 | 350 | -219.8973 | 16 | 293 | 10 | 0 | -103 | 7692 | 3.2013
| 40098.1121 | 60.001 | 3725.6768 |  |  |  | -0.79956 | 3.5335 |  | 0 | 3778.2753 | 3765.641 | 3783.4259 | 3779.3439 | 3758.8548 | 633 | [6 empty] | 0 | 633 | -1553.355 | [13 empty] | 40098.1121 | 60.001 | 3725.6768 | 350 | -219.8973 | 16 | 293.5 | 10 | 0 | -103 | 7693 | -0.79956
| 40098.1121 | 60.004 | 3727.7542 |  |  |  | -3.2013 | 1.1763 |  | 0 | 3775.9181 | 3765.5514 | 3783.4082 | 3779.3439 | 3758.9034 | 633 | [6 empty] | 0 | 633 | -1676.8951 | [13 empty] | 40098.1121 | 60.004 | 3727.7542 | 350 | -231.1754 | 16 | 294 | 10 | 0 | -103 | 7693 | -3.2013
| 40098.1121 | 60.004 | 3727.7542 |  |  |  | -3.2013 | -0.35583 |  | 0 | 3774.3859 | 3765.4623 | 3783.3869 | 3779.3439 | 3758.9517 | 633 | [6 empty] | 0 | 633 | -1676.8951 | [13 empty] | 40098.1121 | 60.004 | 3727.7542 | 350 | -231.1754 | 16 | 294 | 10 | 0 | -103 | 7693 | -3.2013
| 40098.1121 | 60.006 | 3727.6833 |  |  |  | -4.8004 | -1.9114 |  | 0 | 3772.8303 | 3765.3734 | 3783.3621 | 3779.3439 | 3758.9998 | 633 | [6 empty] | 0 | 633 | -1770.6573 | [13 empty] | 40098.1121 | 60.006 | 3727.6833 | 350 | -231.1754 | 16 | 294.5 | 10 | 0 | -103 | 7694 | -4.8004
| 40098.1122 | 60.014 | 3727.2314 |  |  |  | -11.2 | -5.1624 |  | 0 | 3769.5793 | 3765.2839 | 3783.3297 | 3779.3439 | 3759.0477 | 633 | [6 empty] | 0 | 633 | -2281.0798 | [13 empty] | 40098.1122 | 60.014 | 3727.2314 | 350 | -231.1754 | 16 | 295 | 10 | 0 | -103 | 7694 | -11.2
| 40098.1122 | 60.014 | 3727.2314 |  |  |  | -11.2 | -7.2756 |  | 0 | 3767.4662 | 3765.1947 | 3783.2926 | 3779.3439 | 3759.0953 | 633 | [6 empty] | 0 | 633 | -2281.0798 | [13 empty] | 40098.1122 | 60.014 | 3727.2314 | 350 | -231.1754 | 16 | 295 | 10 | 0 | -103 | 7694 | -11.2
| 40098.1122 | 60.019 | 3726.4463 |  |  |  | -15.2008 | -10.0494 |  | 0 | 3764.6923 | 3765.1042 | 3783.2491 | 3779.3439 | 3759.1427 | 633 | [6 empty] | 0 | 633 | -2782.5464 | [13 empty] | 40098.1122 | 60.019 | 3726.4463 | 350 | -231.1754 | 16 | 295.5 | 10 | 0 | -103 | 7695 | -15.2008
| 40098.1122 | 60.025 | 3726.0156 |  |  |  | -20.0012 | -13.5325 |  | 0 | 3761.2092 | 3765.0131 | 3783.1977 | 3779.3439 | 3759.1899 | 633 | [6 empty] | 0 | 633 | -3779.4591 | [13 empty] | 40098.1122 | 60.025 | 3726.0156 | 350 | -231.1754 | 16 | 296 | 10 | 0 | -103 | 7695 | -20.0012
| 40098.1123 | 60.025 | 3726.0156 |  |  |  | -20.0012 | -15.7966 |  | 0 | 3758.9452 | 3764.9224 | 3783.1413 | 3779.3439 | 3759.2369 | 633 | [6 empty] | 0 | 633 | -3779.4591 | [13 empty] | 40098.1123 | 60.025 | 3726.0156 | 350 | -231.1754 | 16 | 296 | 10 | 0 | -103 | 7695 | -20.0012
| 40098.1123 | 60.026 | 3716.3745 |  |  |  | -20.8008 | -17.548 |  | 0 | 3757.1937 | 3764.8098 | 3783.0811 | 3779.3439 | 3759.2837 | 633 | [6 empty] | 0 | 633 | -4019.3085 | [13 empty] | 40098.1123 | 60.026 | 3716.3745 | 350 | -226.6341 | 16 | 296.5 | 10 | 0 | -103 | 7695 | -20.8008
| 40098.1123 | 60.029 | 3717.3325 |  |  |  | -23.1995 | -19.526 |  | 0 | 3755.2157 | 3764.6999 | 3783.0166 | 3779.3439 | 3759.3302 | 633 | [6 empty] | 0 | 633 | -4964.4623 | [13 empty] | 40098.1123 | 60.029 | 3717.3325 | 350 | -226.6341 | 16 | 297 | 10 | 0 | -103 | 7696 | -23.1995
| 40098.1123 | 60.029 | 3717.3325 |  |  |  | -23.1995 | -20.8117 |  | 0 | 3753.93 | 3764.5905 | 3782.9494 | 3779.3439 | 3759.3765 | 633 | [6 empty] | 0 | 633 | -4964.4623 | [13 empty] | 40098.1123 | 60.029 | 3717.3325 | 350 | -226.6341 | 16 | 297 | 10 | 0 | -103 | 7696 | -23.1995
| 40098.1123 | 60.029 | 3717.1421 |  |  |  | -23.1995 | -21.6474 |  | 0 | 3753.0943 | 3764.4811 | 3782.8806 | 3779.3439 | 3759.4227 | 633 | [6 empty] | 0 | 633 | -4964.4623 | [13 empty] | 40098.1123 | 60.029 | 3717.1421 | 350 | -226.6341 | 16 | 297.5 | 10 | 0 | -103 | 7696 | -23.1995
| 40098.1124 | 60.036 | 3715.166 |  |  |  | -28.7994 | -24.1506 |  | 0 | 3750.5911 | 3764.3678 | 3782.8064 | 3779.3439 | 3759.4686 | 633 | [6 empty] | 0 | 633 | -11007.4396 | [13 empty] | 40098.1124 | 60.036 | 3715.166 | 350 | -226.6341 | 16 | 298 | 10 | 0 | -103 | 7697 | -28.7994
| 40098.1124 | 60.036 | 3715.166 |  |  |  | -28.7994 | -25.7777 |  | 0 | 3748.964 | 3764.2549 | 3782.7288 | 3779.3439 | 3759.5142 | 633 | [6 empty] | 0 | 633 | -11007.4396 | [13 empty] | 40098.1124 | 60.036 | 3715.166 | 350 | -226.6341 | 16 | 298 | 10 | 0 | -103 | 7697 | -28.7994
| 40098.1124 | 60.037 | 3710.2834 |  |  |  | -29.599 | -27.1152 |  | 0 | 3747.6266 | 3764.1314 | 3782.6485 | 3779.3439 | 3759.5597 | 633 | [6 empty] | 0 | 633 | -13322.9347 | [13 empty] | 40098.1124 | 60.037 | 3710.2834 | 350 | -226.6341 | 16 | 298.5 | 10 | 0 | -103 | 7697 | -29.599
| 40098.1124 | 60.036 | 3710.1577 |  |  |  | -28.7994 | -27.7047 |  | 0 | 3747.0371 | 3764.0082 | 3782.5672 | 3779.3439 | 3759.605 | 633 | [6 empty] | 0 | 633 | -11007.4396 | [13 empty] | 40098.1124 | 60.036 | 3710.1577 | 350 | -227.2551 | 16 | 299 | 10 | 0 | -103 | 7697 | -28.7994
| 40098.1125 | 60.036 | 3710.1577 |  |  |  | -28.7994 | -28.0878 |  | 0 | 3746.6539 | 3763.8855 | 3782.4854 | 3779.3439 | 3759.6501 | 633 | [6 empty] | 0 | 633 | -11007.4396 | [13 empty] | 40098.1125 | 60.036 | 3710.1577 | 350 | -227.2551 | 16 | 299 | 10 | 0 | -103 | 7697 | -28.7994
| 40098.1125 | 60.041 | 3698.5911 |  |  |  | -32.8003 | -29.7372 |  | 0 | 3745.0045 | 3763.7371 | 3782.4002 | 3779.3439 | 3759.6949 | 633 | [6 empty] | 0 | 633 | -84446.3878 | [13 empty] | 40098.1125 | 60.041 | 3698.5911 | 350 | -227.2551 | 16 | 299.5 | 10 | 0 | -103 | 7698 | -32.8003
| 40098.1125 | 60.044 | 3704.5913 |  |  |  | -35.199 | -31.6488 |  | 0 | 3743.0929 | 3763.603 | 3782.311 | 3779.3439 | 3759.7396 | 633 | [6 empty] | 0 | 633 | 28148.7959 | [13 empty] | 40098.1125 | 60.044 | 3704.5913 | 350 | -227.2551 | 16 | 300 | 10 | 0 | -103 | 7698 | -35.199
| 40098.1125 | 60.044 | 3704.5913 |  |  |  | -35.199 | -32.8914 |  | 0 | 3741.8504 | 3763.4695 | 3782.2195 | 3779.3439 | 3759.784 | 633 | [6 empty] | 0 | 633 | 28148.7959 | [13 empty] | 40098.1125 | 60.044 | 3704.5913 | 350 | -227.2551 | 16 | 300 | 10 | 0 | -103 | 7698 | -35.199
| 40098.1126 | 60.043 | 3702.4824 |  |  |  | -34.3994 | -33.4192 |  | 0 | 3741.3225 | 3763.3318 | 3782.1272 | 3779.3439 | 3759.8283 | 633 | [6 empty] | 0 | 633 | 50667.8327 | [13 empty] | 40098.1126 | 60.043 | 3702.4824 | 350 | -227.2551 | 16 | 300.5 | 10 | 0 | -103 | 7698.33 | -34.3994
| 40098.1126 | 60.048 | 3701.3164 |  |  |  | -38.4003 | -35.1626 |  | 0 | 3739.5792 | 3763.1921 | 3782.0314 | 3779.3439 | 3759.8723 | 633 | [6 empty] | 0 | 633 | 10127.3819 | [13 empty] | 40098.1126 | 60.048 | 3701.3164 | 350 | -227.2551 | 16 | 301 | 10 | 0 | -103 | 7698.66 | -38.4003
| 40098.1126 | 60.048 | 3701.3164 |  |  |  | -38.4003 | -36.2958 |  | 0 | 3738.446 | 3763.0531 | 3781.9334 | 3779.3439 | 3759.9162 | 633 | [6 empty] | 0 | 633 | 10127.3819 | [13 empty] | 40098.1126 | 60.048 | 3701.3164 | 350 | -227.2551 | 16 | 301 | 10 | 0 | -103 | 7698.66 | -38.4003
| 40098.1126 | 60.046 | 3699.5286 |  |  |  | -36.8011 | -36.4726 |  | 0 | 3738.2691 | 3762.9107 | 3781.8355 | 3779.3439 | 3759.9599 | 633 | [6 empty] | 0 | 633 | 14888.9324 | [13 empty] | 40098.1126 | 60.046 | 3699.5286 | 350 | -229.2902 | 16 | 301.5 | 10 | 0 | -103 | 7698.99 | -36.8011
| 40098.1127 | 60.043 | 3699.7261 |  |  |  | -34.3994 | -35.747 |  | 0 | 3738.9947 | 3762.7693 | 3781.7397 | 3779.3439 | 3760.0033 | 633 | [6 empty] | 0 | 633 | 50667.8327 | [13 empty] | 40098.1127 | 60.043 | 3699.7261 | 350 | -229.2902 | 16 | 302 | 10 | 0 | -103 | 7699.32 | -34.3994
| 40098.1127 | 60.043 | 3699.7261 |  |  |  | -34.3994 | -35.2754 |  | 0 | 3739.4664 | 3762.6286 | 3781.6453 | 3779.3439 | 3760.0466 | 633 | [6 empty] | 0 | 633 | 50667.8327 | [13 empty] | 40098.1127 | 60.043 | 3699.7261 | 350 | -229.2902 | 16 | 302 | 10 | 0 | -103 | 7699.32 | -34.3994
| 40098.1127 | 60.043 | 3690.4773 |  |  |  | -34.3994 | -34.9688 |  | 0 | 3739.773 | 3762.4679 | 3781.5521 | 3779.3439 | 3760.0897 | 633 | [6 empty] | 0 | 633 | 50667.8327 | [13 empty] | 40098.1127 | 60.043 | 3690.4773 | 350 | -229.2902 | 16 | 302.5 | 10 | 0 | -103 | 7699.65 | -34.3994
| 40098.1127 | 60.043 | 3696.8645 |  |  |  | -34.3994 | -34.7695 |  | 0 | 3739.9722 | 3762.3221 | 3781.4597 | 3779.3439 | 3760.1325 | 633 | [6 empty] | 0 | 633 | 50667.8327 | [13 empty] | 40098.1127 | 60.043 | 3696.8645 | 350 | -229.2902 | 16 | 303 | 10 | 0 | -103 | 7699.98 | -34.3994
| 40098.1127 | 60.043 | 3696.8645 |  |  |  | -34.3994 | -34.64 |  | 0 | 3740.1018 | 3762.177 | 3781.368 | 3779.3439 | 3760.1752 | 633 | [6 empty] | 0 | 633 | 50667.8327 | [13 empty] | 40098.1127 | 60.043 | 3696.8645 | 350 | -229.2902 | 16 | 303 | 10 | 0 | -103 | 7699.98 | -34.3994
Note on L13: TC allowable range 0.050 to 1.000 with 1.0 turning filter off. Beginning Target slope should align with Actual slope.

## Graph 20 to 52s
60.0417

## Form 1 Summary Data
[6 empty] | Interconnection Performance | [9 empty] | Value A Data |  | BA Performance | [8 empty] | Value B |  | 12 to 24 second Average Period Evaluation | [11 empty] | Value B | 18 to 30 second Average Period Evaluation | [12 empty] | Value B | 20 to 40 second Average Period Evaluation | [12 empty] | Value B | 18 to 52 second Average Period Evaluation | [12 empty] | Value B | 20 to 52 second Average Period Evaluation
[18 empty] | JOU | Non- |  |  | Transferred | Contingent | [5 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent
Date | A Point | FPointA | A Value | t(0) Time | C Value | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias
| Time | Hz | Hz |  | Hz | 12 to 24 sec | 12 to 24 sec | 18 to 30 sec | 18 to 30 sec | 20 to 40 sec | 20 to 40 sec | 18 to 52 sec | 18 to 52 sec | 20 to 52 sec | 20 to 52 sec |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting
[6 empty] | Average | Average | Average | Average | Average | Average | Average | Average | Average | Average | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR
[6 empty] | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Hz | MW | MW | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW | Hz | MW | MW | MW | MW | MW | MW | MW | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | P.U. | P.U. | P.U. | MW | MW | MW | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | P.U. | P.U. | P.U. | MW | MW | MW | Hz | MW | MW | MW | MW | MW | MW | MW | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW | Hz | MW | MW | MW | MW | MW | MW | MW | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW
2009-10-12 02:27 | 40098.1023 | 60.039 | 60.0417 | 40098.1023 | 59.836 | 59.8823 | -397.4363 | 59.8844 | -402.6343 | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | 60.0417 | 3647.0459 | 350 | -165.4296 | 0 | 151.8125 | -4.175 | 15 | -103 | 7600.1963 | -43.0025 | 59.8823 | 3766.6891 | 335 | -209.8855 | 0.42857 | 156.1429 | 11.7714 | 0 | 1.3592 | 0.93786 | 0.90839 | -103 | 7570 | 121.2453 | 59.8844 | 3778.5405 | 335 | -211.256 | 0.85714 | 157.1429 | 11.5571 | 0 | 1.4731 | 1.0448 | 0.90839 | -103 | 7570 | 119.0383 | 59.8892 | 3783.7721 | 335 | -212.6609 | 1.0909 | 158.1818 | 11.0818 | 0 | 1.5669 | 1.1202 | 0.90839 | -103 | 7570 | 114.1422 | 59.8879 | 3786.576 | 335 | -212.6617 | 2 | 159 | 11.2055 | 0 | 1.562 | 1.134 | 0.90839 | -103 | 7570 | 115.4171 | 59.8887 | 3787.775 | 335 | -165.4296 | 2.1176 | 159.1765 | 11.1294 | 0 | 1.5785 | 1.1494 | 0.90839 | -103 | 7570 | 114.6328