## Instructions
Steps | To be completed for each event evaluated.
1 | Set-up Data collection in exact same order as the "Data" sheet of this work book. Data should be in this order:
Column A: Date and Time in this format, mm/dd/yy HH:MM:SS
Column B: Frequency Hz
Column C: Net Actual Interchange
Column D: Joint Owned Unit dynamic schedule
Column E: Non Conforming Load
Column F: Pumped Hydro
Column G: Ramping units
Column H: Transferred Frequency Response
Column I: Contingent BA Lost load or generation
Column J: BA Bias Setting
Column K: BA Load
2 | Note: Columns D, E, F, G and H are optional data. If you choose not to use these, leave the columns blank. Do not delete the columns. Use the sign (+/-) convention defined in FRS Form 1.
3 | Data compression must be turned off for each data point. Quality data will give you quality results in the evaluation.
4 | Data must be at 4 second sample rate for the full 25 minute minimum collection period that starts a minimum of two (2) minutes before the event begins and includes a minimum of 15 minutes after the beginning of the event.
The spreadsheet will work with up to 60 minutes of data. Be sure "Data" worksheet is clear of any old data.
If using PI historian as your data source, use "PasteSpecial/Values" to enter data into the spreadsheet. Do not include historian data collection formulas in the data.
5 | Once data is in place in the "Data" worksheet, determine when the beginning of the event occurred. This is accomplished by knowing the UTC event time from the master event list.
Convert the UTC event time to your PI data time and then scroll through the Data worksheet column B data of frequency and observe when frequency moves from the normal, pre-event frequency.
This will usually be a single change in frequency of 0.008 to 0.010 Hz more or less. Note the row number in the worksheet that this change occurs. In this sample data spreadsheet this occurs in row 237 of the data.
6 | Edit cell "C8" of the "Entry Data" worksheet, change the formula in the cell "C8" to reference the row number identified in step 5 above. In the sample data of this workbook this formula is: "=Data!A237"
If the correct row is selected, the "Graph 20 to 52s" worksheet will indicate the first change in frequency of the event on the center vertical grid line of the graph (Red Trend).
7 | Determine the end of the event to be evaluated. Use the same rules that are used for DCS only look at frequency instead of ACE. Scroll down the frequency data in column B of the "Data" worksheet until frequency reaches 60 Hz or the
pre-disturbance value. Note the row number in the worksheet that this occurs. In this sample data spreadsheet this occurs in row 323.
8 | Edit cell "C11" of the "Entry Data" worksheet, change the formula in the cell "C11" to reference the row number identified in step 7 above. In the sample data of this workbook this formula is: "=Data!A323"
9 | In cell "R41" of the "Evaluation" spreadsheet, enter the MW value of the unit(s) that tripped (from the Master Event List). This is only necessary for the "Interconnection" evaluation if you're interested.
It is not necessary to do this for the BA evaluation but it will provide a comparison of the BA frequency response as compared to the Interconnection frequency response.
10 | Use the "copy" button provided to copy the evaluation and event specific data for the "FRS Form 1" of this field trial. This data is summarized in the correct order on worksheet "Form 1 Summary Data" of this workbook.
Use PasteSpecial/Values when pasting the data into FRS Form 1 on the appropriate event row.
Steps | To be completed once at the initial setup of the evaluation spreadsheet for your BA.
A | Enter the Balancing Authority name as you want it to appear on the graphs in cell "B1" of the "Entry Data" worksheet. For example: "NYISO".
B | Enter your Balancing Authorities Frequency Response Obligation in cell "B2" of the "Entry Data" worksheet. For example: -80 MW/0.1 Hz (This value could change annually)
C | For informational and educational purposes, a "Sustained" performance evaluation is provided in the "Evaluation" worksheet and in the "Sustained" Graph. This evaluation uses a Time Constant (TC) to model the frequency response of your BA.
The time constant is located in cell "L13" of the "Evaluation" spreadsheet and should be edited for the types of generators in your BA. Presently this time constant is set at 0.35.
The higher the value of the time constant, the faster the delivery of frequency response is expected. Setting the TC to 1.0 effectively turns off the delay and instantaneous frequency response will be modeled. Do not set higher than 1.0.
This time constant is only used in the "Sustained" evaluation and is not used for the Field Trial evaluation of performance to the FRO.
A typical setting for this time constant is 0.08 to 0.15 for hydro units, 0.10 to 0.20 for large steam turbines and 0.20 to 0.40 for combustion turbines.
By observing the slope of your "Interchange Actual" on the "Sustained" Graph, adjust the time constant until the initial slope of the "Target" is similar.
When set appropriately, the "Target" trend on the "Sustained" graph will model what Interchange Actual should have done during the event recovery period based on your minimum FRO.
Note: For ease of use, only the necessary worksheets are displayed. If you are interested in viewing graphs and other hidden worksheets, select the "tab" at the bottom, right click, select unhide and select the worksheet you wish to unhide.

## Data
|  |  | JOU | Non- |  |  | Transferred | Contingent
|  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA
|  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load
|  | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting
Time (T) | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW
2009-10-12 02:12 | 59.981 | 3669.8784 | 350 | 351.3615 | 0 | 0 | 10 | 15 | -103 | 7500
2009-10-12 02:12 | 59.981 | 3671.6997 | 350 | 351.3615 | 0 | 0.5 | 10 | 15 | -103 | 7500.33
2009-10-12 02:12 | 59.98 | 3671.6985 | 350 | 351.3615 | 0 | 1 | 10 | 15 | -103 | 7500.66
2009-10-12 02:12 | 59.981 | 3672.3103 | 350 | 357.9475 | 0 | 1.5 | 10 | 15 | -103 | 7500.99
2009-10-12 02:12 | 59.981 | 3672.1741 | 350 | 357.9475 | 0 | 2 | 10 | 15 | -103 | 7501.32
2009-10-12 02:12 | 59.979 | 3674.2634 | 350 | 357.9475 | 0 | 2.5 | 10 | 15 | -103 | 7501.65
2009-10-12 02:12 | 59.98 | 3673.8438 | 350 | 357.9475 | 0 | 3 | 10 | 15 | -103 | 7501.98
2009-10-12 02:12 | 59.983 | 3672.1062 | 350 | 357.9475 | 0 | 3.5 | 10 | 15 | -103 | 7502.31
2009-10-12 02:13 | 59.986 | 3669.168 | 350 | 360.2347 | 0 | 4 | 10 | 15 | -103 | 7502.64
2009-10-12 02:13 | 59.976 | 3673.5603 | 350 | 360.2347 | 0 | 4.5 | 10 | 15 | -103 | 7502.97
2009-10-12 02:13 | 59.979 | 3673.8342 | 350 | 360.2347 | 0 | 5 | 10 | 15 | -103 | 7503.3
2009-10-12 02:13 | 59.982 | 3671.6345 | 350 | 360.2347 | 0 | 5.5 | 10 | 15 | -103 | 7503.63
2009-10-12 02:13 | 59.99 | 3671.5603 | 350 | 360.2347 | 0 | 6 | 10 | 15 | -103 | 7503.96
2009-10-12 02:13 | 59.994 | 3670.772 | 350 | 346.5259 | 0 | 6.5 | 10 | 15 | -103 | 7504.29
2009-10-12 02:13 | 59.995 | 3668.1289 | 350 | 346.5259 | 0 | 7 | 10 | 15 | -103 | 7504.62
2009-10-12 02:13 | 59.995 | 3669.2913 | 350 | 346.5259 | 0 | 7.5 | 10 | 15 | -103 | 7504.95
2009-10-12 02:13 | 59.994 | 3671.2539 | 350 | 346.5259 | 0 | 8 | 10 | 15 | -103 | 7505.28
2009-10-12 02:13 | 59.995 | 3670.1558 | 350 | 346.5259 | 0 | 8.5 | 10 | 15 | -103 | 7505.61
2009-10-12 02:13 | 60.001 | 3670.7124 | 350 | 296.4434 | 0 | 9 | 10 | 15 | -103 | 7505.94
2009-10-12 02:13 | 60.001 | 3671.1836 | 350 | 296.4434 | 0 | 9.5 | 10 | 15 | -103 | 7506.27
2009-10-12 02:13 | 60.003 | 3670.2671 | 350 | 296.4434 | 0 | 10 | 10 | 15 | -103 | 7506.6
2009-10-12 02:13 | 60.003 | 3671.0923 | 350 | 296.4434 | 0 | 10.5 | 10 | 15 | -103 | 7506.93
2009-10-12 02:13 | 60.001 | 3670.6699 | 350 | 296.4434 | 0 | 11 | 10 | 15 | -103 | 7507.26
2009-10-12 02:14 | 60.004 | 3669.5342 | 350 | 341.0612 | 0 | 11.5 | 10 | 15 | -103 | 7507.59
2009-10-12 02:14 | 60.001 | 3671.6284 | 350 | 341.0612 | 0 | 12 | 10 | 15 | -103 | 7507.92
2009-10-12 02:14 | 60.001 | 3671.9683 | 350 | 341.0612 | 0 | 12.5 | 10 | 15 | -103 | 7508.25
2009-10-12 02:14 | 60.004 | 3671.8716 | 350 | 341.0612 | 0 | 13 | 10 | 15 | -103 | 7508.58
2009-10-12 02:14 | 60.004 | 3671.0657 | 350 | 341.0612 | 0 | 13.5 | 10 | 15 | -103 | 7508.91
2009-10-12 02:14 | 60.003 | 3673.2351 | 350 | 322.8263 | 0 | 14 | 10 | 15 | -103 | 7509.24
2009-10-12 02:14 | 60.003 | 3673.5305 | 350 | 322.8263 | 0 | 14.5 | 10 | 15 | -103 | 7509.57
2009-10-12 02:14 | 59.999 | 3673.1863 | 350 | 322.8263 | 0 | 15 | 10 | 15 | -103 | 7509.9
2009-10-12 02:14 | 59.997 | 3673.5764 | 350 | 322.8263 | 0 | 15.5 | 10 | 15 | -103 | 7510.23
2009-10-12 02:14 | 59.996 | 3671.8206 | 350 | 322.8263 | 0 | 16 | 10 | 15 | -103 | 7510.56
2009-10-12 02:14 | 59.993 | 3671.998 | 350 | 321.5444 | 0 | 16.5 | 10 | 15 | -103 | 7510.89
2009-10-12 02:14 | 59.996 | 3671.0725 | 350 | 321.5444 | 0 | 17 | 10 | 15 | -103 | 7511.22
2009-10-12 02:14 | 60.001 | 3671.4414 | 350 | 321.5444 | 0 | 17.5 | 10 | 15 | -103 | 7511.55
2009-10-12 02:14 | 60.007 | 3670.1619 | 350 | 321.5444 | 0 | 18 | 10 | 15 | -103 | 7511.88
2009-10-12 02:14 | 60.005 | 3670.6199 | 350 | 321.5444 | 0 | 18.5 | 10 | 15 | -103 | 7512.21
2009-10-12 02:15 | 59.999 | 3672.0857 | 350 | 362.1363 | 0 | 19 | 10 | 15 | -103 | 7512.54
2009-10-12 02:15 | 59.999 | 3670.8257 | 350 | 362.1363 | 0 | 19.5 | 10 | 15 | -103 | 7512.87
2009-10-12 02:15 | 60.007 | 3671.8091 | 350 | 362.1363 | 0 | 20 | 10 | 15 | -103 | 7513.2
2009-10-12 02:15 | 60.011 | 3672.7358 | 350 | 362.1363 | 0 | 20.5 | 10 | 15 | -103 | 7513.53
2009-10-12 02:15 | 60.003 | 3674.4146 | 350 | 362.1363 | 0 | 21 | 10 | 15 | -103 | 7513.86
2009-10-12 02:15 | 59.995 | 3674.7546 | 350 | 336.3118 | 0 | 21.5 | 10 | 15 | -103 | 7514.19
2009-10-12 02:15 | 59.994 | 3675.3105 | 350 | 336.3118 | 0 | 22 | 10 | 15 | -103 | 7514.52
2009-10-12 02:15 | 60.001 | 3675.1655 | 350 | 336.3118 | 0 | 22.5 | 10 | 15 | -103 | 7514.85
2009-10-12 02:15 | 59.998 | 3674.3191 | 350 | 336.3118 | 0 | 23 | 10 | 15 | -103 | 7515.18
2009-10-12 02:15 | 59.992 | 3676.3286 | 350 | 336.3118 | 0 | 23.5 | 10 | 15 | -103 | 7515.51
2009-10-12 02:15 | 59.986 | 3677.791 | 350 | 316.4431 | 0 | 24 | 10 | 15 | -103 | 7515.84
2009-10-12 02:15 | 59.988 | 3675.543 | 350 | 316.4431 | 0 | 24.5 | 10 | 15 | -103 | 7516.17
2009-10-12 02:15 | 59.988 | 3676.9314 | 350 | 316.4431 | 0 | 25 | 10 | 15 | -103 | 7516.5
2009-10-12 02:15 | 59.985 | 3677.0671 | 350 | 316.4431 | 0 | 25.5 | 10 | 15 | -103 | 7516.83
2009-10-12 02:15 | 59.983 | 3678.4553 | 350 | 316.4431 | 0 | 26 | 10 | 15 | -103 | 7517.16
2009-10-12 02:16 | 59.984 | 3679.7314 | 350 | 325.4643 | 0 | 26.5 | 10 | 15 | -103 | 7517.49
2009-10-12 02:16 | 59.985 | 3677.627 | 350 | 325.4643 | 0 | 27 | 10 | 15 | -103 | 7517.82
2009-10-12 02:16 | 59.987 | 3676.4094 | 350 | 325.4643 | 0 | 27.5 | 10 | 15 | -103 | 7518.15
2009-10-12 02:16 | 59.99 | 3677.3711 | 350 | 325.4643 | 0 | 28 | 10 | 15 | -103 | 7518.48
2009-10-12 02:16 | 59.983 | 3678.0864 | 350 | 325.4643 | 0 | 28.5 | 10 | 15 | -103 | 7518.81
2009-10-12 02:16 | 59.979 | 3680.1631 | 350 | 336.6142 | 0 | 29 | 10 | 15 | -103 | 7519.14
2009-10-12 02:16 | 59.987 | 3678.3442 | 350 | 336.6142 | 0 | 29.5 | 10 | 15 | -103 | 7519.47
2009-10-12 02:16 | 59.988 | 3677.6777 | 350 | 336.6142 | 0 | 30 | 10 | 15 | -103 | 7519.8
2009-10-12 02:16 | 59.983 | 3679.2791 | 350 | 336.6142 | 0 | 30.5 | 10 | 15 | -103 | 7520.13
2009-10-12 02:16 | 59.979 | 3679.6057 | 350 | 336.6142 | 0 | 31 | 10 | 15 | -103 | 7520.46
2009-10-12 02:16 | 59.989 | 3679.0259 | 350 | 316.7262 | 0 | 31.5 | 10 | 15 | -103 | 7520.79
2009-10-12 02:16 | 59.988 | 3678.4885 | 350 | 316.7262 | 0 | 32 | 10 | 15 | -103 | 7521.12
2009-10-12 02:16 | 59.989 | 3678.7402 | 350 | 316.7262 | 0 | 32.5 | 10 | 15 | -103 | 7521.45
2009-10-12 02:16 | 59.989 | 3679.3901 | 350 | 316.7262 | 0 | 33 | 10 | 15 | -103 | 7521.78
2009-10-12 02:16 | 59.993 | 3678.3301 | 350 | 316.7262 | 0 | 33.5 | 10 | 15 | -103 | 7522.11
2009-10-12 02:17 | 59.996 | 3677.9443 | 350 | 320.1955 | 0 | 34 | 10 | 15 | -103 | 7522.44
2009-10-12 02:17 | 59.998 | 3678.9509 | 350 | 320.1955 | 0 | 34.5 | 10 | 15 | -103 | 7522.77
2009-10-12 02:17 | 59.999 | 3679.1484 | 350 | 320.1955 | 0 | 35 | 10 | 15 | -103 | 7523.1
2009-10-12 02:17 | 59.991 | 3680.041 | 350 | 320.1955 | 0 | 35.5 | 10 | 15 | -103 | 7523.43
2009-10-12 02:17 | 59.995 | 3677.8604 | 350 | 320.1955 | 0 | 36 | 10 | 15 | -103 | 7523.76
2009-10-12 02:17 | 60.001 | 3678.2668 | 350 | 341.8661 | 0 | 36.5 | 10 | 15 | -103 | 7524.09
2009-10-12 02:17 | 60.006 | 3677.8987 | 350 | 341.8661 | 0 | 37 | 10 | 15 | -103 | 7524.42
2009-10-12 02:17 | 60.009 | 3679.2087 | 350 | 341.8661 | 0 | 37.5 | 10 | 15 | -103 | 7524.75
2009-10-12 02:17 | 60.012 | 3678.6526 | 350 | 341.8661 | 0 | 38 | 10 | 15 | -103 | 7525.08
2009-10-12 02:17 | 60.01 | 3679.7026 | 350 | 341.8661 | 0 | 38.5 | 10 | 15 | -103 | 7525.41
2009-10-12 02:17 | 60.007 | 3679.8059 | 350 | 348.5978 | 0 | 39 | 10 | 15 | -103 | 7525.74
2009-10-12 02:17 | 60.012 | 3680.2627 | 350 | 348.5978 | 0 | 39.5 | 10 | 15 | -103 | 7526.07
2009-10-12 02:17 | 60.01 | 3679.5608 | 350 | 348.5978 | 0 | 40 | 10 | 15 | -103 | 7526.4
2009-10-12 02:17 | 60.007 | 3679.4399 | 350 | 348.5978 | 0 | 40.5 | 10 | 15 | -103 | 7526.73
2009-10-12 02:17 | 60.009 | 3679.5166 | 350 | 348.5978 | 0 | 41 | 10 | 15 | -103 | 7527.06
2009-10-12 02:18 | 60.006 | 3679.6082 | 350 | 329.085 | 0 | 41.5 | 10 | 15 | -103 | 7527.39
2009-10-12 02:18 | 60.009 | 3679.2607 | 350 | 329.085 | 0 | 42 | 10 | 15 | -103 | 7527.72
2009-10-12 02:18 | 60.009 | 3679.0247 | 350 | 329.085 | 0 | 42.5 | 10 | 15 | -103 | 7528.05
2009-10-12 02:18 | 60.005 | 3678.5723 | 350 | 329.085 | 0 | 43 | 10 | 15 | -103 | 7528.38
2009-10-12 02:18 | 60.001 | 3678.2488 | 350 | 329.085 | 0 | 43.5 | 10 | 15 | -103 | 7528.71
2009-10-12 02:18 | 59.993 | 3677.8296 | 350 | 342.4182 | 0 | 44 | 10 | 15 | -103 | 7529.04
2009-10-12 02:18 | 59.994 | 3677.7722 | 350 | 342.4182 | 0 | 44.5 | 10 | 15 | -103 | 7529.37
2009-10-12 02:18 | 59.994 | 3677.0933 | 350 | 342.4182 | 0 | 45 | 10 | 15 | -103 | 7529.7
2009-10-12 02:18 | 59.994 | 3676.4006 | 350 | 342.4182 | 0 | 45.5 | 10 | 15 | -103 | 7530.03
2009-10-12 02:18 | 59.993 | 3679.8721 | 350 | 342.4182 | 0 | 46 | 10 | 15 | -103 | 7530.36
2009-10-12 02:18 | 59.99 | 3678.7432 | 350 | 338.7946 | 0 | 46.5 | 10 | 15 | -103 | 7530.69
2009-10-12 02:18 | 59.983 | 3677.9211 | 350 | 338.7946 | 0 | 47 | 10 | 15 | -103 | 7531.02
2009-10-12 02:18 | 59.977 | 3682.0701 | 350 | 338.7946 | 0 | 47.5 | 10 | 15 | -103 | 7531.35
2009-10-12 02:18 | 59.995 | 3678.6555 | 350 | 338.7946 | 0 | 48 | 10 | 15 | -103 | 7531.68
2009-10-12 02:18 | 59.994 | 3677.78 | 350 | 338.7946 | 0 | 48.5 | 10 | 15 | -103 | 7532.01
2009-10-12 02:19 | 59.987 | 3678.4731 | 350 | 335.931 | 0 | 49 | 10 | 15 | -103 | 7532.34
2009-10-12 02:19 | 59.984 | 3677.8223 | 350 | 335.931 | 0 | 49.5 | 10 | 15 | -103 | 7532.67
2009-10-12 02:19 | 59.985 | 3677.3975 | 350 | 335.931 | 0 | 50 | 10 | 15 | -103 | 7533
2009-10-12 02:19 | 59.985 | 3677.9497 | 350 | 335.931 | 0 | 50.5 | 10 | 15 | -103 | 7533.33
2009-10-12 02:19 | 59.98 | 3678.9626 | 350 | 335.931 | 0 | 51 | 10 | 15 | -103 | 7533.66
2009-10-12 02:19 | 59.981 | 3680.7373 | 350 | 339.7124 | 0 | 51.5 | 10 | 15 | -103 | 7533.99
2009-10-12 02:19 | 59.998 | 3678.1614 | 350 | 339.7124 | 0 | 52 | 10 | 15 | -103 | 7534.32
2009-10-12 02:19 | 60.007 | 3676.2222 | 350 | 339.7124 | 0 | 52.5 | 10 | 15 | -103 | 7534.65
2009-10-12 02:19 | 59.986 | 3677.4971 | 350 | 339.7124 | 0 | 53 | 10 | 15 | -103 | 7534.98
2009-10-12 02:19 | 59.977 | 3675.1858 | 350 | 339.7124 | 0 | 53.5 | 10 | 15 | -103 | 7535.31
2009-10-12 02:19 | 59.976 | 3680.4509 | 350 | 332.0247 | 0 | 54 | 10 | 15 | -103 | 7535.64
2009-10-12 02:19 | 59.974 | 3683.8286 | 350 | 332.0247 | 0 | 54.5 | 10 | 15 | -103 | 7535.97
2009-10-12 02:19 | 59.979 | 3681.1084 | 350 | 332.0247 | 0 | 55 | 10 | 15 | -103 | 7536.3
2009-10-12 02:19 | 59.982 | 3678.229 | 350 | 332.0247 | 0 | 55.5 | 10 | 15 | -103 | 7536.63
2009-10-12 02:19 | 59.987 | 3675.7593 | 350 | 332.0247 | 0 | 56 | 10 | 15 | -103 | 7536.96
2009-10-12 02:20 | 59.988 | 3671.1655 | 350 | 330.759 | 0 | 56.5 | 10 | 15 | -103 | 7537.29
2009-10-12 02:20 | 59.987 | 3670.1287 | 350 | 330.759 | 0 | 57 | 10 | 15 | -103 | 7537.62
2009-10-12 02:20 | 59.985 | 3672.0479 | 350 | 330.759 | 0 | 57.5 | 10 | 15 | -103 | 7537.95
2009-10-12 02:20 | 59.982 | 3672.1035 | 350 | 330.759 | 0 | 58 | 10 | 15 | -103 | 7538.28
2009-10-12 02:20 | 59.989 | 3671.8823 | 350 | 330.759 | 0 | 58.5 | 10 | 15 | -103 | 7538.61
2009-10-12 02:20 | 59.988 | 3671.3359 | 350 | 323.42 | 0 | 59 | 10 | 15 | -103 | 7538.94
2009-10-12 02:20 | 59.982 | 3670.3721 | 350 | 323.42 | 0 | 59.5 | 10 | 15 | -103 | 7539.27
2009-10-12 02:20 | 59.981 | 3671.4009 | 350 | 323.42 | 0 | 60 | 10 | 15 | -103 | 7539.6
2009-10-12 02:20 | 59.983 | 3672.1814 | 350 | 323.42 | 0 | 60.5 | 10 | 15 | -103 | 7539.93
2009-10-12 02:20 | 59.989 | 3668.0708 | 350 | 323.42 | 0 | 61 | 10 | 15 | -103 | 7540.26
2009-10-12 02:20 | 59.985 | 3669.9082 | 350 | 342.3509 | 0 | 61.5 | 10 | 15 | -103 | 7540.59
2009-10-12 02:20 | 59.98 | 3670.2627 | 350 | 342.3509 | 0 | 62 | 10 | 15 | -103 | 7540.92
2009-10-12 02:20 | 59.98 | 3670.1021 | 350 | 342.3509 | 0 | 62.5 | 10 | 15 | -103 | 7541.25
2009-10-12 02:20 | 59.979 | 3671.4026 | 350 | 342.3509 | 0 | 63 | 10 | 15 | -103 | 7541.58
2009-10-12 02:20 | 59.981 | 3672.3718 | 350 | 342.3509 | 0 | 63.5 | 10 | 15 | -103 | 7541.91
2009-10-12 02:21 | 59.98 | 3670.9375 | 350 | 345.0818 | 0 | 64 | 10 | 15 | -103 | 7542.24
2009-10-12 02:21 | 59.98 | 3670.1372 | 350 | 345.0818 | 0 | 64.5 | 10 | 15 | -103 | 7542.57
2009-10-12 02:21 | 59.977 | 3672.3909 | 350 | 345.0818 | 0 | 65 | 10 | 15 | -103 | 7542.9
2009-10-12 02:21 | 59.981 | 3674.0518 | 350 | 345.0818 | 0 | 65.5 | 10 | 15 | -103 | 7543.23
2009-10-12 02:21 | 59.976 | 3671.8003 | 350 | 345.0818 | 0 | 66 | 10 | 15 | -103 | 7543.56
2009-10-12 02:21 | 59.972 | 3673.8735 | 350 | 346.5374 | 0 | 66.5 | 10 | 15 | -103 | 7543.89
2009-10-12 02:21 | 59.973 | 3676.6233 | 350 | 346.5374 | 0 | 67 | 10 | 15 | -103 | 7544.22
2009-10-12 02:21 | 59.973 | 3676.543 | 350 | 346.5374 | 0 | 67.5 | 10 | 15 | -103 | 7544.55
2009-10-12 02:21 | 59.971 | 3675.7524 | 350 | 346.5374 | 0 | 68 | 10 | 15 | -103 | 7544.88
2009-10-12 02:21 | 59.977 | 3674.8696 | 350 | 346.5374 | 0 | 68.5 | 10 | 15 | -103 | 7545.21
2009-10-12 02:21 | 59.975 | 3671.5933 | 350 | 342.9058 | 0 | 69 | 10 | 15 | -103 | 7545.54
2009-10-12 02:21 | 59.98 | 3669.9629 | 350 | 342.9058 | 0 | 69.5 | 10 | 15 | -103 | 7545.87
2009-10-12 02:21 | 59.981 | 3669.4968 | 350 | 342.9058 | 0 | 70 | 10 | 15 | -103 | 7546.2
2009-10-12 02:21 | 59.982 | 3667.6765 | 350 | 342.9058 | 0 | 70.5 | 10 | 15 | -103 | 7546.53
2009-10-12 02:21 | 59.982 | 3666.5994 | 350 | 342.9058 | 0 | 71 | 10 | 15 | -103 | 7546.86
2009-10-12 02:22 | 59.982 | 3666.4417 | 350 | 340.0944 | 0 | 71.5 | 10 | 15 | -103 | 7547.19
2009-10-12 02:22 | 59.985 | 3667.4563 | 350 | 340.0944 | 0 | 72 | 10 | 15 | -103 | 7547.52
2009-10-12 02:22 | 59.989 | 3665.2617 | 350 | 340.0944 | 0 | 72.5 | 10 | 15 | -103 | 7547.85
2009-10-12 02:22 | 59.996 | 3663.825 | 350 | 340.0944 | 0 | 73 | 10 | 15 | -103 | 7548.18
2009-10-12 02:22 | 59.998 | 3662.0549 | 350 | 340.0944 | 0 | 73.5 | 10 | 15 | -103 | 7548.51
2009-10-12 02:22 | 60.007 | 3662.0762 | 350 | 342.7712 | 0 | 74 | 10 | 15 | -103 | 7548.84
2009-10-12 02:22 | 60.013 | 3662.9595 | 350 | 342.7712 | 0 | 74.5 | 10 | 15 | -103 | 7549.17
2009-10-12 02:22 | 60.013 | 3664.1392 | 350 | 342.7712 | 0 | 75 | 10 | 15 | -103 | 7549.5
2009-10-12 02:22 | 60.008 | 3664.1587 | 350 | 342.7712 | 0 | 75.5 | 10 | 15 | -103 | 7549.83
2009-10-12 02:22 | 60.019 | 3663.1836 | 350 | 342.7712 | 0 | 76 | 10 | 15 | -103 | 7550.16
2009-10-12 02:22 | 60.023 | 3661.5122 | 350 | 342.9099 | 0 | 76.5 | 10 | 15 | -103 | 7550.49
2009-10-12 02:22 | 60.02 | 3658.6614 | 350 | 342.9099 | 0 | 77 | 10 | 15 | -103 | 7550.82
2009-10-12 02:22 | 60.021 | 3657.571 | 350 | 342.9099 | 0 | 77.5 | 10 | 15 | -103 | 7551.15
2009-10-12 02:22 | 60.019 | 3657.7104 | 350 | 342.9099 | 0 | 78 | 10 | 15 | -103 | 7551.48
2009-10-12 02:22 | 60.022 | 3660.2275 | 350 | 342.9099 | 0 | 78.5 | 10 | 15 | -103 | 7551.81
2009-10-12 02:23 | 60.025 | 3658.6982 | 350 | 343.286 | 0 | 79 | 10 | 15 | -103 | 7552.14
2009-10-12 02:23 | 60.02 | 3658.1545 | 350 | 343.286 | 0 | 79.5 | 10 | 15 | -103 | 7552.47
2009-10-12 02:23 | 60.018 | 3659.7776 | 350 | 343.286 | 0 | 80 | 10 | 15 | -103 | 7552.8
2009-10-12 02:23 | 60.02 | 3662.5315 | 350 | 343.286 | 0 | 80.5 | 10 | 15 | -103 | 7553.13
2009-10-12 02:23 | 60.019 | 3662.0789 | 350 | 343.286 | 0 | 81 | 10 | 15 | -103 | 7553.46
2009-10-12 02:23 | 60.022 | 3662.6782 | 350 | 331.853 | 0 | 81.5 | 10 | 15 | -103 | 7553.79
2009-10-12 02:23 | 60.025 | 3663.5386 | 350 | 331.853 | 0 | 82 | 10 | 15 | -103 | 7554.12
2009-10-12 02:23 | 60.02 | 3662.5525 | 350 | 331.853 | 0 | 82.5 | 10 | 15 | -103 | 7554.45
2009-10-12 02:23 | 60.02 | 3663.6006 | 350 | 331.853 | 0 | 83 | 10 | 15 | -103 | 7554.78
2009-10-12 02:23 | 60.021 | 3663.6899 | 350 | 331.853 | 0 | 83.5 | 10 | 15 | -103 | 7555.11
2009-10-12 02:23 | 60.018 | 3663.3958 | 350 | 329.9882 | 0 | 84 | 10 | 15 | -103 | 7555.44
2009-10-12 02:23 | 60.014 | 3664.3154 | 350 | 329.9882 | 0 | 84.5 | 10 | 15 | -103 | 7555.77
2009-10-12 02:23 | 60.013 | 3665.7976 | 350 | 329.9882 | 0 | 85 | 10 | 15 | -103 | 7556.1
2009-10-12 02:23 | 60.01 | 3666.7258 | 350 | 329.9882 | 0 | 85.5 | 10 | 15 | -103 | 7556.43
2009-10-12 02:23 | 60.011 | 3667.5454 | 350 | 329.9882 | 0 | 86 | 10 | 15 | -103 | 7556.76
2009-10-12 02:24 | 60.012 | 3666.4487 | 350 | 255.4442 | 0 | 86.5 | 10 | 15 | -103 | 7557.09
2009-10-12 02:24 | 60.009 | 3667.696 | 350 | 255.4442 | 0 | 87 | 10 | 15 | -103 | 7557.42
2009-10-12 02:24 | 60.009 | 3667.043 | 350 | 255.4442 | 0 | 87.5 | 10 | 15 | -103 | 7557.75
2009-10-12 02:24 | 60.005 | 3666.2227 | 350 | 255.4442 | 0 | 88 | 10 | 15 | -103 | 7558.08
2009-10-12 02:24 | 59.999 | 3665.4033 | 350 | 255.4442 | 0 | 88.5 | 10 | 15 | -103 | 7558.41
2009-10-12 02:24 | 59.995 | 3665.6797 | 350 | 254.8383 | 0 | 89 | 10 | 15 | -103 | 7558.74
2009-10-12 02:24 | 59.998 | 3664.9475 | 350 | 254.8383 | 0 | 89.5 | 10 | 15 | -103 | 7559.07
2009-10-12 02:24 | 59.998 | 3666.1333 | 350 | 254.8383 | 0 | 90 | 10 | 15 | -103 | 7559.4
2009-10-12 02:24 | 59.995 | 3666.7346 | 350 | 254.8383 | 0 | 90.5 | 10 | 15 | -103 | 7559.73
2009-10-12 02:24 | 59.992 | 3667.5574 | 350 | 254.8383 | 0 | 91 | 10 | 15 | -103 | 7560.06
2009-10-12 02:24 | 59.988 | 3667.8533 | 350 | 257.147 | 0 | 91.5 | 10 | 15 | -103 | 7560.39
2009-10-12 02:24 | 59.982 | 3668.6909 | 350 | 257.147 | 0 | 92 | 10 | 15 | -103 | 7560.72
2009-10-12 02:24 | 59.982 | 3669.6062 | 350 | 257.147 | 0 | 92.5 | 10 | 15 | -103 | 7561.05
2009-10-12 02:24 | 59.984 | 3670.25 | 350 | 257.147 | 0 | 93 | 10 | 15 | -103 | 7561.38
2009-10-12 02:24 | 59.978 | 3671.5488 | 350 | 257.147 | 0 | 93.5 | 10 | 15 | -103 | 7561.71
2009-10-12 02:25 | 59.976 | 3674.2629 | 350 | 262.2894 | 0 | 94 | 10 | 15 | -103 | 7562.04
2009-10-12 02:25 | 59.974 | 3676.4182 | 350 | 262.2894 | 0 | 94.5 | 10 | 15 | -103 | 7562.37
2009-10-12 02:25 | 59.979 | 3674.6375 | 350 | 262.2894 | 0 | 95 | 10 | 15 | -103 | 7562.7
2009-10-12 02:25 | 59.981 | 3675.2261 | 350 | 262.2894 | 0 | 95.5 | 10 | 15 | -103 | 7563.03
2009-10-12 02:25 | 59.984 | 3674.3994 | 350 | 262.2894 | 0 | 96 | 10 | 15 | -103 | 7563.36
2009-10-12 02:25 | 59.988 | 3673.0396 | 350 | 256.6479 | 0 | 96.5 | 10 | 15 | -103 | 7563.69
2009-10-12 02:25 | 59.99 | 3673.0564 | 350 | 256.6479 | 0 | 97 | 10 | 15 | -103 | 7564.02
2009-10-12 02:25 | 59.991 | 3671.4932 | 350 | 256.6479 | 0 | 97.5 | 10 | 15 | -103 | 7564.35
2009-10-12 02:25 | 59.991 | 3670.0662 | 350 | 256.6479 | 0 | 98 | 10 | 15 | -103 | 7564.68
2009-10-12 02:25 | 59.993 | 3671.7441 | 350 | 256.6479 | 0 | 98.5 | 10 | 15 | -103 | 7565.01
2009-10-12 02:25 | 60.002 | 3672.6255 | 350 | 256.3073 | 0 | 99 | 10 | 15 | -103 | 7565.34
2009-10-12 02:25 | 60.003 | 3673.8186 | 350 | 256.3073 | 0 | 99.5 | 10 | 15 | -103 | 7565.67
2009-10-12 02:25 | 60.005 | 3673.1821 | 350 | 256.3073 | 0 | 100 | 10 | 15 | -103 | 7566
2009-10-12 02:25 | 60.002 | 3672.418 | 350 | 256.3073 | 0 | 100.5 | 10 | 15 | -103 | 7566.33
2009-10-12 02:25 | 60.008 | 3672.2168 | 350 | 256.3073 | 0 | 101 | 10 | 15 | -103 | 7566.66
2009-10-12 02:26 | 60.01 | 3673.1821 | 350 | 249.0864 | 0 | 101.5 | 10 | 15 | -103 | 7566.99
2009-10-12 02:26 | 60.011 | 3673.5535 | 350 | 249.0864 | 0 | 102 | 10 | 15 | -103 | 7567.32
2009-10-12 02:26 | 60.014 | 3674.5371 | 350 | 249.0864 | 0 | 102.5 | 10 | 15 | -103 | 7567.65
2009-10-12 02:26 | 60.012 | 3673.2036 | 350 | 249.0864 | 0 | 103 | 10 | 15 | -103 | 7567.98
2009-10-12 02:26 | 60.011 | 3673.0676 | 350 | 249.0864 | 0 | 103.5 | 10 | 15 | -103 | 7568.31
2009-10-12 02:26 | 60.022 | 3672.5195 | 350 | 253.7425 | 0 | 104 | 10 | 15 | -103 | 7568.64
2009-10-12 02:26 | 60.014 | 3671.2881 | 350 | 253.7425 | 0 | 104.5 | 10 | 15 | -103 | 7568.97
2009-10-12 02:26 | 60.014 | 3672.9817 | 350 | 253.7425 | 0 | 105 | 10 | 15 | -103 | 7569.3
2009-10-12 02:26 | 60.017 | 3671.9517 | 350 | 253.7425 | 0 | 105.5 | 10 | 15 | -103 | 7569.63
2009-10-12 02:26 | 60.019 | 3671.6272 | 350 | 253.7425 | 0 | 106 | 10 | 15 | -103 | 7569.96
2009-10-12 02:26 | 60.027 | 3668.6106 | 350 | 257.4212 | 0 | 106.5 | 10 | 15 | -103 | 7570.29
2009-10-12 02:26 | 60.026 | 3664.4951 | 350 | 257.4212 | 0 | 107 | 10 | 15 | -103 | 7570.62
2009-10-12 02:26 | 60.019 | 3666.8208 | 350 | 257.4212 | 0 | 107.5 | 10 | 15 | -103 | 7570.95
2009-10-12 02:26 | 60.019 | 3670.4536 | 350 | 257.4212 | 0 | 108 | 10 | 15 | -103 | 7571.28
2009-10-12 02:26 | 60.019 | 3671.668 | 350 | 257.4212 | 0 | 108.5 | 10 | 15 | -103 | 7571.61
2009-10-12 02:27 | 60.021 | 3672.6851 | 350 | 261.7382 | 0 | 109 | 10 | 15 | -103 | 7571.94
2009-10-12 02:27 | 60.019 | 3672.1641 | 350 | 261.7382 | 0 | 109.5 | 10 | 15 | -103 | 7572.27
2009-10-12 02:27 | 60.022 | 3669.9829 | 350 | 165.1017 | 0 | 110 | 10 | 15 | -103 | 7572.6
2009-10-12 02:27 | 60.037 | 3663.7581 | 350 | 165.4764 | 0 | 110.5 | 10 | 15 | -103 | 7572.93
2009-10-12 02:27 | 60.036 | 3660.6724 | 350 | 165.4764 | 0 | 111 | 10 | 15 | -103 | 7573.26
2009-10-12 02:27 | 60.046 | 3649.1904 | 350 | 165.4764 | 0 | 111.5 | 10 | 15 | -103 | 7573.59
2009-10-12 02:27 | 60.048 | 3648.2463 | 350 | 165.4764 | 0 | 112 | 10 | 15 | -103 | 7573.92
2009-10-12 02:27 | 60.041 | 3654.2944 | 350 | 165.1017 | 0 | 112.5 | 10 | 15 | -103 | 7574.25
2009-10-12 02:27 | 60.041 | 3651.8743 | 350 | 165.4764 | 0 | 113 | 10 | 15 | -103 | 7574.58
2009-10-12 02:27 | 60.041 | 3649.187 | 350 | 165.4764 | 0 | 113.5 | 10 | 15 | -103 | 7574.91
2009-10-12 02:27 | 60.045 | 3645.387 | 350 | 165.4764 | 0 | 114 | 10 | 15 | -103 | 7575.24
2009-10-12 02:27 | 60.041 | 3645.4458 | 350 | 165.4764 | 0 | 114.5 | 10 | 15 | -103 | 7575.57
2009-10-12 02:27 | 60.041 | 3641.1912 | 350 | 165.4764 | 0 | 115 | 10 | 15 | -103 | 7575.9
2009-10-12 02:27 | 59.978 | 3696.3623 | 350 | 206.4591 | 1 | 115.5 | 10 | 15 | -103 | 7576.23
2009-10-12 02:27 | 59.836 | 3734.6726 | 335 | 206.4591 | 1 | 116 | 10 | 0 | -103 | 7576.56
2009-10-12 02:28 | 59.892 | 3761.2495 | 335 | 206.4591 | 1 | 116.5 | 10 | 0 | -103 | 7576.89
2009-10-12 02:28 | 59.88 | 3766.1938 | 335 | 206.4591 | 1 | 117 | 10 | 0 | -103 | 7577.22
2009-10-12 02:28 | 59.875 | 3769.925 | 335 | 206.4591 | 1 | 117.5 | 10 | 0 | -103 | 7577.55
2009-10-12 02:28 | 59.887 | 3781.5918 | 335 | 211.256 | 1 | 118 | 10 | 0 | -103 | 7577.88
2009-10-12 02:28 | 59.885 | 3784.9619 | 335 | 211.256 | 1 | 118.5 | 10 | 0 | -103 | 7578.21
2009-10-12 02:28 | 59.888 | 3784.4189 | 335 | 211.256 | 2 | 119 | 10 | 0 | -103 | 7578.54
2009-10-12 02:28 | 59.895 | 3788.3276 | 335 | 211.256 | 3 | 119.5 | 10 | 0 | -103 | 7578.87
2009-10-12 02:28 | 59.893 | 3788.4719 | 335 | 211.256 | 4 | 120 | 10 | 0 | -103 | 7579.2
2009-10-12 02:28 | 59.894 | 3793.0745 | 335 | 214.3467 | 5 | 120.5 | 10 | 0 | -103 | 7579.53
2009-10-12 02:28 | 59.89 | 3799.4277 | 335 | 214.3467 | 6 | 121 | 10 | 0 | -103 | 7579.86
2009-10-12 02:28 | 59.885 | 3799.9592 | 335 | 214.3467 | 7 | 121.5 | 10 | 0 | -103 | 7580.19
2009-10-12 02:28 | 59.887 | 3802.925 | 335 | 214.3467 | 8 | 122 | 10 | 0 | -103 | 7580.52
2009-10-12 02:28 | 59.888 | 3804.3879 | 335 | 214.3467 | 9 | 122.5 | 10 | 0 | -103 | 7580.85
2009-10-12 02:28 | 59.889 | 3805.6167 | 335 | 212.1727 | 10 | 123 | 10 | 0 | -103 | 7581.18
2009-10-12 02:28 | 59.873 | 3811.5029 | 335 | 212.1727 | 11 | 123.5 | 10 | 0 | -103 | 7581.51
2009-10-12 02:29 | 59.849 | 3815.8889 | 335 | 212.1727 | 12 | 124 | 10 | 0 | -103 | 7581.84
2009-10-12 02:29 | 59.858 | 3826.0532 | 335 | 212.1727 | 13 | 124.5 | 10 | 0 | -103 | 7582.17
2009-10-12 02:29 | 59.866 | 3827.5239 | 335 | 212.1727 | 14 | 125 | 10 | 0 | -103 | 7582.5
2009-10-12 02:29 | 59.867 | 3826.7834 | 335 | 215.5982 | 15 | 125.5 | 10 | 0 | -103 | 7582.83
2009-10-12 02:29 | 59.871 | 3825.7134 | 335 | 215.5982 | 16 | 126 | 10 | 0 | -103 | 7583.16
2009-10-12 02:29 | 59.879 | 3822.5054 | 335 | 215.5982 | 16 | 126.5 | 10 | 0 | -103 | 7583.49
2009-10-12 02:29 | 59.883 | 3818.0552 | 335 | 215.5982 | 16 | 127 | 10 | 0 | -103 | 7583.82
2009-10-12 02:29 | 59.89 | 3815.0098 | 335 | 215.5982 | 16 | 127.5 | 10 | 0 | -103 | 7584.15
2009-10-12 02:29 | 59.889 | 3811.8384 | 335 | 218.3273 | 16 | 128 | 10 | 0 | -103 | 7584.48
2009-10-12 02:29 | 59.899 | 3806.9722 | 335 | 218.3273 | 16 | 128.5 | 10 | 0 | -103 | 7584.81
2009-10-12 02:29 | 59.902 | 3804.1885 | 335 | 218.3273 | 16 | 129 | 10 | 0 | -103 | 7585.14
2009-10-12 02:29 | 59.904 | 3793.9751 | 335 | 218.3273 | 16 | 129.5 | 10 | 0 | -103 | 7585.47
2009-10-12 02:29 | 59.911 | 3791.502 | 335 | 218.3273 | 16 | 130 | 10 | 0 | -103 | 7585.8
2009-10-12 02:29 | 59.916 | 3788.1321 | 335 | 217.3794 | 16 | 130.5 | 10 | 0 | -103 | 7586.13
2009-10-12 02:29 | 59.918 | 3783.0283 | 335 | 217.3794 | 16 | 131 | 10 | 0 | -103 | 7586.46
2009-10-12 02:30 | 59.921 | 3776.3584 | 335 | 217.3794 | 16 | 131.5 | 10 | 0 | -103 | 7586.79
2009-10-12 02:30 | 59.917 | 3774.6042 | 335 | 217.3794 | 16 | 132 | 10 | 0 | -103 | 7587.12
2009-10-12 02:30 | 59.921 | 3773.9578 | 335 | 217.3794 | 16 | 132.5 | 10 | 0 | -103 | 7587.45
2009-10-12 02:30 | 59.926 | 3771.6704 | 335 | 214.8304 | 16 | 133 | 10 | 0 | -103 | 7587.78
2009-10-12 02:30 | 59.928 | 3768.707 | 335 | 214.8304 | 16 | 133.5 | 10 | 0 | -103 | 7588.11
2009-10-12 02:30 | 59.932 | 3767.021 | 335 | 214.8304 | 16 | 134 | 10 | 0 | -103 | 7588.44
2009-10-12 02:30 | 59.928 | 3766.7881 | 335 | 214.8304 | 16 | 134.5 | 10 | 0 | -103 | 7588.77
2009-10-12 02:30 | 59.929 | 3765.6716 | 335 | 214.8304 | 16 | 135 | 10 | 0 | -103 | 7589.1
2009-10-12 02:30 | 59.933 | 3764.2427 | 335 | 227.6559 | 16 | 135.5 | 10 | 0 | -103 | 7589.43
2009-10-12 02:30 | 59.937 | 3762.9353 | 335 | 227.6559 | 16 | 136 | 10 | 0 | -103 | 7589.76
2009-10-12 02:30 | 59.949 | 3753.9224 | 335 | 227.6559 | 0 | 136.5 | 10 | 0 | -103 | 7590.09
2009-10-12 02:30 | 59.942 | 3746.8887 | 335 | 227.6559 | 0 | 137 | 10 | 0 | -103 | 7590.42
2009-10-12 02:30 | 59.942 | 3749.5933 | 335 | 227.6559 | 0 | 137.5 | 10 | 0 | -103 | 7590.75
2009-10-12 02:30 | 59.948 | 3746.7061 | 335 | 225.0181 | 0 | 138 | 10 | 0 | -103 | 7591.08
2009-10-12 02:30 | 59.949 | 3742.7415 | 335 | 225.0181 | 0 | 138.5 | 10 | 0 | -103 | 7591.41
2009-10-12 02:31 | 59.952 | 3736.1392 | 335 | 225.0181 | 0 | 139 | 10 | 0 | -103 | 7591.74
2009-10-12 02:31 | 59.951 | 3727.8384 | 335 | 225.0181 | 0 | 139.5 | 10 | 0 | -103 | 7592.07
2009-10-12 02:31 | 59.952 | 3722.6489 | 335 | 225.0181 | 0 | 140 | 10 | 0 | -103 | 7592.4
2009-10-12 02:31 | 59.955 | 3717.9961 | 335 | 228.3652 | 0 | 140.5 | 10 | 0 | -103 | 7592.73
2009-10-12 02:31 | 59.954 | 3715.7527 | 335 | 228.3652 | 0 | 141 | 10 | 0 | -103 | 7593.06
2009-10-12 02:31 | 59.953 | 3713.4836 | 335 | 228.3652 | 0 | 141.5 | 10 | 0 | -103 | 7593.39
2009-10-12 02:31 | 59.952 | 3710.8101 | 335 | 228.3652 | 0 | 142 | 10 | 0 | -103 | 7593.72
2009-10-12 02:31 | 59.954 | 3714.6226 | 335 | 228.3652 | 0 | 142.5 | 10 | 0 | -103 | 7594.05
2009-10-12 02:31 | 59.957 | 3716.1682 | 335 | 234.0753 | 0 | 143 | 10 | 0 | -103 | 7594.38
2009-10-12 02:31 | 59.954 | 3716.98 | 335 | 234.0753 | 0 | 143.5 | 10 | 0 | -103 | 7594.71
2009-10-12 02:31 | 59.955 | 3722.3613 | 335 | 234.0753 | 0 | 144 | 10 | 0 | -103 | 7595.04
2009-10-12 02:31 | 59.961 | 3722.658 | 335 | 234.0753 | 0 | 144.5 | 10 | 0 | -103 | 7595.37
2009-10-12 02:31 | 59.962 | 3722.2776 | 335 | 234.0753 | 0 | 145 | 10 | 0 | -103 | 7595.7
2009-10-12 02:31 | 59.966 | 3723.0908 | 335 | 228.7982 | 0 | 145.5 | 10 | 0 | -103 | 7596.03
2009-10-12 02:31 | 59.968 | 3723.4346 | 335 | 228.7982 | 0 | 146 | 10 | 0 | -103 | 7596.36
2009-10-12 02:32 | 59.974 | 3725.4028 | 335 | 228.7982 | 0 | 146.5 | 10 | 0 | -103 | 7596.69
2009-10-12 02:32 | 59.969 | 3728.053 | 335 | 228.7982 | 0 | 147 | 10 | 0 | -103 | 7597.02
2009-10-12 02:32 | 59.97 | 3732.53 | 335 | 228.7982 | 0 | 147.5 | 10 | 0 | -103 | 7597.35
2009-10-12 02:32 | 59.973 | 3736.5352 | 335 | 229.467 | 0 | 148 | 10 | 0 | -103 | 7597.68
2009-10-12 02:32 | 59.976 | 3736.8218 | 335 | 229.467 | 0 | 148.5 | 10 | 0 | -103 | 7598.01
2009-10-12 02:32 | 59.978 | 3739.9438 | 335 | 229.467 | 0 | 149 | 10 | 0 | -103 | 7598.34
2009-10-12 02:32 | 59.978 | 3741.7937 | 335 | 229.467 | 0 | 149.5 | 10 | 0 | -103 | 7598.67
2009-10-12 02:32 | 59.978 | 3746.6079 | 335 | 229.467 | 0 | 150 | 10 | 0 | -103 | 7599
2009-10-12 02:32 | 59.98 | 3750.7163 | 335 | 228.9802 | 0 | 150.5 | 10 | 0 | -103 | 7599.33
2009-10-12 02:32 | 59.981 | 3752.7476 | 335 | 228.9802 | 0 | 151 | 10 | 0 | -103 | 7599.66
2009-10-12 02:32 | 59.979 | 3756.4072 | 335 | 228.9802 | 0 | 151.5 | 10 | 0 | -103 | 7599.99
2009-10-12 02:32 | 59.979 | 3760.4053 | 335 | 228.9802 | 0 | 152 | 10 | 0 | -103 | 7600.32
2009-10-12 02:32 | 59.983 | 3761.407 | 335 | 228.9802 | 0 | 152.5 | 10 | 0 | -103 | 7600.65
2009-10-12 02:32 | 59.988 | 3763.2122 | 335 | 219.9756 | 0 | 153 | 10 | 0 | -103 | 7600.98
2009-10-12 02:32 | 59.987 | 3766.0852 | 335 | 219.9756 | 0 | 153.5 | 10 | 0 | -103 | 7601.31
2009-10-12 02:33 | 59.991 | 3767.251 | 335 | 219.9756 | 0 | 154 | 10 | 0 | -103 | 7601.64
2009-10-12 02:33 | 59.992 | 3768.6335 | 335 | 219.9756 | 0 | 154.5 | 10 | 0 | -103 | 7601.97
2009-10-12 02:33 | 59.989 | 3772.4446 | 335 | 219.9756 | 0 | 155 | 10 | 0 | -103 | 7602.3
2009-10-12 02:33 | 59.983 | 3774.6685 | 335 | 229.0892 | 0 | 155.5 | 10 | 0 | -103 | 7602.63
2009-10-12 02:33 | 59.988 | 3775.3633 | 335 | 229.0892 | 0 | 156 | 10 | 0 | -103 | 7602.96
2009-10-12 02:33 | 59.996 | 3775.4917 | 335 | 229.0892 | 0 | 156.5 | 10 | 0 | -103 | 7603.29
2009-10-12 02:33 | 59.999 | 3778.5537 | 335 | 229.0892 | 0 | 157 | 10 | 0 | -103 | 7603.62
2009-10-12 02:33 | 59.999 | 3781.2559 | 335 | 229.0892 | 0 | 157.5 | 10 | 0 | -103 | 7603.95
2009-10-12 02:33 | 59.999 | 3783.092 | 335 | 229.6633 | 0 | 158 | 10 | 0 | -103 | 7604.28
2009-10-12 02:33 | 60.005 | 3784.4209 | 335 | 229.6633 | 0 | 158.5 | 10 | 0 | -103 | 7604.61
2009-10-12 02:33 | 60.008 | 3785.4626 | 335 | 229.6633 | 0 | 159 | 10 | 0 | -103 | 7604.94
2009-10-12 02:33 | 60.014 | 3786.3042 | 335 | 229.6633 | 0 | 159.5 | 10 | 0 | -103 | 7605.27
2009-10-12 02:33 | 60.019 | 3787.5159 | 335 | 229.6633 | 0 | 160 | 10 | 0 | -103 | 7605.6
2009-10-12 02:33 | 60.017 | 3788.0303 | 335 | 229.2339 | 0 | 160.5 | 10 | 0 | -103 | 7605.93
2009-10-12 02:33 | 60.019 | 3789.2158 | 335 | 229.2339 | 0 | 161 | 10 | 0 | -103 | 7606.26
2009-10-12 02:34 | 60.024 | 3785.8418 | 335 | 229.2339 | 0 | 161.5 | 10 | 0 | -103 | 7606.59
2009-10-12 02:34 | 60.021 | 3787.9304 | 335 | 229.2339 | 0 | 162 | 10 | 0 | -103 | 7606.92
2009-10-12 02:34 | 60.024 | 3786.8748 | 335 | 262.1026 | 0 | 162.5 | 10 | 0 | -103 | 7607.25
2009-10-12 02:34 | 60.021 | 3787.3577 | 335 | 262.1026 | 0 | 163 | 10 | 0 | -103 | 7607.58
2009-10-12 02:34 | 60.025 | 3785.614 | 335 | 262.1026 | 0 | 163.5 | 10 | 0 | -103 | 7607.91
2009-10-12 02:34 | 60.02 | 3785.8037 | 335 | 262.717 | 0 | 164 | 10 | 0 | -103 | 7608.24
2009-10-12 02:34 | 60.022 | 3786.8772 | 335 | 262.717 | 0 | 164.5 | 10 | 0 | -103 | 7608.57
2009-10-12 02:34 | 60.022 | 3785.7261 | 335 | 262.717 | 0 | 165 | 10 | 0 | -103 | 7608.9
2009-10-12 02:34 | 60.021 | 3785.821 | 335 | 262.717 | 0 | 165.5 | 10 | 0 | -103 | 7609.23
2009-10-12 02:34 | 60.023 | 3786.2842 | 335 | 262.717 | 0 | 166 | 10 | 0 | -103 | 7609.56
2009-10-12 02:34 | 60.019 | 3787.6274 | 335 | 260.0165 | 0 | 166.5 | 10 | 0 | -103 | 7609.89
2009-10-12 02:34 | 60.018 | 3789.6733 | 335 | 260.0165 | 0 | 167 | 10 | 0 | -103 | 7610.22
2009-10-12 02:34 | 60.018 | 3788.4788 | 335 | 260.0165 | 0 | 167.5 | 10 | 0 | -103 | 7610.55
2009-10-12 02:34 | 60.019 | 3789.3689 | 335 | 260.0165 | 0 | 168 | 10 | 0 | -103 | 7610.88
2009-10-12 02:34 | 60.015 | 3788.6646 | 335 | 260.0165 | 0 | 168.5 | 10 | 0 | -103 | 7611.21
2009-10-12 02:35 | 60.014 | 3790.667 | 335 | 263.8732 | 0 | 169 | 10 | 0 | -103 | 7611.54
2009-10-12 02:35 | 60.012 | 3790.4111 | 335 | 263.8732 | 0 | 169.5 | 10 | 0 | -103 | 7611.87
2009-10-12 02:35 | 60.01 | 3791.5398 | 335 | 263.8732 | 0 | 170 | 10 | 0 | -103 | 7612.2
2009-10-12 02:35 | 60.007 | 3791.0271 | 335 | 263.8732 | 0 | 170.5 | 10 | 0 | -103 | 7612.53
2009-10-12 02:35 | 60.009 | 3791.426 | 335 | 263.8732 | 0 | 171 | 10 | 0 | -103 | 7612.86
2009-10-12 02:35 | 60.003 | 3790.4573 | 335 | 264.5979 | 0 | 171.5 | 10 | 0 | -103 | 7613.19
2009-10-12 02:35 | 59.995 | 3789.585 | 335 | 264.5979 | 0 | 172 | 10 | 0 | -103 | 7613.52
2009-10-12 02:35 | 59.991 | 3788.105 | 335 | 264.5979 | 0 | 172.5 | 10 | 0 | -103 | 7613.85
2009-10-12 02:35 | 59.992 | 3788.1895 | 335 | 264.5979 | 0 | 173 | 10 | 0 | -103 | 7614.18
2009-10-12 02:35 | 59.986 | 3788.54 | 335 | 264.5979 | 0 | 173.5 | 10 | 0 | -103 | 7614.51
2009-10-12 02:35 | 59.984 | 3788.1011 | 335 | 262.4159 | 0 | 174 | 10 | 0 | -103 | 7614.84
2009-10-12 02:35 | 59.984 | 3786.4529 | 335 | 262.4159 | 0 | 174.5 | 10 | 0 | -103 | 7615.17
2009-10-12 02:35 | 59.981 | 3788.8135 | 335 | 262.4159 | 0 | 175 | 10 | 0 | -103 | 7615.5
2009-10-12 02:35 | 59.979 | 3788.2563 | 335 | 262.4159 | 0 | 175.5 | 10 | 0 | -103 | 7615.83
2009-10-12 02:35 | 59.976 | 3790.4673 | 335 | 262.4159 | 0 | 176 | 10 | 0 | -103 | 7616.16
2009-10-12 02:36 | 59.979 | 3790.4204 | 335 | 259.6852 | 0 | 176.5 | 10 | 0 | -103 | 7616.49
2009-10-12 02:36 | 59.978 | 3789.2671 | 335 | 259.6852 | 0 | 177 | 10 | 0 | -103 | 7616.82
2009-10-12 02:36 | 59.974 | 3790.4304 | 335 | 259.6852 | 0 | 177.5 | 10 | 0 | -103 | 7617.15
2009-10-12 02:36 | 59.977 | 3786.2432 | 335 | 259.6852 | 0 | 178 | 10 | 0 | -103 | 7617.48
2009-10-12 02:36 | 59.975 | 3788.9629 | 335 | 259.6852 | 0 | 178.5 | 10 | 0 | -103 | 7617.81
2009-10-12 02:36 | 59.969 | 3791.877 | 335 | 255.911 | 0 | 179 | 10 | 0 | -103 | 7618.14
2009-10-12 02:36 | 59.971 | 3792.3113 | 335 | 255.911 | 0 | 179.5 | 10 | 0 | -103 | 7618.47
2009-10-12 02:36 | 59.978 | 3788.0796 | 335 | 255.911 | 0 | 180 | 10 | 0 | -103 | 7618.8
2009-10-12 02:36 | 59.978 | 3787.135 | 335 | 255.911 | 0 | 180.5 | 10 | 0 | -103 | 7619.13
2009-10-12 02:36 | 59.972 | 3786.9961 | 335 | 255.911 | 0 | 181 | 10 | 0 | -103 | 7619.46
2009-10-12 02:36 | 59.975 | 3786.4868 | 335 | 258.1482 | 0 | 181.5 | 10 | 0 | -103 | 7619.79
2009-10-12 02:36 | 59.969 | 3789.2139 | 335 | 258.1482 | 0 | 182 | 10 | 0 | -103 | 7620.12
2009-10-12 02:36 | 59.965 | 3791.2212 | 335 | 258.1482 | 0 | 182.5 | 10 | 0 | -103 | 7620.45
2009-10-12 02:36 | 59.969 | 3790.9595 | 335 | 258.1482 | 0 | 183 | 10 | 0 | -103 | 7620.78
2009-10-12 02:36 | 59.968 | 3789.0264 | 335 | 258.1482 | 0 | 183.5 | 10 | 0 | -103 | 7621.11
2009-10-12 02:37 | 59.964 | 3787.394 | 335 | 258.8736 | 0 | 184 | 10 | 0 | -103 | 7621.44
2009-10-12 02:37 | 59.972 | 3784.8306 | 335 | 258.8736 | 0 | 184.5 | 10 | 0 | -103 | 7621.77
2009-10-12 02:37 | 59.967 | 3784.3203 | 335 | 258.8736 | 0 | 185 | 10 | 0 | -103 | 7622.1
2009-10-12 02:37 | 59.968 | 3782.1099 | 335 | 258.8736 | 0 | 185.5 | 10 | 0 | -103 | 7622.43
2009-10-12 02:37 | 59.967 | 3779.0562 | 335 | 258.8736 | 0 | 186 | 10 | 0 | -103 | 7622.76
2009-10-12 02:37 | 59.966 | 3779.2117 | 335 | 249.3376 | 0 | 186.5 | 10 | 0 | -103 | 7623.09
2009-10-12 02:37 | 59.971 | 3776.4292 | 335 | 249.3376 | 0 | 187 | 10 | 0 | -103 | 7623.42
2009-10-12 02:37 | 59.965 | 3776.5967 | 335 | 249.3376 | 0 | 187.5 | 10 | 0 | -103 | 7623.75
2009-10-12 02:37 | 59.964 | 3776.0229 | 335 | 249.3376 | 0 | 188 | 10 | 0 | -103 | 7624.08
2009-10-12 02:37 | 59.967 | 3771.7305 | 335 | 249.3376 | 0 | 188.5 | 10 | 0 | -103 | 7624.41
2009-10-12 02:37 | 59.968 | 3768.5029 | 335 | 258.2782 | 0 | 189 | 10 | 0 | -103 | 7624.74
2009-10-12 02:37 | 59.965 | 3767.3662 | 335 | 258.2782 | 0 | 189.5 | 10 | 0 | -103 | 7625.07
2009-10-12 02:37 | 59.973 | 3760.2954 | 335 | 258.2782 | 0 | 190 | 10 | 0 | -103 | 7625.4
2009-10-12 02:37 | 59.965 | 3761.8938 | 335 | 258.2782 | 0 | 190.5 | 10 | 0 | -103 | 7625.73
2009-10-12 02:37 | 59.969 | 3760.5825 | 335 | 258.2782 | 0 | 191 | 10 | 0 | -103 | 7626.06
2009-10-12 02:38 | 59.964 | 3759.781 | 335 | 258.4064 | 0 | 191.5 | 10 | 0 | -103 | 7626.39
2009-10-12 02:38 | 59.979 | 3757.7729 | 335 | 258.4064 | 0 | 192 | 10 | 0 | -103 | 7626.72
2009-10-12 02:38 | 59.983 | 3753.0874 | 335 | 258.4064 | 0 | 192.5 | 10 | 0 | -103 | 7627.05
2009-10-12 02:38 | 59.967 | 3753.751 | 335 | 258.4064 | 0 | 193 | 10 | 0 | -103 | 7627.38
2009-10-12 02:38 | 59.962 | 3759.2498 | 335 | 258.4064 | 0 | 193.5 | 10 | 0 | -103 | 7627.71
2009-10-12 02:38 | 59.961 | 3760.9648 | 335 | 260.5389 | 0 | 194 | 10 | 0 | -103 | 7628.04
2009-10-12 02:38 | 59.96 | 3763.8223 | 335 | 260.5389 | 0 | 194.5 | 10 | 0 | -103 | 7628.37
2009-10-12 02:38 | 59.959 | 3763.8582 | 335 | 260.5389 | 0 | 195 | 10 | 0 | -103 | 7628.7
2009-10-12 02:38 | 59.951 | 3766.1267 | 335 | 260.5389 | 0 | 195.5 | 10 | 0 | -103 | 7629.03
2009-10-12 02:38 | 59.954 | 3767.9722 | 335 | 260.5389 | 0 | 196 | 10 | 0 | -103 | 7629.36
2009-10-12 02:38 | 59.956 | 3765.6064 | 335 | 257.8821 | 0 | 196.5 | 10 | 0 | -103 | 7629.69
2009-10-12 02:38 | 59.963 | 3761.5703 | 335 | 257.8821 | 0 | 197 | 10 | 0 | -103 | 7630.02
2009-10-12 02:38 | 59.959 | 3759.627 | 335 | 257.8821 | 0 | 197.5 | 10 | 0 | -103 | 7630.35
2009-10-12 02:38 | 59.963 | 3752.4287 | 335 | 257.8821 | 0 | 198 | 10 | 0 | -103 | 7630.68
2009-10-12 02:38 | 59.968 | 3753.8296 | 335 | 257.8821 | 0 | 198.5 | 10 | 0 | -103 | 7631.01
2009-10-12 02:39 | 59.968 | 3753.5229 | 335 | 258.5887 | 0 | 199 | 10 | 0 | -103 | 7631.34
2009-10-12 02:39 | 59.973 | 3753.1782 | 335 | 258.5887 | 0 | 199.5 | 10 | 0 | -103 | 7631.67
2009-10-12 02:39 | 59.965 | 3753.2905 | 335 | 258.5887 | 0 | 200 | 10 | 0 | -103 | 7632
2009-10-12 02:39 | 59.967 | 3752.3586 | 335 | 258.5887 | 0 | 200.5 | 10 | 0 | -103 | 7632.33
2009-10-12 02:39 | 59.976 | 3747.4758 | 335 | 258.5887 | 0 | 201 | 10 | 0 | -103 | 7632.66
2009-10-12 02:39 | 59.969 | 3741.2852 | 335 | 261.9062 | 0 | 201.5 | 10 | 0 | -103 | 7632.99
2009-10-12 02:39 | 59.974 | 3745.7383 | 335 | 261.9062 | 0 | 202 | 10 | 0 | -103 | 7633.32
2009-10-12 02:39 | 59.981 | 3741.6182 | 335 | 261.9062 | 0 | 202.5 | 10 | 0 | -103 | 7633.65
2009-10-12 02:39 | 59.981 | 3738.4844 | 335 | 261.9062 | 0 | 203 | 10 | 0 | -103 | 7633.98
2009-10-12 02:39 | 59.982 | 3737.4036 | 335 | 261.9062 | 0 | 203.5 | 10 | 0 | -103 | 7634.31
2009-10-12 02:39 | 59.982 | 3736.3083 | 335 | 256.7478 | 0 | 204 | 10 | 0 | -103 | 7634.64
2009-10-12 02:39 | 59.979 | 3735.4482 | 335 | 256.7478 | 0 | 204.5 | 10 | 0 | -103 | 7634.97
2009-10-12 02:39 | 59.978 | 3737.5405 | 335 | 256.7478 | 0 | 205 | 10 | 0 | -103 | 7635.3
2009-10-12 02:39 | 59.98 | 3736.7476 | 350 | 256.7478 | 0 | 205.5 | 10 | 0 | -103 | 7635.63
2009-10-12 02:39 | 59.98 | 3736.0674 | 350 | 256.7478 | 0 | 206 | 10 | 0 | -103 | 7635.96
2009-10-12 02:40 | 59.976 | 3736.575 | 350 | 167.432 | 0 | 206.5 | 10 | 0 | -103 | 7636.29
2009-10-12 02:40 | 59.971 | 3738.8748 | 350 | 167.432 | 0 | 207 | 10 | 0 | -103 | 7636.62
2009-10-12 02:40 | 59.974 | 3738.647 | 350 | 167.432 | 0 | 207.5 | 10 | 0 | -103 | 7636.95
2009-10-12 02:40 | 59.976 | 3737.3821 | 350 | 167.432 | 0 | 208 | 10 | 0 | -103 | 7637.28
2009-10-12 02:40 | 59.969 | 3740.0168 | 350 | 167.432 | 0 | 208.5 | 10 | 0 | -103 | 7637.61
2009-10-12 02:40 | 59.974 | 3742.0527 | 350 | 164.9734 | 0 | 209 | 10 | 0 | -103 | 7637.94
2009-10-12 02:40 | 59.972 | 3742.5244 | 350 | 164.9734 | 0 | 209.5 | 10 | 0 | -103 | 7638.27
2009-10-12 02:40 | 59.977 | 3741.7231 | 350 | 164.9734 | 0 | 210 | 10 | 0 | -103 | 7638.6
2009-10-12 02:40 | 59.978 | 3740.6292 | 350 | 164.9734 | 0 | 210.5 | 10 | 0 | -103 | 7638.93
2009-10-12 02:40 | 59.973 | 3740.7751 | 350 | 164.9734 | 0 | 211 | 10 | 0 | -103 | 7639.26
2009-10-12 02:40 | 59.977 | 3741.2678 | 350 | 157.6281 | 0 | 211.5 | 10 | 0 | -103 | 7639.59
2009-10-12 02:40 | 59.978 | 3738.9658 | 350 | 157.6281 | 0 | 212 | 10 | 0 | -103 | 7639.92
2009-10-12 02:40 | 59.981 | 3738.8787 | 350 | 157.6281 | 0 | 212.5 | 10 | 0 | -103 | 7640.25
2009-10-12 02:40 | 59.974 | 3738.1016 | 350 | 157.6281 | 0 | 213 | 10 | 0 | -103 | 7640.58
2009-10-12 02:40 | 59.971 | 3743.5068 | 350 | 157.6281 | 0 | 213.5 | 10 | 0 | -103 | 7640.91
2009-10-12 02:41 | 59.972 | 3745.2507 | 350 | 155.5317 | 0 | 214 | 10 | 0 | -103 | 7641.24
2009-10-12 02:41 | 59.966 | 3747.3396 | 350 | 155.5317 | 0 | 214.5 | 10 | 0 | -103 | 7641.57
2009-10-12 02:41 | 59.971 | 3749.75 | 350 | 155.5317 | 0 | 215 | 10 | 0 | -103 | 7641.9
2009-10-12 02:41 | 59.972 | 3744.6826 | 350 | 155.5317 | 0 | 215.5 | 10 | 0 | -103 | 7642.23
2009-10-12 02:41 | 59.972 | 3743.1489 | 350 | 155.5317 | 0 | 216 | 10 | 0 | -103 | 7642.56
2009-10-12 02:41 | 59.973 | 3739.4526 | 350 | 160.4472 | 0 | 216.5 | 10 | 0 | -103 | 7642.89
2009-10-12 02:41 | 59.971 | 3731.8296 | 350 | 160.4472 | 0 | 217 | 10 | 0 | -103 | 7643.22
2009-10-12 02:41 | 59.982 | 3736.2295 | 350 | 160.4472 | 0 | 217.5 | 10 | 0 | -103 | 7643.55
2009-10-12 02:41 | 59.985 | 3733.4338 | 350 | 160.4472 | 0 | 218 | 10 | 0 | -103 | 7643.88
2009-10-12 02:41 | 59.987 | 3730.5098 | 350 | 160.4472 | 0 | 218.5 | 10 | 0 | -103 | 7644.21
2009-10-12 02:41 | 59.989 | 3725.4587 | 350 | 163.9586 | 0 | 219 | 10 | 0 | -103 | 7644.54
2009-10-12 02:41 | 59.987 | 3720.1079 | 350 | 163.9586 | 0 | 219.5 | 10 | 0 | -103 | 7644.87
2009-10-12 02:41 | 59.994 | 3725.6614 | 350 | 163.9586 | 0 | 220 | 10 | 0 | -103 | 7645.2
2009-10-12 02:41 | 60.001 | 3727.7542 | 350 | 163.9586 | 0 | 220.5 | 10 | 0 | -103 | 7645.53
2009-10-12 02:41 | 60.004 | 3727.6833 | 350 | 163.9586 | 0 | 221 | 10 | 0 | -103 | 7645.86
2009-10-12 02:42 | 60.012 | 3725.0122 | 350 | 166.0724 | 0 | 221.5 | 10 | 0 | -103 | 7646.19
2009-10-12 02:42 | 60.019 | 3726.0156 | 350 | 166.0724 | 0 | 222 | 10 | 0 | -103 | 7646.52
2009-10-12 02:42 | 60.025 | 3716.3745 | 350 | 166.0724 | 0 | 222.5 | 10 | 0 | -103 | 7646.85
2009-10-12 02:42 | 60.027 | 3717.5598 | 350 | 166.0724 | 0 | 223 | 10 | 0 | -103 | 7647.18
2009-10-12 02:42 | 60.029 | 3715.166 | 350 | 166.0724 | 0 | 223.5 | 10 | 0 | -103 | 7647.51
2009-10-12 02:42 | 60.036 | 3710.2834 | 350 | 163.7666 | 0 | 224 | 10 | 0 | -103 | 7647.84
2009-10-12 02:42 | 60.037 | 3699.3557 | 350 | 163.7666 | 0 | 224.5 | 10 | 0 | -103 | 7648.17
2009-10-12 02:42 | 60.041 | 3704.5913 | 350 | 163.7666 | 0 | 225 | 10 | 0 | -103 | 7648.5
2009-10-12 02:42 | 60.044 | 3702.4824 | 350 | 163.7666 | 0 | 225.5 | 10 | 0 | -103 | 7648.83
2009-10-12 02:42 | 60.046 | 3700.8259 | 350 | 163.7666 | 0 | 226 | 10 | 0 | -103 | 7649.16
2009-10-12 02:42 | 60.046 | 3699.7261 | 350 | 165.1017 | 0 | 226.5 | 10 | 0 | -103 | 7649.49
2009-10-12 02:42 | 60.043 | 3690.4773 | 350 | 165.1017 | 0 | 227 | 10 | 0 | -103 | 7649.82
2009-10-12 02:42 | 60.044 | 3696.8772 | 350 | 165.1017 | 0 | 227.5 | 10 | 0 | -103 | 7650.15
2009-10-12 02:42 | 60.043 | 3696.5413 | 350 | 165.1017 | 0 | 228 | 10 | 0 | -103 | 7650.48
2009-10-12 02:42 | 60.04 | 3698.686 | 350 | 165.1017 | 0 | 228.5 | 10 | 0 | -103 | 7650.81
2009-10-12 02:43 | 60.039 | 3698.7869 | 350 | 165.4764 | 0 | 229 | 10 | 0 | -103 | 7651.14
2009-10-12 02:43 | 60.036 | 3700.1057 | 350 | 165.4764 | 0 | 229.5 | 10 | 0 | -103 | 7651.47
2009-10-12 02:43 | 60.033 | 3701.1218 | 350 | 165.4764 | 0 | 230 | 10 | 0 | -103 | 7651.8
2009-10-12 02:43 | 60.037 | 3701.6138 | 350 | 165.4764 | 0 | 230.5 | 10 | 0 | -103 | 7652.13
2009-10-12 02:43 | 60.035 | 3702.9126 | 350 | 165.4764 | 0 | 231 | 10 | 0 | -103 | 7652.46
2009-10-12 02:43 | 60.033 | 3705.5225 | 350 | 206.4591 | 0 | 231.5 | 10 | 0 | -103 | 7652.79
2009-10-12 02:43 | 60.033 | 3704.0874 | 350 | 206.4591 | 0 | 232 | 10 | 0 | -103 | 7616
2009-10-12 02:43 | 60.032 | 3703.7063 | 335 | 206.4591 | 0 | 232.5 | 10 | 0 | -103 | 7626
2009-10-12 02:43 | 60.034 | 3705.4353 | 335 | 206.4591 | 0 | 233 | 10 | 0 | -103 | 7632
2009-10-12 02:43 | 60.037 | 3702.5879 | 335 | 206.4591 | 0 | 233.5 | 10 | 0 | -103 | 7632
2009-10-12 02:43 | 60.035 | 3701.9419 | 335 | 211.256 | 0 | 234 | 10 | 0 | -103 | 7632
2009-10-12 02:43 | 60.039 | 3703.3179 | 335 | 211.256 | 1 | 234.5 | 10 | 0 | -103 | 7632
2009-10-12 02:43 | 60.039 | 3702.5249 | 335 | 211.256 | 1 | 235 | 10 | 0 | -103 | 7632
2009-10-12 02:43 | 60.034 | 3703.8435 | 335 | 211.256 | 1 | 235.5 | 10 | 0 | -103 | 7632
2009-10-12 02:43 | 60.037 | 3702.5176 | 335 | 211.256 | 1 | 236 | 10 | 0 | -103 | 7632
2009-10-12 02:44 | 60.037 | 3692.427 | 335 | 214.3467 | 1 | 236.5 | 10 | 0 | -103 | 7632
2009-10-12 02:44 | 60.04 | 3700.2759 | 335 | 214.3467 | 1 | 237 | 10 | 0 | -103 | 7632
2009-10-12 02:44 | 60.045 | 3697.7285 | 335 | 214.3467 | 1 | 237.5 | 10 | 0 | -103 | 7632
2009-10-12 02:44 | 60.042 | 3697.3684 | 335 | 214.3467 | 2 | 238 | 10 | 0 | -103 | 7632
2009-10-12 02:44 | 60.04 | 3698.4292 | 335 | 214.3467 | 3 | 238.5 | 10 | 0 | -103 | 7632
2009-10-12 02:44 | 60.046 | 3693.5837 | 335 | 212.1727 | 4 | 239 | 10 | 0 | -103 | 7632
2009-10-12 02:44 | 60.034 | 3696.7983 | 335 | 212.1727 | 5 | 239.5 | 10 | 0 | -103 | 7632
2009-10-12 02:44 | 60.039 | 3701.791 | 335 | 212.1727 | 6 | 240 | 10 | 0 | -103 | 7632
2009-10-12 02:44 | 60.037 | 3700.7534 | 335 | 212.1727 | 7 | 240.5 | 10 | 0 | -103 | 7632
2009-10-12 02:44 | 60.033 | 3705.2126 | 335 | 212.1727 | 8 | 241 | 10 | 0 | -103 | 7632
2009-10-12 02:44 | 60.031 | 3707.2866 | 335 | 215.5982 | 9 | 241.5 | 10 | 0 | -103 | 7632
2009-10-12 02:44 | 60.027 | 3707.3403 | 335 | 215.5982 | 10 | 242 | 10 | 0 | -103 | 7632
2009-10-12 02:44 | 60.032 | 3707.3838 | 335 | 215.5982 | 11 | 242.5 | 10 | 0 | -103 | 7632
2009-10-12 02:44 | 60.031 | 3707.6152 | 335 | 215.5982 | 12 | 243 | 10 | 0 | -103 | 7632
2009-10-12 02:44 | 60.039 | 3703.7461 | 335 | 215.5982 | 13 | 243.5 | 10 | 0 | -103 | 7632
2009-10-12 02:45 | 60.038 | 3700.8474 | 335 | 218.3273 | 14 | 244 | 10 | 0 | -103 | 7632
2009-10-12 02:45 | 60.035 | 3702.2122 | 335 | 218.3273 | 15 | 244.5 | 10 | 0 | -103 | 7632
2009-10-12 02:45 | 60.04 | 3700.3975 | 335 | 218.3273 | 16 | 245 | 10 | 0 | -103 | 7632
2009-10-12 02:45 | 60.035 | 3700.3665 | 335 | 218.3273 | 16 | 245.5 | 10 | 0 | -103 | 7632
2009-10-12 02:45 | 60.04 | 3700.6616 | 335 | 218.3273 | 16 | 246 | 10 | 0 | -103 | 7632
2009-10-12 02:45 | 60.045 | 3695.6882 | 335 | 217.3794 | 16 | 246.5 | 10 | 0 | -103 | 7632
2009-10-12 02:45 | 60.042 | 3693.8242 | 335 | 217.3794 | 16 | 247 | 10 | 0 | -103 | 7632
2009-10-12 02:45 | 60.044 | 3696.897 | 335 | 217.3794 | 16 | 247.5 | 10 | 0 | -103 | 7631
2009-10-12 02:45 | 60.041 | 3697.5024 | 335 | 217.3794 | 16 | 248 | 10 | 0 | -103 | 7625
2009-10-12 02:45 | 60.04 | 3699.4268 | 335 | 217.3794 | 16 | 248.5 | 10 | 0 | -103 | 7623
2009-10-12 02:45 | 60.044 | 3699.8064 | 335 | 214.8304 | 16 | 249 | 10 | 0 | -103 | 7621
2009-10-12 02:45 | 60.039 | 3697.6807 | 335 | 214.8304 | 16 | 249.5 | 10 | 0 | -103 | 7623
2009-10-12 02:45 | 60.042 | 3698.3589 | 335 | 214.8304 | 16 | 250 | 10 | 0 | -103 | 7625
2009-10-12 02:45 | 60.038 | 3699.0771 | 335 | 214.8304 | 16 | 250.5 | 10 | 0 | -103 | 7627
2009-10-12 02:45 | 60.037 | 3701.5918 | 335 | 214.8304 | 16 | 251 | 10 | 0 | -103 | 7628
2009-10-12 02:46 | 60.038 | 3700.1428 | 335 | 227.6559 | 16 | 251.5 | 10 | 0 | -103 | 7628
2009-10-12 02:46 | 60.039 | 3701.1394 | 335 | 227.6559 | 16 | 252 | 10 | 0 | -103 | 7629
2009-10-12 02:46 | 60.038 | 3700.2644 | 335 | 227.6559 | 16 | 252.5 | 10 | 0 | -103 | 7630
2009-10-12 02:46 | 60.04 | 3699.7212 | 335 | 227.6559 | 16 | 253 | 10 | 0 | -103 | 7631
2009-10-12 02:46 | 60.037 | 3699.5051 | 335 | 227.6559 | 16 | 253.5 | 10 | 0 | -103 | 7635
2009-10-12 02:46 | 60.039 | 3699.2161 | 335 | 225.0181 | 16 | 254 | 10 | 0 | -103 | 7638
2009-10-12 02:46 | 60.036 | 3700.6614 | 335 | 225.0181 | 16 | 254.5 | 10 | 0 | -103 | 7639
2009-10-12 02:46 | 60.033 | 3702.9675 | 335 | 225.0181 | 16 | 255 | 10 | 0 | -103 | 7642
2009-10-12 02:46 | 60.03 | 3704.9517 | 335 | 225.0181 | 16 | 255.5 | 10 | 0 | -103 | 7644
2009-10-12 02:46 | 60.032 | 3705.6213 | 335 | 225.0181 | 16 | 256 | 10 | 0 | -103 | 7645
2009-10-12 02:46 | 60.042 | 3701.9812 | 335 | 228.3652 | 16 | 256.5 | 10 | 0 | -103 | 7647
2009-10-12 02:46 | 60.036 | 3700.7471 | 335 | 228.3652 | 16 | 257 | 10 | 0 | -103 | 7648
2009-10-12 02:46 | 60.032 | 3705.0593 | 335 | 228.3652 | 16 | 257.5 | 10 | 0 | -103 | 7649
2009-10-12 02:46 | 60.034 | 3704.4487 | 335 | 228.3652 | 16 | 258 | 10 | 0 | -103 | 7650
2009-10-12 02:46 | 60.032 | 3703.6196 | 335 | 228.3652 | 16 | 258.5 | 10 | 0 | -103 | 7651
2009-10-12 02:47 | 60.043 | 3701.4316 | 335 | 234.0753 | 16 | 259 | 10 | 0 | -103 | 7652
2009-10-12 02:47 | 60.042 | 3696.2495 | 335 | 234.0753 | 16 | 259.5 | 10 | 0 | -103 | 7653
2009-10-12 02:47 | 60.04 | 3693.5181 | 335 | 234.0753 | 16 | 260 | 10 | 0 | -103 | 7654
2009-10-12 02:47 | 60.043 | 3695.197 | 335 | 234.0753 | 16 | 260.5 | 10 | 0 | -103 | 7655
2009-10-12 02:47 | 60.041 | 3693.7861 | 335 | 234.0753 | 16 | 261 | 10 | 0 | -103 | 7655
2009-10-12 02:47 | 60.038 | 3694.9263 | 335 | 228.7982 | 16 | 261.5 | 10 | 0 | -103 | 7656
2009-10-12 02:47 | 60.044 | 3694.1594 | 335 | 228.7982 | 16 | 262 | 10 | 0 | -103 | 7656
2009-10-12 02:47 | 60.036 | 3692.6863 | 335 | 228.7982 | 16 | 262.5 | 10 | 0 | -103 | 7657
2009-10-12 02:47 | 60.041 | 3693.3901 | 335 | 228.7982 | 16 | 263 | 10 | 0 | -103 | 7657
2009-10-12 02:47 | 60.043 | 3690.9514 | 335 | 228.7982 | 16 | 263.5 | 10 | 0 | -103 | 7658
2009-10-12 02:47 | 60.036 | 3692.0422 | 335 | 229.467 | 16 | 264 | 10 | 0 | -103 | 7658
2009-10-12 02:47 | 60.039 | 3694.1172 | 335 | 229.467 | 16 | 264.5 | 10 | 0 | -103 | 7659
2009-10-12 02:47 | 60.034 | 3695.5808 | 335 | 229.467 | 16 | 265 | 10 | 0 | -103 | 7659
2009-10-12 02:47 | 60.035 | 3695.4912 | 335 | 229.467 | 16 | 265.5 | 10 | 0 | -103 | 7659
2009-10-12 02:47 | 60.036 | 3696.4863 | 335 | 229.467 | 16 | 266 | 10 | 0 | -103 | 7660
2009-10-12 02:48 | 60.03 | 3699.1709 | 335 | 228.9802 | 16 | 266.5 | 10 | 0 | -103 | 7660
2009-10-12 02:48 | 60.031 | 3699.2512 | 335 | 228.9802 | 16 | 267 | 10 | 0 | -103 | 7661
2009-10-12 02:48 | 60.032 | 3699.1052 | 335 | 228.9802 | 16 | 267.5 | 10 | 0 | -103 | 7661
2009-10-12 02:48 | 60.032 | 3698.9543 | 335 | 228.9802 | 16 | 268 | 10 | 0 | -103 | 7662
2009-10-12 02:48 | 60.032 | 3698.2773 | 335 | 228.9802 | 16 | 268.5 | 10 | 0 | -103 | 7662
2009-10-12 02:48 | 60.037 | 3695.9404 | 335 | 219.9756 | 16 | 269 | 10 | 0 | -103 | 7663
2009-10-12 02:48 | 60.039 | 3693.2236 | 335 | 219.9756 | 16 | 269.5 | 10 | 0 | -103 | 7663
2009-10-12 02:48 | 60.036 | 3691.9189 | 335 | 219.9756 | 16 | 270 | 10 | 0 | -103 | 7664
2009-10-12 02:48 | 60.041 | 3691.5815 | 335 | 219.9756 | 16 | 270.5 | 10 | 0 | -103 | 7664
2009-10-12 02:48 | 60.035 | 3693.3018 | 335 | 219.9756 | 16 | 271 | 10 | 0 | -103 | 7665
2009-10-12 02:48 | 60.038 | 3694.3313 | 335 | 229.0892 | 16 | 271.5 | 10 | 0 | -103 | 7666
2009-10-12 02:48 | 60.041 | 3693.6172 | 335 | 229.0892 | 16 | 272 | 10 | 0 | -103 | 7666
2009-10-12 02:48 | 60.036 | 3694.27 | 335 | 229.0892 | 16 | 272.5 | 10 | 0 | -103 | 7667
2009-10-12 02:48 | 60.034 | 3693.7476 | 335 | 229.0892 | 16 | 273 | 10 | 0 | -103 | 7668
2009-10-12 02:48 | 60.04 | 3691.4453 | 335 | 229.0892 | 16 | 273.5 | 10 | 0 | -103 | 7668
2009-10-12 02:49 | 60.037 | 3691.7988 | 335 | 229.6633 | 16 | 274 | 10 | 0 | -103 | 7669
2009-10-12 02:49 | 60.036 | 3693.7271 | 335 | 229.6633 | 16 | 274.5 | 10 | 0 | -103 | 7669
2009-10-12 02:49 | 60.038 | 3692.6406 | 335 | 229.6633 | 16 | 275 | 10 | 0 | -103 | 7670
2009-10-12 02:49 | 60.038 | 3689.0195 | 335 | 229.6633 | 16 | 275.5 | 10 | 0 | -103 | 7670
2009-10-12 02:49 | 60.033 | 3690.0918 | 335 | 229.6633 | 16 | 276 | 10 | 0 | -103 | 7671
2009-10-12 02:49 | 60.034 | 3693.3208 | 335 | 229.2339 | 16 | 276.5 | 10 | 0 | -103 | 7671
2009-10-12 02:49 | 60.029 | 3695.2249 | 335 | 229.2339 | 16 | 277 | 10 | 0 | -103 | 7672
2009-10-12 02:49 | 60.03 | 3693.4116 | 335 | 229.2339 | 16 | 277.5 | 10 | 0 | -103 | 7673
2009-10-12 02:49 | 60.026 | 3696.0259 | 335 | 229.2339 | 16 | 278 | 10 | 0 | -103 | 7673
2009-10-12 02:49 | 60.021 | 3699.0615 | 350 | 229.2339 | 16 | 278.5 | 10 | 0 | -103 | 7673
2009-10-12 02:49 | 60.023 | 3698.9351 | 350 | 231.4099 | 16 | 279 | 10 | 0 | -103 | 7673
2009-10-12 02:49 | 60.021 | 3700.5442 | 350 | 231.4099 | 16 | 279.5 | 10 | 0 | -103 | 7673
2009-10-12 02:49 | 60.025 | 3698.5957 | 350 | 231.4099 | 16 | 280 | 10 | 0 | -103 | 7673
2009-10-12 02:49 | 60.026 | 3699.9138 | 350 | 231.4099 | 16 | 280.5 | 10 | 0 | -103 | 7673
2009-10-12 02:49 | 60.024 | 3701.3013 | 350 | 231.4099 | 16 | 281 | 10 | 0 | -103 | 7673
2009-10-12 02:50 | 60.025 | 3701.3486 | 350 | 218.6223 | 16 | 281.5 | 10 | 0 | -103 | 7673
2009-10-12 02:50 | 60.023 | 3701.7017 | 350 | 218.6223 | 16 | 282 | 10 | 0 | -103 | 7673
2009-10-12 02:50 | 60.026 | 3701.9648 | 350 | 218.6223 | 16 | 282.5 | 10 | 0 | -103 | 7673
2009-10-12 02:50 | 60.026 | 3700.2412 | 350 | 218.6223 | 16 | 283 | 10 | 0 | -103 | 7673
2009-10-12 02:50 | 60.021 | 3701.2681 | 350 | 218.6223 | 16 | 283.5 | 10 | 0 | -103 | 7673
2009-10-12 02:50 | 60.025 | 3700.5874 | 350 | 213.5359 | 16 | 284 | 10 | 0 | -103 | 7673
2009-10-12 02:50 | 60.023 | 3700.1768 | 350 | 213.5359 | 16 | 284.5 | 10 | 0 | -103 | 7673
2009-10-12 02:50 | 60.024 | 3700.2773 | 350 | 213.5359 | 16 | 285 | 10 | 0 | -103 | 7673
2009-10-12 02:50 | 60.023 | 3700.8628 | 350 | 213.5359 | 16 | 285.5 | 10 | 0 | -103 | 7674
2009-10-12 02:50 | 60.025 | 3700.0525 | 350 | 213.5359 | 16 | 286 | 10 | 0 | -103 | 7675
2009-10-12 02:50 | 60.02 | 3700.9648 | 350 | 225.6519 | 16 | 286.5 | 10 | 0 | -103 | 7676
2009-10-12 02:50 | 60.015 | 3703.5161 | 350 | 225.6519 | 16 | 287 | 10 | 0 | -103 | 7677
2009-10-12 02:50 | 60.017 | 3703.6724 | 350 | 225.6519 | 16 | 287.5 | 10 | 0 | -103 | 7678
2009-10-12 02:50 | 60.015 | 3703.0034 | 350 | 225.6519 | 16 | 288 | 10 | 0 | -103 | 7679
2009-10-12 02:50 | 60.017 | 3702.9995 | 350 | 225.6519 | 16 | 288.5 | 10 | 0 | -103 | 7680
2009-10-12 02:51 | 60.01 | 3703.9182 | 350 | 212.5736 | 16 | 289 | 10 | 0 | -103 | 7681
2009-10-12 02:51 | 60.002 | 3703.7754 | 350 | 212.5736 | 16 | 289.5 | 10 | 0 | -103 | 7682
2009-10-12 02:51 | 59.999 | 3701.5337 | 350 | 212.5736 | 16 | 290 | 10 | 0 | -103 | 7684
2009-10-12 02:51 | 60.003 | 3700.8804 | 350 | 212.5736 | 16 | 290.5 | 10 | 0 | -103 | 7685
2009-10-12 02:51 | 60.001 | 3701.3889 | 350 | 212.5736 | 16 | 291 | 10 | 0 | -103 | 7687
2009-10-12 02:51 | 59.993 | 3700.6714 | 350 | 219.8973 | 16 | 291.5 | 10 | 0 | -103 | 7689
2009-10-12 02:51 | 59.989 | 3700.9771 | 350 | 219.8973 | 16 | 292 | 10 | 0 | -103 | 7690
2009-10-12 02:51 | 59.985 | 3699.8538 | 350 | 219.8973 | 16 | 292.5 | 10 | 0 | -103 | 7692
2009-10-12 02:51 | 59.986 | 3700.3423 | 350 | 219.8973 | 16 | 293 | 10 | 0 | -103 | 7692
2009-10-12 02:51 | 59.981 | 3700.7893 | 350 | 219.8973 | 16 | 293.5 | 10 | 0 | -103 | 7693
2009-10-12 02:51 | 59.977 | 3703.1658 | 350 | 231.1754 | 16 | 294 | 10 | 0 | -103 | 7693
2009-10-12 02:51 | 59.976 | 3704.7847 | 350 | 231.1754 | 16 | 294.5 | 10 | 0 | -103 | 7694
2009-10-12 02:51 | 59.974 | 3706.958 | 350 | 231.1754 | 16 | 295 | 10 | 0 | -103 | 7694
2009-10-12 02:51 | 59.975 | 3706.543 | 350 | 231.1754 | 16 | 295.5 | 10 | 0 | -103 | 7695
2009-10-12 02:51 | 59.971 | 3707.0266 | 350 | 231.1754 | 16 | 296 | 10 | 0 | -103 | 7695
2009-10-12 02:52 | 59.976 | 3710.5312 | 350 | 226.6341 | 16 | 296.5 | 10 | 0 | -103 | 7695
2009-10-12 02:52 | 59.98 | 3708.0181 | 350 | 226.6341 | 16 | 297 | 10 | 0 | -103 | 7696
2009-10-12 02:52 | 59.982 | 3706.3425 | 350 | 226.6341 | 16 | 297.5 | 10 | 0 | -103 | 7696
2009-10-12 02:52 | 59.983 | 3706.3105 | 350 | 226.6341 | 16 | 298 | 10 | 0 | -103 | 7697
2009-10-12 02:52 | 59.979 | 3706.1904 | 350 | 226.6341 | 16 | 298.5 | 10 | 0 | -103 | 7697
2009-10-12 02:52 | 59.976 | 3709.4089 | 350 | 227.2551 | 16 | 299 | 10 | 0 | -103 | 7697
2009-10-12 02:52 | 59.977 | 3708.5305 | 350 | 227.2551 | 16 | 299.5 | 10 | 0 | -103 | 7698
2009-10-12 02:52 | 59.978 | 3707.24 | 350 | 227.2551 | 16 | 300 | 10 | 0 | -103 | 7698
2009-10-12 02:52 | 59.971 | 3709.9612 | 350 | 227.2551 | 16 | 300.5 | 10 | 0 | -103 | 7698.33
2009-10-12 02:52 | 59.97 | 3711.9805 | 350 | 227.2551 | 16 | 301 | 10 | 0 | -103 | 7698.66
2009-10-12 02:52 | 59.99 | 3707.8667 | 350 | 229.2902 | 16 | 301.5 | 10 | 0 | -103 | 7698.99
2009-10-12 02:52 | 59.999 | 3705.6392 | 350 | 229.2902 | 16 | 302 | 10 | 0 | -103 | 7699.32
2009-10-12 02:52 | 59.998 | 3703.1909 | 350 | 229.2902 | 16 | 302.5 | 10 | 0 | -103 | 7699.65
2009-10-12 02:52 | 60.003 | 3699.51 | 350 | 229.2902 | 16 | 303 | 10 | 0 | -103 | 7699.98
2009-10-12 02:52 | 60.005 | 3698.1367 | 350 | 229.2902 | 16 | 303.5 | 10 | 0 | -103 | 7700.31
2009-10-12 02:53 | 60.013 | 3698.6682 | 350 | 221.4614 | 16 | 304 | 10 | 0 | -103 | 7700.64
2009-10-12 02:53 | 60.022 | 3697.8684 | 350 | 221.4614 | 16 | 304.5 | 10 | 0 | -103 | 7700.97
2009-10-12 02:53 | 60.025 | 3693.9121 | 350 | 221.4614 | 16 | 305 | 10 | 0 | -103 | 7701.3
2009-10-12 02:53 | 60.024 | 3688.3013 | 350 | 221.4614 | 16 | 305.5 | 10 | 0 | -103 | 7701.63
2009-10-12 02:53 | 60.029 | 3689.1431 | 350 | 221.4614 | 16 | 306 | 10 | 0 | -103 | 7701.96
2009-10-12 02:53 | 60.029 | 3687.8779 | 350 | 241.2744 | 16 | 306.5 | 10 | 0 | -103 | 7702.29
2009-10-12 02:53 | 60.028 | 3686.6831 | 350 | 241.2744 | 16 | 307 | 10 | 0 | -103 | 7702.62
2009-10-12 02:53 | 60.032 | 3685.5762 | 350 | 241.2744 | 16 | 307.5 | 10 | 0 | -103 | 7702.95
2009-10-12 02:53 | 60.031 | 3686.418 | 350 | 241.2744 | 16 | 308 | 10 | 0 | -103 | 7703.28
2009-10-12 02:53 | 60.022 | 3687.873 | 350 | 241.2744 | 16 | 308.5 | 10 | 0 | -103 | 7703.61
2009-10-12 02:53 | 60.019 | 3690.4258 | 350 | 243.0719 | 16 | 309 | 10 | 0 | -103 | 7703.94
2009-10-12 02:53 | 60.017 | 3692.7153 | 350 | 243.0719 | 16 | 309.5 | 10 | 0 | -103 | 7704.27
2009-10-12 02:53 | 60.016 | 3692.4617 | 350 | 243.0719 | 16 | 310 | 10 | 0 | -103 | 7704.6
2009-10-12 02:53 | 60.015 | 3693.2488 | 350 | 243.0719 | 16 | 310.5 | 10 | 0 | -103 | 7704.93
2009-10-12 02:53 | 60.009 | 3695.1243 | 350 | 243.0719 | 16 | 311 | 10 | 0 | -103 | 7705.26
2009-10-12 02:54 | 60.008 | 3694.7407 | 350 | 241.6702 | 16 | 311.5 | 10 | 0 | -103 | 7705.59
2009-10-12 02:54 | 60.005 | 3693.7495 | 350 | 241.6702 | 16 | 312 | 10 | 0 | -103 | 7705.92
2009-10-12 02:54 | 59.999 | 3692.8062 | 350 | 241.6702 | 16 | 312.5 | 10 | 0 | -103 | 7706.25
2009-10-12 02:54 | 59.999 | 3691.4067 | 350 | 241.6702 | 16 | 313 | 10 | 0 | -103 | 7706.58
2009-10-12 02:54 | 59.998 | 3690.5876 | 350 | 241.6702 | 16 | 313.5 | 10 | 0 | -103 | 7706.91
2009-10-12 02:54 | 59.994 | 3688.4827 | 350 | 228.1493 | 16 | 314 | 10 | 0 | -103 | 7707.24
2009-10-12 02:54 | 59.993 | 3689.5535 | 350 | 228.1493 | 16 | 314.5 | 10 | 0 | -103 | 7707.57
2009-10-12 02:54 | 59.985 | 3689.7356 | 350 | 228.1493 | 16 | 315 | 10 | 0 | -103 | 7707.9
2009-10-12 02:54 | 59.988 | 3688.2402 | 350 | 228.1493 | 16 | 315.5 | 10 | 0 | -103 | 7708.23
2009-10-12 02:54 | 59.985 | 3687.4753 | 350 | 228.1493 | 16 | 316 | 10 | 0 | -103 | 7708.56
2009-10-12 02:54 | 59.983 | 3685.6597 | 350 | 235.129 | 16 | 316.5 | 10 | 0 | -103 | 7708.89
2009-10-12 02:54 | 59.986 | 3684.3335 | 350 | 235.129 | 16 | 317 | 10 | 0 | -103 | 7709.22
2009-10-12 02:54 | 59.99 | 3683.7349 | 350 | 235.129 | 16 | 317.5 | 10 | 0 | -103 | 7709.55
2009-10-12 02:54 | 59.985 | 3683.811 | 350 | 235.129 | 16 | 318 | 10 | 0 | -103 | 7709.88
2009-10-12 02:54 | 59.983 | 3684.2578 | 350 | 235.129 | 16 | 318.5 | 10 | 0 | -103 | 7710.21
2009-10-12 02:55 | 59.982 | 3685.0918 | 350 | 246.4331 | 16 | 319 | 10 | 0 | -103 | 7710.54
2009-10-12 02:55 | 59.978 | 3685.0869 | 350 | 246.4331 | 16 | 319.5 | 10 | 0 | -103 | 7710.87
2009-10-12 02:55 | 59.975 | 3685.196 | 350 | 246.4331 | 16 | 320 | 10 | 0 | -103 | 7711.2
2009-10-12 02:55 | 59.975 | 3688.417 | 350 | 246.4331 | 16 | 320.5 | 10 | 0 | -103 | 7711.53
2009-10-12 02:55 | 59.976 | 3687.8477 | 350 | 246.4331 | 16 | 321 | 10 | 0 | -103 | 7711.86
2009-10-12 02:55 | 59.982 | 3685.7822 | 350 | 236.5535 | 16 | 321.5 | 10 | 0 | -103 | 7712.19
2009-10-12 02:55 | 59.979 | 3685.1426 | 350 | 236.5535 | 16 | 322 | 10 | 0 | -103 | 7712.52
2009-10-12 02:55 | 59.977 | 3684.0933 | 350 | 236.5535 | 16 | 322.5 | 10 | 0 | -103 | 7712.85
2009-10-12 02:55 | 59.978 | 3682.8142 | 350 | 236.5535 | 16 | 323 | 10 | 0 | -103 | 7713.18
2009-10-12 02:55 | 59.979 | 3682.3657 | 350 | 236.5535 | 16 | 323.5 | 10 | 0 | -103 | 7713.51
2009-10-12 02:55 | 59.981 | 3682.8555 | 350 | 230.2976 | 16 | 324 | 10 | 0 | -103 | 7713.84
2009-10-12 02:55 | 59.978 | 3684.0518 | 350 | 230.2976 | 16 | 324.5 | 10 | 0 | -103 | 7714.17
2009-10-12 02:55 | 59.978 | 3686.0488 | 350 | 230.2976 | 16 | 325 | 10 | 0 | -103 | 7714.5
2009-10-12 02:55 | 59.983 | 3685.2864 | 350 | 230.2976 | 16 | 325.5 | 10 | 0 | -103 | 7714.83
2009-10-12 02:55 | 59.99 | 3682.416 | 350 | 230.2976 | 16 | 326 | 10 | 0 | -103 | 7715.16
2009-10-12 02:56 | 59.993 | 3679.0125 | 350 | 231.1755 | 16 | 326.5 | 10 | 0 | -103 | 7715.49
2009-10-12 02:56 | 59.988 | 3671.7612 | 350 | 231.1755 | 16 | 327 | 10 | 0 | -103 | 7715.82
2009-10-12 02:56 | 59.99 | 3670.1594 | 350 | 231.1755 | 16 | 327.5 | 10 | 0 | -103 | 7716.15
2009-10-12 02:56 | 59.994 | 3680.1763 | 350 | 231.1755 | 16 | 328 | 10 | 0 | -103 | 7716.48
2009-10-12 02:56 | 59.994 | 3682.7004 | 350 | 231.1755 | 16 | 328.5 | 10 | 0 | -103 | 7716.81
2009-10-12 02:56 | 59.993 | 3685.0303 | 350 | 225.6176 | 16 | 329 | 10 | 0 | -103 | 7717.14
2009-10-12 02:56 | 59.984 | 3684.165 | 350 | 225.6176 | 16 | 329.5 | 10 | 0 | -103 | 7717.47
2009-10-12 02:56 | 59.985 | 3685.5837 | 350 | 225.6176 | 16 | 330 | 10 | 0 | -103 | 7717.8
2009-10-12 02:56 | 59.987 | 3684.5867 | 350 | 225.6176 | 16 | 330.5 | 10 | 0 | -103 | 7718.13
2009-10-12 02:56 | 59.987 | 3683.6743 | 350 | 225.6176 | 16 | 331 | 10 | 0 | -103 | 7718.46
2009-10-12 02:56 | 59.982 | 3684.2446 | 350 | 230.7344 | 16 | 331.5 | 10 | 0 | -103 | 7718.79
2009-10-12 02:56 | 59.982 | 3685.5891 | 350 | 230.7344 | 16 | 332 | 10 | 0 | -103 | 7719.12
2009-10-12 02:56 | 59.992 | 3682.5789 | 350 | 230.7344 | 16 | 332.5 | 10 | 0 | -103 | 7719.45
2009-10-12 02:56 | 60 | 3682.1377 | 350 | 230.7344 | 16 | 333 | 10 | 0 | -103 | 7719.78
2009-10-12 02:56 | 60.003 | 3681.689 | 350 | 230.7344 | 16 | 333.5 | 10 | 0 | -103 | 7720.11
2009-10-12 02:57 | 60.002 | 3681.6504 | 350 | 234.8471 | 16 | 334 | 10 | 0 | -103 | 7720.44
2009-10-12 02:57 | 60.002 | 3680.167 | 350 | 234.8471 | 16 | 334.5 | 10 | 0 | -103 | 7720.77
2009-10-12 02:57 | 60.004 | 3679.4292 | 350 | 234.8471 | 16 | 335 | 10 | 0 | -103 | 7721.1
2009-10-12 02:57 | 60.006 | 3678.9812 | 350 | 234.8471 | 16 | 335.5 | 10 | 0 | -103 | 7721.43
2009-10-12 02:57 | 60.012 | 3676.7961 | 350 | 234.8471 | 16 | 336 | 10 | 0 | -103 | 7721.76
2009-10-12 02:57 | 60.021 | 3674.7976 | 350 | 228.9609 | 16 | 336.5 | 10 | 0 | -103 | 7722.09
2009-10-12 02:57 | 60.021 | 3671.145 | 350 | 228.9609 | 16 | 337 | 10 | 0 | -103 | 7722.42
2009-10-12 02:57 | 60.018 | 3673.6479 | 350 | 228.9609 | 16 | 337.5 | 10 | 0 | -103 | 7722.75
2009-10-12 02:57 | 60.02 | 3675.8647 | 350 | 228.9609 | 16 | 338 | 10 | 0 | -103 | 7723.08
2009-10-12 02:57 | 60.018 | 3676.4038 | 350 | 228.9609 | 16 | 338.5 | 10 | 0 | -103 | 7723.41
2009-10-12 02:57 | 60.019 | 3677.1848 | 350 | 231.1779 | 16 | 339 | 10 | 0 | -103 | 7723.74
2009-10-12 02:57 | 60.018 | 3678.8284 | 350 | 231.1779 | 16 | 339.5 | 10 | 0 | -103 | 7724.07
2009-10-12 02:57 | 60.016 | 3678.9146 | 350 | 231.1779 | 16 | 340 | 10 | 0 | -103 | 7724.4
2009-10-12 02:57 | 60.016 | 3678.5986 | 350 | 231.1779 | 16 | 340.5 | 10 | 0 | -103 | 7724.73
2009-10-12 02:57 | 60.014 | 3678.2505 | 350 | 231.1779 | 16 | 341 | 10 | 0 | -103 | 7725.06
2009-10-12 02:58 | 60.013 | 3677.251 | 350 | 236.4893 | 16 | 341.5 | 10 | 0 | -103 | 7725.39
2009-10-12 02:58 | 60.015 | 3674.6694 | 350 | 236.4893 | 16 | 342 | 10 | 0 | -103 | 7725.72
2009-10-12 02:58 | 60.016 | 3674.4019 | 350 | 236.4893 | 16 | 342.5 | 10 | 0 | -103 | 7726.05
2009-10-12 02:58 | 60.021 | 3672.9688 | 350 | 236.4893 | 16 | 343 | 10 | 0 | -103 | 7726.38
2009-10-12 02:58 | 60.02 | 3671.9819 | 350 | 236.4893 | 16 | 343.5 | 10 | 0 | -103 | 7726.71
2009-10-12 02:58 | 60.024 | 3670.821 | 350 | 245.0389 | 16 | 344 | 10 | 0 | -103 | 7727.04
2009-10-12 02:58 | 60.025 | 3671.5386 | 350 | 245.0389 | 16 | 344.5 | 10 | 0 | -103 | 7727.37
2009-10-12 02:58 | 60.022 | 3674.0095 | 350 | 245.0389 | 16 | 345 | 10 | 0 | -103 | 7727.7
2009-10-12 02:58 | 60.022 | 3675.2842 | 350 | 245.0389 | 16 | 345.5 | 10 | 0 | -103 | 7728.03
2009-10-12 02:58 | 60.027 | 3675.7036 | 350 | 245.0389 | 16 | 346 | 10 | 0 | -103 | 7728.36
2009-10-12 02:58 | 60.028 | 3671.3428 | 350 | 223.6057 | 16 | 346.5 | 10 | 0 | -103 | 7728.69
2009-10-12 02:58 | 60.032 | 3668.6538 | 350 | 223.6057 | 16 | 347 | 10 | 0 | -103 | 7729.02
2009-10-12 02:58 | 60.03 | 3666.3123 | 350 | 223.6057 | 16 | 347.5 | 10 | 0 | -103 | 7729.35
2009-10-12 02:58 | 60.021 | 3657.1641 | 350 | 223.6057 | 16 | 348 | 10 | 0 | -103 | 7729.68
2009-10-12 02:58 | 60.024 | 3668.6375 | 350 | 223.6057 | 16 | 348.5 | 10 | 0 | -103 | 7730.01
2009-10-12 02:59 | 60.024 | 3670.1123 | 350 | 231.1194 | 16 | 349 | 10 | 0 | -103 | 7730.34
2009-10-12 02:59 | 60.023 | 3671.332 | 350 | 231.1194 | 16 | 349.5 | 10 | 0 | -103 | 7730.67
2009-10-12 02:59 | 60.02 | 3672.6831 | 350 | 231.1194 | 16 | 350 | 10 | 0 | -103 | 7731
2009-10-12 02:59 | 60.02 | 3674.6448 | 350 | 231.1194 | 16 | 350.5 | 10 | 0 | -103 | 7731.33
2009-10-12 02:59 | 60.017 | 3675.9707 | 350 | 231.1194 | 16 | 351 | 10 | 0 | -103 | 7731.66
2009-10-12 02:59 | 60.012 | 3678.3137 | 350 | 237.2066 | 16 | 351.5 | 10 | 0 | -103 | 7731.99
2009-10-12 02:59 | 60.011 | 3680.0203 | 350 | 237.2066 | 16 | 352 | 10 | 0 | -103 | 7732.32
2009-10-12 02:59 | 60.01 | 3679.5967 | 350 | 237.2066 | 16 | 352.5 | 10 | 0 | -103 | 7732.65
2009-10-12 02:59 | 60.012 | 3680.1104 | 350 | 237.2066 | 16 | 353 | 10 | 0 | -103 | 7732.98
2009-10-12 02:59 | 60.013 | 3679.1272 | 350 | 237.2066 | 16 | 353.5 | 10 | 0 | -103 | 7733.31
2009-10-12 02:59 | 60.013 | 3679.6367 | 350 | 240.5164 | 16 | 354 | 10 | 0 | -103 | 7733.64
2009-10-12 02:59 | 60.011 | 3678.4177 | 350 | 240.5164 | 16 | 354.5 | 10 | 0 | -103 | 7733.97
2009-10-12 02:59 | 60.008 | 3679.6809 | 350 | 240.5164 | 16 | 355 | 10 | 0 | -103 | 7734.3
2009-10-12 02:59 | 60.011 | 3679.1382 | 350 | 240.5164 | 16 | 355.5 | 10 | 0 | -103 | 7734.63
2009-10-12 02:59 | 60.016 | 3678.4985 | 350 | 240.5164 | 16 | 356 | 10 | 0 | -103 | 7734.96
2009-10-12 03:00 | 60.019 | 3677.6152 | 350 | 237.5661 | 16 | 356.5 | 10 | 0 | -103 | 7735.29
2009-10-12 03:00 | 60.019 | 3677.4314 | 350 | 237.5661 | 16 | 357 | 10 | 0 | -103 | 7735.62
2009-10-12 03:00 | 60.02 | 3677.3154 | 350 | 237.5661 | 16 | 357.5 | 10 | 0 | -103 | 7735.95
2009-10-12 03:00 | 60.018 | 3678.3621 | 350 | 237.5661 | 16 | 358 | 10 | 0 | -103 | 7736.28
2009-10-12 03:00 | 60.016 | 3680.7708 | 350 | 237.5661 | 16 | 358.5 | 10 | 0 | -103 | 7736.61
2009-10-12 03:00 | 60.023 | 3680.353 | 350 | 231.5814 | 16 | 359 | 10 | 0 | -103 | 7736.94
2009-10-12 03:00 | 60.018 | 3679.5532 | 350 | 231.5814 | 16 | 359.5 | 10 | 0 | -103 | 7737.27
2009-10-12 03:00 | 60.016 | 3682.7297 | 350 | 231.5814 | 16 | 360 | 10 | 0 | -103 | 7737.6
2009-10-12 03:00 | 60.015 | 3681.9146 | 350 | 231.5814 | 16 | 360.5 | 10 | 0 | -103 | 7737.93
2009-10-12 03:00 | 60.004 | 3682.4834 | 350 | 231.5814 | 16 | 361 | 10 | 0 | -103 | 7738.26
2009-10-12 03:00 | 59.995 | 3685.3064 | 350 | 235.8508 | 16 | 361.5 | 10 | 0 | -103 | 7738.59
2009-10-12 03:00 | 59.982 | 3684.6426 | 350 | 235.8508 | 16 | 362 | 10 | 0 | -103 | 7738.92
2009-10-12 03:00 | 59.97 | 3689.4038 | 350 | 235.8508 | 16 | 362.5 | 10 | 0 | -103 | 7739.25
2009-10-12 03:00 | 59.968 | 3692.9663 | 350 | 235.8508 | 16 | 363 | 10 | 0 | -103 | 7739.58
2009-10-12 03:00 | 59.968 | 3694.3972 | 350 | 235.8508 | 16 | 363.5 | 10 | 0 | -103 | 7739.91
2009-10-12 03:01 | 59.967 | 3697.407 | 350 | 233.56 | 16 | 364 | 10 | 0 | -103 | 7740.24
2009-10-12 03:01 | 59.964 | 3698.6169 | 350 | 233.56 | 16 | 364.5 | 10 | 0 | -103 | 7740.57
2009-10-12 03:01 | 59.966 | 3699.8501 | 350 | 233.56 | 16 | 365 | 10 | 0 | -103 | 7740.9
2009-10-12 03:01 | 59.963 | 3701.9885 | 350 | 233.56 | 16 | 365.5 | 10 | 0 | -103 | 7741.23
2009-10-12 03:01 | 59.968 | 3704.0234 | 350 | 233.56 | 16 | 366 | 10 | 0 | -103 | 7741.56
2009-10-12 03:01 | 59.97 | 3702.9883 | 350 | 219.01 | 16 | 366.5 | 10 | 0 | -103 | 7741.89
2009-10-12 03:01 | 59.973 | 3704.8994 | 350 | 219.01 | 16 | 367 | 10 | 0 | -103 | 7742.22
2009-10-12 03:01 | 59.976 | 3704.2935 | 350 | 219.01 | 16 | 367.5 | 10 | 0 | -103 | 7742.55
2009-10-12 03:01 | 59.975 | 3701.9438 | 350 | 219.01 | 16 | 368 | 10 | 0 | -103 | 7742.88
2009-10-12 03:01 | 59.976 | 3704.6689 | 350 | 219.01 | 16 | 368.5 | 10 | 0 | -103 | 7743.21
2009-10-12 03:01 | 59.974 | 3705.6624 | 350 | 205.3389 | 16 | 369 | 10 | 0 | -103 | 7743.54
2009-10-12 03:01 | 59.974 | 3706.7764 | 350 | 205.3389 | 16 | 369.5 | 10 | 0 | -103 | 7743.87
2009-10-12 03:01 | 59.976 | 3706.9282 | 350 | 205.3389 | 16 | 370 | 10 | 0 | -103 | 7744.2
2009-10-12 03:01 | 59.979 | 3706.335 | 350 | 205.3389 | 16 | 370.5 | 10 | 0 | -103 | 7744.53
2009-10-12 03:01 | 59.983 | 3705.9431 | 350 | 205.3389 | 16 | 371 | 10 | 0 | -103 | 7744.86
2009-10-12 03:02 | 59.983 | 3704.7773 | 350 | 236.2854 | 16 | 371.5 | 10 | 0 | -103 | 7745.19
2009-10-12 03:02 | 59.979 | 3705.9675 | 350 | 236.2854 | 16 | 372 | 10 | 0 | -103 | 7745.52
2009-10-12 03:02 | 59.987 | 3704.6831 | 350 | 236.2854 | 16 | 372.5 | 10 | 0 | -103 | 7745.85
2009-10-12 03:02 | 59.984 | 3704.3606 | 350 | 236.2854 | 16 | 373 | 10 | 0 | -103 | 7746.18
2009-10-12 03:02 | 59.982 | 3705.0498 | 350 | 236.2854 | 16 | 373.5 | 10 | 0 | -103 | 7746.51
2009-10-12 03:02 | 59.985 | 3703.7407 | 350 | 223.0157 | 16 | 374 | 10 | 0 | -103 | 7746.84
2009-10-12 03:02 | 59.989 | 3701.7952 | 350 | 223.0157 | 16 | 374.5 | 10 | 0 | -103 | 7747.17
2009-10-12 03:02 | 59.996 | 3701.3081 | 350 | 223.0157 | 16 | 375 | 10 | 0 | -103 | 7747.5
2009-10-12 03:02 | 59.997 | 3700.9128 | 350 | 223.0157 | 16 | 375.5 | 10 | 0 | -103 | 7747.83
2009-10-12 03:02 | 59.997 | 3699.9265 | 350 | 223.0157 | 16 | 376 | 10 | 0 | -103 | 7748.16
2009-10-12 03:02 | 59.996 | 3700.5486 | 350 | 223.0157 | 16 | 376.5 | 10 | 0 | -103 | 7748.49
2009-10-12 03:02 | 59.996 | 3700.2239 | 350 | 223.0157 | 16 | 377 | 10 | 0 | -103 | 7748.82
2009-10-12 03:02 | 60.003 | 3698.0317 | 350 | 223.0157 | 16 | 377.5 | 10 | 0 | -103 | 7749.15
2009-10-12 03:02 | 60.01 | 3699.4087 | 350 | 223.0157 | 16 | 378 | 10 | 0 | -103 | 7749.48
2009-10-12 03:02 | 60.005 | 3700.7383 | 350 | 223.0157 | 16 | 378.5 | 10 | 0 | -103 | 7749.81
2009-10-12 03:03 | 60.006 | 3701.2378 | 350 | 223.0157 | 16 | 379 | 10 | 0 | -103 | 7750.14
2009-10-12 03:03 | 60.001 | 3700.2202 | 350 | 223.0157 | 16 | 379.5 | 10 | 0 | -103 | 7750.47
2009-10-12 03:03 | 60.004 | 3702.5542 | 350 | 223.0157 | 16 | 380 | 10 | 0 | -103 | 7750.8
2009-10-12 03:03 | 60.007 | 3701.0264 | 350 | 223.0157 | 16 | 380.5 | 10 | 0 | -103 | 7751.13
2009-10-12 03:03 | 60.008 | 3702.9431 | 350 | 223.0157 | 16 | 381 | 10 | 0 | -103 | 7751.46
2009-10-12 03:03 | 60.006 | 3703.9604 | 350 | 223.0157 | 16 | 381.5 | 10 | 0 | -103 | 7751.79
2009-10-12 03:03 | 60.005 | 3704.4551 | 350 | 223.0157 | 16 | 382 | 10 | 0 | -103 | 7752.12
2009-10-12 03:03 | 59.999 | 3705.3291 | 350 | 223.0157 | 16 | 382.5 | 10 | 0 | -103 | 7752.45
2009-10-12 03:03 | 60 | 3704.4048 | 350 | 223.0157 | 16 | 383 | 10 | 0 | -103 | 7752.78
2009-10-12 03:03 | 60.008 | 3702.748 | 350 | 223.0157 | 16 | 383.5 | 10 | 0 | -103 | 7753.11
2009-10-12 03:03 | 60.015 | 3703.0166 | 350 | 223.0157 | 16 | 384 | 10 | 0 | -103 | 7753.44
2009-10-12 03:03 | 60.012 | 3703.2974 | 350 | 223.0157 | 16 | 384.5 | 10 | 0 | -103 | 7753.77
2009-10-12 03:03 | 60.005 | 3705.2791 | 350 | 223.0157 | 16 | 385 | 10 | 0 | -103 | 7754.1
2009-10-12 03:03 | 60.011 | 3704.0513 | 350 | 223.0157 | 16 | 385.5 | 10 | 0 | -103 | 7754.43
2009-10-12 03:03 | 60.013 | 3704.2551 | 350 | 223.0157 | 16 | 386 | 10 | 0 | -103 | 7754.76
2009-10-12 03:04 | 60.018 | 3703.8303 | 350 | 223.0157 | 16 | 386.5 | 10 | 0 | -103 | 7755.09
2009-10-12 03:04 | 60.019 | 3704.1392 | 350 | 223.0157 | 16 | 387 | 10 | 0 | -103 | 7755.42
2009-10-12 03:04 | 60.013 | 3705.4294 | 350 | 223.0157 | 16 | 387.5 | 10 | 0 | -103 | 7755.75
2009-10-12 03:04 | 60.009 | 3705.5398 | 350 | 223.0157 | 16 | 388 | 10 | 0 | -103 | 7756.08
2009-10-12 03:04 | 60.008 | 3705.7485 | 350 | 223.0157 | 16 | 388.5 | 10 | 0 | -103 | 7756.41
2009-10-12 03:04 | 60.011 | 3706.9453 | 350 | 223.0157 | 16 | 389 | 10 | 0 | -103 | 7756.74
2009-10-12 03:04 | 60.02 | 3705.6545 | 350 | 223.0157 | 16 | 389.5 | 10 | 0 | -103 | 7757.07
2009-10-12 03:04 | 60.018 | 3704.2239 | 350 | 223.0157 | 16 | 390 | 10 | 0 | -103 | 7757.4
2009-10-12 03:04 | 60.019 | 3704.6484 | 350 | 223.0157 | 16 | 390.5 | 10 | 0 | -103 | 7757.73
2009-10-12 03:04 | 60.021 | 3704.1665 | 350 | 223.0157 | 16 | 391 | 10 | 0 | -103 | 7758.06
2009-10-12 03:04 | 60.025 | 3702.0083 | 350 | 223.0157 | 16 | 391.5 | 10 | 0 | -103 | 7758.39
2009-10-12 03:04 | 60.03 | 3701.063 | 350 | 223.0157 | 16 | 392 | 10 | 0 | -103 | 7758.72
2009-10-12 03:04 | 60.023 | 3699.3694 | 350 | 223.0157 | 16 | 392.5 | 10 | 0 | -103 | 7759.05
2009-10-12 03:04 | 60.023 | 3702.9587 | 350 | 223.0157 | 16 | 393 | 10 | 0 | -103 | 7759.38
2009-10-12 03:04 | 60.02 | 3703.6211 | 350 | 223.0157 | 16 | 393.5 | 10 | 0 | -103 | 7759.71
2009-10-12 03:05 | 60.024 | 3703.0359 | 350 | 223.0157 | 16 | 394 | 10 | 0 | -103 | 7760.04
2009-10-12 03:05 | 60.022 | 3704.9473 | 350 | 223.0157 | 16 | 394.5 | 10 | 0 | -103 | 7760.37
2009-10-12 03:05 | 60.025 | 3703.5413 | 350 | 223.0157 | 16 | 395 | 10 | 0 | -103 | 7760.7
2009-10-12 03:05 | 60.024 | 3703.3975 | 350 | 223.0157 | 16 | 395.5 | 10 | 0 | -103 | 7761.03
2009-10-12 03:05 | 60.018 | 3705.4412 | 350 | 223.0157 | 16 | 396 | 10 | 0 | -103 | 7761.36
2009-10-12 03:05 | 60.008 | 3710.072 | 350 | 223.0157 | 16 | 396.5 | 10 | 0 | -103 | 7761.69
2009-10-12 03:05 | 60.017 | 3707.7671 | 350 | 223.0157 | 16 | 397 | 10 | 0 | -103 | 7762.02
2009-10-12 03:05 | 60.019 | 3708.8311 | 350 | 223.0157 | 16 | 397.5 | 10 | 0 | -103 | 7762.35
2009-10-12 03:05 | 60.016 | 3709.8135 | 350 | 223.0157 | 16 | 398 | 10 | 0 | -103 | 7762.68
2009-10-12 03:05 | 60.016 | 3709.9905 | 350 | 223.0157 | 16 | 398.5 | 10 | 0 | -103 | 7763.01
2009-10-12 03:05 | 60.016 | 3709.6416 | 350 | 223.0157 | 16 | 399 | 10 | 0 | -103 | 7763.34
2009-10-12 03:05 | 60.019 | 3709.9331 | 350 | 223.0157 | 16 | 399.5 | 10 | 0 | -103 | 7763.67
2009-10-12 03:05 | 60.014 | 3710.5911 | 350 | 223.0157 | 16 | 400 | 10 | 0 | -103 | 7764
2009-10-12 03:05 | 60.018 | 3707.696 | 350 | 223.0157 | 16 | 400.5 | 10 | 0 | -103 | 7764.33
2009-10-12 03:05 | 60.023 | 3707.1201 | 350 | 223.0157 | 16 | 401 | 10 | 0 | -103 | 7764.66
2009-10-12 03:06 | 60.026 | 3705.8481 | 350 | 223.0157 | 16 | 401.5 | 10 | 0 | -103 | 7764.99
2009-10-12 03:06 | 60.024 | 3704.4058 | 350 | 223.0157 | 16 | 402 | 10 | 0 | -103 | 7765.32
2009-10-12 03:06 | 60.02 | 3706.5674 | 350 | 223.0157 | 16 | 402.5 | 10 | 0 | -103 | 7765.65
2009-10-12 03:06 | 60.022 | 3704.8687 | 350 | 223.0157 | 16 | 403 | 10 | 0 | -103 | 7765.98
2009-10-12 03:06 | 60.028 | 3704.7734 | 350 | 223.0157 | 16 | 403.5 | 10 | 0 | -103 | 7766.31
2009-10-12 03:06 | 60.031 | 3702.6855 | 350 | 223.0157 | 16 | 404 | 10 | 0 | -103 | 7766.64
2009-10-12 03:06 | 60.026 | 3703.1692 | 350 | 223.0157 | 16 | 404.5 | 10 | 0 | -103 | 7766.97
2009-10-12 03:06 | 60.029 | 3701.5195 | 350 | 223.0157 | 16 | 405 | 10 | 0 | -103 | 7767.3
2009-10-12 03:06 | 60.033 | 3698.2217 | 350 | 223.0157 | 16 | 405.5 | 10 | 0 | -103 | 7767.63
2009-10-12 03:06 | 60.022 | 3700.2798 | 350 | 223.0157 | 16 | 406 | 10 | 0 | -103 | 7767.96
2009-10-12 03:06 | 60.019 | 3703.8147 | 350 | 223.0157 | 16 | 406.5 | 10 | 0 | -103 | 7768.29
2009-10-12 03:06 | 60.028 | 3699.9561 | 350 | 223.0157 | 16 | 407 | 10 | 0 | -103 | 7768.62
2009-10-12 03:06 | 60.015 | 3703.8022 | 350 | 223.0157 | 16 | 407.5 | 10 | 0 | -103 | 7768.95
2009-10-12 03:06 | 60.012 | 3708.5273 | 350 | 223.0157 | 16 | 408 | 10 | 0 | -103 | 7769.28
2009-10-12 03:06 | 60.014 | 3707.6475 | 350 | 223.0157 | 16 | 408.5 | 10 | 0 | -103 | 7769.61
2009-10-12 03:07 | 60.014 | 3707.4949 | 350 | 223.0157 | 16 | 409 | 10 | 0 | -103 | 7769.94
2009-10-12 03:07 | 60.016 | 3705.3979 | 350 | 223.0157 | 16 | 409.5 | 10 | 0 | -103 | 7770.27
2009-10-12 03:07 | 60.013 | 3709.144 | 350 | 223.0157 | 16 | 410 | 10 | 0 | -103 | 7770.6
2009-10-12 03:07 | 59.997 | 3708.291 | 350 | 223.0157 | 16 | 410.5 | 10 | 0 | -103 | 7770.93
2009-10-12 03:07 | 59.993 | 3707.3037 | 350 | 223.0157 | 16 | 411 | 10 | 0 | -103 | 7771.26
2009-10-12 03:07 | 59.993 | 3706.7603 | 350 | 223.0157 | 16 | 411.5 | 10 | 0 | -103 | 7771.59
2009-10-12 03:07 | 59.993 | 3706.6831 | 350 | 223.0157 | 16 | 412 | 10 | 0 | -103 | 7771.92
2009-10-12 03:07 | 59.993 | 3704.9336 | 350 | 223.0157 | 16 | 412.5 | 10 | 0 | -103 | 7772.25
2009-10-12 03:07 | 59.988 | 3706.481 | 350 | 223.0157 | 16 | 413 | 10 | 0 | -103 | 7772.58
2009-10-12 03:07 | 59.983 | 3706.6963 | 350 | 223.0157 | 16 | 413.5 | 10 | 0 | -103 | 7772.91
2009-10-12 03:07 | 59.98 | 3708.2458 | 350 | 223.0157 | 16 | 414 | 10 | 0 | -103 | 7773.24
2009-10-12 03:07 | 59.981 | 3710.4194 | 350 | 223.0157 | 16 | 414.5 | 10 | 0 | -103 | 7773.57
2009-10-12 03:07 | 59.978 | 3708.7078 | 350 | 223.0157 | 16 | 415 | 10 | 0 | -103 | 7773.9
2009-10-12 03:07 | 59.98 | 3709.1919 | 350 | 223.0157 | 16 | 415.5 | 10 | 0 | -103 | 7774.23
2009-10-12 03:07 | 59.98 | 3709.3994 | 350 | 223.0157 | 16 | 416 | 10 | 0 | -103 | 7774.56
2009-10-12 03:08 | 59.984 | 3709.0039 | 350 | 223.0157 | 16 | 416.5 | 10 | 0 | -103 | 7774.89
2009-10-12 03:08 | 59.981 | 3709.689 | 350 | 223.0157 | 16 | 417 | 10 | 0 | -103 | 7775.22
2009-10-12 03:08 | 59.981 | 3706.541 | 350 | 223.0157 | 16 | 417.5 | 10 | 0 | -103 | 7775.55
2009-10-12 03:08 | 59.981 | 3711.3621 | 350 | 223.0157 | 16 | 418 | 10 | 0 | -103 | 7775.88
2009-10-12 03:08 | 59.978 | 3712.0122 | 350 | 223.0157 | 16 | 418.5 | 10 | 0 | -103 | 7776.21
2009-10-12 03:08 | 59.979 | 3712.0928 | 350 | 223.0157 | 16 | 419 | 10 | 0 | -103 | 7776.54
2009-10-12 03:08 | 59.976 | 3714.6121 | 350 | 223.0157 | 16 | 419.5 | 10 | 0 | -103 | 7776.87
2009-10-12 03:08 | 59.975 | 3715.3228 | 350 | 223.0157 | 16 | 420 | 10 | 0 | -103 | 7777.2
2009-10-12 03:08 | 59.975 | 3714.7173 | 350 | 223.0157 | 16 | 420.5 | 10 | 0 | -103 | 7777.53
2009-10-12 03:08 | 59.978 | 3715.0012 | 350 | 223.0157 | 16 | 421 | 10 | 0 | -103 | 7777.86
2009-10-12 03:08 | 59.976 | 3714.0627 | 350 | 223.0157 | 16 | 421.5 | 10 | 0 | -103 | 7778.19
2009-10-12 03:08 | 59.977 | 3715.6311 | 350 | 223.0157 | 16 | 422 | 10 | 0 | -103 | 7778.52
2009-10-12 03:08 | 59.976 | 3715.5674 | 350 | 223.0157 | 16 | 422.5 | 10 | 0 | -103 | 7778.85
2009-10-12 03:08 | 59.98 | 3714.8481 | 350 | 223.0157 | 16 | 423 | 10 | 0 | -103 | 7779.18
2009-10-12 03:08 | 59.978 | 3713.3584 | 350 | 223.0157 | 16 | 423.5 | 10 | 0 | -103 | 7779.51
2009-10-12 03:09 | 59.982 | 3712.6194 | 350 | 223.0157 | 16 | 424 | 10 | 0 | -103 | 7779.84
2009-10-12 03:09 | 59.987 | 3710.0503 | 350 | 223.0157 | 16 | 424.5 | 10 | 0 | -103 | 7780.17
2009-10-12 03:09 | 59.984 | 3710.4719 | 350 | 223.0157 | 16 | 425 | 10 | 0 | -103 | 7780.5
2009-10-12 03:09 | 59.979 | 3710.9463 | 350 | 223.0157 | 16 | 425.5 | 10 | 0 | -103 | 7780.83
2009-10-12 03:09 | 59.979 | 3710.4746 | 350 | 223.0157 | 16 | 426 | 10 | 0 | -103 | 7781.16
2009-10-12 03:09 | 59.975 | 3710.803 | 350 | 223.0157 | 16 | 426.5 | 10 | 0 | -103 | 7781.49
2009-10-12 03:09 | 59.982 | 3710.573 | 350 | 223.0157 | 16 | 427 | 10 | 0 | -103 | 7781.82
2009-10-12 03:09 | 59.983 | 3708.3711 | 350 | 223.0157 | 16 | 427.5 | 10 | 0 | -103 | 7782.15
2009-10-12 03:09 | 59.99 | 3706.512 | 350 | 223.0157 | 16 | 428 | 10 | 0 | -103 | 7782.48
2009-10-12 03:09 | 59.984 | 3708.9624 | 350 | 223.0157 | 16 | 428.5 | 10 | 0 | -103 | 7782.81
2009-10-12 03:09 | 59.979 | 3712.3035 | 350 | 223.0157 | 16 | 429 | 10 | 0 | -103 | 7783.14
2009-10-12 03:09 | 59.983 | 3711.6272 | 350 | 223.0157 | 16 | 429.5 | 10 | 0 | -103 | 7783.47
2009-10-12 03:09 | 59.981 | 3712.3926 | 350 | 223.0157 | 16 | 430 | 10 | 0 | -103 | 7783.8
2009-10-12 03:09 | 59.975 | 3713.5103 | 350 | 223.0157 | 16 | 430.5 | 10 | 0 | -103 | 7784.13
2009-10-12 03:09 | 59.989 | 3715.4429 | 350 | 223.0157 | 16 | 431 | 10 | 0 | -103 | 7784.46
2009-10-12 03:10 | 59.994 | 3713.906 | 350 | 223.0157 | 16 | 431.5 | 10 | 0 | -103 | 7784.79
2009-10-12 03:10 | 59.986 | 3714.9531 | 350 | 223.0157 | 16 | 432 | 10 | 0 | -103 | 7785.12
2009-10-12 03:10 | 59.983 | 3716.3083 | 350 | 223.0157 | 16 | 432.5 | 10 | 0 | -103 | 7785.45
2009-10-12 03:10 | 59.98 | 3714.7637 | 350 | 223.0157 | 16 | 433 | 10 | 0 | -103 | 7785.78
2009-10-12 03:10 | 59.995 | 3715.0676 | 350 | 223.0157 | 16 | 433.5 | 10 | 0 | -103 | 7786.11
2009-10-12 03:10 | 59.99 | 3715.7913 | 350 | 223.0157 | 16 | 434 | 10 | 0 | -103 | 7786.44
2009-10-12 03:10 | 59.991 | 3715.3245 | 350 | 223.0157 | 16 | 434.5 | 10 | 0 | -103 | 7786.77
2009-10-12 03:10 | 60 | 3711.7085 | 350 | 223.0157 | 16 | 435 | 10 | 0 | -103 | 7787.1
2009-10-12 03:10 | 60.004 | 3712.8506 | 350 | 223.0157 | 16 | 435.5 | 10 | 0 | -103 | 7787.43
2009-10-12 03:10 | 60.002 | 3716.6414 | 350 | 223.0157 | 16 | 436 | 10 | 0 | -103 | 7787.76
2009-10-12 03:10 | 59.998 | 3719.0791 | 350 | 223.0157 | 16 | 436.5 | 10 | 0 | -103 | 7788.09
2009-10-12 03:10 | 59.996 | 3717.8152 | 350 | 223.0157 | 16 | 437 | 10 | 0 | -103 | 7788.42
2009-10-12 03:10 | 60.002 | 3718.5603 | 350 | 223.0157 | 16 | 437.5 | 10 | 0 | -103 | 7788.75
2009-10-12 03:10 | 60.003 | 3719.0212 | 350 | 223.0157 | 16 | 438 | 10 | 0 | -103 | 7789.08
2009-10-12 03:10 | 60.004 | 3719.8975 | 350 | 223.0157 | 16 | 438.5 | 10 | 0 | -103 | 7789.41
2009-10-12 03:11 | 60.004 | 3719.6428 | 350 | 223.0157 | 16 | 439 | 10 | 0 | -103 | 7789.74
2009-10-12 03:11 | 60.003 | 3719.731 | 350 | 223.0157 | 16 | 439.5 | 10 | 0 | -103 | 7790.07
2009-10-12 03:11 | 60.006 | 3718.5796 | 350 | 223.0157 | 16 | 440 | 10 | 0 | -103 | 7790.4
2009-10-12 03:11 | 60.009 | 3718.9822 | 350 | 223.0157 | 16 | 440.5 | 10 | 0 | -103 | 7790.73
2009-10-12 03:11 | 60.009 | 3720.6089 | 350 | 223.0157 | 16 | 441 | 10 | 0 | -103 | 7791.06
2009-10-12 03:11 | 60.015 | 3721.2388 | 350 | 223.0157 | 16 | 441.5 | 10 | 0 | -103 | 7791.39
2009-10-12 03:11 | 60.009 | 3719.4473 | 350 | 223.0157 | 16 | 442 | 10 | 0 | -103 | 7791.72
2009-10-12 03:11 | 60.008 | 3721.2722 | 350 | 223.0157 | 16 | 442.5 | 10 | 0 | -103 | 7792.05
2009-10-12 03:11 | 60.01 | 3721.2446 | 350 | 223.0157 | 16 | 443 | 10 | 0 | -103 | 7792.38
2009-10-12 03:11 | 60.013 | 3722.1763 | 350 | 223.0157 | 16 | 443.5 | 10 | 0 | -103 | 7792.71
2009-10-12 03:11 | 60.014 | 3721.646 | 350 | 223.0157 | 16 | 444 | 10 | 0 | -103 | 7793.04
2009-10-12 03:11 | 60.012 | 3720.8596 | 350 | 223.0157 | 16 | 444.5 | 10 | 0 | -103 | 7793.37
2009-10-12 03:11 | 60.011 | 3723.8157 | 350 | 223.0157 | 16 | 445 | 10 | 0 | -103 | 7793.7
2009-10-12 03:11 | 60.003 | 3724.656 | 350 | 223.0157 | 16 | 445.5 | 10 | 0 | -103 | 7794.03
2009-10-12 03:11 | 60 | 3724.6606 | 350 | 223.0157 | 16 | 446 | 10 | 0 | -103 | 7794.36
2009-10-12 03:12 | 59.998 | 3723.5801 | 350 | 223.0157 | 16 | 446.5 | 10 | 0 | -103 | 7794.69
2009-10-12 03:12 | 60.002 | 3721.8789 | 350 | 223.0157 | 16 | 447 | 10 | 0 | -103 | 7795.02
2009-10-12 03:12 | 60.003 | 3722.9065 | 350 | 223.0157 | 16 | 447.5 | 10 | 0 | -103 | 7795.35
2009-10-12 03:12 | 59.998 | 3723.6504 | 350 | 223.0157 | 16 | 448 | 10 | 0 | -103 | 7795.68
2009-10-12 03:12 | 59.995 | 3723.6389 | 350 | 223.0157 | 16 | 448.5 | 10 | 0 | -103 | 7796.01
2009-10-12 03:12 | 59.987 | 3724.6543 | 350 | 223.0157 | 16 | 449 | 10 | 0 | -103 | 7796.34
2009-10-12 03:12 | 59.988 | 3724.9438 | 350 | 223.0157 | 16 | 449.5 | 10 | 0 | -103 | 7796.67
2009-10-12 03:12 | 59.992 | 3723.6926 | 350 | 223.0157 | 16 | 450 | 10 | 0 | -103 | 7797

## Entry Data
Balancing Authority Name: | My BA
Balancing Authority Frequency Response Obligation (FRO from FRS Form 1) | -80
Note: See "Instruction" tab for more detailed instructions.
Step 1. | Copy and Paste Event Data into the appropriate cells of the "Data" worksheet.
Maintain date and time format of mm/dd/yy hh:mm:ss.
Step 2. | Determine Time of T(0) and edit formula in cell "C8" to reference the correct row of the "Data" worksheet. | 40098.1024
T(0) is the first change in frequency of about 0.010 Hz (10 mHz) which should be the first scan of frequency data of the event.
Step 3. | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1063
Step 4. | Enter MW output of generator or load that caused event (+ for gen loss, - for load loss) | 633 | MW
(Value from NERC Event List. If multiple units, enter total MW loss.)
If MW loss value is not known, enter a default 1000 MW.
Step 5. | Hit the big blue button to copy your data for pasting into FRS Form 1 "BA Event Data" worksheet.
Step 6. | Paste data into "FRS Form 1" in the appropriate row on the "BA Event Data" worksheet.
Step 7. | Save this workbook using the following file name format:MyBA_yymmdd_hhmm_FRS_Form2.xlsm
| 2009-10-12 02:27 | Date yymmdd
| 40098.1024 | Time hh:ss of T(0)
Where "MyBA" = your BA mnemonic
Note on C8: Cell "C8": Observe the first change in frequency that identifies the beginning of the event. Look in column "B" of the "Data" worksheet. Select and edit the formula in this cell ("=Data!Axxx") to reference that row number in the "Data" sheet of this first change in frequency where xxx is that row number.
Note on C11: Cell "C11": Similar to identifying the end of a DCS event but only looking at frequency, observe frequency following the beginning of the event. When actual frequency recovers to 60.00 Hz or to the pre-event frequency, edit the formula in this cell to reference that row number in the "Data" worksheet that this occurs. ("=Data!Axxx")
Copy Form 2 Data for Pasting into Form 1

## IPFR (hidden)
IPFR = Interconnection Primary Frequency Response

## Evaluation
scan rate | 2 | seconds |  |  | Date: | 2009-10-12 02:27 |  |  | Balancing Authority | My BA | [10 empty] | A Point | 40098.1023 |  |  |  |  | A Point | 40098.1023 | [13 empty] | Non-Conforming Load sign convention | + | (If Data is positive for Load then enter "+" else "-") | [11 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27
[5 empty] | Time of T(0) | 40098.1024 |  |  | Grid Nominal Frequency | 60 | Hz | [9 empty] | FPointA | 60.041 | 40098.1023 |  |  |  | FPointA | 60.041 | 40098.1023 | [26 empty] | Time of T(0) | 40098.1024 | [12 empty] | Time of T(0) | 40098.1024 | [12 empty] | Time of T(0) | 40098.1024 | [12 empty] | Time of T(0) | 40098.1024 | [12 empty] | Time of T(0) | 40098.1024
[5 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1063 |  |  | Capacity @ Droop for Minimum Performance | 2400 | MW | [9 empty] | A Value | 60.042 |  |  |  |  | A Value | 60.042 | [27 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1063 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1063 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1063 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1063 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1063
[5 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.042 | Hz |  | Droop Setting | 5% | 3 | Hz | [8 empty] | C Value | 59.836 | 40098.1025 |  |  |  | C Value | 59.836 | #N/A | [26 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.042 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.042 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.042 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.042 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.042 | Hz
[5 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+52)] | 59.8888 | Hz |  | Deadband Setting | 0 | Hz | [9 empty] | Delta FCA | -0.206 |  |  |  |  | Delta FC | [28 empty] | Value B Post-Perturbation Average Frequency [T(+12 to T(+24)] | 59.8823 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+18 to T(+30)] | 59.8831 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+40)] | 59.8883 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+18 to T(+52)] | 59.888 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+52)] | 59.8888 | Hz
[5 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15324 | Hz |  | Hz Span | 3 | Hz | [9 empty] | FR C | -307.2796 | MW/0.1 Hz | [32 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15971 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15886 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15373 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.154 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15324 | Hz
[5 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3645.3027 | MW |  | Frequency Response Obligation (FRO) | -80 | MW/0.1 Hz | [9 empty] | Slope A-C dF/dT | -0.0205 | Hz/second |  |  |  |  | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | [18 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3645.3027 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3645.3027 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3645.3027 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3645.3027 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3645.3027 | MW
[5 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+52)] | 3788.8466 | MW | [13 empty] | C Value Maximum Resource Loss | 633 | [5 empty] | 12 to 24 sec | 12 to 24 sec | 18 to 30 sec | 18 to 30 sec | 20 to 40 sec | 20 to 40 sec | 18 to 52 sec | 18 to 52 sec | 20 to 52 sec | 20 to 52 sec | [18 empty] | Value B Post-Perturbation Average Interchange MW [T(+12 to T(+24)] | 3770.953 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+18 to T(+30)] | 3779.6252 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+40)] | 3784.1336 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+18 to T(+52)] | 3787.7954 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+52)] | 3788.8466 | MW
[5 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 143.5439 | MW | [13 empty] | Secondary C Value | No | n/a | Time |  |  | B Frequency Value | 59.8823 |  | 59.8831 |  | 59.8888 |  | 59.888 |  | 59.8888 | [19 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 125.6503 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 134.3225 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 138.8309 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 142.4927 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 143.5439 | MW
[5 empty] | Initial Performance Ramp Magnitude Adjustment | -17.2648 | MW | [19 empty] | Delta FB | -0.15971 | -396.9069 | -0.15886 | -398.8954 | -0.15324 | -412.2881 | -0.154 | -411.6043 | -0.15324 | -413.5197 | [18 empty] | Net Total Adjustments | -52.2747 | MW | [11 empty] | Net Total Adjustments | -53.4877 | MW | [11 empty] | Net Total Adjustments | -53.2663 | MW | [11 empty] | Net Total Adjustments | -52.2936 | MW | [11 empty] | Net Total Adjustments | -52.4266 | MW
[5 empty] | EPFR Pre-Perturbation Average | -33.5999 | MW | [19 empty] | Slope B dF/dT | -0.0079857 |  | -0.0079429 |  | -0.0076618 |  | -0.0077 |  | -0.0076618 | [19 empty] | EPFR for FRO Pre-Perturbation Average | -33.5999 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -33.5999 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -33.5999 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -33.5999 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -33.5999 | MW
[5 empty] | EPFR Post-Perturbation Average | 88.9882 | MW | [19 empty] | RatioB-C | 77.5305 |  | 77.1146 |  | 74.3855 |  | 74.7567 |  | 74.3855 | [19 empty] | EPFR for FRO Post-Perturbation Average | 94.1711 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 93.4858 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 89.3815 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 89.5999 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 88.9882 | MW
[5 empty] | EPFR Delta | 122.588 | MW |  | TC (frequency response filter constant) | 0.35 | Time Constant for delayed delivery of PFR during Sustained Measure | [15 empty] | Sustainability Index | -0.015285 |  | -0.016142 |  | -0.021764 |  | -0.020999 |  | -0.021764 | [19 empty] | EPFR for FRO Delta | 127.771 | MW | [11 empty] | EPFR for FRO Delta | 127.0857 | MW | [11 empty] | EPFR for FRO Delta | 122.9814 | MW | [11 empty] | EPFR for FRO Delta | 123.1998 | MW | [11 empty] | EPFR for FRO Delta | 122.588 | MW
[21 empty] | Tzero | 40098.1023 | [33 empty] | EPFR for FRO Adjusted | 75.4962 | MW | [11 empty] | EPFR for FRO Adjusted | 73.598 | MW | [11 empty] | EPFR for FRO Adjusted | 69.7151 | MW | [11 empty] | EPFR for FRO Adjusted | 70.9062 | MW | [11 empty] | EPFR for FRO Adjusted | 70.1615 | MW
[21 empty] | FT+4 | 59.978 | [33 empty] | Pre JOU Dynamic Schedules MW | 350 |  |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 350 |  |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 350 | MW |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 350 | MW |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 350 | MW |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz
[9 empty] | Low Hz | Delta Hz Event | [10 empty] | FT+10 | 59.892 | [33 empty] | Pre Non-Conforming Load MW | -165.4764 |  |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | -165.4764 |  |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | -165.4764 | MW |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | -165.4764 | MW |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | -165.4764 | MW |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz
[9 empty] | 3765.2244 | Actual Interchange MW Average during frequency recovery period | [10 empty] | FT+20 | 59.875 | [33 empty] | Pre Pumped Hydro MW | 0 |  |  |  | EPFR for Bias Setting Pre-Perturbation Average | -43.2598 | MW | [6 empty] | Pre Pumped Hydro MW | 0 |  |  |  | EPFR for Bias Setting Pre-Perturbation Average | -43.2598 | MW | [6 empty] | Pre Pumped Hydro MW | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | -43.2598 | MW | [6 empty] | Pre Pumped Hydro MW | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | -43.2598 | MW | [6 empty] | Pre Pumped Hydro MW | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | -43.2598 | MW
[9 empty] | 3779.7829 | Target Interchange MW Average during frequency recovery period | [10 empty] | FT+60 | 59.888 | [33 empty] | Pre Ramping Units MW | 114.25 |  |  |  | EPFR for Bias Setting Post-Perturbation Average | 121.2453 | MW | [6 empty] | Pre Ramping Units MW | 114.25 |  |  |  | EPFR for Bias Setting Post-Perturbation Average | 120.363 | MW | [6 empty] | Pre Ramping Units MW | 114.25 | MW |  |  | EPFR for Bias Setting Post-Perturbation Average | 115.0787 | MW | [6 empty] | Pre Ramping Units MW | 114.25 | MW |  |  | EPFR for Bias Setting Post-Perturbation Average | 115.3599 | MW | [6 empty] | Pre Ramping Units MW | 114.25 | MW |  |  | EPFR for Bias Setting Post-Perturbation Average | 114.5723 | MW
|  |  | EPFR = Expected Primary Frequency Response |  | EPFR(Final) | 105.3232 | MW |  | 3727.4829 | Interchange Average Ramp MW during frequency recovery period | [8 empty] | Interconnection Evaluation | [36 empty] | Pre Transferred Frequency Response MW | -4.2 |  |  |  | EPFR for Bias Setting Delta | 164.5052 | MW | [6 empty] | Pre Transferred Frequency Response MW | -4.2 |  |  |  | EPFR for Bias Setting Delta | 163.6228 | MW | [6 empty] | Pre Transferred Frequency Response MW | -4.2 | MW |  |  | EPFR for Bias Setting Delta | 158.3386 | MW | [6 empty] | Pre Transferred Frequency Response MW | -4.2 | MW |  |  | EPFR for Bias Setting Delta | 158.6197 | MW | [6 empty] | Pre Transferred Frequency Response MW | -4.2 | MW |  |  | EPFR for Bias Setting Delta | 157.8321 | MW
[5 empty] | MW Response in right direction for frequency delta | Yes |  |  | 3641.1912 | Actual MW @ T(-4) | [45 empty] | Pre Contingent BA Lost Generation MW | 15 |  |  |  | Primary Frequency Response Delivery of Bias | 76.38% | [7 empty] | Pre Contingent BA Lost Generation MW | 15 |  |  |  | Primary Frequency Response Delivery of Bias | 82.09% | [7 empty] | Pre Contingent BA Lost Generation MW | 15 | MW |  |  | Primary Frequency Response Delivery of Bias | 87.68% | [7 empty] | Pre Contingent BA Lost Generation MW | 15 | MW |  |  | Primary Frequency Response Delivery of Bias | 89.83% | [7 empty] | Pre Contingent BA Lost Generation MW | 15 | MW |  |  | Primary Frequency Response Delivery of Bias | 90.95%
[9 empty] | 107.358 | Starting and Ending Difference in Interchange MW during frequency recovery period (indicates ramp direction during recovery period) | [45 empty] | Sum of Pre Perturbation Adjustments | 309.5736 | [12 empty] | Sum of Pre Perturbation Adjustments | 309.5736 | [12 empty] | Sum of Pre Perturbation Adjustments | 309.5736 | MW | [11 empty] | Sum of Pre Perturbation Adjustments | 309.5736 | MW | [11 empty] | Sum of Pre Perturbation Adjustments | 309.5736 | MW
[9 empty] | 0:06 | Event Duration (h:mm:ss)
[9 empty] | No | Target MW Average minus MW @ T(-4) less than zero | [10 empty] | B Value Average Resource Loss | 633 | [33 empty] | Post JOU Dynamic Schedules MW | 335 |  |  |  | Pre-Perturbation BA Load | 7575.405 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 335 |  |  |  | Pre-Perturbation BA Load | 7575.405 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 335 | MW |  |  | Pre-Perturbation BA Load | 7575.405 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 335 | MW |  |  | Pre-Perturbation BA Load | 7575.405 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 335 | MW |  |  | Pre-Perturbation BA Load | 7575.405 | MW
[9 empty] | 138.5917 | Interchange Target Relative Average Change - MW (Low Frequency Event) | [10 empty] | B Value Average LaaR Loss | 0 | [33 empty] | Post Non-Conforming Load MW | -207.8297 |  |  |  | Post-Perturbation BA Load | 7577.4557 | MW | [6 empty] | Post Non-Conforming Load MW | -209.8855 |  |  |  | Post-Perturbation BA Load | 7577.9743 | MW | [6 empty] | Post Non-Conforming Load MW | -210.82 | MW |  |  | Post-Perturbation BA Load | 7578.45 | MW | [6 empty] | Post Non-Conforming Load MW | -211.7533 | MW |  |  | Post-Perturbation BA Load | 7578.87 | MW | [6 empty] | Post Non-Conforming Load MW | -212.0647 | MW |  |  | Post-Perturbation BA Load | 7578.9476 | MW
[9 empty] | 124.0333 | Interchange Actual Relative Average Change - MW (Low Frequency Event) | [10 empty] | B Value Average Net Loss | 633 | [33 empty] | Post Pumped Hydro MW | 1 |  |  |  | Pre to Post Perturbation BA Load Change | 2.0507 | MW | [6 empty] | Post Pumped Hydro MW | 1.1429 |  |  |  | Pre to Post Perturbation BA Load Change | 2.5693 | MW | [6 empty] | Post Pumped Hydro MW | 2.0909 | MW |  |  | Pre to Post Perturbation BA Load Change | 3.045 | MW | [6 empty] | Post Pumped Hydro MW | 3.3333 | MW |  |  | Pre to Post Perturbation BA Load Change | 3.465 | MW | [6 empty] | Post Pumped Hydro MW | 3.4706 | MW |  |  | Pre to Post Perturbation BA Load Change | 3.5426 | MW
[9 empty] | No | Interchange Actual Average minus MW @ T(-4) less than zero | [45 empty] | Post Ramping Units MW | 117.3571 |  |  |  | Load Dampening Frequency Response | 1.284 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 118.1429 |  |  |  | Load Dampening Frequency Response | 1.6174 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 118.8636 | MW |  |  | Load Dampening Frequency Response | 1.9808 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 119.5 | MW |  |  | Load Dampening Frequency Response | 2.25 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 119.6176 | MW |  |  | Load Dampening Frequency Response | 2.3119 | MW/0.1 Hz
[9 empty] | Yes | Interchange Average MW minus MW @ T(-4) greater than zero | [13 empty] | Interconnection Bias Total | [31 empty] | Post Transferred Frequency Response MW | 11.7714 |  |  |  | Load Dampening % of Total BA Frequency Response | -1.632% | [7 empty] | Post Transferred Frequency Response MW | 11.6857 |  |  |  | Load Dampening % of Total BA Frequency Response | -1.913% | [7 empty] | Post Transferred Frequency Response MW | 11.1727 | MW |  |  | Load Dampening % of Total BA Frequency Response | -2.193% | [7 empty] | Post Transferred Frequency Response MW | 11.2 | MW |  |  | Load Dampening % of Total BA Frequency Response | -2.432% | [7 empty] | Post Transferred Frequency Response MW | 11.1235 | MW |  |  | Load Dampening % of Total BA Frequency Response | -2.468%
[9 empty] | Yes | Interchange Target MW Average minus MW @ T(-4) greater than zero | [13 empty] | EI | ERCOT | WECC | [29 empty] | Post Contingent BA Lost Generation MW | 0 | [12 empty] | Post Contingent BA Lost Generation MW | 0 | [12 empty] | Post Contingent BA Lost Generation MW | 0 | MW | [11 empty] | Post Contingent BA Lost Generation MW | 0 | MW | [11 empty] | Post Contingent BA Lost Generation MW | 0 | MW
[9 empty] | 31.2337 | Interchange Target Relative Average Change - MW (High Frequency Event) | [10 empty] | Interconnection Bias Setting | -660 |  | -6349 | -660 | -2024 | [29 empty] | Sum of Post Perturbation Adjustments | 257.2989 | [12 empty] | Sum of Post Perturbation Adjustments | 256.086 | [12 empty] | Sum of Post Perturbation Adjustments | 256.3073 | MW | [11 empty] | Sum of Post Perturbation Adjustments | 257.2801 | MW | [11 empty] | Sum of Post Perturbation Adjustments | 257.1471 | MW
[9 empty] | 16.6753 | Interchange Actual Relative Average Change - MW (High Frequency Event) | [10 empty] | IPFR as a % of Bias Setting | 0% | [33 empty] | Net Total Adjustments MW | -52.2747 | [12 empty] | Net Total Adjustments MW | -53.4877 | [12 empty] | Net Total Adjustments MW | -53.2663 | MW | [11 empty] | Net Total Adjustments MW | -52.2936 | MW | [11 empty] | Net Total Adjustments MW | -52.4266 | MW
[9 empty] | Up | Ramp Direction during frequency recovery period | [10 empty] | Interconnection Total Energy | 37446 | 60.07%
[21 empty] | Interconnection Peak Energy | 62339 |  |  |  |  | Frequency and Interconnection Frequency Response @ different Average periods of B | [11 empty] | Frequency, Actual Interchange, Adjustment Data, Bias and Load used in the evaluation | [12 empty] | 12 to 24 second Average Period Evaluation | [13 empty] | 18 to 30 second Average Period Evaluation | [13 empty] | 20 to 40 second Average Period Evaluation | [13 empty] | 18 to 52 second Average Period Evaluation | [13 empty] | 20 to 52 second Average Period Evaluation
[5 empty] | Initial Response P.U. Performance | 1.3629 | P.U. |  | 0.89495 | P.U. Sustianed Response P.U. Performance | [45 empty] | Initial P.U. Performance for FRO | 0.9834 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.0569 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.1289 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.1566 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.1709 | P.U.
[56 empty] | Initial P.U. Performance Adjusted for FRO | 1.3925 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 1.4778 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 1.562 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 1.5811 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 1.5986 | P.U.
[9 empty] | Initial | [6 empty] | Generator | Generator | Generator | Generator | Generator | Generator | Generator | LaaR | Total | Interconnection | FR B | [15 empty] | JOU | Non- |  |  | Transferred | Contingent | [7 empty] | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected
[7 empty] | FRO |  | Measure |  |  | Average | Average |  | Average | Trip | Trip | Trip | Trip | Trip | Trip | Trip | Trip | Generation | Primary | 20 to 52 sec |  | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Expected |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net
[7 empty] | (EPFR) | (TC) | Final |  |  | Output | Target |  | Ramp | MW | MW | MW | MW | MW | MW | MW | MW | Trip | Frequency | Average |  | 12 to 24 sec | 12 to 24 sec | 18 to 30 sec | 18 to 30 sec | 20 to 40 sec | 20 to 40 sec | 18 to 52 sec | 18 to 52 sec | 20 to 52 sec | 20 to 52 sec |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Primary |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual
|  |  |  | Value B |  |  | Expected | Delayed | Expected |  | Recovery | During | During | Recovery | During | [8 empty] | MW | Response | MW |  | Average | Average | Average | Average | Average | Average | Average | Average | Average | Average |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | Freq Response |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange
|  |  |  | 20 to 52 sec |  |  | Primary | Delivery | Primary | Average | Period | Recovery | Recovery | Period | Recovery | [12 empty] | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW
|  | Frequency | Interchange | Average | Average |  | Frequency | Frequency | Frequency | Ramp | Target | Period | Period | Ramp | Period
| T | Hz | MW | Frequency | MW |  | Response | Response | Response | MW/scan | MW | MW | MW | MW | MW | 633 | [8 empty] | MW/0.1 Hz
0
T-72 sec | 40098.1015 | 60.027 | 3668.6106 |  |  |  | -21.6003 | -7.5601 | [15 empty] | 0 |  |  | T-72 sec | [10 empty] | T-72 sec | 40098.1015 | 60.027 | 3668.6106 | 350 | -257.4212 | 0 | 106.5 | 10 | 15 | -103 | 7570.29 | -21.6003 | T-72 sec | 40098.1015 | [12 empty] | T-72 sec | 40098.1015 | [12 empty] | T-72 sec | 40098.1015 | [12 empty] | T-72 sec | 40098.1015 | [12 empty] | T-72 sec | 40098.1015
T-70 sec | 40098.1016 | 60.027 | 3668.6106 |  |  |  | -21.6003 | -12.4742 | [15 empty] | 0 |  |  | T-70 sec | [10 empty] | T-70 sec | 40098.1016 | 60.027 | 3668.6106 | 350 | -257.4212 | 0 | 106.5 | 10 | 15 | -103 | 7570.29 | -21.6003 | T-70 sec | 40098.1016 | [12 empty] | T-70 sec | 40098.1016 | [12 empty] | T-70 sec | 40098.1016 | [12 empty] | T-70 sec | 40098.1016 | [12 empty] | T-70 sec | 40098.1016
T-68 sec | 40098.1016 | 60.026 | 3664.4951 |  |  |  | -20.8008 | -15.3885 | [15 empty] | 0 |  |  | T-68 sec | [10 empty] | T-68 sec | 40098.1016 | 60.026 | 3664.4951 | 350 | -257.4212 | 0 | 107 | 10 | 15 | -103 | 7570.62 | -20.8008 | T-68 sec | 40098.1016 | [12 empty] | T-68 sec | 40098.1016 | [12 empty] | T-68 sec | 40098.1016 | [12 empty] | T-68 sec | 40098.1016 | [12 empty] | T-68 sec | 40098.1016
T-66 sec | 40098.1016 | 60.026 | 3664.4951 |  |  |  | -20.8008 | -17.2828 | [15 empty] | 0 |  |  | T-66 sec | [10 empty] | T-66 sec | 40098.1016 | 60.026 | 3664.4951 | 350 | -257.4212 | 0 | 107 | 10 | 15 | -103 | 7570.62 | -20.8008 | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016
T-64 sec | 40098.1016 | 60.019 | 3666.8208 |  |  |  | -15.2008 | -16.5541 | [15 empty] | 0 |  |  | T-64 sec | [10 empty] | T-64 sec | 40098.1016 | 60.019 | 3666.8208 | 350 | -257.4212 | 0 | 107.5 | 10 | 15 | -103 | 7570.95 | -15.2008 | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016
T-62 sec | 40098.1016 | 60.019 | 3666.8208 |  |  |  | -15.2008 | -16.0804 | [15 empty] | 0 |  |  | T-62 sec | [10 empty] | T-62 sec | 40098.1016 | 60.019 | 3666.8208 | 350 | -257.4212 | 0 | 107.5 | 10 | 15 | -103 | 7570.95 | -15.2008 | T-62 sec | 40098.1016 | [12 empty] | T-62 sec | 40098.1016 | [12 empty] | T-62 sec | 40098.1016 | [12 empty] | T-62 sec | 40098.1016 | [12 empty] | T-62 sec | 40098.1016
T-60 sec | 40098.1017 | 60.019 | 3670.4536 |  |  |  | -15.2008 | -15.7726 |  | -0.4099 | 3670.4536 | [12 empty] | 0 |  |  | T-60 sec | [10 empty] | T-60 sec | 40098.1017 | 60.019 | 3670.4536 | 350 | -257.4212 | 0 | 108 | 10 | 15 | -103 | 7571.28 | -15.2008 | T-60 sec | 40098.1017 | [12 empty] | T-60 sec | 40098.1017 | [12 empty] | T-60 sec | 40098.1017 | [12 empty] | T-60 sec | 40098.1017 | [12 empty] | T-60 sec | 40098.1017
T-58 sec | 40098.1017 | 60.019 | 3670.4536 |  |  |  | -15.2008 | -15.5725 |  | -0.4099 | 3670.2438 | [12 empty] | 0 |  |  | T-58 sec | [10 empty] | T-58 sec | 40098.1017 | 60.019 | 3670.4536 | 350 | -257.4212 | 0 | 108 | 10 | 15 | -103 | 7571.28 | -15.2008 | T-58 sec | 40098.1017 | [12 empty] | T-58 sec | 40098.1017 | [12 empty] | T-58 sec | 40098.1017 | [12 empty] | T-58 sec | 40098.1017 | [12 empty] | T-58 sec | 40098.1017
T-56 sec | 40098.1017 | 60.019 | 3671.668 |  |  |  | -15.2008 | -15.4424 |  | -0.4099 | 3669.964 | [12 empty] | 0 |  |  | T-56 sec | [10 empty] | T-56 sec | 40098.1017 | 60.019 | 3671.668 | 350 | -257.4212 | 0 | 108.5 | 10 | 15 | -103 | 7571.61 | -15.2008 | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017
T-54 sec | 40098.1017 | 60.019 | 3671.668 |  |  |  | -15.2008 | -15.3578 |  | -0.4099 | 3669.6387 | [12 empty] | 0 |  |  | T-54 sec | [10 empty] | T-54 sec | 40098.1017 | 60.019 | 3671.668 | 350 | -257.4212 | 0 | 108.5 | 10 | 15 | -103 | 7571.61 | -15.2008 | T-54 sec | 40098.1017 | [12 empty] | T-54 sec | 40098.1017 | [12 empty] | T-54 sec | 40098.1017 | [12 empty] | T-54 sec | 40098.1017 | [12 empty] | T-54 sec | 40098.1017
T-52 sec | 40098.1018 | 60.021 | 3672.6851 |  |  |  | -16.7999 | -15.8626 |  | -0.4099 | 3668.724 | [12 empty] | 0 |  |  | T-52 sec | [10 empty] | T-52 sec | 40098.1018 | 60.021 | 3672.6851 | 350 | -261.7382 | 0 | 109 | 10 | 15 | -103 | 7571.94 | -16.7999 | T-52 sec | 40098.1018 | [12 empty] | T-52 sec | 40098.1018 | [12 empty] | T-52 sec | 40098.1018 | [12 empty] | T-52 sec | 40098.1018 | [12 empty] | T-52 sec | 40098.1018
T-50 sec | 40098.1018 | 60.021 | 3672.6851 |  |  |  | -16.7999 | -16.1906 |  | -0.4099 | 3667.986 | [12 empty] | 0 |  |  | T-50 sec | [10 empty] | T-50 sec | 40098.1018 | 60.021 | 3672.6851 | 350 | -261.7382 | 0 | 109 | 10 | 15 | -103 | 7571.94 | -16.7999 | T-50 sec | 40098.1018 | [12 empty] | T-50 sec | 40098.1018 | [12 empty] | T-50 sec | 40098.1018 | [12 empty] | T-50 sec | 40098.1018 | [12 empty] | T-50 sec | 40098.1018
T-48 sec | 40098.1018 | 60.019 | 3672.1641 |  |  |  | -15.2008 | -15.8442 |  | -0.4099 | 3667.9226 | [12 empty] | 0 |  |  | T-48 sec | [10 empty] | T-48 sec | 40098.1018 | 60.019 | 3672.1641 | 350 | -261.7382 | 0 | 109.5 | 10 | 15 | -103 | 7572.27 | -15.2008 | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018
T-46 sec | 40098.1018 | 60.019 | 3672.1641 |  |  |  | -15.2008 | -15.619 |  | -0.4099 | 3667.7379 | [12 empty] | 0 |  |  | T-46 sec | [10 empty] | T-46 sec | 40098.1018 | 60.019 | 3672.1641 | 350 | -261.7382 | 0 | 109.5 | 10 | 15 | -103 | 7572.27 | -15.2008 | T-46 sec | 40098.1018 | [12 empty] | T-46 sec | 40098.1018 | [12 empty] | T-46 sec | 40098.1018 | [12 empty] | T-46 sec | 40098.1018 | [12 empty] | T-46 sec | 40098.1018
T-44 sec | 40098.1019 | 60.022 | 3669.9829 |  |  |  | -17.5995 | -16.3122 |  | -0.4099 | 3666.6348 | [12 empty] | 0 |  |  | T-44 sec | [10 empty] | T-44 sec | 40098.1019 | 60.022 | 3669.9829 | 350 | -165.1017 | 0 | 110 | 10 | 15 | -103 | 7572.6 | -17.5995 | T-44 sec | 40098.1019 | [12 empty] | T-44 sec | 40098.1019 | [12 empty] | T-44 sec | 40098.1019 | [12 empty] | T-44 sec | 40098.1019 | [12 empty] | T-44 sec | 40098.1019
T-42 sec | 40098.1019 | 60.022 | 3669.9829 |  |  |  | -17.5995 | -16.7627 |  | -0.4099 | 3665.7743 | [12 empty] | 0 |  |  | T-42 sec | [10 empty] | T-42 sec | 40098.1019 | 60.022 | 3669.9829 | 350 | -165.1017 | 0 | 110 | 10 | 15 | -103 | 7572.6 | -17.5995 | T-42 sec | 40098.1019 | [12 empty] | T-42 sec | 40098.1019 | [12 empty] | T-42 sec | 40098.1019 | [12 empty] | T-42 sec | 40098.1019 | [12 empty] | T-42 sec | 40098.1019
T-40 sec | 40098.1019 | 60.037 | 3663.7581 |  |  |  | -29.599 | -21.2554 |  | -0.4099 | 3660.8717 | [12 empty] | 0 |  |  | T-40 sec | [10 empty] | T-40 sec | 40098.1019 | 60.037 | 3663.7581 | 350 | -165.4764 | 0 | 110.5 | 10 | 15 | -103 | 7572.93 | -29.599 | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019
T-38 sec | 40098.1019 | 60.037 | 3663.7581 |  |  |  | -29.599 | -24.1757 |  | -0.4099 | 3657.5416 | [12 empty] | 0 |  |  | T-38 sec | [10 empty] | T-38 sec | 40098.1019 | 60.037 | 3663.7581 | 350 | -165.4764 | 0 | 110.5 | 10 | 15 | -103 | 7572.93 | -29.599 | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019
T-36 sec | 40098.1019 | 60.036 | 3660.6724 |  |  |  | -28.7994 | -25.794 |  | -0.4099 | 3655.5134 | [12 empty] | 0 |  |  | T-36 sec | [10 empty] | T-36 sec | 40098.1019 | 60.036 | 3660.6724 | 350 | -165.4764 | 0 | 111 | 10 | 15 | -103 | 7573.26 | -28.7994 | T-36 sec | 40098.1019 | [12 empty] | T-36 sec | 40098.1019 | [12 empty] | T-36 sec | 40098.1019 | [12 empty] | T-36 sec | 40098.1019 | [12 empty] | T-36 sec | 40098.1019
T-34 sec | 40098.102 | 60.036 | 3660.6724 |  |  |  | -28.7994 | -26.8459 |  | -0.4099 | 3654.0516 | [12 empty] | 0 |  |  | T-34 sec | [10 empty] | T-34 sec | 40098.102 | 60.036 | 3660.6724 | 350 | -165.4764 | 0 | 111 | 10 | 15 | -103 | 7573.26 | -28.7994 | T-34 sec | 40098.102 | [12 empty] | T-34 sec | 40098.102 | [12 empty] | T-34 sec | 40098.102 | [12 empty] | T-34 sec | 40098.102 | [12 empty] | T-34 sec | 40098.102
T-32 sec | 40098.102 | 60.046 | 3649.1904 |  |  |  | -36.8011 | -30.3302 |  | -0.4099 | 3650.1573 | [12 empty] | 0 |  |  | T-32 sec | [10 empty] | T-32 sec | 40098.102 | 60.046 | 3649.1904 | 350 | -165.4764 | 0 | 111.5 | 10 | 15 | -103 | 7573.59 | -36.8011 | T-32 sec | 40098.102 | [12 empty] | T-32 sec | 40098.102 | [12 empty] | T-32 sec | 40098.102 | [12 empty] | T-32 sec | 40098.102 | [12 empty] | T-32 sec | 40098.102
T-30 sec | 40098.102 | 60.046 | 3649.1904 |  |  |  | -36.8011 | -32.5951 |  | -0.4099 | 3647.4826 | [12 empty] | 0 |  |  | T-30 sec | [10 empty] | T-30 sec | 40098.102 | 60.046 | 3649.1904 | 350 | -165.4764 | 0 | 111.5 | 10 | 15 | -103 | 7573.59 | -36.8011 | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102
T-28 sec | 40098.102 | 60.048 | 3648.2463 |  |  |  | -38.4003 | -34.6269 |  | -0.4099 | 3645.0409 | [12 empty] | 0 |  |  | T-28 sec | [10 empty] | T-28 sec | 40098.102 | 60.048 | 3648.2463 | 350 | -165.4764 | 0 | 112 | 10 | 15 | -103 | 7573.92 | -38.4003 | T-28 sec | 40098.102 | [12 empty] | T-28 sec | 40098.102 | [12 empty] | T-28 sec | 40098.102 | [12 empty] | T-28 sec | 40098.102 | [12 empty] | T-28 sec | 40098.102
T-26 sec | 40098.1021 | 60.048 | 3648.2463 |  |  |  | -38.4003 | -35.9476 |  | -0.4099 | 3643.3103 | [12 empty] | 0 |  |  | T-26 sec | [10 empty] | T-26 sec | 40098.1021 | 60.048 | 3648.2463 | 350 | -165.4764 | 0 | 112 | 10 | 15 | -103 | 7573.92 | -38.4003 | T-26 sec | 40098.1021 | [12 empty] | T-26 sec | 40098.1021 | [12 empty] | T-26 sec | 40098.1021 | [12 empty] | T-26 sec | 40098.1021 | [12 empty] | T-26 sec | 40098.1021
T-24 sec | 40098.1021 | 60.041 | 3654.2944 |  |  |  | -32.8003 | -34.846 |  | -0.4099 | 3644.0019 | [12 empty] | 0 |  |  | T-24 sec | [10 empty] | T-24 sec | 40098.1021 | 60.041 | 3654.2944 | 350 | -165.1017 | 0 | 112.5 | 10 | 15 | -103 | 7574.25 | -32.8003 | T-24 sec | 40098.1021 | [12 empty] | T-24 sec | 40098.1021 | [12 empty] | T-24 sec | 40098.1021 | [12 empty] | T-24 sec | 40098.1021 | [12 empty] | T-24 sec | 40098.1021
T-22 sec | 40098.1021 | 60.041 | 3654.2944 |  |  |  | -32.8003 | -34.13 |  | -0.4099 | 3644.3081 | [12 empty] | 0 |  |  | T-22 sec | [10 empty] | T-22 sec | 40098.1021 | 60.041 | 3654.2944 | 350 | -165.1017 | 0 | 112.5 | 10 | 15 | -103 | 7574.25 | -32.8003 | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021
T-20 sec | 40098.1021 | 60.041 | 3651.8743 |  |  |  | -32.8003 | -33.6646 |  | -0.4099 | 3644.3636 | [12 empty] | 0 |  |  | T-20 sec | [10 empty] | T-20 sec | 40098.1021 | 60.041 | 3651.8743 | 350 | -165.4764 | 0 | 113 | 10 | 15 | -103 | 7574.58 | -32.8003 | T-20 sec | 40098.1021 | [12 empty] | T-20 sec | 40098.1021 | [12 empty] | T-20 sec | 40098.1021 | [12 empty] | T-20 sec | 40098.1021 | [12 empty] | T-20 sec | 40098.1021
T-18 sec | 40098.1022 | 60.041 | 3651.8743 |  |  |  | -32.8003 | -33.3621 |  | -0.4099 | 3644.2562 | [12 empty] | 0 |  |  | T-18 sec | [10 empty] | T-18 sec | 40098.1022 | 60.041 | 3651.8743 | 350 | -165.4764 | 0 | 113 | 10 | 15 | -103 | 7574.58 | -32.8003 | T-18 sec | 40098.1022 | [12 empty] | T-18 sec | 40098.1022 | [12 empty] | T-18 sec | 40098.1022 | [12 empty] | T-18 sec | 40098.1022 | [12 empty] | T-18 sec | 40098.1022
T-16 sec | 40098.1022 | 60.041 | 3649.187 | 60.042 | 3645.3027 |  | -32.8003 | -33.1655 |  | -0.4099 | 3644.0429 | [12 empty] | 0 |  |  | T-16 sec | 60.042 | [9 empty] | T-16 sec | 40098.1022 | 60.041 | 3649.187 | 350 | -165.4764 | 0 | 113.5 | 10 | 15 | -103 | 7574.91 | -32.8003 | T-16 sec | 40098.1022 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-16 sec | 40098.1022 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-16 sec | 40098.1022 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-16 sec | 40098.1022 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-16 sec | 40098.1022 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999
T-14 sec | 40098.1022 | 60.041 | 3649.187 | 60.042 | 3645.3027 |  | -32.8003 | -33.0377 |  | -0.4099 | 3643.7608 | [12 empty] | 0 |  |  | T-14 sec | 60.042 | [9 empty] | T-14 sec | 40098.1022 | 60.041 | 3649.187 | 350 | -165.4764 | 0 | 113.5 | 10 | 15 | -103 | 7574.91 | -32.8003 | T-14 sec | 40098.1022 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-14 sec | 40098.1022 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-14 sec | 40098.1022 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-14 sec | 40098.1022 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-14 sec | 40098.1022 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999
T-12 sec | 40098.1022 | 60.045 | 3645.387 | 60.042 | 3645.3027 |  | -35.9985 | -34.074 |  | -0.4099 | 3642.3146 | [12 empty] | 0 |  |  | T-12 sec | 60.042 | [9 empty] | T-12 sec | 40098.1022 | 60.045 | 3645.387 | 350 | -165.4764 | 0 | 114 | 10 | 15 | -103 | 7575.24 | -35.9985 | T-12 sec | 40098.1022 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-12 sec | 40098.1022 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-12 sec | 40098.1022 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-12 sec | 40098.1022 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-12 sec | 40098.1022 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999
T-10 sec | 40098.1022 | 60.045 | 3645.387 | 60.042 | 3645.3027 |  | -35.9985 | -34.7476 |  | -0.4099 | 3641.2311 | [12 empty] | 0 |  |  | T-10 sec | 60.042 | [9 empty] | T-10 sec | 40098.1022 | 60.045 | 3645.387 | 350 | -165.4764 | 0 | 114 | 10 | 15 | -103 | 7575.24 | -35.9985 | T-10 sec | 40098.1022 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-10 sec | 40098.1022 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-10 sec | 40098.1022 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-10 sec | 40098.1022 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-10 sec | 40098.1022 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999
T-08 sec | 40098.1023 | 60.041 | 3645.4458 | 60.042 | 3645.3027 |  | -32.8003 | -34.066 |  | -0.4099 | 3641.5027 | [12 empty] | 0 |  |  | T-08 sec | 60.042 | [9 empty] | T-08 sec | 40098.1023 | 60.041 | 3645.4458 | 350 | -165.4764 | 0 | 114.5 | 10 | 15 | -103 | 7575.57 | -32.8003 | T-08 sec | 40098.1023 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-08 sec | 40098.1023 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-08 sec | 40098.1023 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-08 sec | 40098.1023 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-08 sec | 40098.1023 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999
T-06 sec | 40098.1023 | 60.041 | 3645.4458 | 60.042 | 3645.3027 |  | -32.8003 | -33.623 |  | -0.4099 | 3641.5358 | [12 empty] | 0 |  |  | T-06 sec | 60.042 | [9 empty] | T-06 sec | 40098.1023 | 60.041 | 3645.4458 | 350 | -165.4764 | 0 | 114.5 | 10 | 15 | -103 | 7575.57 | -32.8003 | T-06 sec | 40098.1023 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-06 sec | 40098.1023 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-06 sec | 40098.1023 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-06 sec | 40098.1023 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-06 sec | 40098.1023 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999
T-04 sec | 40098.1023 | 60.041 | 3641.1912 | 60.042 | 3645.3027 |  | -32.8003 | -33.3351 |  | -0.4099 | 3641.4139 | [12 empty] | 0 |  |  | T-04 sec | 60.042 | [9 empty] | T-04 sec | 40098.1023 | 60.041 | 3641.1912 | 350 | -165.4764 | 0 | 115 | 10 | 15 | -103 | 7575.9 | -32.8003 | T-04 sec | 40098.1023 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-04 sec | 40098.1023 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-04 sec | 40098.1023 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-04 sec | 40098.1023 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-04 sec | 40098.1023 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999
T-02 sec | 40098.1023 | 60.041 | 3641.1912 | 60.042 | 3645.3027 |  | -32.8003 | -33.1479 |  | -0.4099 | 3641.1912 | [12 empty] | 0 |  |  | T-02 sec | 60.042 | [9 empty] | T-02 sec | 40098.1023 | 60.041 | 3641.1912 | 350 | -165.4764 | 0 | 115 | 10 | 15 | -103 | 7575.9 | -32.8003 | T-02 sec | 40098.1023 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-02 sec | 40098.1023 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-02 sec | 40098.1023 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-02 sec | 40098.1023 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999 |  | T-02 sec | 40098.1023 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | 10 | 15 | -103 | 7575.405 | -33.5999
T+0 sec | 40098.1024 | 59.978 | 3696.3623 |  |  |  | 17.5995 | -15.3863 |  | 0 | 3658.9527 |  |  |  |  | 633 | [7 empty] | 633 | -989.0752 |  | T+0 sec | [10 empty] | T+0 sec | 40098.1024 | 59.978 | 3696.3623 | 350 | -206.4591 | 1 | 115.5 | 10 | 15 | -103 | 7576.23 | 17.5995 | T+0 sec | 40098.1024 | [12 empty] | T+0 sec | 40098.1024 | [12 empty] | T+0 sec | 40098.1024 | [12 empty] | T+0 sec | 40098.1024 | [12 empty] | T+0 sec | 40098.1024
T+02 sec | 40098.1024 | 59.978 | 3696.3623 |  |  |  | 17.5995 | -3.8413 |  | 0.62417 | 3671.1219 | 3696.3623 | 3665.0373 | 3674.1163 | 3674.1163 | 633 | [7 empty] | 633 | -989.0752 |  | T+02 sec | [10 empty] | T+02 sec | 40098.1024 | 59.978 | 3696.3623 | 350 | -206.4591 | 1 | 115.5 | 10 | 15 | -103 | 7576.23 | 17.5995 | T+02 sec | 40098.1024 | [12 empty] | T+02 sec | 40098.1024 | [12 empty] | T+02 sec | 40098.1024 | [12 empty] | T+02 sec | 40098.1024 | [12 empty] | T+02 sec | 40098.1024
T+04 sec | 40098.1024 | 59.978 | 3696.3623 |  |  |  | 17.5995 | 3.663 |  | 0.62417 | 3679.2504 | 3696.3623 | 3669.775 | 3674.7405 | 3674.4284 | 633 | [7 empty] | 633 | -989.0752 |  | T+04 sec | [10 empty] | T+04 sec | 40098.1024 | 59.978 | 3696.3623 | 350 | -206.4591 | 1 | 115.5 | 10 | 15 | -103 | 7576.23 | 17.5995 | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024
T+06 sec | 40098.1024 | 59.836 | 3734.6726 |  |  |  | 131.2012 | 48.3014 |  | 0.62417 | 3724.5129 | 3705.9399 | 3683.4595 | 3675.3647 | 3674.7405 | 633 | [6 empty] | 0 | 633 | -307.2796 |  | T+06 sec | [10 empty] | T+06 sec | 40098.1024 | 59.836 | 3734.6726 | 335 | -206.4591 | 1 | 116 | 10 | 0 | -103 | 7576.56 | 131.2012 | T+06 sec | 40098.1024 | [12 empty] | T+06 sec | 40098.1024 | [12 empty] | T+06 sec | 40098.1024 | [12 empty] | T+06 sec | 40098.1024 | [12 empty] | T+06 sec | 40098.1024
T+08 sec | 40098.1025 | 59.836 | 3734.6726 |  |  |  | 131.2012 | 77.3163 |  | 0.62417 | 3754.152 | 3711.6864 | 3697.598 | 3675.9888 | 3675.0526 | 633 | [6 empty] | 0 | 633 | -307.2796 |  | T+08 sec | [10 empty] | T+08 sec | 40098.1025 | 59.836 | 3734.6726 | 335 | -206.4591 | 1 | 116 | 10 | 0 | -103 | 7576.56 | 131.2012 | T+08 sec | 40098.1025 | [12 empty] | T+08 sec | 40098.1025 | [12 empty] | T+08 sec | 40098.1025 | [12 empty] | T+08 sec | 40098.1025 | [12 empty] | T+08 sec | 40098.1025
T+10 sec | 40098.1025 | 59.892 | 3761.2495 |  |  |  | 86.4014 | 80.4961 |  | 0.62417 | 3757.956 | 3719.9469 | 3707.6577 | 3676.613 | 3675.3647 | 633 | [6 empty] | 0 | 633 | -421.9957 |  | T+10 sec | [10 empty] | T+10 sec | 40098.1025 | 59.892 | 3761.2495 | 335 | -206.4591 | 1 | 116.5 | 10 | 0 | -103 | 7576.89 | 86.4014 | T+10 sec | 40098.1025 | [12 empty] | T+10 sec | 40098.1025 | [12 empty] | T+10 sec | 40098.1025 | [12 empty] | T+10 sec | 40098.1025 | [12 empty] | T+10 sec | 40098.1025
T+12 sec | 40098.1025 | 59.892 | 3761.2495 |  |  |  | 86.4014 | 82.5629 |  | 0.62417 | 3760.647 | 3725.8473 | 3715.2276 | 3677.2372 | 3675.6767 | 633 | [6 empty] | 0 | 633 | -421.9957 |  | T+12 sec | 59.8823 | -396.9069 | [8 empty] | T+12 sec | 40098.1025 | 59.892 | 3761.2495 | 335 | -206.4591 | 1 | 116.5 | 10 | 0 | -103 | 7576.89 | 86.4014 | T+12 sec | 40098.1025 | 59.8823 | 3770.953 | 335 | -207.8297 | 1 | 117.3571 | 10 | 0 | -103 | 7577.4557 | 94.1711 | 3720.799 | T+12 sec | 40098.1025 | [12 empty] | T+12 sec | 40098.1025 | [12 empty] | T+12 sec | 40098.1025 | [12 empty] | T+12 sec | 40098.1025
T+14 sec | 40098.1025 | 59.88 | 3766.1938 |  |  |  | 95.9991 | 87.2656 |  | 0.62417 | 3765.9738 | 3730.8906 | 3721.5709 | 3677.8613 | 3675.9888 | 633 | [6 empty] | 0 | 633 | -390.7438 |  | T+14 sec | 59.8823 | -396.9069 | [8 empty] | T+14 sec | 40098.1025 | 59.88 | 3766.1938 | 335 | -206.4591 | 1 | 117 | 10 | 0 | -103 | 7577.22 | 95.9991 | T+14 sec | 40098.1025 | 59.8823 | 3770.953 | 335 | -207.8297 | 1 | 117.3571 | 10 | 0 | -103 | 7577.4557 | 94.1711 | 3720.799 | T+14 sec | 40098.1025 | [12 empty] | T+14 sec | 40098.1025 | [12 empty] | T+14 sec | 40098.1025 | [12 empty] | T+14 sec | 40098.1025
T+16 sec | 40098.1025 | 59.88 | 3766.1938 |  |  |  | 95.9991 | 90.3223 |  | 0.62417 | 3769.6548 | 3734.8132 | 3726.9135 | 3678.4855 | 3676.3009 | 633 | [6 empty] | 0 | 633 | -390.7438 |  | T+16 sec | 59.8823 | -396.9069 | [8 empty] | T+16 sec | 40098.1025 | 59.88 | 3766.1938 | 335 | -206.4591 | 1 | 117 | 10 | 0 | -103 | 7577.22 | 95.9991 | T+16 sec | 40098.1025 | 59.8823 | 3770.953 | 335 | -207.8297 | 1 | 117.3571 | 10 | 0 | -103 | 7577.4557 | 94.1711 | 3720.799 | T+16 sec | 40098.1025 | [12 empty] | T+16 sec | 40098.1025 | [12 empty] | T+16 sec | 40098.1025 | [12 empty] | T+16 sec | 40098.1025
T+18 sec | 40098.1026 | 59.875 | 3769.925 |  |  |  | 100 | 93.7095 |  | 0.62417 | 3773.6661 | 3738.3244 | 3731.5888 | 3679.1097 | 3676.613 | 633 | [6 empty] | 0 | 633 | -379.0423 |  | T+18 sec | 59.8823 | -396.9069 | 59.8831 | -398.8954 |  |  | 59.888 | -411.6043 |  |  | T+18 sec | 40098.1026 | 59.875 | 3769.925 | 335 | -206.4591 | 1 | 117.5 | 10 | 0 | -103 | 7577.55 | 100 | T+18 sec | 40098.1026 | 59.8823 | 3770.953 | 335 | -207.8297 | 1 | 117.3571 | 10 | 0 | -103 | 7577.4557 | 94.1711 | 3720.799 | T+18 sec | 40098.1026 | 59.8831 | 3779.6252 | 335 | -209.8855 | 1.1429 | 118.1429 | 10 | 0 | -103 | 7577.9743 | 93.4858 | 3718.9007 | T+18 sec | 40098.1026 | [12 empty] | T+18 sec | 40098.1026 | 59.888 | 3787.7954 | 335 | -211.7533 | 3.3333 | 119.5 | 10 | 0 | -103 | 7578.87 | 89.5999 | 3716.209 | T+18 sec | 40098.1026
T+20 sec | 40098.1026 | 59.875 | 3769.925 | 59.8888 | 3788.8466 |  | 100 | 95.9112 | 3750.6259 | 0.62417 | 3776.4919 | 3741.1972 | 3735.6709 | 3679.7339 | 3676.9251 | 633 | [6 empty] | 0 | 633 | -379.0423 | -413.5197 | T+20 sec | 59.8823 | -396.9069 | 59.8831 | -398.8954 | 59.8888 | -412.2881 | 59.888 | -411.6043 | 59.8888 | -413.5197 | T+20 sec | 40098.1026 | 59.875 | 3769.925 | 335 | -206.4591 | 1 | 117.5 | 10 | 0 | -103 | 7577.55 | 100 | T+20 sec | 40098.1026 | 59.8823 | 3770.953 | 335 | -207.8297 | 1 | 117.3571 | 10 | 0 | -103 | 7577.4557 | 94.1711 | 3720.799 | T+20 sec | 40098.1026 | 59.8831 | 3779.6252 | 335 | -209.8855 | 1.1429 | 118.1429 | 10 | 0 | -103 | 7577.9743 | 93.4858 | 3718.9007 | T+20 sec | 40098.1026 | 59.8883 | 3784.1336 | 335 | -210.82 | 2.0909 | 118.8636 | 10 | 0 | -103 | 7578.45 | 89.3815 | 3715.0178 | T+20 sec | 40098.1026 | 59.888 | 3787.7954 | 335 | -211.7533 | 3.3333 | 119.5 | 10 | 0 | -103 | 7578.87 | 89.5999 | 3716.209 | T+20 sec | 40098.1026 | 59.8888 | 3788.8466 | 335 | -212.0647 | 3.4706 | 119.6176 | 10 | 0 | -103 | 7578.9476 | 88.9882 | 3715.4642
T+22 sec | 40098.1026 | 59.887 | 3781.5918 | 59.8888 | 3788.8466 |  | 90.3992 | 93.982 | 3750.6259 | 0.62417 | 3775.1869 | 3744.5634 | 3738.9639 | 3680.358 | 3677.2372 | 633 | [6 empty] | 0 | 633 | -408.3903 | -413.5197 | T+22 sec | 59.8823 | -396.9069 | 59.8831 | -398.8954 | 59.8888 | -412.2881 | 59.888 | -411.6043 | 59.8888 | -413.5197 | T+22 sec | 40098.1026 | 59.887 | 3781.5918 | 335 | -211.256 | 1 | 118 | 10 | 0 | -103 | 7577.88 | 90.3992 | T+22 sec | 40098.1026 | 59.8823 | 3770.953 | 335 | -207.8297 | 1 | 117.3571 | 10 | 0 | -103 | 7577.4557 | 94.1711 | 3720.799 | T+22 sec | 40098.1026 | 59.8831 | 3779.6252 | 335 | -209.8855 | 1.1429 | 118.1429 | 10 | 0 | -103 | 7577.9743 | 93.4858 | 3718.9007 | T+22 sec | 40098.1026 | 59.8883 | 3784.1336 | 335 | -210.82 | 2.0909 | 118.8636 | 10 | 0 | -103 | 7578.45 | 89.3815 | 3715.0178 | T+22 sec | 40098.1026 | 59.888 | 3787.7954 | 335 | -211.7533 | 3.3333 | 119.5 | 10 | 0 | -103 | 7578.87 | 89.5999 | 3716.209 | T+22 sec | 40098.1026 | 59.8888 | 3788.8466 | 335 | -212.0647 | 3.4706 | 119.6176 | 10 | 0 | -103 | 7578.9476 | 88.9882 | 3715.4642
T+24 sec | 40098.1026 | 59.887 | 3781.5918 | 59.8888 | 3788.8466 |  | 90.3992 | 92.728 | 3750.6259 | 0.62417 | 3774.5571 | 3747.4117 | 3741.7018 | 3680.9822 | 3677.5493 | 633 | [6 empty] | 0 | 633 | -408.3903 | -413.5197 | T+24 sec | 59.8823 | -396.9069 | 59.8831 | -398.8954 | 59.8888 | -412.2881 | 59.888 | -411.6043 | 59.8888 | -413.5197 | T+24 sec | 40098.1026 | 59.887 | 3781.5918 | 335 | -211.256 | 1 | 118 | 10 | 0 | -103 | 7577.88 | 90.3992 | T+24 sec | 40098.1026 | 59.8823 | 3770.953 | 335 | -207.8297 | 1 | 117.3571 | 10 | 0 | -103 | 7577.4557 | 94.1711 | 3720.799 | T+24 sec | 40098.1026 | 59.8831 | 3779.6252 | 335 | -209.8855 | 1.1429 | 118.1429 | 10 | 0 | -103 | 7577.9743 | 93.4858 | 3718.9007 | T+24 sec | 40098.1026 | 59.8883 | 3784.1336 | 335 | -210.82 | 2.0909 | 118.8636 | 10 | 0 | -103 | 7578.45 | 89.3815 | 3715.0178 | T+24 sec | 40098.1026 | 59.888 | 3787.7954 | 335 | -211.7533 | 3.3333 | 119.5 | 10 | 0 | -103 | 7578.87 | 89.5999 | 3716.209 | T+24 sec | 40098.1026 | 59.8888 | 3788.8466 | 335 | -212.0647 | 3.4706 | 119.6176 | 10 | 0 | -103 | 7578.9476 | 88.9882 | 3715.4642
T+26 sec | 40098.1027 | 59.885 | 3784.9619 | 59.8888 | 3788.8466 |  | 92.0013 | 92.4737 | 3750.6259 | 0.62417 | 3774.9269 | 3750.0939 | 3744.075 | 3681.6064 | 3677.8613 | 633 | [6 empty] | 0 | 633 | -403.1809 | -413.5197 | T+26 sec |  |  | 59.8831 | -398.8954 | 59.8888 | -412.2881 | 59.888 | -411.6043 | 59.8888 | -413.5197 | T+26 sec | 40098.1027 | 59.885 | 3784.9619 | 335 | -211.256 | 1 | 118.5 | 10 | 0 | -103 | 7578.21 | 92.0013 | T+26 sec | 40098.1027 | [12 empty] | T+26 sec | 40098.1027 | 59.8831 | 3779.6252 | 335 | -209.8855 | 1.1429 | 118.1429 | 10 | 0 | -103 | 7577.9743 | 93.4858 | 3718.9007 | T+26 sec | 40098.1027 | 59.8883 | 3784.1336 | 335 | -210.82 | 2.0909 | 118.8636 | 10 | 0 | -103 | 7578.45 | 89.3815 | 3715.0178 | T+26 sec | 40098.1027 | 59.888 | 3787.7954 | 335 | -211.7533 | 3.3333 | 119.5 | 10 | 0 | -103 | 7578.87 | 89.5999 | 3716.209 | T+26 sec | 40098.1027 | 59.8888 | 3788.8466 | 335 | -212.0647 | 3.4706 | 119.6176 | 10 | 0 | -103 | 7578.9476 | 88.9882 | 3715.4642
T+28 sec | 40098.1027 | 59.885 | 3784.9619 | 59.8888 | 3788.8466 |  | 92.0013 | 92.3084 | 3750.6259 | 0.62417 | 3775.3858 | 3752.4184 | 3746.1624 | 3682.2305 | 3678.1734 | 633 | [6 empty] | 0 | 633 | -403.1809 | -413.5197 | T+28 sec |  |  | 59.8831 | -398.8954 | 59.8888 | -412.2881 | 59.888 | -411.6043 | 59.8888 | -413.5197 | T+28 sec | 40098.1027 | 59.885 | 3784.9619 | 335 | -211.256 | 1 | 118.5 | 10 | 0 | -103 | 7578.21 | 92.0013 | T+28 sec | 40098.1027 | [12 empty] | T+28 sec | 40098.1027 | 59.8831 | 3779.6252 | 335 | -209.8855 | 1.1429 | 118.1429 | 10 | 0 | -103 | 7577.9743 | 93.4858 | 3718.9007 | T+28 sec | 40098.1027 | 59.8883 | 3784.1336 | 335 | -210.82 | 2.0909 | 118.8636 | 10 | 0 | -103 | 7578.45 | 89.3815 | 3715.0178 | T+28 sec | 40098.1027 | 59.888 | 3787.7954 | 335 | -211.7533 | 3.3333 | 119.5 | 10 | 0 | -103 | 7578.87 | 89.5999 | 3716.209 | T+28 sec | 40098.1027 | 59.8888 | 3788.8466 | 335 | -212.0647 | 3.4706 | 119.6176 | 10 | 0 | -103 | 7578.9476 | 88.9882 | 3715.4642
T+30 sec | 40098.1027 | 59.888 | 3784.4189 | 59.8888 | 3788.8466 |  | 89.5996 | 91.3603 | 3750.6259 | 0.62417 | 3775.0619 | 3754.4185 | 3747.9686 | 3682.8547 | 3678.4855 | 633 | [6 empty] | 0 | 633 | -411.0408 | -413.5197 | T+30 sec |  |  | 59.8831 | -398.8954 | 59.8888 | -412.2881 | 59.888 | -411.6043 | 59.8888 | -413.5197 | T+30 sec | 40098.1027 | 59.888 | 3784.4189 | 335 | -211.256 | 2 | 119 | 10 | 0 | -103 | 7578.54 | 89.5996 | T+30 sec | 40098.1027 | [12 empty] | T+30 sec | 40098.1027 | 59.8831 | 3779.6252 | 335 | -209.8855 | 1.1429 | 118.1429 | 10 | 0 | -103 | 7577.9743 | 93.4858 | 3718.9007 | T+30 sec | 40098.1027 | 59.8883 | 3784.1336 | 335 | -210.82 | 2.0909 | 118.8636 | 10 | 0 | -103 | 7578.45 | 89.3815 | 3715.0178 | T+30 sec | 40098.1027 | 59.888 | 3787.7954 | 335 | -211.7533 | 3.3333 | 119.5 | 10 | 0 | -103 | 7578.87 | 89.5999 | 3716.209 | T+30 sec | 40098.1027 | 59.8888 | 3788.8466 | 335 | -212.0647 | 3.4706 | 119.6176 | 10 | 0 | -103 | 7578.9476 | 88.9882 | 3715.4642
T+32 sec | 40098.1027 | 59.888 | 3784.4189 | 59.8888 | 3788.8466 |  | 89.5996 | 90.7441 | 3750.6259 | 0.62417 | 3775.0698 | 3756.1832 | 3749.5628 | 3683.4789 | 3678.7976 | 633 | [6 empty] | 0 | 633 | -411.0408 | -413.5197 | T+32 sec |  |  |  |  | 59.8888 | -412.2881 | 59.888 | -411.6043 | 59.8888 | -413.5197 | T+32 sec | 40098.1027 | 59.888 | 3784.4189 | 335 | -211.256 | 2 | 119 | 10 | 0 | -103 | 7578.54 | 89.5996 | T+32 sec | 40098.1027 | [12 empty] | T+32 sec | 40098.1027 | [12 empty] | T+32 sec | 40098.1027 | 59.8883 | 3784.1336 | 335 | -210.82 | 2.0909 | 118.8636 | 10 | 0 | -103 | 7578.45 | 89.3815 | 3715.0178 | T+32 sec | 40098.1027 | 59.888 | 3787.7954 | 335 | -211.7533 | 3.3333 | 119.5 | 10 | 0 | -103 | 7578.87 | 89.5999 | 3716.209 | T+32 sec | 40098.1027 | 59.8888 | 3788.8466 | 335 | -212.0647 | 3.4706 | 119.6176 | 10 | 0 | -103 | 7578.9476 | 88.9882 | 3715.4642
T+34 sec | 40098.1028 | 59.895 | 3788.3276 | 59.8888 | 3788.8466 |  | 83.9996 | 88.3835 | 3750.6259 | 0.62417 | 3773.3335 | 3757.969 | 3750.8834 | 3684.103 | 3679.1097 | 633 | [6 empty] | 0 | 633 | -430.6141 | -413.5197 | T+34 sec |  |  |  |  | 59.8888 | -412.2881 | 59.888 | -411.6043 | 59.8888 | -413.5197 | T+34 sec | 40098.1028 | 59.895 | 3788.3276 | 335 | -211.256 | 3 | 119.5 | 10 | 0 | -103 | 7578.87 | 83.9996 | T+34 sec | 40098.1028 | [12 empty] | T+34 sec | 40098.1028 | [12 empty] | T+34 sec | 40098.1028 | 59.8883 | 3784.1336 | 335 | -210.82 | 2.0909 | 118.8636 | 10 | 0 | -103 | 7578.45 | 89.3815 | 3715.0178 | T+34 sec | 40098.1028 | 59.888 | 3787.7954 | 335 | -211.7533 | 3.3333 | 119.5 | 10 | 0 | -103 | 7578.87 | 89.5999 | 3716.209 | T+34 sec | 40098.1028 | 59.8888 | 3788.8466 | 335 | -212.0647 | 3.4706 | 119.6176 | 10 | 0 | -103 | 7578.9476 | 88.9882 | 3715.4642
T+36 sec | 40098.1028 | 59.895 | 3788.3276 | 59.8888 | 3788.8466 |  | 83.9996 | 86.8492 | 3750.6259 | 0.62417 | 3772.4233 | 3759.5668 | 3752.0171 | 3684.7272 | 3679.4218 | 633 | [6 empty] | 0 | 633 | -430.6141 | -413.5197 | T+36 sec |  |  |  |  | 59.8888 | -412.2881 | 59.888 | -411.6043 | 59.8888 | -413.5197 | T+36 sec | 40098.1028 | 59.895 | 3788.3276 | 335 | -211.256 | 3 | 119.5 | 10 | 0 | -103 | 7578.87 | 83.9996 | T+36 sec | 40098.1028 | [12 empty] | T+36 sec | 40098.1028 | [12 empty] | T+36 sec | 40098.1028 | 59.8883 | 3784.1336 | 335 | -210.82 | 2.0909 | 118.8636 | 10 | 0 | -103 | 7578.45 | 89.3815 | 3715.0178 | T+36 sec | 40098.1028 | 59.888 | 3787.7954 | 335 | -211.7533 | 3.3333 | 119.5 | 10 | 0 | -103 | 7578.87 | 89.5999 | 3716.209 | T+36 sec | 40098.1028 | 59.8888 | 3788.8466 | 335 | -212.0647 | 3.4706 | 119.6176 | 10 | 0 | -103 | 7578.9476 | 88.9882 | 3715.4642
T+38 sec | 40098.1028 | 59.893 | 3788.4719 | 59.8888 | 3788.8466 |  | 85.5988 | 86.4115 | 3750.6259 | 0.62417 | 3772.6098 | 3761.0121 | 3753.0467 | 3685.3514 | 3679.7339 | 633 | [6 empty] | 0 | 633 | -424.8372 | -413.5197 | T+38 sec |  |  |  |  | 59.8888 | -412.2881 | 59.888 | -411.6043 | 59.8888 | -413.5197 | T+38 sec | 40098.1028 | 59.893 | 3788.4719 | 335 | -211.256 | 4 | 120 | 10 | 0 | -103 | 7579.2 | 85.5988 | T+38 sec | 40098.1028 | [12 empty] | T+38 sec | 40098.1028 | [12 empty] | T+38 sec | 40098.1028 | 59.8883 | 3784.1336 | 335 | -210.82 | 2.0909 | 118.8636 | 10 | 0 | -103 | 7578.45 | 89.3815 | 3715.0178 | T+38 sec | 40098.1028 | 59.888 | 3787.7954 | 335 | -211.7533 | 3.3333 | 119.5 | 10 | 0 | -103 | 7578.87 | 89.5999 | 3716.209 | T+38 sec | 40098.1028 | 59.8888 | 3788.8466 | 335 | -212.0647 | 3.4706 | 119.6176 | 10 | 0 | -103 | 7578.9476 | 88.9882 | 3715.4642
T+40 sec | 40098.1028 | 59.893 | 3788.4719 | 59.8888 | 3788.8466 |  | 85.5988 | 86.127 | 3750.6259 | 0.62417 | 3772.9495 | 3762.3197 | 3753.9945 | 3685.9756 | 3680.0459 | 633 | [6 empty] | 0 | 633 | -424.8372 | -413.5197 | T+40 sec |  |  |  |  | 59.8888 | -412.2881 | 59.888 | -411.6043 | 59.8888 | -413.5197 | T+40 sec | 40098.1028 | 59.893 | 3788.4719 | 335 | -211.256 | 4 | 120 | 10 | 0 | -103 | 7579.2 | 85.5988 | T+40 sec | 40098.1028 | [12 empty] | T+40 sec | 40098.1028 | [12 empty] | T+40 sec | 40098.1028 | 59.8883 | 3784.1336 | 335 | -210.82 | 2.0909 | 118.8636 | 10 | 0 | -103 | 7578.45 | 89.3815 | 3715.0178 | T+40 sec | 40098.1028 | 59.888 | 3787.7954 | 335 | -211.7533 | 3.3333 | 119.5 | 10 | 0 | -103 | 7578.87 | 89.5999 | 3716.209 | T+40 sec | 40098.1028 | 59.8888 | 3788.8466 | 335 | -212.0647 | 3.4706 | 119.6176 | 10 | 0 | -103 | 7578.9476 | 88.9882 | 3715.4642
T+42 sec | 40098.1028 | 59.894 | 3793.0745 | 59.8888 | 3788.8466 |  | 84.7992 | 85.6623 | 3750.6259 | 0.62417 | 3773.1089 | 3763.7176 | 3754.8633 | 3686.5997 | 3680.358 | 633 | [6 empty] | 0 | 633 | -427.7061 | -413.5197 | T+42 sec | [6 empty] | 59.888 | -411.6043 | 59.8888 | -413.5197 | T+42 sec | 40098.1028 | 59.894 | 3793.0745 | 335 | -214.3467 | 5 | 120.5 | 10 | 0 | -103 | 7579.53 | 84.7992 | T+42 sec | 40098.1028 | [12 empty] | T+42 sec | 40098.1028 | [12 empty] | T+42 sec | 40098.1028 | [12 empty] | T+42 sec | 40098.1028 | 59.888 | 3787.7954 | 335 | -211.7533 | 3.3333 | 119.5 | 10 | 0 | -103 | 7578.87 | 89.5999 | 3716.209 | T+42 sec | 40098.1028 | 59.8888 | 3788.8466 | 335 | -212.0647 | 3.4706 | 119.6176 | 10 | 0 | -103 | 7578.9476 | 88.9882 | 3715.4642
T+44 sec | 40098.1029 | 59.894 | 3793.0745 | 59.8888 | 3788.8466 |  | 84.7992 | 85.3602 | 3750.6259 | 0.62417 | 3773.431 | 3764.994 | 3755.6706 | 3687.2239 | 3680.6701 | 633 | [6 empty] | 0 | 633 | -427.7061 | -413.5197 | T+44 sec | [6 empty] | 59.888 | -411.6043 | 59.8888 | -413.5197 | T+44 sec | 40098.1029 | 59.894 | 3793.0745 | 335 | -214.3467 | 5 | 120.5 | 10 | 0 | -103 | 7579.53 | 84.7992 | T+44 sec | 40098.1029 | [12 empty] | T+44 sec | 40098.1029 | [12 empty] | T+44 sec | 40098.1029 | [12 empty] | T+44 sec | 40098.1029 | 59.888 | 3787.7954 | 335 | -211.7533 | 3.3333 | 119.5 | 10 | 0 | -103 | 7578.87 | 89.5999 | 3716.209 | T+44 sec | 40098.1029 | 59.8888 | 3788.8466 | 335 | -212.0647 | 3.4706 | 119.6176 | 10 | 0 | -103 | 7578.9476 | 88.9882 | 3715.4642
T+46 sec | 40098.1029 | 59.89 | 3799.4277 | 59.8888 | 3788.8466 |  | 88.0005 | 86.2843 | 3750.6259 | 0.62417 | 3774.9793 | 3766.4288 | 3756.4751 | 3687.8481 | 3680.9822 | 633 | [6 empty] | 0 | 633 | -416.4462 | -413.5197 | T+46 sec | [6 empty] | 59.888 | -411.6043 | 59.8888 | -413.5197 | T+46 sec | 40098.1029 | 59.89 | 3799.4277 | 335 | -214.3467 | 6 | 121 | 10 | 0 | -103 | 7579.86 | 88.0005 | T+46 sec | 40098.1029 | [12 empty] | T+46 sec | 40098.1029 | [12 empty] | T+46 sec | 40098.1029 | [12 empty] | T+46 sec | 40098.1029 | 59.888 | 3787.7954 | 335 | -211.7533 | 3.3333 | 119.5 | 10 | 0 | -103 | 7578.87 | 89.5999 | 3716.209 | T+46 sec | 40098.1029 | 59.8888 | 3788.8466 | 335 | -212.0647 | 3.4706 | 119.6176 | 10 | 0 | -103 | 7578.9476 | 88.9882 | 3715.4642
T+48 sec | 40098.1029 | 59.89 | 3799.4277 | 59.8888 | 3788.8466 |  | 88.0005 | 86.885 | 3750.6259 | 0.62417 | 3776.2041 | 3767.7487 | 3757.2643 | 3688.4722 | 3681.2943 | 633 | [6 empty] | 0 | 633 | -416.4462 | -413.5197 | T+48 sec | [6 empty] | 59.888 | -411.6043 | 59.8888 | -413.5197 | T+48 sec | 40098.1029 | 59.89 | 3799.4277 | 335 | -214.3467 | 6 | 121 | 10 | 0 | -103 | 7579.86 | 88.0005 | T+48 sec | 40098.1029 | [12 empty] | T+48 sec | 40098.1029 | [12 empty] | T+48 sec | 40098.1029 | [12 empty] | T+48 sec | 40098.1029 | 59.888 | 3787.7954 | 335 | -211.7533 | 3.3333 | 119.5 | 10 | 0 | -103 | 7578.87 | 89.5999 | 3716.209 | T+48 sec | 40098.1029 | 59.8888 | 3788.8466 | 335 | -212.0647 | 3.4706 | 119.6176 | 10 | 0 | -103 | 7578.9476 | 88.9882 | 3715.4642
T+50 sec | 40098.1029 | 59.885 | 3799.9592 | 59.8888 | 3788.8466 |  | 92.0013 | 88.6757 | 3750.6259 | 0.62417 | 3778.619 | 3768.9876 | 3758.0856 | 3689.0964 | 3681.6064 | 633 | [6 empty] | 0 | 633 | -403.1809 | -413.5197 | T+50 sec | [6 empty] | 59.888 | -411.6043 | 59.8888 | -413.5197 | T+50 sec | 40098.1029 | 59.885 | 3799.9592 | 335 | -214.3467 | 7 | 121.5 | 10 | 0 | -103 | 7580.19 | 92.0013 | T+50 sec | 40098.1029 | [12 empty] | T+50 sec | 40098.1029 | [12 empty] | T+50 sec | 40098.1029 | [12 empty] | T+50 sec | 40098.1029 | 59.888 | 3787.7954 | 335 | -211.7533 | 3.3333 | 119.5 | 10 | 0 | -103 | 7578.87 | 89.5999 | 3716.209 | T+50 sec | 40098.1029 | 59.8888 | 3788.8466 | 335 | -212.0647 | 3.4706 | 119.6176 | 10 | 0 | -103 | 7578.9476 | 88.9882 | 3715.4642
T+52 sec | 40098.103 | 59.885 | 3799.9592 | 59.8888 | 3788.8466 |  | 92.0013 | 89.8397 | 3750.6259 | 0.62417 | 3780.4072 | 3770.1347 | 3758.9124 | 3689.7206 | 3681.9185 | 633 | [6 empty] | 0 | 633 | -403.1809 | -413.5197 | T+52 sec | [6 empty] | 59.888 | -411.6043 | 59.8888 | -413.5197 | T+52 sec | 40098.103 | 59.885 | 3799.9592 | 335 | -214.3467 | 7 | 121.5 | 10 | 0 | -103 | 7580.19 | 92.0013 | T+52 sec | 40098.103 | [12 empty] | T+52 sec | 40098.103 | [12 empty] | T+52 sec | 40098.103 | [12 empty] | T+52 sec | 40098.103 | 59.888 | 3787.7954 | 335 | -211.7533 | 3.3333 | 119.5 | 10 | 0 | -103 | 7578.87 | 89.5999 | 3716.209 | T+52 sec | 40098.103 | 59.8888 | 3788.8466 | 335 | -212.0647 | 3.4706 | 119.6176 | 10 | 0 | -103 | 7578.9476 | 88.9882 | 3715.4642
T+54 sec | 40098.103 | 59.887 | 3802.925 |  |  |  | 90.3992 | 90.0355 |  | 0.62417 | 3781.2272 | 3771.3058 | 3759.7093 | 3690.3448 | 3682.2305 | 633 | [6 empty] | 0 | 633 | -408.3903 |  | T+54 sec | [10 empty] | T+54 sec | 40098.103 | 59.887 | 3802.925 | 335 | -214.3467 | 8 | 122 | 10 | 0 | -103 | 7580.52 | 90.3992 | T+54 sec | 40098.103 | [12 empty] | T+54 sec | 40098.103 | [12 empty] | T+54 sec | 40098.103 | [12 empty] | T+54 sec | 40098.103 | [12 empty] | T+54 sec | 40098.103
T+56 sec | 40098.103 | 59.887 | 3802.925 |  |  |  | 90.3992 | 90.1628 |  | 0.62417 | 3781.9786 | 3772.3961 | 3760.4772 | 3690.9689 | 3682.5426 | 633 | [6 empty] | 0 | 633 | -408.3903 |  | T+56 sec | [10 empty] | T+56 sec | 40098.103 | 59.887 | 3802.925 | 335 | -214.3467 | 8 | 122 | 10 | 0 | -103 | 7580.52 | 90.3992 | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103
T+58 sec | 40098.103 | 59.888 | 3804.3879 |  |  |  | 89.5996 | 89.9657 |  | 0.62417 | 3782.4057 | 3773.4625 | 3761.2082 | 3691.5931 | 3682.8547 | 633 | [6 empty] | 0 | 633 | -411.0408 |  | T+58 sec | [10 empty] | T+58 sec | 40098.103 | 59.888 | 3804.3879 | 335 | -214.3467 | 9 | 122.5 | 10 | 0 | -103 | 7580.85 | 89.5996 | T+58 sec | 40098.103 | [12 empty] | T+58 sec | 40098.103 | [12 empty] | T+58 sec | 40098.103 | [12 empty] | T+58 sec | 40098.103 | [12 empty] | T+58 sec | 40098.103
T+60 sec | 40098.1031 | 59.888 | 3804.3879 |  |  |  | 89.5996 | 89.8376 |  | 0.62417 | 3782.9017 | 3774.4601 | 3761.908 | 3692.2173 | 3683.1668 | 633 | [6 empty] | 0 | 633 | -411.0408 |  | T+60 sec | [10 empty] | T+60 sec | 40098.1031 | 59.888 | 3804.3879 | 335 | -214.3467 | 9 | 122.5 | 10 | 0 | -103 | 7580.85 | 89.5996 | T+60 sec | 40098.1031 | [12 empty] | T+60 sec | 40098.1031 | [12 empty] | T+60 sec | 40098.1031 | [12 empty] | T+60 sec | 40098.1031 | [12 empty] | T+60 sec | 40098.1031
T+62 sec | 40098.1031 | 59.889 | 3805.6167 |  |  |  | 88.8 | 89.4744 |  | 0.62417 | 3783.1628 | 3775.4337 | 3762.5722 | 3692.8414 | 3683.4789 | 633 | [6 empty] | 0 | 633 | -413.7258 |  | T+62 sec | [10 empty] | T+62 sec | 40098.1031 | 59.889 | 3805.6167 | 335 | -212.1727 | 10 | 123 | 10 | 0 | -103 | 7581.18 | 88.8 | T+62 sec | 40098.1031 | [12 empty] | T+62 sec | 40098.1031 | [12 empty] | T+62 sec | 40098.1031 | [12 empty] | T+62 sec | 40098.1031 | [12 empty] | T+62 sec | 40098.1031
T+64 sec | 40098.1031 | 59.889 | 3805.6167 |  |  |  | 88.8 | 89.2384 |  | 0.62417 | 3783.5509 | 3776.3484 | 3763.2079 | 3693.4656 | 3683.791 | 633 | [6 empty] | 0 | 633 | -413.7258 |  | T+64 sec | [10 empty] | T+64 sec | 40098.1031 | 59.889 | 3805.6167 | 335 | -212.1727 | 10 | 123 | 10 | 0 | -103 | 7581.18 | 88.8 | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031
T+66 sec | 40098.1031 | 59.873 | 3811.5029 |  |  |  | 101.5991 | 93.5646 |  | 0.62417 | 3788.5013 | 3777.3823 | 3763.9518 | 3694.0898 | 3684.103 | 633 | [6 empty] | 0 | 633 | -374.5591 |  | T+66 sec | [10 empty] | T+66 sec | 40098.1031 | 59.873 | 3811.5029 | 335 | -212.1727 | 11 | 123.5 | 10 | 0 | -103 | 7581.51 | 101.5991 | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031
T+68 sec | 40098.1031 | 59.873 | 3811.5029 |  |  |  | 101.5991 | 96.3767 |  | 0.62417 | 3791.9376 | 3778.3572 | 3764.7514 | 3694.7139 | 3684.4151 | 633 | [6 empty] | 0 | 633 | -374.5591 |  | T+68 sec | [10 empty] | T+68 sec | 40098.1031 | 59.873 | 3811.5029 | 335 | -212.1727 | 11 | 123.5 | 10 | 0 | -103 | 7581.51 | 101.5991 | T+68 sec | 40098.1031 | [12 empty] | T+68 sec | 40098.1031 | [12 empty] | T+68 sec | 40098.1031 | [12 empty] | T+68 sec | 40098.1031 | [12 empty] | T+68 sec | 40098.1031
T+70 sec | 40098.1032 | 59.849 | 3815.8889 |  |  |  | 120.8008 | 104.9251 |  | 0.62417 | 3801.1102 | 3779.3997 | 3765.7614 | 3695.3381 | 3684.7272 | 633 | [6 empty] | 0 | 633 | -327.9779 |  | T+70 sec | [10 empty] | T+70 sec | 40098.1032 | 59.849 | 3815.8889 | 335 | -212.1727 | 12 | 124 | 10 | 0 | -103 | 7581.84 | 120.8008 | T+70 sec | 40098.1032 | [12 empty] | T+70 sec | 40098.1032 | [12 empty] | T+70 sec | 40098.1032 | [12 empty] | T+70 sec | 40098.1032 | [12 empty] | T+70 sec | 40098.1032
T+72 sec | 40098.1032 | 59.849 | 3815.8889 |  |  |  | 120.8008 | 110.4816 |  | 0.62417 | 3807.2908 | 3780.3859 | 3766.8838 | 3695.9623 | 3685.0393 | 633 | [6 empty] | 0 | 633 | -327.9779 |  | T+72 sec | [10 empty] | T+72 sec | 40098.1032 | 59.849 | 3815.8889 | 335 | -212.1727 | 12 | 124 | 10 | 0 | -103 | 7581.84 | 120.8008 | T+72 sec | 40098.1032 | [12 empty] | T+72 sec | 40098.1032 | [12 empty] | T+72 sec | 40098.1032 | [12 empty] | T+72 sec | 40098.1032 | [12 empty] | T+72 sec | 40098.1032
T+74 sec | 40098.1032 | 59.858 | 3826.0532 |  |  |  | 113.5986 | 111.5726 |  | 0.62417 | 3809.0059 | 3781.5877 | 3767.9923 | 3696.5865 | 3685.3514 | 633 | [6 empty] | 0 | 633 | -344.0253 |  | T+74 sec | [10 empty] | T+74 sec | 40098.1032 | 59.858 | 3826.0532 | 335 | -212.1727 | 13 | 124.5 | 10 | 0 | -103 | 7582.17 | 113.5986 | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032
T+76 sec | 40098.1032 | 59.858 | 3826.0532 |  |  |  | 113.5986 | 112.2817 |  | 0.62417 | 3810.3392 | 3782.7278 | 3769.0781 | 3697.2106 | 3685.6635 | 633 | [6 empty] | 0 | 633 | -344.0253 |  | T+76 sec | [10 empty] | T+76 sec | 40098.1032 | 59.858 | 3826.0532 | 335 | -212.1727 | 13 | 124.5 | 10 | 0 | -103 | 7582.17 | 113.5986 | T+76 sec | 40098.1032 | [12 empty] | T+76 sec | 40098.1032 | [12 empty] | T+76 sec | 40098.1032 | [12 empty] | T+76 sec | 40098.1032 | [12 empty] | T+76 sec | 40098.1032
T+78 sec | 40098.1033 | 59.866 | 3827.5239 |  |  |  | 107.1991 | 110.5028 |  | 0.62417 | 3809.1845 | 3783.8477 | 3770.0808 | 3697.8348 | 3685.9756 | 633 | [6 empty] | 0 | 633 | -359.6618 |  | T+78 sec | [10 empty] | T+78 sec | 40098.1033 | 59.866 | 3827.5239 | 335 | -212.1727 | 14 | 125 | 10 | 0 | -103 | 7582.5 | 107.1991 | T+78 sec | 40098.1033 | [12 empty] | T+78 sec | 40098.1033 | [12 empty] | T+78 sec | 40098.1033 | [12 empty] | T+78 sec | 40098.1033 | [12 empty] | T+78 sec | 40098.1033
T+80 sec | 40098.1033 | 59.866 | 3827.5239 |  |  |  | 107.1991 | 109.3465 |  | 0.62417 | 3808.6524 | 3784.913 | 3771.0215 | 3698.459 | 3686.2876 | 633 | [6 empty] | 0 | 633 | -359.6618 |  | T+80 sec | [10 empty] | T+80 sec | 40098.1033 | 59.866 | 3827.5239 | 335 | -212.1727 | 14 | 125 | 10 | 0 | -103 | 7582.5 | 107.1991 | T+80 sec | 40098.1033 | [12 empty] | T+80 sec | 40098.1033 | [12 empty] | T+80 sec | 40098.1033 | [12 empty] | T+80 sec | 40098.1033 | [12 empty] | T+80 sec | 40098.1033
| 40098.1033 | 59.867 | 3826.7834 |  |  |  | 106.3995 | 108.3151 |  | 0.62417 | 3808.2451 | 3785.9099 | 3771.9078 | 3699.0831 | 3686.5997 | 633 | [6 empty] | 0 | 633 | -361.7159 | [13 empty] | 40098.1033 | 59.867 | 3826.7834 | 335 | -215.5982 | 15 | 125.5 | 10 | 0 | -103 | 7582.83 | 106.3995
| 40098.1033 | 59.867 | 3826.7834 |  |  |  | 106.3995 | 107.6446 |  | 0.62417 | 3808.1988 | 3786.8605 | 3772.7518 | 3699.7073 | 3686.9118 | 633 | [6 empty] | 0 | 633 | -361.7159 | [13 empty] | 40098.1033 | 59.867 | 3826.7834 | 335 | -215.5982 | 15 | 125.5 | 10 | 0 | -103 | 7582.83 | 106.3995
| 40098.1034 | 59.871 | 3825.7134 |  |  |  | 103.2013 | 106.0895 |  | 0.62417 | 3807.2678 | 3787.7435 | 3773.5362 | 3700.3315 | 3687.2239 | 633 | [6 empty] | 0 | 633 | -370.1723 | [13 empty] | 40098.1034 | 59.871 | 3825.7134 | 335 | -215.5982 | 16 | 126 | 10 | 0 | -103 | 7583.16 | 103.2013
| 40098.1034 | 59.871 | 3825.7134 |  |  |  | 103.2013 | 105.0786 |  | 0.62417 | 3806.8812 | 3788.5873 | 3774.2772 | 3700.9557 | 3687.536 | 633 | [6 empty] | 0 | 633 | -370.1723 | [13 empty] | 40098.1034 | 59.871 | 3825.7134 | 335 | -215.5982 | 16 | 126 | 10 | 0 | -103 | 7583.16 | 103.2013
| 40098.1034 | 59.879 | 3822.5054 |  |  |  | 96.7987 | 102.1806 |  | 0.62417 | 3804.6074 | 3789.3246 | 3774.9366 | 3701.5798 | 3687.8481 | 633 | [6 empty] | 0 | 633 | -388.3478 | [13 empty] | 40098.1034 | 59.879 | 3822.5054 | 335 | -215.5982 | 16 | 126.5 | 10 | 0 | -103 | 7583.49 | 96.7987
| 40098.1034 | 59.879 | 3822.5054 |  |  |  | 96.7987 | 100.297 |  | 0.62417 | 3803.3479 | 3790.0306 | 3775.5411 | 3702.204 | 3688.1602 | 633 | [6 empty] | 0 | 633 | -388.3478 | [13 empty] | 40098.1034 | 59.879 | 3822.5054 | 335 | -215.5982 | 16 | 126.5 | 10 | 0 | -103 | 7583.49 | 96.7987
| 40098.1034 | 59.883 | 3818.0552 |  |  |  | 93.6005 | 97.9532 |  | 0.62417 | 3801.6283 | 3790.6144 | 3776.0846 | 3702.8282 | 3688.4722 | 633 | [6 empty] | 0 | 633 | -398.1122 | [13 empty] | 40098.1034 | 59.883 | 3818.0552 | 335 | -215.5982 | 16 | 127 | 10 | 0 | -103 | 7583.82 | 93.6005
| 40098.1035 | 59.883 | 3818.0552 |  |  |  | 93.6005 | 96.4297 |  | 0.62417 | 3800.729 | 3791.1745 | 3776.5875 | 3703.4523 | 3688.7843 | 633 | [6 empty] | 0 | 633 | -398.1122 | [13 empty] | 40098.1035 | 59.883 | 3818.0552 | 335 | -215.5982 | 16 | 127 | 10 | 0 | -103 | 7583.82 | 93.6005
| 40098.1035 | 59.89 | 3815.0098 |  |  |  | 88.0005 | 93.4795 |  | 0.62417 | 3798.4029 | 3791.6512 | 3777.0238 | 3704.0765 | 3689.0964 | 633 | [6 empty] | 0 | 633 | -416.4462 | [13 empty] | 40098.1035 | 59.89 | 3815.0098 | 335 | -215.5982 | 16 | 127.5 | 10 | 0 | -103 | 7584.15 | 88.0005
| 40098.1035 | 59.89 | 3815.0098 |  |  |  | 88.0005 | 91.5618 |  | 0.62417 | 3797.1094 | 3792.1092 | 3777.4176 | 3704.7007 | 3689.4085 | 633 | [6 empty] | 0 | 633 | -416.4462 | [13 empty] | 40098.1035 | 59.89 | 3815.0098 | 335 | -215.5982 | 16 | 127.5 | 10 | 0 | -103 | 7584.15 | 88.0005
| 40098.1035 | 59.889 | 3811.8384 |  |  |  | 88.8 | 90.5952 |  | 0.62417 | 3796.767 | 3792.4886 | 3777.7898 | 3705.3248 | 3689.7206 | 633 | [6 empty] | 0 | 633 | -413.7258 | [13 empty] | 40098.1035 | 59.889 | 3811.8384 | 335 | -218.3273 | 16 | 128 | 10 | 0 | -103 | 7584.48 | 88.8
| 40098.1036 | 59.889 | 3811.8384 |  |  |  | 88.8 | 89.9669 |  | 0.62417 | 3796.7628 | 3792.8537 | 3778.1477 | 3705.949 | 3690.0327 | 633 | [6 empty] | 0 | 633 | -413.7258 | [13 empty] | 40098.1036 | 59.889 | 3811.8384 | 335 | -218.3273 | 16 | 128 | 10 | 0 | -103 | 7584.48 | 88.8
| 40098.1036 | 59.899 | 3806.9722 |  |  |  | 80.8014 | 86.759 |  | 0.62417 | 3794.1791 | 3793.1151 | 3778.4446 | 3706.5732 | 3690.3448 | 633 | [6 empty] | 0 | 633 | -442.6525 | [13 empty] | 40098.1036 | 59.899 | 3806.9722 | 335 | -218.3273 | 16 | 128.5 | 10 | 0 | -103 | 7584.81 | 80.8014
| 40098.1036 | 59.899 | 3806.9722 |  |  |  | 80.8014 | 84.6738 |  | 0.62417 | 3792.7181 | 3793.3671 | 3778.7041 | 3707.1974 | 3690.6568 | 633 | [6 empty] | 0 | 633 | -442.6525 | [13 empty] | 40098.1036 | 59.899 | 3806.9722 | 335 | -218.3273 | 16 | 128.5 | 10 | 0 | -103 | 7584.81 | 80.8014
| 40098.1036 | 59.902 | 3804.1885 |  |  |  | 78.3997 | 82.4779 |  | 0.62417 | 3791.1463 | 3793.5603 | 3778.9263 | 3707.8215 | 3690.9689 | 633 | [6 empty] | 0 | 633 | -452.1448 | [13 empty] | 40098.1036 | 59.902 | 3804.1885 | 335 | -218.3273 | 16 | 129 | 10 | 0 | -103 | 7585.14 | 78.3997
| 40098.1037 | 59.902 | 3804.1885 |  |  |  | 78.3997 | 81.0505 |  | 0.62417 | 3790.3431 | 3793.7468 | 3779.1266 | 3708.4457 | 3691.281 | 633 | [6 empty] | 0 | 633 | -452.1448 | [13 empty] | 40098.1037 | 59.902 | 3804.1885 | 335 | -218.3273 | 16 | 129 | 10 | 0 | -103 | 7585.14 | 78.3997
| 40098.1037 | 59.904 | 3793.9751 |  |  |  | 76.8005 | 79.563 |  | 0.62417 | 3789.4798 | 3793.7507 | 3779.3051 | 3709.0699 | 3691.5931 | 633 | [6 empty] | 0 | 633 | -458.694 | [13 empty] | 40098.1037 | 59.904 | 3793.9751 | 335 | -218.3273 | 16 | 129.5 | 10 | 0 | -103 | 7585.47 | 76.8005
| 40098.1037 | 59.904 | 3793.9751 |  |  |  | 76.8005 | 78.5961 |  | 0.62417 | 3789.1371 | 3793.7545 | 3779.4717 | 3709.694 | 3691.9052 | 633 | [6 empty] | 0 | 633 | -458.694 | [13 empty] | 40098.1037 | 59.904 | 3793.9751 | 335 | -218.3273 | 16 | 129.5 | 10 | 0 | -103 | 7585.47 | 76.8005
| 40098.1037 | 59.911 | 3791.502 |  |  |  | 71.2006 | 76.0077 |  | 0.62417 | 3787.1728 | 3793.717 | 3779.6001 | 3710.3182 | 3692.2173 | 633 | [6 empty] | 0 | 633 | -483.2042 | [13 empty] | 40098.1037 | 59.911 | 3791.502 | 335 | -218.3273 | 16 | 130 | 10 | 0 | -103 | 7585.8 | 71.2006
| 40098.1037 | 59.911 | 3791.502 |  |  |  | 71.2006 | 74.3252 |  | 0.62417 | 3786.1145 | 3793.6807 | 3779.7069 | 3710.9424 | 3692.5294 | 633 | [6 empty] | 0 | 633 | -483.2042 | [13 empty] | 40098.1037 | 59.911 | 3791.502 | 335 | -218.3273 | 16 | 130 | 10 | 0 | -103 | 7585.8 | 71.2006
| 40098.1038 | 59.916 | 3788.1321 |  |  |  | 67.1997 | 71.8313 |  | 0.62417 | 3784.2447 | 3793.5912 | 3779.7801 | 3711.5665 | 3692.8414 | 633 | [6 empty] | 0 | 633 | -502.3831 | [13 empty] | 40098.1038 | 59.916 | 3788.1321 | 335 | -217.3794 | 16 | 130.5 | 10 | 0 | -103 | 7586.13 | 67.1997
| 40098.1038 | 59.916 | 3788.1321 |  |  |  | 67.1997 | 70.2102 |  | 0.62417 | 3783.2478 | 3793.5045 | 3779.8351 | 3712.1907 | 3693.1535 | 633 | [6 empty] | 0 | 633 | -502.3831 | [13 empty] | 40098.1038 | 59.916 | 3788.1321 | 335 | -217.3794 | 16 | 130.5 | 10 | 0 | -103 | 7586.13 | 67.1997
| 40098.1038 | 59.918 | 3783.0283 |  |  |  | 65.6006 | 68.5969 |  | 0.62417 | 3782.2586 | 3793.3408 | 3779.873 | 3712.8149 | 3693.4656 | 633 | [6 empty] | 0 | 633 | -510.4816 | [13 empty] | 40098.1038 | 59.918 | 3783.0283 | 335 | -217.3794 | 16 | 131 | 10 | 0 | -103 | 7586.46 | 65.6006
| 40098.1038 | 59.918 | 3783.0283 |  |  |  | 65.6006 | 67.5482 |  | 0.62417 | 3781.8341 | 3793.1822 | 3779.9032 | 3713.4391 | 3693.7777 | 633 | [6 empty] | 0 | 633 | -510.4816 | [13 empty] | 40098.1038 | 59.918 | 3783.0283 | 335 | -217.3794 | 16 | 131 | 10 | 0 | -103 | 7586.46 | 65.6006
| 40098.1039 | 59.921 | 3776.3584 |  |  |  | 63.1989 | 66.0259 |  | 0.62417 | 3780.936 | 3792.9273 | 3779.9188 | 3714.0632 | 3694.0898 | 633 | [6 empty] | 0 | 633 | -523.1475 | [13 empty] | 40098.1039 | 59.921 | 3776.3584 | 335 | -217.3794 | 16 | 131.5 | 10 | 0 | -103 | 7586.79 | 63.1989
| 40098.1039 | 59.921 | 3776.3584 |  |  |  | 63.1989 | 65.0364 |  | 0.62417 | 3780.5707 | 3792.68 | 3779.9285 | 3714.6874 | 3694.4019 | 633 | [6 empty] | 0 | 633 | -523.1475 | [13 empty] | 40098.1039 | 59.921 | 3776.3584 | 335 | -217.3794 | 16 | 131.5 | 10 | 0 | -103 | 7586.79 | 63.1989
| 40098.1039 | 59.917 | 3774.6042 |  |  |  | 66.4001 | 65.5137 |  | 0.62417 | 3781.6722 | 3792.4141 | 3779.9542 | 3715.3116 | 3694.7139 | 633 | [6 empty] | 0 | 633 | -506.4 | [13 empty] | 40098.1039 | 59.917 | 3774.6042 | 335 | -217.3794 | 16 | 132 | 10 | 0 | -103 | 7587.12 | 66.4001
| 40098.1039 | 59.917 | 3774.6042 |  |  |  | 66.4001 | 65.824 |  | 0.62417 | 3782.6066 | 3792.156 | 3779.9926 | 3715.9357 | 3695.026 | 633 | [6 empty] | 0 | 633 | -506.4 | [13 empty] | 40098.1039 | 59.917 | 3774.6042 | 335 | -217.3794 | 16 | 132 | 10 | 0 | -103 | 7587.12 | 66.4001
| 40098.104 | 59.921 | 3773.9578 |  |  |  | 63.1989 | 64.9052 |  | 0.62417 | 3782.312 | 3791.8961 | 3780.0258 | 3716.5599 | 3695.3381 | 633 | [6 empty] | 0 | 633 | -523.1475 | [13 empty] | 40098.104 | 59.921 | 3773.9578 | 335 | -217.3794 | 16 | 132.5 | 10 | 0 | -103 | 7587.45 | 63.1989
| 40098.104 | 59.921 | 3773.9578 |  |  |  | 63.1989 | 64.308 |  | 0.62417 | 3782.339 | 3791.6434 | 3780.0583 | 3717.1841 | 3695.6502 | 633 | [6 empty] | 0 | 633 | -523.1475 | [13 empty] | 40098.104 | 59.921 | 3773.9578 | 335 | -217.3794 | 16 | 132.5 | 10 | 0 | -103 | 7587.45 | 63.1989
| 40098.104 | 59.926 | 3771.6704 |  |  |  | 59.201 | 62.5205 |  | 0.62417 | 3781.1757 | 3791.366 | 3780.0739 | 3717.8083 | 3695.9623 | 633 | [6 empty] | 0 | 633 | -545.6843 | [13 empty] | 40098.104 | 59.926 | 3771.6704 | 335 | -214.8304 | 16 | 133 | 10 | 0 | -103 | 7587.78 | 59.201
| 40098.104 | 59.926 | 3771.6704 |  |  |  | 59.201 | 61.3587 |  | 0.62417 | 3780.638 | 3791.0962 | 3780.0816 | 3718.4324 | 3696.2744 | 633 | [6 empty] | 0 | 633 | -545.6843 | [13 empty] | 40098.104 | 59.926 | 3771.6704 | 335 | -214.8304 | 16 | 133 | 10 | 0 | -103 | 7587.78 | 59.201
| 40098.1041 | 59.928 | 3768.707 |  |  |  | 57.5989 | 60.0428 |  | 0.62417 | 3779.9463 | 3790.7936 | 3780.0798 | 3719.0566 | 3696.5865 | 633 | [6 empty] | 0 | 633 | -555.2709 | [13 empty] | 40098.1041 | 59.928 | 3768.707 | 335 | -214.8304 | 16 | 133.5 | 10 | 0 | -103 | 7588.11 | 57.5989
| 40098.1041 | 59.928 | 3768.707 |  |  |  | 57.5989 | 59.1874 |  | 0.62417 | 3779.7151 | 3790.4992 | 3780.0749 | 3719.6808 | 3696.8985 | 633 | [6 empty] | 0 | 633 | -555.2709 | [13 empty] | 40098.1041 | 59.928 | 3768.707 | 335 | -214.8304 | 16 | 133.5 | 10 | 0 | -103 | 7588.11 | 57.5989
| 40098.1041 | 59.932 | 3767.021 |  |  |  | 54.4006 | 57.512 |  | 0.62417 | 3778.6639 | 3790.1902 | 3780.0563 | 3720.3049 | 3697.2106 | 633 | [6 empty] | 0 | 633 | -575.4514 | [13 empty] | 40098.1041 | 59.932 | 3767.021 | 335 | -214.8304 | 16 | 134 | 10 | 0 | -103 | 7588.44 | 54.4006
| 40098.1041 | 59.932 | 3767.021 |  |  |  | 54.4006 | 56.423 |  | 0.62417 | 3778.1991 | 3789.8893 | 3780.0322 | 3720.9291 | 3697.5227 | 633 | [6 empty] | 0 | 633 | -575.4514 | [13 empty] | 40098.1041 | 59.932 | 3767.021 | 335 | -214.8304 | 16 | 134 | 10 | 0 | -103 | 7588.44 | 54.4006
| 40098.1041 | 59.928 | 3766.7881 |  |  |  | 57.5989 | 56.8346 |  | 0.62417 | 3779.2348 | 3789.5932 | 3780.022 | 3721.5533 | 3697.8348 | 633 | [6 empty] | 0 | 633 | -555.2709 | [13 empty] | 40098.1041 | 59.928 | 3766.7881 | 335 | -214.8304 | 16 | 134.5 | 10 | 0 | -103 | 7588.77 | 57.5989
| 40098.1042 | 59.928 | 3766.7881 |  |  |  | 57.5989 | 57.1021 |  | 0.62417 | 3780.1264 | 3789.3045 | 3780.0233 | 3722.1774 | 3698.1469 | 633 | [6 empty] | 0 | 633 | -555.2709 | [13 empty] | 40098.1042 | 59.928 | 3766.7881 | 335 | -214.8304 | 16 | 134.5 | 10 | 0 | -103 | 7588.77 | 57.5989
| 40098.1042 | 59.929 | 3765.6716 |  |  |  | 56.7993 | 56.9961 |  | 0.62417 | 3780.6446 | 3789.0091 | 3780.0311 | 3722.8016 | 3698.459 | 633 | [6 empty] | 0 | 633 | -560.1821 | [13 empty] | 40098.1042 | 59.929 | 3765.6716 | 335 | -214.8304 | 16 | 135 | 10 | 0 | -103 | 7589.1 | 56.7993
| 40098.1042 | 59.929 | 3765.6716 |  |  |  | 56.7993 | 56.9272 |  | 0.62417 | 3781.1999 | 3788.721 | 3780.0455 | 3723.4258 | 3698.7711 | 633 | [6 empty] | 0 | 633 | -560.1821 | [13 empty] | 40098.1042 | 59.929 | 3765.6716 | 335 | -214.8304 | 16 | 135 | 10 | 0 | -103 | 7589.1 | 56.7993
| 40098.1042 | 59.933 | 3764.2427 |  |  |  | 53.6011 | 55.7631 |  | 0.62417 | 3780.6599 | 3788.4224 | 3780.053 | 3724.05 | 3699.0831 | 633 | [6 empty] | 0 | 633 | -580.7278 | [13 empty] | 40098.1042 | 59.933 | 3764.2427 | 335 | -227.6559 | 16 | 135.5 | 10 | 0 | -103 | 7589.43 | 53.6011
| 40098.1043 | 59.933 | 3764.2427 |  |  |  | 53.6011 | 55.0064 |  | 0.62417 | 3780.5274 | 3788.1311 | 3780.0587 | 3724.6741 | 3699.3952 | 633 | [6 empty] | 0 | 633 | -580.7278 | [13 empty] | 40098.1043 | 59.933 | 3764.2427 | 335 | -227.6559 | 16 | 135.5 | 10 | 0 | -103 | 7589.43 | 53.6011
| 40098.1043 | 59.937 | 3762.9353 |  |  |  | 50.3998 | 53.3941 |  | 0.62417 | 3779.5393 | 3787.8312 | 3780.0525 | 3725.2983 | 3699.7073 | 633 | [6 empty] | 0 | 633 | -602.8598 | [13 empty] | 40098.1043 | 59.937 | 3762.9353 | 335 | -227.6559 | 16 | 136 | 10 | 0 | -103 | 7589.76 | 50.3998
| 40098.1043 | 59.937 | 3762.9353 |  |  |  | 50.3998 | 52.3461 |  | 0.62417 | 3779.1154 | 3787.5383 | 3780.0415 | 3725.9225 | 3700.0194 | 633 | [6 empty] | 0 | 633 | -602.8598 | [13 empty] | 40098.1043 | 59.937 | 3762.9353 | 335 | -227.6559 | 16 | 136 | 10 | 0 | -103 | 7589.76 | 50.3998
| 40098.1043 | 59.949 | 3753.9224 |  |  |  | 40.799 | 48.3046 |  | 0.62417 | 3775.6981 | 3787.1474 | 3779.991 | 3726.5466 | 3700.3315 | 633 | [6 empty] | 0 | 633 | -680.6561 | [13 empty] | 40098.1043 | 59.949 | 3753.9224 | 335 | -227.6559 | 0 | 136.5 | 10 | 0 | -103 | 7590.09 | 40.799
| 40098.1044 | 59.949 | 3753.9224 |  |  |  | 40.799 | 45.6776 |  | 0.62417 | 3773.6953 | 3786.7655 | 3779.9186 | 3727.1708 | 3700.6436 | 633 | [6 empty] | 0 | 633 | -680.6561 | [13 empty] | 40098.1044 | 59.949 | 3753.9224 | 335 | -227.6559 | 0 | 136.5 | 10 | 0 | -103 | 7590.09 | 40.799
| 40098.1044 | 59.942 | 3746.8887 |  |  |  | 46.3989 | 45.9301 |  | 0.62417 | 3774.5719 | 3786.3124 | 3779.8579 | 3727.795 | 3700.9557 | 633 | [6 empty] | 0 | 633 | -633.0097 | [13 empty] | 40098.1044 | 59.942 | 3746.8887 | 335 | -227.6559 | 0 | 137 | 10 | 0 | -103 | 7590.42 | 46.3989
| 40098.1044 | 59.942 | 3746.8887 |  |  |  | 46.3989 | 46.0942 |  | 0.62417 | 3775.3602 | 3785.8694 | 3779.8073 | 3728.4191 | 3701.2677 | 633 | [6 empty] | 0 | 633 | -633.0097 | [13 empty] | 40098.1044 | 59.942 | 3746.8887 | 335 | -227.6559 | 0 | 137 | 10 | 0 | -103 | 7590.42 | 46.3989
| 40098.1044 | 59.942 | 3749.5933 |  |  |  | 46.3989 | 46.2008 |  | 0.62417 | 3776.0911 | 3785.4663 | 3779.7661 | 3729.0433 | 3701.5798 | 633 | [6 empty] | 0 | 633 | -633.0097 | [13 empty] | 40098.1044 | 59.942 | 3749.5933 | 335 | -227.6559 | 0 | 137.5 | 10 | 0 | -103 | 7590.75 | 46.3989
| 40098.1044 | 59.942 | 3749.5933 |  |  |  | 46.3989 | 46.2702 |  | 0.62417 | 3776.7846 | 3785.0721 | 3779.7333 | 3729.6675 | 3701.8919 | 633 | [6 empty] | 0 | 633 | -633.0097 | [13 empty] | 40098.1044 | 59.942 | 3749.5933 | 335 | -227.6559 | 0 | 137.5 | 10 | 0 | -103 | 7590.75 | 46.3989
| 40098.1045 | 59.948 | 3746.7061 |  |  |  | 41.5985 | 44.6351 |  | 0.62417 | 3775.7736 | 3784.6551 | 3779.6903 | 3730.2917 | 3702.204 | 633 | [6 empty] | 0 | 633 | -673.4189 | [13 empty] | 40098.1045 | 59.948 | 3746.7061 | 335 | -225.0181 | 0 | 138 | 10 | 0 | -103 | 7591.08 | 41.5985
| 40098.1045 | 59.948 | 3746.7061 |  |  |  | 41.5985 | 43.5723 |  | 0.62417 | 3775.335 | 3784.247 | 3779.6434 | 3730.9158 | 3702.5161 | 633 | [6 empty] | 0 | 633 | -673.4189 | [13 empty] | 40098.1045 | 59.948 | 3746.7061 | 335 | -225.0181 | 0 | 138 | 10 | 0 | -103 | 7591.08 | 41.5985
| 40098.1045 | 59.949 | 3742.7415 |  |  |  | 40.799 | 42.6016 |  | 0.62417 | 3774.9885 | 3783.8055 | 3779.5939 | 3731.54 | 3702.8282 | 633 | [6 empty] | 0 | 633 | -680.6561 | [13 empty] | 40098.1045 | 59.949 | 3742.7415 | 335 | -225.0181 | 0 | 138.5 | 10 | 0 | -103 | 7591.41 | 40.799
| 40098.1045 | 59.949 | 3742.7415 |  |  |  | 40.799 | 41.9707 |  | 0.62417 | 3774.9818 | 3783.3732 | 3779.5454 | 3732.1642 | 3703.1402 | 633 | [6 empty] | 0 | 633 | -680.6561 | [13 empty] | 40098.1045 | 59.949 | 3742.7415 | 335 | -225.0181 | 0 | 138.5 | 10 | 0 | -103 | 7591.41 | 40.799
| 40098.1046 | 59.952 | 3736.1392 |  |  |  | 38.4003 | 40.721 |  | 0.62417 | 3774.3563 | 3782.8812 | 3779.4913 | 3732.7883 | 3703.4523 | 633 | [6 empty] | 0 | 633 | -703.3321 | [13 empty] | 40098.1046 | 59.952 | 3736.1392 | 335 | -225.0181 | 0 | 139 | 10 | 0 | -103 | 7591.74 | 38.4003
| 40098.1046 | 59.952 | 3736.1392 |  |  |  | 38.4003 | 39.9088 |  | 0.62417 | 3774.1682 | 3782.3993 | 3779.4364 | 3733.4125 | 3703.7644 | 633 | [6 empty] | 0 | 633 | -703.3321 | [13 empty] | 40098.1046 | 59.952 | 3736.1392 | 335 | -225.0181 | 0 | 139 | 10 | 0 | -103 | 7591.74 | 38.4003
| 40098.1046 | 59.951 | 3727.8384 |  |  |  | 39.1998 | 39.6606 |  | 0.62417 | 3774.5442 | 3781.8426 | 3779.3865 | 3734.0367 | 3704.0765 | 633 | [6 empty] | 0 | 633 | -695.6074 | [13 empty] | 40098.1046 | 59.951 | 3727.8384 | 335 | -225.0181 | 0 | 139.5 | 10 | 0 | -103 | 7592.07 | 39.1998
| 40098.1046 | 59.951 | 3727.8384 |  |  |  | 39.1998 | 39.4994 |  | 0.62417 | 3775.0071 | 3781.2971 | 3779.3423 | 3734.6609 | 3704.3886 | 633 | [6 empty] | 0 | 633 | -695.6074 | [13 empty] | 40098.1046 | 59.951 | 3727.8384 | 335 | -225.0181 | 0 | 139.5 | 10 | 0 | -103 | 7592.07 | 39.1998
| 40098.1047 | 59.952 | 3722.6489 |  |  |  | 38.4003 | 39.1147 |  | 0.62417 | 3775.2466 | 3780.7106 | 3779.3013 | 3735.285 | 3704.7007 | 633 | [6 empty] | 0 | 633 | -703.3321 | [13 empty] | 40098.1047 | 59.952 | 3722.6489 | 335 | -225.0181 | 0 | 140 | 10 | 0 | -103 | 7592.4 | 38.4003
| 40098.1047 | 59.952 | 3722.6489 |  |  |  | 38.4003 | 38.8646 |  | 0.62417 | 3775.6207 | 3780.1357 | 3779.2649 | 3735.9092 | 3705.0128 | 633 | [6 empty] | 0 | 633 | -703.3321 | [13 empty] | 40098.1047 | 59.952 | 3722.6489 | 335 | -225.0181 | 0 | 140 | 10 | 0 | -103 | 7592.4 | 38.4003
| 40098.1047 | 59.955 | 3717.9961 |  |  |  | 35.9985 | 37.8615 |  | 0.62417 | 3775.2418 | 3779.5265 | 3779.2254 | 3736.5334 | 3705.3248 | 633 | [6 empty] | 0 | 633 | -727.6031 | [13 empty] | 40098.1047 | 59.955 | 3717.9961 | 335 | -228.3652 | 0 | 140.5 | 10 | 0 | -103 | 7592.73 | 35.9985
| 40098.1047 | 59.955 | 3717.9961 |  |  |  | 35.9985 | 37.2095 |  | 0.62417 | 3775.2139 | 3778.9292 | 3779.1865 | 3737.1575 | 3705.6369 | 633 | [6 empty] | 0 | 633 | -727.6031 | [13 empty] | 40098.1047 | 59.955 | 3717.9961 | 335 | -228.3652 | 0 | 140.5 | 10 | 0 | -103 | 7592.73 | 35.9985
| 40098.1047 | 59.954 | 3715.7527 |  |  |  | 36.8011 | 37.0666 |  | 0.62417 | 3775.6952 | 3778.3217 | 3779.1529 | 3737.7817 | 3705.949 | 633 | [6 empty] | 0 | 633 | -719.308 | [13 empty] | 40098.1047 | 59.954 | 3715.7527 | 335 | -228.3652 | 0 | 141 | 10 | 0 | -103 | 7593.06 | 36.8011
| 40098.1048 | 59.954 | 3715.7527 |  |  |  | 36.8011 | 36.9737 |  | 0.62417 | 3776.2264 | 3777.7258 | 3779.125 | 3738.4059 | 3706.2611 | 633 | [6 empty] | 0 | 633 | -719.308 | [13 empty] | 40098.1048 | 59.954 | 3715.7527 | 335 | -228.3652 | 0 | 141 | 10 | 0 | -103 | 7593.06 | 36.8011
| 40098.1048 | 59.953 | 3713.4836 |  |  |  | 37.6007 | 37.1931 |  | 0.62417 | 3777.0701 | 3777.1197 | 3779.1056 | 3739.03 | 3706.5732 | 633 | [6 empty] | 0 | 633 | -711.2303 | [13 empty] | 40098.1048 | 59.953 | 3713.4836 | 335 | -228.3652 | 0 | 141.5 | 10 | 0 | -103 | 7593.39 | 37.6007
| 40098.1048 | 59.953 | 3713.4836 |  |  |  | 37.6007 | 37.3358 |  | 0.62417 | 3777.8369 | 3776.525 | 3779.0938 | 3739.6542 | 3706.8853 | 633 | [6 empty] | 0 | 633 | -711.2303 | [13 empty] | 40098.1048 | 59.953 | 3713.4836 | 335 | -228.3652 | 0 | 141.5 | 10 | 0 | -103 | 7593.39 | 37.6007
| 40098.1048 | 59.952 | 3710.8101 |  |  |  | 38.4003 | 37.7084 |  | 0.62417 | 3778.8336 | 3775.9165 | 3779.0914 | 3740.2784 | 3707.1974 | 633 | [6 empty] | 0 | 633 | -703.3321 | [13 empty] | 40098.1048 | 59.952 | 3710.8101 | 335 | -228.3652 | 0 | 142 | 10 | 0 | -103 | 7593.72 | 38.4003
| 40098.1049 | 59.952 | 3710.8101 |  |  |  | 38.4003 | 37.9505 |  | 0.62417 | 3779.7 | 3775.3192 | 3779.097 | 3740.9026 | 3707.5094 | 633 | [6 empty] | 0 | 633 | -703.3321 | [13 empty] | 40098.1049 | 59.952 | 3710.8101 | 335 | -228.3652 | 0 | 142 | 10 | 0 | -103 | 7593.72 | 38.4003
| 40098.1049 | 59.954 | 3714.6226 |  |  |  | 36.8011 | 37.5482 |  | 0.62417 | 3779.9219 | 3774.7674 | 3779.1045 | 3741.5267 | 3707.8215 | 633 | [6 empty] | 0 | 633 | -719.308 | [13 empty] | 40098.1049 | 59.954 | 3714.6226 | 335 | -228.3652 | 0 | 142.5 | 10 | 0 | -103 | 7594.05 | 36.8011
| 40098.1049 | 59.954 | 3714.6226 |  |  |  | 36.8011 | 37.2868 |  | 0.62417 | 3780.2846 | 3774.2256 | 3779.1151 | 3742.1509 | 3708.1336 | 633 | [6 empty] | 0 | 633 | -719.308 | [13 empty] | 40098.1049 | 59.954 | 3714.6226 | 335 | -228.3652 | 0 | 142.5 | 10 | 0 | -103 | 7594.05 | 36.8011
| 40098.1049 | 59.957 | 3716.1682 |  |  |  | 34.3994 | 36.2762 |  | 0.62417 | 3779.8982 | 3773.7072 | 3779.1221 | 3742.7751 | 3708.4457 | 633 | [6 empty] | 0 | 633 | -744.7139 | [13 empty] | 40098.1049 | 59.957 | 3716.1682 | 335 | -234.0753 | 0 | 143 | 10 | 0 | -103 | 7594.38 | 34.3994
| 40098.105 | 59.957 | 3716.1682 |  |  |  | 34.3994 | 35.6193 |  | 0.62417 | 3779.8655 | 3773.198 | 3779.1287 | 3743.3992 | 3708.7578 | 633 | [6 empty] | 0 | 633 | -744.7139 | [13 empty] | 40098.105 | 59.957 | 3716.1682 | 335 | -234.0753 | 0 | 143 | 10 | 0 | -103 | 7594.38 | 34.3994
| 40098.105 | 59.954 | 3716.98 |  |  |  | 36.8011 | 36.033 |  | 0.62417 | 3780.9033 | 3772.7049 | 3779.1442 | 3744.0234 | 3709.0699 | 633 | [6 empty] | 0 | 633 | -719.308 | [13 empty] | 40098.105 | 59.954 | 3716.98 | 335 | -234.0753 | 0 | 143.5 | 10 | 0 | -103 | 7594.71 | 36.8011
| 40098.105 | 59.954 | 3716.98 |  |  |  | 36.8011 | 36.3018 |  | 0.62417 | 3781.7963 | 3772.2203 | 3779.1673 | 3744.6476 | 3709.382 | 633 | [6 empty] | 0 | 633 | -719.308 | [13 empty] | 40098.105 | 59.954 | 3716.98 | 335 | -234.0753 | 0 | 143.5 | 10 | 0 | -103 | 7594.71 | 36.8011
| 40098.105 | 59.955 | 3722.3613 |  |  |  | 35.9985 | 36.1957 |  | 0.62417 | 3782.3143 | 3771.7905 | 3779.1944 | 3745.2717 | 3709.694 | 633 | [6 empty] | 0 | 633 | -727.6031 | [13 empty] | 40098.105 | 59.955 | 3722.3613 | 335 | -234.0753 | 0 | 144 | 10 | 0 | -103 | 7595.04 | 35.9985
| 40098.105 | 59.955 | 3722.3613 |  |  |  | 35.9985 | 36.1267 |  | 0.62417 | 3782.8695 | 3771.368 | 3779.2258 | 3745.8959 | 3710.0061 | 633 | [6 empty] | 0 | 633 | -727.6031 | [13 empty] | 40098.105 | 59.955 | 3722.3613 | 335 | -234.0753 | 0 | 144 | 10 | 0 | -103 | 7595.04 | 35.9985
| 40098.1051 | 59.961 | 3722.658 |  |  |  | 31.2012 | 34.4027 |  | 0.62417 | 3781.7697 | 3770.9552 | 3779.2474 | 3746.5201 | 3710.3182 | 633 | [6 empty] | 0 | 633 | -781.4691 | [13 empty] | 40098.1051 | 59.961 | 3722.658 | 335 | -234.0753 | 0 | 144.5 | 10 | 0 | -103 | 7595.37 | 31.2012
| 40098.1051 | 59.961 | 3722.658 |  |  |  | 31.2012 | 33.2822 |  | 0.62417 | 3781.2734 | 3770.5494 | 3779.2644 | 3747.1443 | 3710.6303 | 633 | [6 empty] | 0 | 633 | -781.4691 | [13 empty] | 40098.1051 | 59.961 | 3722.658 | 335 | -234.0753 | 0 | 144.5 | 10 | 0 | -103 | 7595.37 | 31.2012
| 40098.1051 | 59.962 | 3722.2776 |  |  |  | 30.3986 | 32.2729 |  | 0.62417 | 3780.8883 | 3770.1471 | 3779.278 | 3747.7684 | 3710.9424 | 633 | [6 empty] | 0 | 633 | -791.2696 | [13 empty] | 40098.1051 | 59.962 | 3722.2776 | 335 | -234.0753 | 0 | 145 | 10 | 0 | -103 | 7595.7 | 30.3986
| 40098.1051 | 59.962 | 3722.2776 |  |  |  | 30.3986 | 31.6169 |  | 0.62417 | 3780.8564 | 3769.7515 | 3779.291 | 3748.3926 | 3711.2545 | 633 | [6 empty] | 0 | 633 | -791.2696 | [13 empty] | 40098.1051 | 59.962 | 3722.2776 | 335 | -234.0753 | 0 | 145 | 10 | 0 | -103 | 7595.7 | 30.3986
| 40098.1052 | 59.966 | 3723.0908 |  |  |  | 27.2003 | 30.0711 |  | 0.62417 | 3779.9348 | 3769.369 | 3779.2963 | 3749.0168 | 3711.5665 | 633 | [6 empty] | 0 | 633 | -832.8924 | [13 empty] | 40098.1052 | 59.966 | 3723.0908 | 335 | -228.7982 | 0 | 145.5 | 10 | 0 | -103 | 7596.03 | 27.2003
| 40098.1052 | 59.966 | 3723.0908 |  |  |  | 27.2003 | 29.0663 |  | 0.62417 | 3779.5542 | 3768.9928 | 3779.2984 | 3749.6409 | 3711.8786 | 633 | [6 empty] | 0 | 633 | -832.8924 | [13 empty] | 40098.1052 | 59.966 | 3723.0908 | 335 | -228.7982 | 0 | 145.5 | 10 | 0 | -103 | 7596.03 | 27.2003
| 40098.1052 | 59.968 | 3723.4346 |  |  |  | 25.6012 | 27.8535 |  | 0.62417 | 3778.9655 | 3768.6254 | 3779.2957 | 3750.2651 | 3712.1907 | 633 | [6 empty] | 0 | 633 | -855.3902 | [13 empty] | 40098.1052 | 59.968 | 3723.4346 | 335 | -228.7982 | 0 | 146 | 10 | 0 | -103 | 7596.36 | 25.6012
| 40098.1052 | 59.968 | 3723.4346 |  |  |  | 25.6012 | 27.0652 |  | 0.62417 | 3778.8014 | 3768.2639 | 3779.2917 | 3750.8893 | 3712.5028 | 633 | [6 empty] | 0 | 633 | -855.3902 | [13 empty] | 40098.1052 | 59.968 | 3723.4346 | 335 | -228.7982 | 0 | 146 | 10 | 0 | -103 | 7596.36 | 25.6012
| 40098.1053 | 59.974 | 3725.4028 |  |  |  | 20.8008 | 24.8727 |  | 0.62417 | 3777.233 | 3767.9237 | 3779.2754 | 3751.5135 | 3712.8149 | 633 | [6 empty] | 0 | 633 | -930.8715 | [13 empty] | 40098.1053 | 59.974 | 3725.4028 | 335 | -228.7982 | 0 | 146.5 | 10 | 0 | -103 | 7596.69 | 20.8008
| 40098.1053 | 59.974 | 3725.4028 |  |  |  | 20.8008 | 23.4475 |  | 0.62417 | 3776.432 | 3767.5889 | 3779.253 | 3752.1376 | 3713.127 | 633 | [6 empty] | 0 | 633 | -930.8715 | [13 empty] | 40098.1053 | 59.974 | 3725.4028 | 335 | -228.7982 | 0 | 146.5 | 10 | 0 | -103 | 7596.69 | 20.8008
| 40098.1053 | 59.969 | 3728.053 |  |  |  | 24.7986 | 23.9204 |  | 0.62417 | 3777.5291 | 3767.28 | 3779.2395 | 3752.7618 | 3713.4391 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.1053 | 59.969 | 3728.053 | 335 | -228.7982 | 0 | 147 | 10 | 0 | -103 | 7597.02 | 24.7986
| 40098.1053 | 59.969 | 3728.053 |  |  |  | 24.7986 | 24.2278 |  | 0.62417 | 3778.4606 | 3766.9759 | 3779.2335 | 3753.386 | 3713.7511 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.1053 | 59.969 | 3728.053 | 335 | -228.7982 | 0 | 147 | 10 | 0 | -103 | 7597.02 | 24.7986
| 40098.1053 | 59.97 | 3732.53 |  |  |  | 23.999 | 24.1477 |  | 0.62417 | 3779.0047 | 3766.7109 | 3779.2317 | 3754.0101 | 3714.0632 | 633 | [6 empty] | 0 | 633 | -879.1838 | [13 empty] | 40098.1053 | 59.97 | 3732.53 | 335 | -228.7982 | 0 | 147.5 | 10 | 0 | -103 | 7597.35 | 23.999
| 40098.1054 | 59.97 | 3732.53 |  |  |  | 23.999 | 24.0957 |  | 0.62417 | 3779.5769 | 3766.45 | 3779.2344 | 3754.6343 | 3714.3753 | 633 | [6 empty] | 0 | 633 | -879.1838 | [13 empty] | 40098.1054 | 59.97 | 3732.53 | 335 | -228.7982 | 0 | 147.5 | 10 | 0 | -103 | 7597.35 | 23.999
| 40098.1054 | 59.973 | 3736.5352 |  |  |  | 21.6003 | 23.2223 |  | 0.62417 | 3779.3277 | 3766.2234 | 3779.2351 | 3755.2585 | 3714.6874 | 633 | [6 empty] | 0 | 633 | -917.3881 | [13 empty] | 40098.1054 | 59.973 | 3736.5352 | 335 | -229.467 | 0 | 148 | 10 | 0 | -103 | 7597.68 | 21.6003
| 40098.1054 | 59.973 | 3736.5352 |  |  |  | 21.6003 | 22.6546 |  | 0.62417 | 3779.3842 | 3766.0002 | 3779.2362 | 3755.8826 | 3714.9995 | 633 | [6 empty] | 0 | 633 | -917.3881 | [13 empty] | 40098.1054 | 59.973 | 3736.5352 | 335 | -229.467 | 0 | 148 | 10 | 0 | -103 | 7597.68 | 21.6003
| 40098.1054 | 59.976 | 3736.8218 |  |  |  | 19.1986 | 21.445 |  | 0.62417 | 3778.7987 | 3765.7824 | 3779.2329 | 3756.5068 | 3715.3116 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1054 | 59.976 | 3736.8218 | 335 | -229.467 | 0 | 148.5 | 10 | 0 | -103 | 7598.01 | 19.1986
| 40098.1055 | 59.976 | 3736.8218 |  |  |  | 19.1986 | 20.6588 |  | 0.62417 | 3778.6367 | 3765.5679 | 3779.2285 | 3757.131 | 3715.6237 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1055 | 59.976 | 3736.8218 | 335 | -229.467 | 0 | 148.5 | 10 | 0 | -103 | 7598.01 | 19.1986
| 40098.1055 | 59.978 | 3739.9438 |  |  |  | 17.5995 | 19.588 |  | 0.62417 | 3778.1901 | 3765.3795 | 3779.2209 | 3757.7552 | 3715.9357 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1055 | 59.978 | 3739.9438 | 335 | -229.467 | 0 | 149 | 10 | 0 | -103 | 7598.34 | 17.5995
| 40098.1055 | 59.978 | 3739.9438 |  |  |  | 17.5995 | 18.892 |  | 0.62417 | 3778.1183 | 3765.1938 | 3779.2128 | 3758.3793 | 3716.2478 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1055 | 59.978 | 3739.9438 | 335 | -229.467 | 0 | 149 | 10 | 0 | -103 | 7598.34 | 17.5995
| 40098.1055 | 59.978 | 3741.7937 |  |  |  | 17.5995 | 18.4396 |  | 0.62417 | 3778.29 | 3765.0243 | 3779.2061 | 3759.0035 | 3716.5599 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1055 | 59.978 | 3741.7937 | 335 | -229.467 | 0 | 149.5 | 10 | 0 | -103 | 7598.67 | 17.5995
| 40098.1056 | 59.978 | 3741.7937 |  |  |  | 17.5995 | 18.1456 |  | 0.62417 | 3778.6202 | 3764.8571 | 3779.2019 | 3759.6277 | 3716.872 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1056 | 59.978 | 3741.7937 | 335 | -229.467 | 0 | 149.5 | 10 | 0 | -103 | 7598.67 | 17.5995
| 40098.1056 | 59.978 | 3746.6079 |  |  |  | 17.5995 | 17.9545 |  | 0.62417 | 3779.0532 | 3764.7268 | 3779.2009 | 3760.2518 | 3717.1841 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1056 | 59.978 | 3746.6079 | 335 | -229.467 | 0 | 150 | 10 | 0 | -103 | 7599 | 17.5995
| 40098.1056 | 59.978 | 3746.6079 |  |  |  | 17.5995 | 17.8302 |  | 0.62417 | 3779.5531 | 3764.5983 | 3779.2034 | 3760.876 | 3717.4962 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1056 | 59.978 | 3746.6079 | 335 | -229.467 | 0 | 150 | 10 | 0 | -103 | 7599 | 17.5995
| 40098.1056 | 59.98 | 3750.7163 |  |  |  | 16.0004 | 17.1898 |  | 0.62417 | 3779.5368 | 3764.5005 | 3779.2057 | 3761.5002 | 3717.8083 | 633 | [6 empty] | 0 | 633 | -1020.9632 | [13 empty] | 40098.1056 | 59.98 | 3750.7163 | 335 | -228.9802 | 0 | 150.5 | 10 | 0 | -103 | 7599.33 | 16.0004
| 40098.1056 | 59.98 | 3750.7163 |  |  |  | 16.0004 | 16.7735 |  | 0.62417 | 3779.7447 | 3764.4041 | 3779.2095 | 3762.1243 | 3718.1203 | 633 | [6 empty] | 0 | 633 | -1020.9632 | [13 empty] | 40098.1056 | 59.98 | 3750.7163 | 335 | -228.9802 | 0 | 150.5 | 10 | 0 | -103 | 7599.33 | 16.0004
| 40098.1057 | 59.981 | 3752.7476 |  |  |  | 15.2008 | 16.223 |  | 0.62417 | 3779.8185 | 3764.3232 | 3779.2137 | 3762.7485 | 3718.4324 | 633 | [6 empty] | 0 | 633 | -1037.6909 | [13 empty] | 40098.1057 | 59.981 | 3752.7476 | 335 | -228.9802 | 0 | 151 | 10 | 0 | -103 | 7599.66 | 15.2008
| 40098.1057 | 59.981 | 3752.7476 |  |  |  | 15.2008 | 15.8653 |  | 0.62417 | 3780.0849 | 3764.2433 | 3779.2197 | 3763.3727 | 3718.7445 | 633 | [6 empty] | 0 | 633 | -1037.6909 | [13 empty] | 40098.1057 | 59.981 | 3752.7476 | 335 | -228.9802 | 0 | 151 | 10 | 0 | -103 | 7599.66 | 15.2008
| 40098.1057 | 59.979 | 3756.4072 |  |  |  | 16.7999 | 16.1924 |  | 0.62417 | 3781.0362 | 3764.1897 | 3779.2322 | 3763.9969 | 3719.0566 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.1057 | 59.979 | 3756.4072 | 335 | -228.9802 | 0 | 151.5 | 10 | 0 | -103 | 7599.99 | 16.7999
| 40098.1057 | 59.979 | 3756.4072 |  |  |  | 16.7999 | 16.405 |  | 0.62417 | 3781.873 | 3764.1367 | 3779.2501 | 3764.621 | 3719.3687 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.1057 | 59.979 | 3756.4072 | 335 | -228.9802 | 0 | 151.5 | 10 | 0 | -103 | 7599.99 | 16.7999
| 40098.1058 | 59.979 | 3760.4053 |  |  |  | 16.7999 | 16.5432 |  | 0.62417 | 3782.6353 | 3764.1115 | 3779.273 | 3765.2452 | 3719.6808 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.1058 | 59.979 | 3760.4053 | 335 | -228.9802 | 0 | 152 | 10 | 0 | -103 | 7600.32 | 16.7999
| 40098.1058 | 59.979 | 3760.4053 |  |  |  | 16.7999 | 16.6331 |  | 0.62417 | 3783.3494 | 3764.0866 | 3779.3004 | 3765.8694 | 3719.9928 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.1058 | 59.979 | 3760.4053 | 335 | -228.9802 | 0 | 152 | 10 | 0 | -103 | 7600.32 | 16.7999
| 40098.1058 | 59.983 | 3761.407 |  |  |  | 13.5986 | 15.571 |  | 0.62417 | 3782.9115 | 3764.0688 | 3779.3244 | 3766.4935 | 3720.3049 | 633 | [6 empty] | 0 | 633 | -1072.9158 | [13 empty] | 40098.1058 | 59.983 | 3761.407 | 335 | -228.9802 | 0 | 152.5 | 10 | 0 | -103 | 7600.65 | 13.5986
| 40098.1058 | 59.983 | 3761.407 |  |  |  | 13.5986 | 14.8807 |  | 0.62417 | 3782.8453 | 3764.0512 | 3779.3478 | 3767.1177 | 3720.617 | 633 | [6 empty] | 0 | 633 | -1072.9158 | [13 empty] | 40098.1058 | 59.983 | 3761.407 | 335 | -228.9802 | 0 | 152.5 | 10 | 0 | -103 | 7600.65 | 13.5986
| 40098.1059 | 59.988 | 3763.2122 |  |  |  | 9.6008 | 13.0327 |  | 0.62417 | 3781.6215 | 3764.0456 | 3779.3627 | 3767.7419 | 3720.9291 | 633 | [6 empty] | 0 | 633 | -1172.2037 | [13 empty] | 40098.1059 | 59.988 | 3763.2122 | 335 | -219.9756 | 0 | 153 | 10 | 0 | -103 | 7600.98 | 9.6008
| 40098.1059 | 59.988 | 3763.2122 |  |  |  | 9.6008 | 11.8316 |  | 0.62417 | 3781.0445 | 3764.0402 | 3779.3737 | 3768.3661 | 3721.2412 | 633 | [6 empty] | 0 | 633 | -1172.2037 | [13 empty] | 40098.1059 | 59.988 | 3763.2122 | 335 | -219.9756 | 0 | 153 | 10 | 0 | -103 | 7600.98 | 9.6008
| 40098.1059 | 59.987 | 3766.0852 |  |  |  | 10.4004 | 11.3307 |  | 0.62417 | 3781.1678 | 3764.0535 | 3779.3854 | 3768.9902 | 3721.5533 | 633 | [6 empty] | 0 | 633 | -1150.9027 | [13 empty] | 40098.1059 | 59.987 | 3766.0852 | 335 | -219.9756 | 0 | 153.5 | 10 | 0 | -103 | 7601.31 | 10.4004
| 40098.1059 | 59.987 | 3766.0852 |  |  |  | 10.4004 | 11.0051 |  | 0.62417 | 3781.4664 | 3764.0666 | 3779.3988 | 3769.6144 | 3721.8654 | 633 | [6 empty] | 0 | 633 | -1150.9027 | [13 empty] | 40098.1059 | 59.987 | 3766.0852 | 335 | -219.9756 | 0 | 153.5 | 10 | 0 | -103 | 7601.31 | 10.4004
| 40098.1059 | 59.991 | 3767.251 |  |  |  | 7.1991 | 9.673 |  | 0.62417 | 3780.7584 | 3764.087 | 3779.4075 | 3770.2386 | 3722.1774 | 633 | [6 empty] | 0 | 633 | -1241.2084 | [13 empty] | 40098.1059 | 59.991 | 3767.251 | 335 | -219.9756 | 0 | 154 | 10 | 0 | -103 | 7601.64 | 7.1991
| 40098.106 | 59.991 | 3767.251 |  |  |  | 7.1991 | 8.8071 |  | 0.62417 | 3780.5168 | 3764.1071 | 3779.4146 | 3770.8627 | 3722.4895 | 633 | [6 empty] | 0 | 633 | -1241.2084 | [13 empty] | 40098.106 | 59.991 | 3767.251 | 335 | -219.9756 | 0 | 154 | 10 | 0 | -103 | 7601.64 | 7.1991
| 40098.106 | 59.992 | 3768.6335 |  |  |  | 6.3995 | 7.9645 |  | 0.62417 | 3780.2983 | 3764.1358 | 3779.4202 | 3771.4869 | 3722.8016 | 633 | [6 empty] | 0 | 633 | -1266.0193 | [13 empty] | 40098.106 | 59.992 | 3768.6335 | 335 | -219.9756 | 0 | 154.5 | 10 | 0 | -103 | 7601.97 | 6.3995
| 40098.106 | 59.992 | 3768.6335 |  |  |  | 6.3995 | 7.4167 |  | 0.62417 | 3780.3747 | 3764.1641 | 3779.4262 | 3772.1111 | 3723.1137 | 633 | [6 empty] | 0 | 633 | -1266.0193 | [13 empty] | 40098.106 | 59.992 | 3768.6335 | 335 | -219.9756 | 0 | 154.5 | 10 | 0 | -103 | 7601.97 | 6.3995
| 40098.106 | 59.989 | 3772.4446 |  |  |  | 8.8013 | 7.9013 |  | 0.62417 | 3781.4835 | 3764.2158 | 3779.439 | 3772.7352 | 3723.4258 | 633 | [6 empty] | 0 | 633 | -1194.308 | [13 empty] | 40098.106 | 59.989 | 3772.4446 | 335 | -219.9756 | 0 | 155 | 10 | 0 | -103 | 7602.3 | 8.8013
| 40098.1061 | 59.989 | 3772.4446 |  |  |  | 8.8013 | 8.2163 |  | 0.62417 | 3782.4226 | 3764.2669 | 3779.4575 | 3773.3594 | 3723.7379 | 633 | [6 empty] | 0 | 633 | -1194.308 | [13 empty] | 40098.1061 | 59.989 | 3772.4446 | 335 | -219.9756 | 0 | 155 | 10 | 0 | -103 | 7602.3 | 8.8013
| 40098.1061 | 59.983 | 3774.6685 |  |  |  | 13.5986 | 10.1001 |  | 0.62417 | 3784.9306 | 3764.3311 | 3779.4913 | 3773.9836 | 3724.05 | 633 | [6 empty] | 0 | 633 | -1072.9158 | [13 empty] | 40098.1061 | 59.983 | 3774.6685 | 335 | -229.0892 | 0 | 155.5 | 10 | 0 | -103 | 7602.63 | 13.5986
| 40098.1061 | 59.983 | 3774.6685 |  |  |  | 13.5986 | 11.3246 |  | 0.62417 | 3786.7793 | 3764.3946 | 3779.536 | 3774.6078 | 3724.362 | 633 | [6 empty] | 0 | 633 | -1072.9158 | [13 empty] | 40098.1061 | 59.983 | 3774.6685 | 335 | -229.0892 | 0 | 155.5 | 10 | 0 | -103 | 7602.63 | 13.5986
| 40098.1061 | 59.988 | 3775.3633 |  |  |  | 9.6008 | 10.7213 |  | 0.62417 | 3786.8001 | 3764.4614 | 3779.5803 | 3775.2319 | 3724.6741 | 633 | [6 empty] | 0 | 633 | -1172.2037 | [13 empty] | 40098.1061 | 59.988 | 3775.3633 | 335 | -229.0892 | 0 | 156 | 10 | 0 | -103 | 7602.96 | 9.6008
| 40098.1062 | 59.988 | 3775.3633 |  |  |  | 9.6008 | 10.3291 |  | 0.62417 | 3787.0321 | 3764.5275 | 3779.6255 | 3775.8561 | 3724.9862 | 633 | [6 empty] | 0 | 633 | -1172.2037 | [13 empty] | 40098.1062 | 59.988 | 3775.3633 | 335 | -229.0892 | 0 | 156 | 10 | 0 | -103 | 7602.96 | 9.6008
| 40098.1062 | 59.996 | 3775.4917 |  |  |  | 3.2013 | 7.8344 |  | 0.62417 | 3785.1616 | 3764.5936 | 3779.6588 | 3776.4803 | 3725.2983 | 633 | [6 empty] | 0 | 633 | -1376.0441 | [13 empty] | 40098.1062 | 59.996 | 3775.4917 | 335 | -229.0892 | 0 | 156.5 | 10 | 0 | -103 | 7603.29 | 3.2013
| 40098.1062 | 59.996 | 3775.4917 |  |  |  | 3.2013 | 6.2128 |  | 0.62417 | 3784.1641 | 3764.6588 | 3779.6858 | 3777.1044 | 3725.6104 | 633 | [6 empty] | 0 | 633 | -1376.0441 | [13 empty] | 40098.1062 | 59.996 | 3775.4917 | 335 | -229.0892 | 0 | 156.5 | 10 | 0 | -103 | 7603.29 | 3.2013
| 40098.1062 | 59.999 | 3778.5537 |  |  |  | 0.79956 | 4.3182 |  | 0.62417 | 3782.8937 | 3764.7415 | 3779.7049 | 3777.7286 | 3725.9225 | 633 | [6 empty] | 0 | 633 | -1472.1181 | [13 empty] | 40098.1062 | 59.999 | 3778.5537 | 335 | -229.0892 | 0 | 157 | 10 | 0 | -103 | 7603.62 | 0.79956
| 40098.1062 | 59.999 | 3778.5537 |  |  |  | 0.79956 | 3.0867 |  | 0.62417 | 3782.2863 | 3764.8233 | 3779.7202 | 3778.3528 | 3726.2346 | 633 | [6 empty] | 0 | 633 | -1472.1181 | [13 empty] | 40098.1062 | 59.999 | 3778.5537 | 335 | -229.0892 | 0 | 157 | 10 | 0 | -103 | 7603.62 | 0.79956
| 40098.1063 | 59.999 | 3781.2559 |  |  |  | 0.79956 | 2.2862 |  | 0.62417 | 3782.11 | 3764.9199 | 3779.7343 | 3778.977 | 3726.5466 | 633 | [6 empty] | 0 | 633 | -1472.1181 | [13 empty] | 40098.1063 | 59.999 | 3781.2559 | 335 | -229.0892 | 0 | 157.5 | 10 | 0 | -103 | 7603.95 | 0.79956
| 40098.1063 | 59.999 | 3781.2559 |  |  |  | 0.79956 | 1.7659 |  | 0.62417 | 3782.2139 | 3765.0155 | 3779.7488 | 3779.6011 | 3726.8587 | 633 | [6 empty] | 0 | 633 | -1472.1181 | [13 empty] | 40098.1063 | 59.999 | 3781.2559 | 335 | -229.0892 | 0 | 157.5 | 10 | 0 | -103 | 7603.95 | 0.79956
| 40098.1063 | 59.999 | 3783.092 |  |  |  | 0.79956 | 1.4277 |  | 0.62417 | 3782.4998 | 3765.1206 | 3779.7647 | 3780.2253 | 3727.1708 | 633 | [6 empty] | 0 | 633 | -1472.1181 | [13 empty] | 40098.1063 | 59.999 | 3783.092 | 335 | -229.6633 | 0 | 158 | 10 | 0 | -103 | 7604.28 | 0.79956
| 40098.1063 | 59.999 | 3783.092 |  |  |  | 0.79956 | 1.2078 |  | 0.62417 | 3782.9042 | 3765.2244 | 3779.7829 | 3780.8495 | 3727.4829 | 633 | [6 empty] | 0 | 633 | -1472.1181 | [13 empty] | 40098.1063 | 59.999 | 3783.092 | 335 | -229.6633 | 0 | 158 | 10 | 0 | -103 | 7604.28 | 0.79956
| 40098.1064 | 60.005 | 3784.4209 |  |  |  | -4.0009 | -0.61522 |  | 0 | 3781.0811 | 3765.3348 | 3779.7904 | 3780.8495 | 3727.7914 | 633 | [6 empty] | 0 | 633 | -1710.8687 | [13 empty] | 40098.1064 | 60.005 | 3784.4209 | 335 | -229.6633 | 0 | 158.5 | 10 | 0 | -103 | 7604.61 | -4.0009
| 40098.1064 | 60.005 | 3784.4209 |  |  |  | -4.0009 | -1.8002 |  | 0 | 3779.8962 | 3765.4438 | 3779.791 | 3780.8495 | 3728.0963 | 633 | [6 empty] | 0 | 633 | -1710.8687 | [13 empty] | 40098.1064 | 60.005 | 3784.4209 | 335 | -229.6633 | 0 | 158.5 | 10 | 0 | -103 | 7604.61 | -4.0009
| 40098.1064 | 60.008 | 3785.4626 |  |  |  | -6.3995 | -3.41 |  | 0 | 3778.2864 | 3765.5576 | 3779.7824 | 3780.8495 | 3728.3977 | 633 | [6 empty] | 0 | 633 | -1861.743 | [13 empty] | 40098.1064 | 60.008 | 3785.4626 | 335 | -229.6633 | 0 | 159 | 10 | 0 | -103 | 7604.94 | -6.3995
| 40098.1064 | 60.008 | 3785.4626 |  |  |  | -6.3995 | -4.4563 |  | 0 | 3777.2401 | 3765.67 | 3779.768 | 3780.8495 | 3728.6958 | 633 | [6 empty] | 0 | 633 | -1861.743 | [13 empty] | 40098.1064 | 60.008 | 3785.4626 | 335 | -229.6633 | 0 | 159 | 10 | 0 | -103 | 7604.94 | -6.3995
| 40098.1065 | 60.014 | 3786.3042 |  |  |  | -11.2 | -6.8166 |  | 0 | 3774.8798 | 3765.7859 | 3779.7406 | 3780.8495 | 3728.9904 | 633 | [6 empty] | 0 | 633 | -2260.7241 | [13 empty] | 40098.1065 | 60.014 | 3786.3042 | 335 | -229.6633 | 0 | 159.5 | 10 | 0 | -103 | 7605.27 | -11.2
| 40098.1065 | 60.014 | 3786.3042 |  |  |  | -11.2 | -8.3508 |  | 0 | 3773.3456 | 3765.9006 | 3779.7049 | 3780.8495 | 3729.2818 | 633 | [6 empty] | 0 | 633 | -2260.7241 | [13 empty] | 40098.1065 | 60.014 | 3786.3042 | 335 | -229.6633 | 0 | 159.5 | 10 | 0 | -103 | 7605.27 | -11.2
| 40098.1065 | 60.019 | 3787.5159 |  |  |  | -15.2008 | -10.7483 |  | 0 | 3770.9481 | 3766.0207 | 3779.6562 | 3780.8495 | 3729.5699 | 633 | [6 empty] | 0 | 633 | -2752.3163 | [13 empty] | 40098.1065 | 60.019 | 3787.5159 | 335 | -229.6633 | 0 | 160 | 10 | 0 | -103 | 7605.6 | -15.2008
| 40098.1065 | 60.019 | 3787.5159 |  |  |  | -15.2008 | -12.3067 |  | 0 | 3769.3897 | 3766.1394 | 3779.5995 | 3780.8495 | 3729.8547 | 633 | [6 empty] | 0 | 633 | -2752.3163 | [13 empty] | 40098.1065 | 60.019 | 3787.5159 | 335 | -229.6633 | 0 | 160 | 10 | 0 | -103 | 7605.6 | -15.2008
| 40098.1066 | 60.017 | 3788.0303 |  |  |  | -13.5986 | -12.7589 |  | 0 | 3768.9375 | 3766.2597 | 3779.5409 | 3780.8495 | 3730.1365 | 633 | [6 empty] | 0 | 633 | -2531.8455 | [13 empty] | 40098.1066 | 60.017 | 3788.0303 | 335 | -229.2339 | 0 | 160.5 | 10 | 0 | -103 | 7605.93 | -13.5986
| 40098.1066 | 60.017 | 3788.0303 |  |  |  | -13.5986 | -13.0528 |  | 0 | 3768.6436 | 3766.3787 | 3779.4814 | 3780.8495 | 3730.4151 | 633 | [6 empty] | 0 | 633 | -2531.8455 | [13 empty] | 40098.1066 | 60.017 | 3788.0303 | 335 | -229.2339 | 0 | 160.5 | 10 | 0 | -103 | 7605.93 | -13.5986
| 40098.1066 | 60.019 | 3789.2158 |  |  |  | -15.2008 | -13.8046 |  | 0 | 3767.8918 | 3766.5028 | 3779.4184 | 3780.8495 | 3730.6907 | 633 | [6 empty] | 0 | 633 | -2752.3163 | [13 empty] | 40098.1066 | 60.019 | 3789.2158 | 335 | -229.2339 | 0 | 161 | 10 | 0 | -103 | 7606.26 | -15.2008
| 40098.1066 | 60.019 | 3789.2158 |  |  |  | -15.2008 | -14.2933 |  | 0 | 3767.4031 | 3766.6256 | 3779.3534 | 3780.8495 | 3730.9633 | 633 | [6 empty] | 0 | 633 | -2752.3163 | [13 empty] | 40098.1066 | 60.019 | 3789.2158 | 335 | -229.2339 | 0 | 161 | 10 | 0 | -103 | 7606.26 | -15.2008
| 40098.1066 | 60.024 | 3785.8418 |  |  |  | -19.1986 | -16.0101 |  | 0 | 3765.6862 | 3766.7289 | 3779.2799 | 3780.8495 | 3731.233 | 633 | [6 empty] | 0 | 633 | -3516.3626 | [13 empty] | 40098.1066 | 60.024 | 3785.8418 | 335 | -229.2339 | 0 | 161.5 | 10 | 0 | -103 | 7606.59 | -19.1986
| 40098.1067 | 60.024 | 3785.8418 |  |  |  | -19.1986 | -17.1261 |  | 0 | 3764.5703 | 3766.8311 | 3779.2013 | 3780.8495 | 3731.4997 | 633 | [6 empty] | 0 | 633 | -3516.3626 | [13 empty] | 40098.1067 | 60.024 | 3785.8418 | 335 | -229.2339 | 0 | 161.5 | 10 | 0 | -103 | 7606.59 | -19.1986
| 40098.1067 | 60.021 | 3787.9304 |  |  |  | -16.7999 | -17.0119 |  | 0 | 3764.6844 | 3766.9433 | 3779.1241 | 3780.8495 | 3731.7636 | 633 | [6 empty] | 0 | 633 | -3014.2989 | [13 empty] | 40098.1067 | 60.021 | 3787.9304 | 335 | -229.2339 | 0 | 162 | 10 | 0 | -103 | 7606.92 | -16.7999
| 40098.1067 | 60.021 | 3787.9304 |  |  |  | -16.7999 | -16.9377 |  | 0 | 3764.7586 | 3767.0543 | 3779.0481 | 3780.8495 | 3732.0247 | 633 | [6 empty] | 0 | 633 | -3014.2989 | [13 empty] | 40098.1067 | 60.021 | 3787.9304 | 335 | -229.2339 | 0 | 162 | 10 | 0 | -103 | 7606.92 | -16.7999
| 40098.1067 | 60.024 | 3786.8748 |  |  |  | -19.1986 | -17.729 |  | 0 | 3763.9673 | 3767.1587 | 3778.9687 | 3780.8495 | 3732.2831 | 633 | [6 empty] | 0 | 633 | -3516.3626 | [13 empty] | 40098.1067 | 60.024 | 3786.8748 | 335 | -262.1026 | 0 | 162.5 | 10 | 0 | -103 | 7607.25 | -19.1986
| 40098.1068 | 60.024 | 3786.8748 |  |  |  | -19.1986 | -18.2434 |  | 0 | 3763.453 | 3767.2619 | 3778.8875 | 3780.8495 | 3732.5387 | 633 | [6 empty] | 0 | 633 | -3516.3626 | [13 empty] | 40098.1068 | 60.024 | 3786.8748 | 335 | -262.1026 | 0 | 162.5 | 10 | 0 | -103 | 7607.25 | -19.1986
| 40098.1068 | 60.021 | 3787.3577 |  |  |  | -16.7999 | -17.7382 |  | 0 | 3763.9582 | 3767.3666 | 3778.8097 | 3780.8495 | 3732.7916 | 633 | [6 empty] | 0 | 633 | -3014.2989 | [13 empty] | 40098.1068 | 60.021 | 3787.3577 | 335 | -262.1026 | 0 | 163 | 10 | 0 | -103 | 7607.58 | -16.7999
| 40098.1068 | 60.021 | 3787.3577 |  |  |  | -16.7999 | -17.4098 |  | 0 | 3764.2866 | 3767.4701 | 3778.7344 | 3780.8495 | 3733.0419 | 633 | [6 empty] | 0 | 633 | -3014.2989 | [13 empty] | 40098.1068 | 60.021 | 3787.3577 | 335 | -262.1026 | 0 | 163 | 10 | 0 | -103 | 7607.58 | -16.7999
| 40098.1068 | 60.025 | 3785.614 |  |  |  | -20.0012 | -18.3168 |  | 0 | 3763.3796 | 3767.5637 | 3778.6553 | 3780.8495 | 3733.2896 | 633 | [6 empty] | 0 | 633 | -3723.9038 | [13 empty] | 40098.1068 | 60.025 | 3785.614 | 335 | -262.1026 | 0 | 163.5 | 10 | 0 | -103 | 7607.91 | -20.0012
| 40098.1069 | 60.025 | 3785.614 |  |  |  | -20.0012 | -18.9063 |  | 0 | 3762.79 | 3767.6562 | 3778.5739 | 3780.8495 | 3733.5348 | 633 | [6 empty] | 0 | 633 | -3723.9038 | [13 empty] | 40098.1069 | 60.025 | 3785.614 | 335 | -262.1026 | 0 | 163.5 | 10 | 0 | -103 | 7607.91 | -20.0012
| 40098.1069 | 60.02 | 3785.8037 |  |  |  | -16.0004 | -17.8892 |  | 0 | 3763.8071 | 3767.7488 | 3778.4986 | 3780.8495 | 3733.7774 | 633 | [6 empty] | 0 | 633 | -2877.3565 | [13 empty] | 40098.1069 | 60.02 | 3785.8037 | 335 | -262.717 | 0 | 164 | 10 | 0 | -103 | 7608.24 | -16.0004
| 40098.1069 | 60.02 | 3785.8037 |  |  |  | -16.0004 | -17.2281 |  | 0 | 3764.4682 | 3767.8405 | 3778.4274 | 3780.8495 | 3734.0176 | 633 | [6 empty] | 0 | 633 | -2877.3565 | [13 empty] | 40098.1069 | 60.02 | 3785.8037 | 335 | -262.717 | 0 | 164 | 10 | 0 | -103 | 7608.24 | -16.0004
| 40098.1069 | 60.022 | 3786.8772 |  |  |  | -17.5995 | -17.3581 |  | 0 | 3764.3383 | 3767.9366 | 3778.3562 | 3780.8495 | 3734.2553 | 633 | [6 empty] | 0 | 633 | -3164.9276 | [13 empty] | 40098.1069 | 60.022 | 3786.8772 | 335 | -262.717 | 0 | 164.5 | 10 | 0 | -103 | 7608.57 | -17.5995
| 40098.1069 | 60.022 | 3786.8772 |  |  |  | -17.5995 | -17.4426 |  | 0 | 3764.2538 | 3768.0318 | 3778.2854 | 3780.8495 | 3734.4906 | 633 | [6 empty] | 0 | 633 | -3164.9276 | [13 empty] | 40098.1069 | 60.022 | 3786.8772 | 335 | -262.717 | 0 | 164.5 | 10 | 0 | -103 | 7608.57 | -17.5995
| 40098.107 | 60.022 | 3785.7261 |  |  |  | -17.5995 | -17.4975 |  | 0 | 3764.1989 | 3768.1203 | 3778.2149 | 3780.8495 | 3734.7236 | 633 | [6 empty] | 0 | 633 | -3164.9276 | [13 empty] | 40098.107 | 60.022 | 3785.7261 | 335 | -262.717 | 0 | 165 | 10 | 0 | -103 | 7608.9 | -17.5995
| 40098.107 | 60.022 | 3785.7261 |  |  |  | -17.5995 | -17.5332 |  | 0 | 3764.1632 | 3768.2079 | 3778.145 | 3780.8495 | 3734.9542 | 633 | [6 empty] | 0 | 633 | -3164.9276 | [13 empty] | 40098.107 | 60.022 | 3785.7261 | 335 | -262.717 | 0 | 165 | 10 | 0 | -103 | 7608.9 | -17.5995
| 40098.107 | 60.021 | 3785.821 |  |  |  | -16.7999 | -17.2766 |  | 0 | 3764.4198 | 3768.295 | 3778.0771 | 3780.8495 | 3735.1825 | 633 | [6 empty] | 0 | 633 | -3014.2989 | [13 empty] | 40098.107 | 60.021 | 3785.821 | 335 | -262.717 | 0 | 165.5 | 10 | 0 | -103 | 7609.23 | -16.7999
| 40098.107 | 60.021 | 3785.821 |  |  |  | -16.7999 | -17.1097 |  | 0 | 3764.5866 | 3768.3814 | 3778.0106 | 3780.8495 | 3735.4086 | 633 | [6 empty] | 0 | 633 | -3014.2989 | [13 empty] | 40098.107 | 60.021 | 3785.821 | 335 | -262.717 | 0 | 165.5 | 10 | 0 | -103 | 7609.23 | -16.7999
| 40098.1071 | 60.023 | 3786.2842 |  |  |  | -18.399 | -17.561 |  | 0 | 3764.1354 | 3768.4691 | 3777.9426 | 3780.8495 | 3735.6325 | 633 | [6 empty] | 0 | 633 | -3331.4024 | [13 empty] | 40098.1071 | 60.023 | 3786.2842 | 335 | -262.717 | 0 | 166 | 10 | 0 | -103 | 7609.56 | -18.399
| 40098.1071 | 60.023 | 3786.2842 |  |  |  | -18.399 | -17.8543 |  | 0 | 3763.8421 | 3768.556 | 3777.8738 | 3780.8495 | 3735.8541 | 633 | [6 empty] | 0 | 633 | -3331.4024 | [13 empty] | 40098.1071 | 60.023 | 3786.2842 | 335 | -262.717 | 0 | 166 | 10 | 0 | -103 | 7609.56 | -18.399
| 40098.1071 | 60.019 | 3787.6274 |  |  |  | -15.2008 | -16.9256 |  | 0 | 3764.7708 | 3768.6486 | 3777.8102 | 3780.8495 | 3736.0736 | 633 | [6 empty] | 0 | 633 | -2752.3163 | [13 empty] | 40098.1071 | 60.019 | 3787.6274 | 335 | -260.0165 | 0 | 166.5 | 10 | 0 | -103 | 7609.89 | -15.2008
| 40098.1071 | 60.019 | 3787.6274 |  |  |  | -15.2008 | -16.3219 |  | 0 | 3765.3745 | 3768.7403 | 3777.7501 | 3780.8495 | 3736.291 | 633 | [6 empty] | 0 | 633 | -2752.3163 | [13 empty] | 40098.1071 | 60.019 | 3787.6274 | 335 | -260.0165 | 0 | 166.5 | 10 | 0 | -103 | 7609.89 | -15.2008
| 40098.1072 | 60.018 | 3789.6733 |  |  |  | -14.4012 | -15.6497 |  | 0 | 3766.0467 | 3768.8409 | 3777.6939 | 3780.8495 | 3736.5062 | 633 | [6 empty] | 0 | 633 | -2637.6912 | [13 empty] | 40098.1072 | 60.018 | 3789.6733 | 335 | -260.0165 | 0 | 167 | 10 | 0 | -103 | 7610.22 | -14.4012
| 40098.1072 | 60.018 | 3789.6733 |  |  |  | -14.4012 | -15.2127 |  | 0 | 3766.4836 | 3768.9406 | 3777.6402 | 3780.8495 | 3736.7194 | 633 | [6 empty] | 0 | 633 | -2637.6912 | [13 empty] | 40098.1072 | 60.018 | 3789.6733 | 335 | -260.0165 | 0 | 167 | 10 | 0 | -103 | 7610.22 | -14.4012
| 40098.1072 | 60.018 | 3788.4788 |  |  |  | -14.4012 | -14.9287 |  | 0 | 3766.7677 | 3769.0337 | 3777.5884 | 3780.8495 | 3736.9306 | 633 | [6 empty] | 0 | 633 | -2637.6912 | [13 empty] | 40098.1072 | 60.018 | 3788.4788 | 335 | -260.0165 | 0 | 167.5 | 10 | 0 | -103 | 7610.55 | -14.4012
| 40098.1072 | 60.018 | 3788.4788 |  |  |  | -14.4012 | -14.7441 |  | 0 | 3766.9523 | 3769.1258 | 3777.538 | 3780.8495 | 3737.1397 | 633 | [6 empty] | 0 | 633 | -2637.6912 | [13 empty] | 40098.1072 | 60.018 | 3788.4788 | 335 | -260.0165 | 0 | 167.5 | 10 | 0 | -103 | 7610.55 | -14.4012
| 40098.1072 | 60.019 | 3789.3689 |  |  |  | -15.2008 | -14.9039 |  | 0 | 3766.7924 | 3769.2213 | 3777.4874 | 3780.8495 | 3737.3469 | 633 | [6 empty] | 0 | 633 | -2752.3163 | [13 empty] | 40098.1072 | 60.019 | 3789.3689 | 335 | -260.0165 | 0 | 168 | 10 | 0 | -103 | 7610.88 | -15.2008
| 40098.1073 | 60.019 | 3789.3689 |  |  |  | -15.2008 | -15.0078 |  | 0 | 3766.6885 | 3769.3159 | 3777.4367 | 3780.8495 | 3737.5521 | 633 | [6 empty] | 0 | 633 | -2752.3163 | [13 empty] | 40098.1073 | 60.019 | 3789.3689 | 335 | -260.0165 | 0 | 168 | 10 | 0 | -103 | 7610.88 | -15.2008
| 40098.1073 | 60.015 | 3788.6646 |  |  |  | -11.9995 | -13.9549 |  | 0 | 3767.7414 | 3769.4063 | 3777.3913 | 3780.8495 | 3737.7553 | 633 | [6 empty] | 0 | 633 | -2344.4073 | [13 empty] | 40098.1073 | 60.015 | 3788.6646 | 335 | -260.0165 | 0 | 168.5 | 10 | 0 | -103 | 7611.21 | -11.9995
| 40098.1073 | 60.015 | 3788.6646 |  |  |  | -11.9995 | -13.2705 |  | 0 | 3768.4258 | 3769.4959 | 3777.3496 | 3780.8495 | 3737.9567 | 633 | [6 empty] | 0 | 633 | -2344.4073 | [13 empty] | 40098.1073 | 60.015 | 3788.6646 | 335 | -260.0165 | 0 | 168.5 | 10 | 0 | -103 | 7611.21 | -11.9995
| 40098.1073 | 60.014 | 3790.667 |  |  |  | -11.2 | -12.5458 |  | 0 | 3769.1505 | 3769.5939 | 3777.3117 | 3780.8495 | 3738.1562 | 633 | [6 empty] | 0 | 633 | -2260.7241 | [13 empty] | 40098.1073 | 60.014 | 3790.667 | 335 | -263.8732 | 0 | 169 | 10 | 0 | -103 | 7611.54 | -11.2
| 40098.1074 | 60.014 | 3790.667 |  |  |  | -11.2 | -12.0748 |  | 0 | 3769.6216 | 3769.691 | 3777.2763 | 3780.8495 | 3738.3539 | 633 | [6 empty] | 0 | 633 | -2260.7241 | [13 empty] | 40098.1074 | 60.014 | 3790.667 | 335 | -263.8732 | 0 | 169 | 10 | 0 | -103 | 7611.54 | -11.2
| 40098.1074 | 60.012 | 3790.4111 |  |  |  | -9.6008 | -11.2089 |  | 0 | 3770.4875 | 3769.7861 | 3777.2451 | 3780.8495 | 3738.5497 | 633 | [6 empty] | 0 | 633 | -2110.0859 | [13 empty] | 40098.1074 | 60.012 | 3790.4111 | 335 | -263.8732 | 0 | 169.5 | 10 | 0 | -103 | 7611.87 | -9.6008
| 40098.1074 | 60.012 | 3790.4111 |  |  |  | -9.6008 | -10.6461 |  | 0 | 3771.0503 | 3769.8802 | 3777.2168 | 3780.8495 | 3738.7437 | 633 | [6 empty] | 0 | 633 | -2110.0859 | [13 empty] | 40098.1074 | 60.012 | 3790.4111 | 335 | -263.8732 | 0 | 169.5 | 10 | 0 | -103 | 7611.87 | -9.6008
| 40098.1074 | 60.01 | 3791.5398 |  |  |  | -7.9987 | -9.7195 |  | 0 | 3771.9769 | 3769.9787 | 3777.193 | 3780.8495 | 3738.936 | 633 | [6 empty] | 0 | 633 | -1978.0326 | [13 empty] | 40098.1074 | 60.01 | 3791.5398 | 335 | -263.8732 | 0 | 170 | 10 | 0 | -103 | 7612.2 | -7.9987
| 40098.1075 | 60.01 | 3791.5398 |  |  |  | -7.9987 | -9.1172 |  | 0 | 3772.5792 | 3770.0762 | 3777.1721 | 3780.8495 | 3739.1265 | 633 | [6 empty] | 0 | 633 | -1978.0326 | [13 empty] | 40098.1075 | 60.01 | 3791.5398 | 335 | -263.8732 | 0 | 170 | 10 | 0 | -103 | 7612.2 | -7.9987
| 40098.1075 | 60.007 | 3791.0271 |  |  |  | -5.6 | -7.8862 |  | 0 | 3773.8102 | 3770.1706 | 3777.157 | 3780.8495 | 3739.3153 | 633 | [6 empty] | 0 | 633 | -1808.5793 | [13 empty] | 40098.1075 | 60.007 | 3791.0271 | 335 | -263.8732 | 0 | 170.5 | 10 | 0 | -103 | 7612.53 | -5.6
| 40098.1075 | 60.007 | 3791.0271 |  |  |  | -5.6 | -7.086 |  | 0 | 3774.6104 | 3770.2641 | 3777.1456 | 3780.8495 | 3739.5024 | 633 | [6 empty] | 0 | 633 | -1808.5793 | [13 empty] | 40098.1075 | 60.007 | 3791.0271 | 335 | -263.8732 | 0 | 170.5 | 10 | 0 | -103 | 7612.53 | -5.6
| 40098.1075 | 60.009 | 3791.426 |  |  |  | -7.1991 | -7.1256 |  | 0 | 3774.5708 | 3770.3586 | 3777.1341 | 3780.8495 | 3739.6878 | 633 | [6 empty] | 0 | 633 | -1918.1268 | [13 empty] | 40098.1075 | 60.009 | 3791.426 | 335 | -263.8732 | 0 | 171 | 10 | 0 | -103 | 7612.86 | -7.1991
| 40098.1075 | 60.009 | 3791.426 |  |  |  | -7.1991 | -7.1513 |  | 0 | 3774.5451 | 3770.4523 | 3777.1226 | 3780.8495 | 3739.8716 | 633 | [6 empty] | 0 | 633 | -1918.1268 | [13 empty] | 40098.1075 | 60.009 | 3791.426 | 335 | -263.8732 | 0 | 171 | 10 | 0 | -103 | 7612.86 | -7.1991
| 40098.1076 | 60.003 | 3790.4573 |  |  |  | -2.3987 | -5.4879 |  | 0 | 3776.2085 | 3770.5408 | 3777.1185 | 3780.8495 | 3740.0537 | 633 | [6 empty] | 0 | 633 | -1623.016 | [13 empty] | 40098.1076 | 60.003 | 3790.4573 | 335 | -264.5979 | 0 | 171.5 | 10 | 0 | -103 | 7613.19 | -2.3987
| 40098.1076 | 60.003 | 3790.4573 |  |  |  | -2.3987 | -4.4067 |  | 0 | 3777.2897 | 3770.6285 | 3777.1193 | 3780.8495 | 3740.2342 | 633 | [6 empty] | 0 | 633 | -1623.016 | [13 empty] | 40098.1076 | 60.003 | 3790.4573 | 335 | -264.5979 | 0 | 171.5 | 10 | 0 | -103 | 7613.19 | -2.3987
| 40098.1076 | 59.995 | 3789.585 |  |  |  | 4.0009 | -1.464 |  | 0 | 3780.2323 | 3770.7117 | 3777.1329 | 3780.8495 | 3740.4131 | 633 | [6 empty] | 0 | 633 | -1346.7832 | [13 empty] | 40098.1076 | 59.995 | 3789.585 | 335 | -264.5979 | 0 | 172 | 10 | 0 | -103 | 7613.52 | 4.0009
| 40098.1076 | 59.995 | 3789.585 |  |  |  | 4.0009 | 0.44868 |  | 0 | 3782.145 | 3770.7941 | 3777.1548 | 3780.8495 | 3740.5905 | 633 | [6 empty] | 0 | 633 | -1346.7832 | [13 empty] | 40098.1076 | 59.995 | 3789.585 | 335 | -264.5979 | 0 | 172 | 10 | 0 | -103 | 7613.52 | 4.0009
| 40098.1077 | 59.991 | 3788.105 |  |  |  | 7.1991 | 2.8113 |  | 0 | 3784.5077 | 3770.8693 | 3777.1868 | 3780.8495 | 3740.7663 | 633 | [6 empty] | 0 | 633 | -1241.2084 | [13 empty] | 40098.1077 | 59.991 | 3788.105 | 335 | -264.5979 | 0 | 172.5 | 10 | 0 | -103 | 7613.85 | 7.1991
| 40098.1077 | 59.991 | 3788.105 |  |  |  | 7.1991 | 4.347 |  | 0 | 3786.0434 | 3770.9439 | 3777.2251 | 3780.8495 | 3740.9405 | 633 | [6 empty] | 0 | 633 | -1241.2084 | [13 empty] | 40098.1077 | 59.991 | 3788.105 | 335 | -264.5979 | 0 | 172.5 | 10 | 0 | -103 | 7613.85 | 7.1991
| 40098.1077 | 59.992 | 3788.1895 |  |  |  | 6.3995 | 5.0654 |  | 0 | 3786.7618 | 3771.0183 | 3777.2662 | 3780.8495 | 3741.1133 | 633 | [6 empty] | 0 | 633 | -1266.0193 | [13 empty] | 40098.1077 | 59.992 | 3788.1895 | 335 | -264.5979 | 0 | 173 | 10 | 0 | -103 | 7614.18 | 6.3995
| 40098.1077 | 59.992 | 3788.1895 |  |  |  | 6.3995 | 5.5324 |  | 0 | 3787.2287 | 3771.092 | 3777.309 | 3780.8495 | 3741.2846 | 633 | [6 empty] | 0 | 633 | -1266.0193 | [13 empty] | 40098.1077 | 59.992 | 3788.1895 | 335 | -264.5979 | 0 | 173 | 10 | 0 | -103 | 7614.18 | 6.3995
| 40098.1078 | 59.986 | 3788.54 |  |  |  | 11.2 | 7.516 |  | 0 | 3789.2124 | 3771.1665 | 3777.3599 | 3780.8495 | 3741.4544 | 633 | [6 empty] | 0 | 633 | -1130.3621 | [13 empty] | 40098.1078 | 59.986 | 3788.54 | 335 | -264.5979 | 0 | 173.5 | 10 | 0 | -103 | 7614.51 | 11.2
| 40098.1078 | 59.986 | 3788.54 |  |  |  | 11.2 | 8.8054 |  | 0 | 3790.5018 | 3771.2405 | 3777.4158 | 3780.8495 | 3741.6228 | 633 | [6 empty] | 0 | 633 | -1130.3621 | [13 empty] | 40098.1078 | 59.986 | 3788.54 | 335 | -264.5979 | 0 | 173.5 | 10 | 0 | -103 | 7614.51 | 11.2
| 40098.1078 | 59.984 | 3788.1011 |  |  |  | 12.7991 | 10.2032 |  | 0 | 3791.8995 | 3771.3119 | 3777.4772 | 3780.8495 | 3741.7897 | 633 | [6 empty] | 0 | 633 | -1091.4046 | [13 empty] | 40098.1078 | 59.984 | 3788.1011 | 335 | -262.4159 | 0 | 174 | 10 | 0 | -103 | 7614.84 | 12.7991
| 40098.1078 | 59.984 | 3788.1011 |  |  |  | 12.7991 | 11.1117 |  | 0 | 3792.8081 | 3771.3828 | 3777.5418 | 3780.8495 | 3741.9552 | 633 | [6 empty] | 0 | 633 | -1091.4046 | [13 empty] | 40098.1078 | 59.984 | 3788.1011 | 335 | -262.4159 | 0 | 174 | 10 | 0 | -103 | 7614.84 | 12.7991
| 40098.1078 | 59.984 | 3786.4529 |  |  |  | 12.7991 | 11.7023 |  | 0 | 3793.3987 | 3771.4461 | 3777.6085 | 3780.8495 | 3742.1193 | 633 | [6 empty] | 0 | 633 | -1091.4046 | [13 empty] | 40098.1078 | 59.984 | 3786.4529 | 335 | -262.4159 | 0 | 174.5 | 10 | 0 | -103 | 7615.17 | 12.7991
| 40098.1079 | 59.984 | 3786.4529 |  |  |  | 12.7991 | 12.0862 |  | 0 | 3793.7825 | 3771.5089 | 3777.6761 | 3780.8495 | 3742.282 | 633 | [6 empty] | 0 | 633 | -1091.4046 | [13 empty] | 40098.1079 | 59.984 | 3786.4529 | 335 | -262.4159 | 0 | 174.5 | 10 | 0 | -103 | 7615.17 | 12.7991
| 40098.1079 | 59.981 | 3788.8135 |  |  |  | 15.2008 | 13.1763 |  | 0 | 3794.8727 | 3771.581 | 3777.7478 | 3780.8495 | 3742.4434 | 633 | [6 empty] | 0 | 633 | -1037.6909 | [13 empty] | 40098.1079 | 59.981 | 3788.8135 | 335 | -262.4159 | 0 | 175 | 10 | 0 | -103 | 7615.5 | 15.2008
| 40098.1079 | 59.981 | 3788.8135 |  |  |  | 15.2008 | 13.8849 |  | 0 | 3795.5812 | 3771.6525 | 3777.8218 | 3780.8495 | 3742.6034 | 633 | [6 empty] | 0 | 633 | -1037.6909 | [13 empty] | 40098.1079 | 59.981 | 3788.8135 | 335 | -262.4159 | 0 | 175 | 10 | 0 | -103 | 7615.5 | 15.2008
| 40098.1079 | 59.979 | 3788.2563 |  |  |  | 16.7999 | 14.9051 |  | 0 | 3796.6015 | 3771.7211 | 3777.8994 | 3780.8495 | 3742.7621 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.1079 | 59.979 | 3788.2563 | 335 | -262.4159 | 0 | 175.5 | 10 | 0 | -103 | 7615.83 | 16.7999
| 40098.108 | 59.979 | 3788.2563 |  |  |  | 16.7999 | 15.5683 |  | 0 | 3797.2647 | 3771.7891 | 3777.9791 | 3780.8495 | 3742.9195 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.108 | 59.979 | 3788.2563 | 335 | -262.4159 | 0 | 175.5 | 10 | 0 | -103 | 7615.83 | 16.7999
| 40098.108 | 59.976 | 3790.4673 |  |  |  | 19.1986 | 16.8389 |  | 0 | 3798.5353 | 3771.8657 | 3778.0633 | 3780.8495 | 3743.0756 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.108 | 59.976 | 3790.4673 | 335 | -262.4159 | 0 | 176 | 10 | 0 | -103 | 7616.16 | 19.1986
| 40098.108 | 59.976 | 3790.4673 |  |  |  | 19.1986 | 17.6648 |  | 0 | 3799.3612 | 3771.9416 | 3778.1503 | 3780.8495 | 3743.2304 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.108 | 59.976 | 3790.4673 | 335 | -262.4159 | 0 | 176 | 10 | 0 | -103 | 7616.16 | 19.1986
| 40098.108 | 59.979 | 3790.4204 |  |  |  | 16.7999 | 17.3621 |  | 0 | 3799.0585 | 3772.0167 | 3778.2353 | 3780.8495 | 3743.384 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.108 | 59.979 | 3790.4204 | 335 | -259.6852 | 0 | 176.5 | 10 | 0 | -103 | 7616.49 | 16.7999
| 40098.1081 | 59.979 | 3790.4204 |  |  |  | 16.7999 | 17.1653 |  | 0 | 3798.8617 | 3772.0912 | 3778.3188 | 3780.8495 | 3743.5363 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.1081 | 59.979 | 3790.4204 | 335 | -259.6852 | 0 | 176.5 | 10 | 0 | -103 | 7616.49 | 16.7999
| 40098.1081 | 59.978 | 3789.2671 |  |  |  | 17.5995 | 17.3173 |  | 0 | 3799.0137 | 3772.1605 | 3778.4022 | 3780.8495 | 3743.6873 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1081 | 59.978 | 3789.2671 | 335 | -259.6852 | 0 | 177 | 10 | 0 | -103 | 7616.82 | 17.5995
| 40098.1081 | 59.978 | 3789.2671 |  |  |  | 17.5995 | 17.4161 |  | 0 | 3799.1124 | 3772.2292 | 3778.4854 | 3780.8495 | 3743.8372 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1081 | 59.978 | 3789.2671 | 335 | -259.6852 | 0 | 177 | 10 | 0 | -103 | 7616.82 | 17.5995
| 40098.1081 | 59.974 | 3790.4304 |  |  |  | 20.8008 | 18.6007 |  | 0 | 3800.2971 | 3772.302 | 3778.5726 | 3780.8495 | 3743.9858 | 633 | [6 empty] | 0 | 633 | -930.8715 | [13 empty] | 40098.1081 | 59.974 | 3790.4304 | 335 | -259.6852 | 0 | 177.5 | 10 | 0 | -103 | 7617.15 | 20.8008
| 40098.1081 | 59.974 | 3790.4304 |  |  |  | 20.8008 | 19.3707 |  | 0 | 3801.0671 | 3772.3742 | 3778.6622 | 3780.8495 | 3744.1333 | 633 | [6 empty] | 0 | 633 | -930.8715 | [13 empty] | 40098.1081 | 59.974 | 3790.4304 | 335 | -259.6852 | 0 | 177.5 | 10 | 0 | -103 | 7617.15 | 20.8008
| 40098.1082 | 59.977 | 3786.2432 |  |  |  | 18.399 | 19.0306 |  | 0 | 3800.727 | 3772.4293 | 3778.7498 | 3780.8495 | 3744.2795 | 633 | [6 empty] | 0 | 633 | -973.8667 | [13 empty] | 40098.1082 | 59.977 | 3786.2432 | 335 | -259.6852 | 0 | 178 | 10 | 0 | -103 | 7617.48 | 18.399
| 40098.1082 | 59.977 | 3786.2432 |  |  |  | 18.399 | 18.8096 |  | 0 | 3800.5059 | 3772.4839 | 3778.8358 | 3780.8495 | 3744.4247 | 633 | [6 empty] | 0 | 633 | -973.8667 | [13 empty] | 40098.1082 | 59.977 | 3786.2432 | 335 | -259.6852 | 0 | 178 | 10 | 0 | -103 | 7617.48 | 18.399
| 40098.1082 | 59.975 | 3788.9629 |  |  |  | 20.0012 | 19.2267 |  | 0 | 3800.923 | 3772.5487 | 3778.9228 | 3780.8495 | 3744.5686 | 633 | [6 empty] | 0 | 633 | -944.7572 | [13 empty] | 40098.1082 | 59.975 | 3788.9629 | 335 | -259.6852 | 0 | 178.5 | 10 | 0 | -103 | 7617.81 | 20.0012
| 40098.1082 | 59.975 | 3788.9629 |  |  |  | 20.0012 | 19.4978 |  | 0 | 3801.1941 | 3772.6131 | 3779.0101 | 3780.8495 | 3744.7115 | 633 | [6 empty] | 0 | 633 | -944.7572 | [13 empty] | 40098.1082 | 59.975 | 3788.9629 | 335 | -259.6852 | 0 | 178.5 | 10 | 0 | -103 | 7617.81 | 20.0012
| 40098.1083 | 59.969 | 3791.877 |  |  |  | 24.7986 | 21.353 |  | 0 | 3803.0494 | 3772.6883 | 3779.104 | 3780.8495 | 3744.8532 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.1083 | 59.969 | 3791.877 | 335 | -255.911 | 0 | 179 | 10 | 0 | -103 | 7618.14 | 24.7986
| 40098.1083 | 59.969 | 3791.877 |  |  |  | 24.7986 | 22.559 |  | 0 | 3804.2553 | 3772.763 | 3779.2019 | 3780.8495 | 3744.9938 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.1083 | 59.969 | 3791.877 | 335 | -255.911 | 0 | 179 | 10 | 0 | -103 | 7618.14 | 24.7986
| 40098.1083 | 59.971 | 3792.3113 |  |  |  | 23.1995 | 22.7832 |  | 0 | 3804.4795 | 3772.8388 | 3779.2998 | 3780.8495 | 3745.1333 | 633 | [6 empty] | 0 | 633 | -891.56 | [13 empty] | 40098.1083 | 59.971 | 3792.3113 | 335 | -255.911 | 0 | 179.5 | 10 | 0 | -103 | 7618.47 | 23.1995
| 40098.1083 | 59.971 | 3792.3113 |  |  |  | 23.1995 | 22.9289 |  | 0 | 3804.6252 | 3772.914 | 3779.3976 | 3780.8495 | 3745.2717 | 633 | [6 empty] | 0 | 633 | -891.56 | [13 empty] | 40098.1083 | 59.971 | 3792.3113 | 335 | -255.911 | 0 | 179.5 | 10 | 0 | -103 | 7618.47 | 23.1995
| 40098.1084 | 59.978 | 3788.0796 |  |  |  | 17.5995 | 21.0636 |  | 0 | 3802.7599 | 3772.9723 | 3779.4875 | 3780.8495 | 3745.4091 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1084 | 59.978 | 3788.0796 | 335 | -255.911 | 0 | 180 | 10 | 0 | -103 | 7618.8 | 17.5995
| 40098.1084 | 59.978 | 3788.0796 |  |  |  | 17.5995 | 19.8511 |  | 0 | 3801.5475 | 3773.0302 | 3779.572 | 3780.8495 | 3745.5454 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1084 | 59.978 | 3788.0796 | 335 | -255.911 | 0 | 180 | 10 | 0 | -103 | 7618.8 | 17.5995
| 40098.1084 | 59.978 | 3787.135 |  |  |  | 17.5995 | 19.0631 |  | 0 | 3800.7594 | 3773.084 | 3779.6529 | 3780.8495 | 3745.6807 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1084 | 59.978 | 3787.135 | 335 | -255.911 | 0 | 180.5 | 10 | 0 | -103 | 7619.13 | 17.5995
| 40098.1084 | 59.978 | 3787.135 |  |  |  | 17.5995 | 18.5508 |  | 0 | 3800.2472 | 3773.1374 | 3779.7312 | 3780.8495 | 3745.8149 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1084 | 59.978 | 3787.135 | 335 | -255.911 | 0 | 180.5 | 10 | 0 | -103 | 7619.13 | 17.5995
| 40098.1084 | 59.972 | 3786.9961 |  |  |  | 22.3999 | 19.898 |  | 0 | 3801.5944 | 3773.1899 | 3779.814 | 3780.8495 | 3745.9481 | 633 | [6 empty] | 0 | 633 | -904.2897 | [13 empty] | 40098.1084 | 59.972 | 3786.9961 | 335 | -255.911 | 0 | 181 | 10 | 0 | -103 | 7619.46 | 22.3999
| 40098.1085 | 59.972 | 3786.9961 |  |  |  | 22.3999 | 20.7737 |  | 0 | 3802.47 | 3773.242 | 3779.8995 | 3780.8495 | 3746.0803 | 633 | [6 empty] | 0 | 633 | -904.2897 | [13 empty] | 40098.1085 | 59.972 | 3786.9961 | 335 | -255.911 | 0 | 181 | 10 | 0 | -103 | 7619.46 | 22.3999
| 40098.1085 | 59.975 | 3786.4868 |  |  |  | 20.0012 | 20.5033 |  | 0 | 3802.1997 | 3773.2918 | 3779.9833 | 3780.8495 | 3746.2115 | 633 | [6 empty] | 0 | 633 | -944.7572 | [13 empty] | 40098.1085 | 59.975 | 3786.4868 | 335 | -258.1482 | 0 | 181.5 | 10 | 0 | -103 | 7619.79 | 20.0012
| 40098.1085 | 59.975 | 3786.4868 |  |  |  | 20.0012 | 20.3276 |  | 0 | 3802.0239 | 3773.3412 | 3780.0659 | 3780.8495 | 3746.3418 | 633 | [6 empty] | 0 | 633 | -944.7572 | [13 empty] | 40098.1085 | 59.975 | 3786.4868 | 335 | -258.1482 | 0 | 181.5 | 10 | 0 | -103 | 7619.79 | 20.0012
| 40098.1085 | 59.969 | 3789.2139 |  |  |  | 24.7986 | 21.8924 |  | 0 | 3803.5888 | 3773.4005 | 3780.1536 | 3780.8495 | 3746.471 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.1085 | 59.969 | 3789.2139 | 335 | -258.1482 | 0 | 182 | 10 | 0 | -103 | 7620.12 | 24.7986
| 40098.1086 | 59.969 | 3789.2139 |  |  |  | 24.7986 | 22.9096 |  | 0 | 3804.6059 | 3773.4593 | 3780.2445 | 3780.8495 | 3746.5993 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.1086 | 59.969 | 3789.2139 | 335 | -258.1482 | 0 | 182 | 10 | 0 | -103 | 7620.12 | 24.7986
| 40098.1086 | 59.965 | 3791.2212 |  |  |  | 27.9999 | 24.6912 |  | 0 | 3806.3876 | 3773.525 | 3780.3414 | 3780.8495 | 3746.7266 | 633 | [6 empty] | 0 | 633 | -822.0815 | [13 empty] | 40098.1086 | 59.965 | 3791.2212 | 335 | -258.1482 | 0 | 182.5 | 10 | 0 | -103 | 7620.45 | 27.9999
| 40098.1086 | 59.965 | 3791.2212 |  |  |  | 27.9999 | 25.8492 |  | 0 | 3807.5456 | 3773.5903 | 3780.4417 | 3780.8495 | 3746.853 | 633 | [6 empty] | 0 | 633 | -822.0815 | [13 empty] | 40098.1086 | 59.965 | 3791.2212 | 335 | -258.1482 | 0 | 182.5 | 10 | 0 | -103 | 7620.45 | 27.9999
| 40098.1086 | 59.969 | 3790.9595 |  |  |  | 24.7986 | 25.4815 |  | 0 | 3807.1779 | 3773.6542 | 3780.54 | 3780.8495 | 3746.9784 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.1086 | 59.969 | 3790.9595 | 335 | -258.1482 | 0 | 183 | 10 | 0 | -103 | 7620.78 | 24.7986
| 40098.1087 | 59.969 | 3790.9595 |  |  |  | 24.7986 | 25.2425 |  | 0 | 3806.9388 | 3773.7176 | 3780.6367 | 3780.8495 | 3747.103 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.1087 | 59.969 | 3790.9595 | 335 | -258.1482 | 0 | 183 | 10 | 0 | -103 | 7620.78 | 24.7986
| 40098.1087 | 59.968 | 3789.0264 |  |  |  | 25.6012 | 25.368 |  | 0 | 3807.0644 | 3773.7735 | 3780.7332 | 3780.8495 | 3747.2266 | 633 | [6 empty] | 0 | 633 | -855.3902 | [13 empty] | 40098.1087 | 59.968 | 3789.0264 | 335 | -258.1482 | 0 | 183.5 | 10 | 0 | -103 | 7621.11 | 25.6012
| 40098.1087 | 59.968 | 3789.0264 |  |  |  | 25.6012 | 25.4496 |  | 0 | 3807.146 | 3773.8289 | 3780.8292 | 3780.8495 | 3747.3493 | 633 | [6 empty] | 0 | 633 | -855.3902 | [13 empty] | 40098.1087 | 59.968 | 3789.0264 | 335 | -258.1482 | 0 | 183.5 | 10 | 0 | -103 | 7621.11 | 25.6012
| 40098.1087 | 59.964 | 3787.394 |  |  |  | 28.7994 | 26.6221 |  | 0 | 3808.3184 | 3773.8781 | 3780.9288 | 3780.8495 | 3747.4711 | 633 | [6 empty] | 0 | 633 | -811.5477 | [13 empty] | 40098.1087 | 59.964 | 3787.394 | 335 | -258.8736 | 0 | 184 | 10 | 0 | -103 | 7621.44 | 28.7994
| 40098.1087 | 59.964 | 3787.394 |  |  |  | 28.7994 | 27.3841 |  | 0 | 3809.0805 | 3773.9269 | 3781.0305 | 3780.8495 | 3747.592 | 633 | [6 empty] | 0 | 633 | -811.5477 | [13 empty] | 40098.1087 | 59.964 | 3787.394 | 335 | -258.8736 | 0 | 184 | 10 | 0 | -103 | 7621.44 | 28.7994
| 40098.1088 | 59.972 | 3784.8306 |  |  |  | 22.3999 | 25.6397 |  | 0 | 3807.336 | 3773.9661 | 3781.1251 | 3780.8495 | 3747.7121 | 633 | [6 empty] | 0 | 633 | -904.2897 | [13 empty] | 40098.1088 | 59.972 | 3784.8306 | 335 | -258.8736 | 0 | 184.5 | 10 | 0 | -103 | 7621.77 | 22.3999
| 40098.1088 | 59.972 | 3784.8306 |  |  |  | 22.3999 | 24.5057 |  | 0 | 3806.2021 | 3774.005 | 3781.215 | 3780.8495 | 3747.8313 | 633 | [6 empty] | 0 | 633 | -904.2897 | [13 empty] | 40098.1088 | 59.972 | 3784.8306 | 335 | -258.8736 | 0 | 184.5 | 10 | 0 | -103 | 7621.77 | 22.3999
| 40098.1088 | 59.967 | 3784.3203 |  |  |  | 26.4008 | 25.169 |  | 0 | 3806.8654 | 3774.0419 | 3781.3066 | 3780.8495 | 3747.9496 | 633 | [6 empty] | 0 | 633 | -843.9914 | [13 empty] | 40098.1088 | 59.967 | 3784.3203 | 335 | -258.8736 | 0 | 185 | 10 | 0 | -103 | 7622.1 | 26.4008
| 40098.1088 | 59.967 | 3784.3203 |  |  |  | 26.4008 | 25.6001 |  | 0 | 3807.2965 | 3774.0784 | 3781.3991 | 3780.8495 | 3748.0671 | 633 | [6 empty] | 0 | 633 | -843.9914 | [13 empty] | 40098.1088 | 59.967 | 3784.3203 | 335 | -258.8736 | 0 | 185 | 10 | 0 | -103 | 7622.1 | 26.4008
| 40098.1089 | 59.968 | 3782.1099 |  |  |  | 25.6012 | 25.6005 |  | 0 | 3807.2969 | 3774.1069 | 3781.4909 | 3780.8495 | 3748.1838 | 633 | [6 empty] | 0 | 633 | -855.3902 | [13 empty] | 40098.1089 | 59.968 | 3782.1099 | 335 | -258.8736 | 0 | 185.5 | 10 | 0 | -103 | 7622.43 | 25.6012
| 40098.1089 | 59.968 | 3782.1099 |  |  |  | 25.6012 | 25.6007 |  | 0 | 3807.2971 | 3774.1352 | 3781.5821 | 3780.8495 | 3748.2996 | 633 | [6 empty] | 0 | 633 | -855.3902 | [13 empty] | 40098.1089 | 59.968 | 3782.1099 | 335 | -258.8736 | 0 | 185.5 | 10 | 0 | -103 | 7622.43 | 25.6012
| 40098.1089 | 59.967 | 3779.0562 |  |  |  | 26.4008 | 25.8807 |  | 0 | 3807.5771 | 3774.1525 | 3781.6736 | 3780.8495 | 3748.4147 | 633 | [6 empty] | 0 | 633 | -843.9914 | [13 empty] | 40098.1089 | 59.967 | 3779.0562 | 335 | -258.8736 | 0 | 186 | 10 | 0 | -103 | 7622.76 | 26.4008
| 40098.1089 | 59.967 | 3779.0562 |  |  |  | 26.4008 | 26.0627 |  | 0 | 3807.7591 | 3774.1697 | 3781.7652 | 3780.8495 | 3748.5289 | 633 | [6 empty] | 0 | 633 | -843.9914 | [13 empty] | 40098.1089 | 59.967 | 3779.0562 | 335 | -258.8736 | 0 | 186 | 10 | 0 | -103 | 7622.76 | 26.4008
| 40098.109 | 59.966 | 3779.2117 |  |  |  | 27.2003 | 26.4609 |  | 0 | 3808.1573 | 3774.1874 | 3781.8574 | 3780.8495 | 3748.6423 | 633 | [6 empty] | 0 | 633 | -832.8924 | [13 empty] | 40098.109 | 59.966 | 3779.2117 | 335 | -249.3376 | 0 | 186.5 | 10 | 0 | -103 | 7623.09 | 27.2003
| 40098.109 | 59.966 | 3779.2117 |  |  |  | 27.2003 | 26.7197 |  | 0 | 3808.4161 | 3774.2049 | 3781.95 | 3780.8495 | 3748.7549 | 633 | [6 empty] | 0 | 633 | -832.8924 | [13 empty] | 40098.109 | 59.966 | 3779.2117 | 335 | -249.3376 | 0 | 186.5 | 10 | 0 | -103 | 7623.09 | 27.2003
| 40098.109 | 59.971 | 3776.4292 |  |  |  | 23.1995 | 25.4876 |  | 0 | 3807.184 | 3774.2126 | 3782.0376 | 3780.8495 | 3748.8667 | 633 | [6 empty] | 0 | 633 | -891.56 | [13 empty] | 40098.109 | 59.971 | 3776.4292 | 335 | -249.3376 | 0 | 187 | 10 | 0 | -103 | 7623.42 | 23.1995
| 40098.109 | 59.971 | 3776.4292 |  |  |  | 23.1995 | 24.6868 |  | 0 | 3806.3831 | 3774.2203 | 3782.1218 | 3780.8495 | 3748.9778 | 633 | [6 empty] | 0 | 633 | -891.56 | [13 empty] | 40098.109 | 59.971 | 3776.4292 | 335 | -249.3376 | 0 | 187 | 10 | 0 | -103 | 7623.42 | 23.1995
| 40098.1091 | 59.965 | 3776.5967 |  |  |  | 27.9999 | 25.8464 |  | 0 | 3807.5427 | 3774.2285 | 3782.2095 | 3780.8495 | 3749.088 | 633 | [6 empty] | 0 | 633 | -822.0815 | [13 empty] | 40098.1091 | 59.965 | 3776.5967 | 335 | -249.3376 | 0 | 187.5 | 10 | 0 | -103 | 7623.75 | 27.9999
| 40098.1091 | 59.965 | 3776.5967 |  |  |  | 27.9999 | 26.6001 |  | 0 | 3808.2964 | 3774.2366 | 3782.2991 | 3780.8495 | 3749.1976 | 633 | [6 empty] | 0 | 633 | -822.0815 | [13 empty] | 40098.1091 | 59.965 | 3776.5967 | 335 | -249.3376 | 0 | 187.5 | 10 | 0 | -103 | 7623.75 | 27.9999
| 40098.1091 | 59.964 | 3776.0229 |  |  |  | 28.7994 | 27.3699 |  | 0 | 3809.0662 | 3774.2427 | 3782.3908 | 3780.8495 | 3749.3063 | 633 | [6 empty] | 0 | 633 | -811.5477 | [13 empty] | 40098.1091 | 59.964 | 3776.0229 | 335 | -249.3376 | 0 | 188 | 10 | 0 | -103 | 7624.08 | 28.7994
| 40098.1091 | 59.964 | 3776.0229 |  |  |  | 28.7994 | 27.8702 |  | 0 | 3809.5666 | 3774.2488 | 3782.4836 | 3780.8495 | 3749.4144 | 633 | [6 empty] | 0 | 633 | -811.5477 | [13 empty] | 40098.1091 | 59.964 | 3776.0229 | 335 | -249.3376 | 0 | 188 | 10 | 0 | -103 | 7624.08 | 28.7994
| 40098.1091 | 59.967 | 3771.7305 |  |  |  | 26.4008 | 27.3559 |  | 0 | 3809.0523 | 3774.2402 | 3782.5739 | 3780.8495 | 3749.5216 | 633 | [6 empty] | 0 | 633 | -843.9914 | [13 empty] | 40098.1091 | 59.967 | 3771.7305 | 335 | -249.3376 | 0 | 188.5 | 10 | 0 | -103 | 7624.41 | 26.4008
| 40098.1092 | 59.967 | 3771.7305 |  |  |  | 26.4008 | 27.0216 |  | 0 | 3808.718 | 3774.2317 | 3782.6626 | 3780.8495 | 3749.6282 | 633 | [6 empty] | 0 | 633 | -843.9914 | [13 empty] | 40098.1092 | 59.967 | 3771.7305 | 335 | -249.3376 | 0 | 188.5 | 10 | 0 | -103 | 7624.41 | 26.4008
| 40098.1092 | 59.968 | 3768.5029 |  |  |  | 25.6012 | 26.5245 |  | 0 | 3808.2208 | 3774.2124 | 3782.7489 | 3780.8495 | 3749.734 | 633 | [6 empty] | 0 | 633 | -855.3902 | [13 empty] | 40098.1092 | 59.968 | 3768.5029 | 335 | -258.2782 | 0 | 189 | 10 | 0 | -103 | 7624.74 | 25.6012
| 40098.1092 | 59.968 | 3768.5029 |  |  |  | 25.6012 | 26.2013 |  | 0 | 3807.8977 | 3774.1931 | 3782.8336 | 3780.8495 | 3749.8392 | 633 | [6 empty] | 0 | 633 | -855.3902 | [13 empty] | 40098.1092 | 59.968 | 3768.5029 | 335 | -258.2782 | 0 | 189 | 10 | 0 | -103 | 7624.74 | 25.6012
| 40098.1092 | 59.965 | 3767.3662 |  |  |  | 27.9999 | 26.8308 |  | 0 | 3808.5272 | 3774.1702 | 3782.9198 | 3780.8495 | 3749.9436 | 633 | [6 empty] | 0 | 633 | -822.0815 | [13 empty] | 40098.1092 | 59.965 | 3767.3662 | 335 | -258.2782 | 0 | 189.5 | 10 | 0 | -103 | 7625.07 | 27.9999
| 40098.1093 | 59.965 | 3767.3662 |  |  |  | 27.9999 | 27.24 |  | 0 | 3808.9363 | 3774.1475 | 3783.0068 | 3780.8495 | 3750.0473 | 633 | [6 empty] | 0 | 633 | -822.0815 | [13 empty] | 40098.1093 | 59.965 | 3767.3662 | 335 | -258.2782 | 0 | 189.5 | 10 | 0 | -103 | 7625.07 | 27.9999
| 40098.1093 | 59.973 | 3760.2954 |  |  |  | 21.6003 | 25.2661 |  | 0 | 3806.9625 | 3774.1013 | 3783.0867 | 3780.8495 | 3750.1503 | 633 | [6 empty] | 0 | 633 | -917.3881 | [13 empty] | 40098.1093 | 59.973 | 3760.2954 | 335 | -258.2782 | 0 | 190 | 10 | 0 | -103 | 7625.4 | 21.6003
| 40098.1093 | 59.973 | 3760.2954 |  |  |  | 21.6003 | 23.9831 |  | 0 | 3805.6795 | 3774.0554 | 3783.1617 | 3780.8495 | 3750.2526 | 633 | [6 empty] | 0 | 633 | -917.3881 | [13 empty] | 40098.1093 | 59.973 | 3760.2954 | 335 | -258.2782 | 0 | 190 | 10 | 0 | -103 | 7625.4 | 21.6003
| 40098.1093 | 59.965 | 3761.8938 |  |  |  | 27.9999 | 25.389 |  | 0 | 3807.0853 | 3774.0152 | 3783.2409 | 3780.8495 | 3750.3543 | 633 | [6 empty] | 0 | 633 | -822.0815 | [13 empty] | 40098.1093 | 59.965 | 3761.8938 | 335 | -258.2782 | 0 | 190.5 | 10 | 0 | -103 | 7625.73 | 27.9999
| 40098.1094 | 59.965 | 3761.8938 |  |  |  | 27.9999 | 26.3028 |  | 0 | 3807.9991 | 3773.9752 | 3783.3226 | 3780.8495 | 3750.4553 | 633 | [6 empty] | 0 | 633 | -822.0815 | [13 empty] | 40098.1094 | 59.965 | 3761.8938 | 335 | -258.2782 | 0 | 190.5 | 10 | 0 | -103 | 7625.73 | 27.9999
| 40098.1094 | 59.969 | 3760.5825 |  |  |  | 24.7986 | 25.7763 |  | 0 | 3807.4727 | 3773.9311 | 3783.4021 | 3780.8495 | 3750.5556 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.1094 | 59.969 | 3760.5825 | 335 | -258.2782 | 0 | 191 | 10 | 0 | -103 | 7626.06 | 24.7986
| 40098.1094 | 59.969 | 3760.5825 |  |  |  | 24.7986 | 25.4341 |  | 0 | 3807.1305 | 3773.8873 | 3783.4799 | 3780.8495 | 3750.6552 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.1094 | 59.969 | 3760.5825 | 335 | -258.2782 | 0 | 191 | 10 | 0 | -103 | 7626.06 | 24.7986
| 40098.1094 | 59.964 | 3759.781 |  |  |  | 28.7994 | 26.612 |  | 0 | 3808.3083 | 3773.8412 | 3783.561 | 3780.8495 | 3750.7542 | 633 | [6 empty] | 0 | 633 | -811.5477 | [13 empty] | 40098.1094 | 59.964 | 3759.781 | 335 | -258.4064 | 0 | 191.5 | 10 | 0 | -103 | 7626.39 | 28.7994
| 40098.1094 | 59.964 | 3759.781 |  |  |  | 28.7994 | 27.3776 |  | 0 | 3809.074 | 3773.7954 | 3783.6441 | 3780.8495 | 3750.8526 | 633 | [6 empty] | 0 | 633 | -811.5477 | [13 empty] | 40098.1094 | 59.964 | 3759.781 | 335 | -258.4064 | 0 | 191.5 | 10 | 0 | -103 | 7626.39 | 28.7994
| 40098.1095 | 59.979 | 3757.7729 |  |  |  | 16.7999 | 23.6754 |  | 0 | 3805.3718 | 3773.7434 | 3783.7147 | 3780.8495 | 3750.9503 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.1095 | 59.979 | 3757.7729 | 335 | -258.4064 | 0 | 192 | 10 | 0 | -103 | 7626.72 | 16.7999
| 40098.1095 | 59.979 | 3757.7729 |  |  |  | 16.7999 | 21.269 |  | 0 | 3802.9654 | 3773.6917 | 3783.777 | 3780.8495 | 3751.0474 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.1095 | 59.979 | 3757.7729 | 335 | -258.4064 | 0 | 192 | 10 | 0 | -103 | 7626.72 | 16.7999
| 40098.1095 | 59.983 | 3753.0874 |  |  |  | 13.5986 | 18.5844 |  | 0 | 3800.2807 | 3773.6253 | 3783.8302 | 3780.8495 | 3751.1438 | 633 | [6 empty] | 0 | 633 | -1072.9158 | [13 empty] | 40098.1095 | 59.983 | 3753.0874 | 335 | -258.4064 | 0 | 192.5 | 10 | 0 | -103 | 7627.05 | 13.5986
| 40098.1095 | 59.983 | 3753.0874 |  |  |  | 13.5986 | 16.8394 |  | 0 | 3798.5357 | 3773.5592 | 3783.8775 | 3780.8495 | 3751.2396 | 633 | [6 empty] | 0 | 633 | -1072.9158 | [13 empty] | 40098.1095 | 59.983 | 3753.0874 | 335 | -258.4064 | 0 | 192.5 | 10 | 0 | -103 | 7627.05 | 13.5986
| 40098.1096 | 59.967 | 3753.751 |  |  |  | 26.4008 | 20.1858 |  | 0 | 3801.8822 | 3773.4957 | 3783.9352 | 3780.8495 | 3751.3348 | 633 | [6 empty] | 0 | 633 | -843.9914 | [13 empty] | 40098.1096 | 59.967 | 3753.751 | 335 | -258.4064 | 0 | 193 | 10 | 0 | -103 | 7627.38 | 26.4008
| 40098.1096 | 59.967 | 3753.751 |  |  |  | 26.4008 | 22.3611 |  | 0 | 3804.0574 | 3773.4327 | 3783.9995 | 3780.8495 | 3751.4294 | 633 | [6 empty] | 0 | 633 | -843.9914 | [13 empty] | 40098.1096 | 59.967 | 3753.751 | 335 | -258.4064 | 0 | 193 | 10 | 0 | -103 | 7627.38 | 26.4008
| 40098.1096 | 59.962 | 3759.2498 |  |  |  | 30.3986 | 25.1742 |  | 0 | 3806.8706 | 3773.3875 | 3784.0723 | 3780.8495 | 3751.5234 | 633 | [6 empty] | 0 | 633 | -791.2696 | [13 empty] | 40098.1096 | 59.962 | 3759.2498 | 335 | -258.4064 | 0 | 193.5 | 10 | 0 | -103 | 7627.71 | 30.3986
| 40098.1096 | 59.962 | 3759.2498 |  |  |  | 30.3986 | 27.0027 |  | 0 | 3808.6991 | 3773.3426 | 3784.1505 | 3780.8495 | 3751.6168 | 633 | [6 empty] | 0 | 633 | -791.2696 | [13 empty] | 40098.1096 | 59.962 | 3759.2498 | 335 | -258.4064 | 0 | 193.5 | 10 | 0 | -103 | 7627.71 | 30.3986
| 40098.1097 | 59.961 | 3760.9648 |  |  |  | 31.2012 | 28.4722 |  | 0 | 3810.1685 | 3773.3034 | 3784.2328 | 3780.8495 | 3751.7096 | 633 | [6 empty] | 0 | 633 | -781.4691 | [13 empty] | 40098.1097 | 59.961 | 3760.9648 | 335 | -260.5389 | 0 | 194 | 10 | 0 | -103 | 7628.04 | 31.2012
| 40098.1097 | 59.961 | 3760.9648 |  |  |  | 31.2012 | 29.4273 |  | 0 | 3811.1237 | 3773.2645 | 3784.3177 | 3780.8495 | 3751.8018 | 633 | [6 empty] | 0 | 633 | -781.4691 | [13 empty] | 40098.1097 | 59.961 | 3760.9648 | 335 | -260.5389 | 0 | 194 | 10 | 0 | -103 | 7628.04 | 31.2012
| 40098.1097 | 59.96 | 3763.8223 |  |  |  | 32.0007 | 30.328 |  | 0 | 3812.0244 | 3773.2348 | 3784.4048 | 3780.8495 | 3751.8935 | 633 | [6 empty] | 0 | 633 | -771.9443 | [13 empty] | 40098.1097 | 59.96 | 3763.8223 | 335 | -260.5389 | 0 | 194.5 | 10 | 0 | -103 | 7628.37 | 32.0007
| 40098.1097 | 59.96 | 3763.8223 |  |  |  | 32.0007 | 30.9135 |  | 0 | 3812.6098 | 3773.2053 | 3784.4932 | 3780.8495 | 3751.9845 | 633 | [6 empty] | 0 | 633 | -771.9443 | [13 empty] | 40098.1097 | 59.96 | 3763.8223 | 335 | -260.5389 | 0 | 194.5 | 10 | 0 | -103 | 7628.37 | 32.0007
| 40098.1097 | 59.959 | 3763.8582 |  |  |  | 32.8003 | 31.5739 |  | 0 | 3813.2702 | 3773.1761 | 3784.5831 | 3780.8495 | 3752.075 | 633 | [6 empty] | 0 | 633 | -762.6489 | [13 empty] | 40098.1097 | 59.959 | 3763.8582 | 335 | -260.5389 | 0 | 195 | 10 | 0 | -103 | 7628.7 | 32.8003
| 40098.1098 | 59.959 | 3763.8582 |  |  |  | 32.8003 | 32.0031 |  | 0 | 3813.6995 | 3773.1471 | 3784.6738 | 3780.8495 | 3752.1649 | 633 | [6 empty] | 0 | 633 | -762.6489 | [13 empty] | 40098.1098 | 59.959 | 3763.8582 | 335 | -260.5389 | 0 | 195 | 10 | 0 | -103 | 7628.7 | 32.8003
| 40098.1098 | 59.951 | 3766.1267 |  |  |  | 39.1998 | 34.522 |  | 0 | 3816.2183 | 3773.1253 | 3784.7718 | 3780.8495 | 3752.2543 | 633 | [6 empty] | 0 | 633 | -695.6074 | [13 empty] | 40098.1098 | 59.951 | 3766.1267 | 335 | -260.5389 | 0 | 195.5 | 10 | 0 | -103 | 7629.03 | 39.1998
| 40098.1098 | 59.951 | 3766.1267 |  |  |  | 39.1998 | 36.1592 |  | 0 | 3817.8556 | 3773.1036 | 3784.8742 | 3780.8495 | 3752.3431 | 633 | [6 empty] | 0 | 633 | -695.6074 | [13 empty] | 40098.1098 | 59.951 | 3766.1267 | 335 | -260.5389 | 0 | 195.5 | 10 | 0 | -103 | 7629.03 | 39.1998
| 40098.1098 | 59.954 | 3767.9722 |  |  |  | 36.8011 | 36.3839 |  | 0 | 3818.0803 | 3773.0878 | 3784.9767 | 3780.8495 | 3752.4314 | 633 | [6 empty] | 0 | 633 | -719.308 | [13 empty] | 40098.1098 | 59.954 | 3767.9722 | 335 | -260.5389 | 0 | 196 | 10 | 0 | -103 | 7629.36 | 36.8011
| 40098.1099 | 59.954 | 3767.9722 |  |  |  | 36.8011 | 36.5299 |  | 0 | 3818.2263 | 3773.072 | 3785.079 | 3780.8495 | 3752.5191 | 633 | [6 empty] | 0 | 633 | -719.308 | [13 empty] | 40098.1099 | 59.954 | 3767.9722 | 335 | -260.5389 | 0 | 196 | 10 | 0 | -103 | 7629.36 | 36.8011
| 40098.1099 | 59.956 | 3765.6064 |  |  |  | 35.199 | 36.0641 |  | 0 | 3817.7605 | 3773.0491 | 3785.1793 | 3780.8495 | 3752.6062 | 633 | [6 empty] | 0 | 633 | -736.059 | [13 empty] | 40098.1099 | 59.956 | 3765.6064 | 335 | -257.8821 | 0 | 196.5 | 10 | 0 | -103 | 7629.69 | 35.199
| 40098.1099 | 59.956 | 3765.6064 |  |  |  | 35.199 | 35.7613 |  | 0 | 3817.4577 | 3773.0264 | 3785.278 | 3780.8495 | 3752.6929 | 633 | [6 empty] | 0 | 633 | -736.059 | [13 empty] | 40098.1099 | 59.956 | 3765.6064 | 335 | -257.8821 | 0 | 196.5 | 10 | 0 | -103 | 7629.69 | 35.199
| 40098.1099 | 59.963 | 3761.5703 |  |  |  | 29.599 | 33.6045 |  | 0 | 3815.3009 | 3772.9914 | 3785.3695 | 3780.8495 | 3752.779 | 633 | [6 empty] | 0 | 633 | -801.2804 | [13 empty] | 40098.1099 | 59.963 | 3761.5703 | 335 | -257.8821 | 0 | 197 | 10 | 0 | -103 | 7630.02 | 29.599
| 40098.11 | 59.963 | 3761.5703 |  |  |  | 29.599 | 32.2026 |  | 0 | 3813.8989 | 3772.9567 | 3785.4562 | 3780.8495 | 3752.8646 | 633 | [6 empty] | 0 | 633 | -801.2804 | [13 empty] | 40098.11 | 59.963 | 3761.5703 | 335 | -257.8821 | 0 | 197 | 10 | 0 | -103 | 7630.02 | 29.599
| 40098.11 | 59.959 | 3759.627 |  |  |  | 32.8003 | 32.4118 |  | 0 | 3814.1081 | 3772.9163 | 3785.5431 | 3780.8495 | 3752.9496 | 633 | [6 empty] | 0 | 633 | -762.6489 | [13 empty] | 40098.11 | 59.959 | 3759.627 | 335 | -257.8821 | 0 | 197.5 | 10 | 0 | -103 | 7630.35 | 32.8003
| 40098.11 | 59.959 | 3759.627 |  |  |  | 32.8003 | 32.5478 |  | 0 | 3814.2441 | 3772.8762 | 3785.6298 | 3780.8495 | 3753.0342 | 633 | [6 empty] | 0 | 633 | -762.6489 | [13 empty] | 40098.11 | 59.959 | 3759.627 | 335 | -257.8821 | 0 | 197.5 | 10 | 0 | -103 | 7630.35 | 32.8003
| 40098.11 | 59.963 | 3752.4287 |  |  |  | 29.599 | 31.5157 |  | 0 | 3813.2121 | 3772.8146 | 3785.7129 | 3780.8495 | 3753.1182 | 633 | [6 empty] | 0 | 633 | -801.2804 | [13 empty] | 40098.11 | 59.963 | 3752.4287 | 335 | -257.8821 | 0 | 198 | 10 | 0 | -103 | 7630.68 | 29.599
| 40098.11 | 59.963 | 3752.4287 |  |  |  | 29.599 | 30.8448 |  | 0 | 3812.5412 | 3772.7534 | 3785.7934 | 3780.8495 | 3753.2017 | 633 | [6 empty] | 0 | 633 | -801.2804 | [13 empty] | 40098.11 | 59.963 | 3752.4287 | 335 | -257.8821 | 0 | 198 | 10 | 0 | -103 | 7630.68 | 29.599
| 40098.1101 | 59.968 | 3753.8296 |  |  |  | 25.6012 | 29.0096 |  | 0 | 3810.7059 | 3772.6967 | 3785.868 | 3780.8495 | 3753.2847 | 633 | [6 empty] | 0 | 633 | -855.3902 | [13 empty] | 40098.1101 | 59.968 | 3753.8296 | 335 | -257.8821 | 0 | 198.5 | 10 | 0 | -103 | 7631.01 | 25.6012
| 40098.1101 | 59.968 | 3753.8296 |  |  |  | 25.6012 | 27.8166 |  | 0 | 3809.513 | 3772.6404 | 3785.9386 | 3780.8495 | 3753.3673 | 633 | [6 empty] | 0 | 633 | -855.3902 | [13 empty] | 40098.1101 | 59.968 | 3753.8296 | 335 | -257.8821 | 0 | 198.5 | 10 | 0 | -103 | 7631.01 | 25.6012
| 40098.1101 | 59.968 | 3753.5229 |  |  |  | 25.6012 | 27.0412 |  | 0 | 3808.7376 | 3772.5835 | 3786.0064 | 3780.8495 | 3753.4493 | 633 | [6 empty] | 0 | 633 | -855.3902 | [13 empty] | 40098.1101 | 59.968 | 3753.5229 | 335 | -258.5887 | 0 | 199 | 10 | 0 | -103 | 7631.34 | 25.6012
| 40098.1101 | 59.968 | 3753.5229 |  |  |  | 25.6012 | 26.5372 |  | 0 | 3808.2336 | 3772.5269 | 3786.0724 | 3780.8495 | 3753.5309 | 633 | [6 empty] | 0 | 633 | -855.3902 | [13 empty] | 40098.1101 | 59.968 | 3753.5229 | 335 | -258.5887 | 0 | 199 | 10 | 0 | -103 | 7631.34 | 25.6012
| 40098.1102 | 59.973 | 3753.1782 |  |  |  | 21.6003 | 24.8093 |  | 0 | 3806.5057 | 3772.4697 | 3786.1329 | 3780.8495 | 3753.6119 | 633 | [6 empty] | 0 | 633 | -917.3881 | [13 empty] | 40098.1102 | 59.973 | 3753.1782 | 335 | -258.5887 | 0 | 199.5 | 10 | 0 | -103 | 7631.67 | 21.6003
| 40098.1102 | 59.973 | 3753.1782 |  |  |  | 21.6003 | 23.6862 |  | 0 | 3805.3825 | 3772.4128 | 3786.1896 | 3780.8495 | 3753.6925 | 633 | [6 empty] | 0 | 633 | -917.3881 | [13 empty] | 40098.1102 | 59.973 | 3753.1782 | 335 | -258.5887 | 0 | 199.5 | 10 | 0 | -103 | 7631.67 | 21.6003
| 40098.1102 | 59.965 | 3753.2905 |  |  |  | 27.9999 | 25.196 |  | 0 | 3806.8923 | 3772.3566 | 3786.2505 | 3780.8495 | 3753.7726 | 633 | [6 empty] | 0 | 633 | -822.0815 | [13 empty] | 40098.1102 | 59.965 | 3753.2905 | 335 | -258.5887 | 0 | 200 | 10 | 0 | -103 | 7632 | 27.9999
| 40098.1102 | 59.965 | 3753.2905 |  |  |  | 27.9999 | 26.1773 |  | 0 | 3807.8737 | 3772.3006 | 3786.3139 | 3780.8495 | 3753.8523 | 633 | [6 empty] | 0 | 633 | -822.0815 | [13 empty] | 40098.1102 | 59.965 | 3753.2905 | 335 | -258.5887 | 0 | 200 | 10 | 0 | -103 | 7632 | 27.9999
| 40098.1103 | 59.967 | 3752.3586 |  |  |  | 26.4008 | 26.2555 |  | 0 | 3807.9519 | 3772.2423 | 3786.3772 | 3780.8495 | 3753.9314 | 633 | [6 empty] | 0 | 633 | -843.9914 | [13 empty] | 40098.1103 | 59.967 | 3752.3586 | 335 | -258.5887 | 0 | 200.5 | 10 | 0 | -103 | 7632.33 | 26.4008
| 40098.1103 | 59.967 | 3752.3586 |  |  |  | 26.4008 | 26.3064 |  | 0 | 3808.0027 | 3772.1844 | 3786.4403 | 3780.8495 | 3754.0101 | 633 | [6 empty] | 0 | 633 | -843.9914 | [13 empty] | 40098.1103 | 59.967 | 3752.3586 | 335 | -258.5887 | 0 | 200.5 | 10 | 0 | -103 | 7632.33 | 26.4008
| 40098.1103 | 59.976 | 3747.4758 |  |  |  | 19.1986 | 23.8186 |  | 0 | 3805.515 | 3772.1125 | 3786.4957 | 3780.8495 | 3754.0884 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1103 | 59.976 | 3747.4758 | 335 | -258.5887 | 0 | 201 | 10 | 0 | -103 | 7632.66 | 19.1986
| 40098.1103 | 59.976 | 3747.4758 |  |  |  | 19.1986 | 22.2016 |  | 0 | 3803.898 | 3772.0411 | 3786.5461 | 3780.8495 | 3754.1662 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1103 | 59.976 | 3747.4758 | 335 | -258.5887 | 0 | 201 | 10 | 0 | -103 | 7632.66 | 19.1986
| 40098.1103 | 59.969 | 3741.2852 |  |  |  | 24.7986 | 23.1106 |  | 0 | 3804.8069 | 3771.9522 | 3786.5989 | 3780.8495 | 3754.2435 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.1103 | 59.969 | 3741.2852 | 335 | -261.9062 | 0 | 201.5 | 10 | 0 | -103 | 7632.99 | 24.7986
| 40098.1104 | 59.969 | 3741.2852 |  |  |  | 24.7986 | 23.7014 |  | 0 | 3805.3977 | 3771.8639 | 3786.6531 | 3780.8495 | 3754.3204 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.1104 | 59.969 | 3741.2852 | 335 | -261.9062 | 0 | 201.5 | 10 | 0 | -103 | 7632.99 | 24.7986
| 40098.1104 | 59.974 | 3745.7383 |  |  |  | 20.8008 | 22.6862 |  | 0 | 3804.3825 | 3771.7888 | 3786.704 | 3780.8495 | 3754.3969 | 633 | [6 empty] | 0 | 633 | -930.8715 | [13 empty] | 40098.1104 | 59.974 | 3745.7383 | 335 | -261.9062 | 0 | 202 | 10 | 0 | -103 | 7633.32 | 20.8008
| 40098.1104 | 59.974 | 3745.7383 |  |  |  | 20.8008 | 22.0263 |  | 0 | 3803.7226 | 3771.7141 | 3786.7528 | 3780.8495 | 3754.4729 | 633 | [6 empty] | 0 | 633 | -930.8715 | [13 empty] | 40098.1104 | 59.974 | 3745.7383 | 335 | -261.9062 | 0 | 202 | 10 | 0 | -103 | 7633.32 | 20.8008
| 40098.1104 | 59.981 | 3741.6182 |  |  |  | 15.2008 | 19.6374 |  | 0 | 3801.3337 | 3771.6282 | 3786.7945 | 3780.8495 | 3754.5485 | 633 | [6 empty] | 0 | 633 | -1037.6909 | [13 empty] | 40098.1104 | 59.981 | 3741.6182 | 335 | -261.9062 | 0 | 202.5 | 10 | 0 | -103 | 7633.65 | 15.2008
| 40098.1105 | 59.981 | 3741.6182 |  |  |  | 15.2008 | 18.0846 |  | 0 | 3799.7809 | 3771.5427 | 3786.8315 | 3780.8495 | 3754.6236 | 633 | [6 empty] | 0 | 633 | -1037.6909 | [13 empty] | 40098.1105 | 59.981 | 3741.6182 | 335 | -261.9062 | 0 | 202.5 | 10 | 0 | -103 | 7633.65 | 15.2008
| 40098.1105 | 59.981 | 3738.4844 |  |  |  | 15.2008 | 17.0753 |  | 0 | 3798.7716 | 3771.4487 | 3786.8654 | 3780.8495 | 3754.6983 | 633 | [6 empty] | 0 | 633 | -1037.6909 | [13 empty] | 40098.1105 | 59.981 | 3738.4844 | 335 | -261.9062 | 0 | 203 | 10 | 0 | -103 | 7633.98 | 15.2008
| 40098.1105 | 59.981 | 3738.4844 |  |  |  | 15.2008 | 16.4192 |  | 0 | 3798.1156 | 3771.3554 | 3786.8973 | 3780.8495 | 3754.7726 | 633 | [6 empty] | 0 | 633 | -1037.6909 | [13 empty] | 40098.1105 | 59.981 | 3738.4844 | 335 | -261.9062 | 0 | 203 | 10 | 0 | -103 | 7633.98 | 15.2008
| 40098.1105 | 59.982 | 3737.4036 |  |  |  | 14.4012 | 15.7129 |  | 0 | 3797.4093 | 3771.2594 | 3786.927 | 3780.8495 | 3754.8465 | 633 | [6 empty] | 0 | 633 | -1054.9759 | [13 empty] | 40098.1105 | 59.982 | 3737.4036 | 335 | -261.9062 | 0 | 203.5 | 10 | 0 | -103 | 7634.31 | 14.4012
| 40098.1106 | 59.982 | 3737.4036 |  |  |  | 14.4012 | 15.2538 |  | 0 | 3796.9502 | 3771.1641 | 3786.9552 | 3780.8495 | 3754.9199 | 633 | [6 empty] | 0 | 633 | -1054.9759 | [13 empty] | 40098.1106 | 59.982 | 3737.4036 | 335 | -261.9062 | 0 | 203.5 | 10 | 0 | -103 | 7634.31 | 14.4012
| 40098.1106 | 59.982 | 3736.3083 |  |  |  | 14.4012 | 14.9554 |  | 0 | 3796.6518 | 3771.0662 | 3786.9824 | 3780.8495 | 3754.993 | 633 | [6 empty] | 0 | 633 | -1054.9759 | [13 empty] | 40098.1106 | 59.982 | 3736.3083 | 335 | -256.7478 | 0 | 204 | 10 | 0 | -103 | 7634.64 | 14.4012
| 40098.1106 | 59.982 | 3736.3083 |  |  |  | 14.4012 | 14.7615 |  | 0 | 3796.4578 | 3770.9688 | 3787.009 | 3780.8495 | 3755.0656 | 633 | [6 empty] | 0 | 633 | -1054.9759 | [13 empty] | 40098.1106 | 59.982 | 3736.3083 | 335 | -256.7478 | 0 | 204 | 10 | 0 | -103 | 7634.64 | 14.4012
| 40098.1106 | 59.979 | 3735.4482 |  |  |  | 16.7999 | 15.4749 |  | 0 | 3797.1713 | 3770.8696 | 3787.0374 | 3780.8495 | 3755.1378 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.1106 | 59.979 | 3735.4482 | 335 | -256.7478 | 0 | 204.5 | 10 | 0 | -103 | 7634.97 | 16.7999
| 40098.1106 | 59.979 | 3735.4482 |  |  |  | 16.7999 | 15.9387 |  | 0 | 3797.635 | 3770.7709 | 3787.0669 | 3780.8495 | 3755.2097 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.1106 | 59.979 | 3735.4482 | 335 | -256.7478 | 0 | 204.5 | 10 | 0 | -103 | 7634.97 | 16.7999
| 40098.1107 | 59.978 | 3737.5405 |  |  |  | 17.5995 | 16.52 |  | 0 | 3798.2163 | 3770.6786 | 3787.0978 | 3780.8495 | 3755.2811 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1107 | 59.978 | 3737.5405 | 335 | -256.7478 | 0 | 205 | 10 | 0 | -103 | 7635.3 | 17.5995
| 40098.1107 | 59.978 | 3737.5405 |  |  |  | 17.5995 | 16.8978 |  | 0 | 3798.5942 | 3770.5868 | 3787.1297 | 3780.8495 | 3755.3521 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1107 | 59.978 | 3737.5405 | 335 | -256.7478 | 0 | 205 | 10 | 0 | -103 | 7635.3 | 17.5995
| 40098.1107 | 59.98 | 3736.7476 |  |  |  | 16.0004 | 16.5837 |  | 0 | 3798.2801 | 3770.4933 | 3787.1605 | 3780.8495 | 3755.4227 | 633 | [6 empty] | 0 | 633 | -1020.9632 | [13 empty] | 40098.1107 | 59.98 | 3736.7476 | 350 | -256.7478 | 0 | 205.5 | 10 | 0 | -103 | 7635.63 | 16.0004
| 40098.1107 | 59.98 | 3736.7476 |  |  |  | 16.0004 | 16.3795 |  | 0 | 3798.0759 | 3770.4004 | 3787.1906 | 3780.8495 | 3755.493 | 633 | [6 empty] | 0 | 633 | -1020.9632 | [13 empty] | 40098.1107 | 59.98 | 3736.7476 | 350 | -256.7478 | 0 | 205.5 | 10 | 0 | -103 | 7635.63 | 16.0004
| 40098.1108 | 59.98 | 3736.0674 |  |  |  | 16.0004 | 16.2468 |  | 0 | 3797.9432 | 3770.3061 | 3787.2201 | 3780.8495 | 3755.5628 | 633 | [6 empty] | 0 | 633 | -1020.9632 | [13 empty] | 40098.1108 | 59.98 | 3736.0674 | 350 | -256.7478 | 0 | 206 | 10 | 0 | -103 | 7635.96 | 16.0004
| 40098.1108 | 59.98 | 3736.0674 |  |  |  | 16.0004 | 16.1606 |  | 0 | 3797.8569 | 3770.2122 | 3787.2492 | 3780.8495 | 3755.6323 | 633 | [6 empty] | 0 | 633 | -1020.9632 | [13 empty] | 40098.1108 | 59.98 | 3736.0674 | 350 | -256.7478 | 0 | 206 | 10 | 0 | -103 | 7635.96 | 16.0004
| 40098.1108 | 59.976 | 3736.575 |  |  |  | 19.1986 | 17.2239 |  | 0 | 3798.9202 | 3770.1203 | 3787.2811 | 3780.8495 | 3755.7014 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1108 | 59.976 | 3736.575 | 350 | -167.432 | 0 | 206.5 | 10 | 0 | -103 | 7636.29 | 19.1986
| 40098.1108 | 59.976 | 3736.575 |  |  |  | 19.1986 | 17.915 |  | 0 | 3799.6114 | 3770.0289 | 3787.3147 | 3780.8495 | 3755.7701 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1108 | 59.976 | 3736.575 | 350 | -167.432 | 0 | 206.5 | 10 | 0 | -103 | 7636.29 | 19.1986
| 40098.1109 | 59.971 | 3738.8748 |  |  |  | 23.1995 | 19.7646 |  | 0 | 3801.4609 | 3769.9443 | 3787.3532 | 3780.8495 | 3755.8384 | 633 | [6 empty] | 0 | 633 | -891.56 | [13 empty] | 40098.1109 | 59.971 | 3738.8748 | 350 | -167.432 | 0 | 207 | 10 | 0 | -103 | 7636.62 | 23.1995
| 40098.1109 | 59.971 | 3738.8748 |  |  |  | 23.1995 | 20.9668 |  | 0 | 3802.6632 | 3769.8601 | 3787.3947 | 3780.8495 | 3755.9064 | 633 | [6 empty] | 0 | 633 | -891.56 | [13 empty] | 40098.1109 | 59.971 | 3738.8748 | 350 | -167.432 | 0 | 207 | 10 | 0 | -103 | 7636.62 | 23.1995
| 40098.1109 | 59.974 | 3738.647 |  |  |  | 20.8008 | 20.9087 |  | 0 | 3802.6051 | 3769.7757 | 3787.4358 | 3780.8495 | 3755.974 | 633 | [6 empty] | 0 | 633 | -930.8715 | [13 empty] | 40098.1109 | 59.974 | 3738.647 | 350 | -167.432 | 0 | 207.5 | 10 | 0 | -103 | 7636.95 | 20.8008
| 40098.1109 | 59.974 | 3738.647 |  |  |  | 20.8008 | 20.8709 |  | 0 | 3802.5673 | 3769.6918 | 3787.4766 | 3780.8495 | 3756.0412 | 633 | [6 empty] | 0 | 633 | -930.8715 | [13 empty] | 40098.1109 | 59.974 | 3738.647 | 350 | -167.432 | 0 | 207.5 | 10 | 0 | -103 | 7636.95 | 20.8008
| 40098.1109 | 59.976 | 3737.3821 |  |  |  | 19.1986 | 20.2856 |  | 0 | 3801.982 | 3769.605 | 3787.5156 | 3780.8495 | 3756.1081 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1109 | 59.976 | 3737.3821 | 350 | -167.432 | 0 | 208 | 10 | 0 | -103 | 7637.28 | 19.1986
| 40098.111 | 59.976 | 3737.3821 |  |  |  | 19.1986 | 19.9052 |  | 0 | 3801.6015 | 3769.5186 | 3787.5533 | 3780.8495 | 3756.1746 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.111 | 59.976 | 3737.3821 | 350 | -167.432 | 0 | 208 | 10 | 0 | -103 | 7637.28 | 19.1986
| 40098.111 | 59.969 | 3740.0168 |  |  |  | 24.7986 | 21.6179 |  | 0 | 3803.3142 | 3769.4397 | 3787.5955 | 3780.8495 | 3756.2407 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.111 | 59.969 | 3740.0168 | 350 | -167.432 | 0 | 208.5 | 10 | 0 | -103 | 7637.61 | 24.7986
| 40098.111 | 59.969 | 3740.0168 |  |  |  | 24.7986 | 22.7311 |  | 0 | 3804.4275 | 3769.3612 | 3787.6403 | 3780.8495 | 3756.3065 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.111 | 59.969 | 3740.0168 | 350 | -167.432 | 0 | 208.5 | 10 | 0 | -103 | 7637.61 | 24.7986
| 40098.111 | 59.974 | 3742.0527 |  |  |  | 20.8008 | 22.0555 |  | 0 | 3803.7519 | 3769.2886 | 3787.6832 | 3780.8495 | 3756.372 | 633 | [6 empty] | 0 | 633 | -930.8715 | [13 empty] | 40098.111 | 59.974 | 3742.0527 | 350 | -164.9734 | 0 | 209 | 10 | 0 | -103 | 7637.94 | 20.8008
| 40098.1111 | 59.974 | 3742.0527 |  |  |  | 20.8008 | 21.6163 |  | 0 | 3803.3127 | 3769.2164 | 3787.7246 | 3780.8495 | 3756.4371 | 633 | [6 empty] | 0 | 633 | -930.8715 | [13 empty] | 40098.1111 | 59.974 | 3742.0527 | 350 | -164.9734 | 0 | 209 | 10 | 0 | -103 | 7637.94 | 20.8008
| 40098.1111 | 59.972 | 3742.5244 |  |  |  | 22.3999 | 21.8906 |  | 0 | 3803.587 | 3769.1457 | 3787.7666 | 3780.8495 | 3756.5018 | 633 | [6 empty] | 0 | 633 | -904.2897 | [13 empty] | 40098.1111 | 59.972 | 3742.5244 | 350 | -164.9734 | 0 | 209.5 | 10 | 0 | -103 | 7638.27 | 22.3999
| 40098.1111 | 59.972 | 3742.5244 |  |  |  | 22.3999 | 22.0688 |  | 0 | 3803.7652 | 3769.0755 | 3787.8088 | 3780.8495 | 3756.5663 | 633 | [6 empty] | 0 | 633 | -904.2897 | [13 empty] | 40098.1111 | 59.972 | 3742.5244 | 350 | -164.9734 | 0 | 209.5 | 10 | 0 | -103 | 7638.27 | 22.3999
| 40098.1111 | 59.977 | 3741.7231 |  |  |  | 18.399 | 20.7844 |  | 0 | 3802.4808 | 3769.0035 | 3787.8474 | 3780.8495 | 3756.6303 | 633 | [6 empty] | 0 | 633 | -973.8667 | [13 empty] | 40098.1111 | 59.977 | 3741.7231 | 350 | -164.9734 | 0 | 210 | 10 | 0 | -103 | 7638.6 | 18.399
| 40098.1112 | 59.977 | 3741.7231 |  |  |  | 18.399 | 19.9495 |  | 0 | 3801.6459 | 3768.9319 | 3787.8837 | 3780.8495 | 3756.6941 | 633 | [6 empty] | 0 | 633 | -973.8667 | [13 empty] | 40098.1112 | 59.977 | 3741.7231 | 350 | -164.9734 | 0 | 210 | 10 | 0 | -103 | 7638.6 | 18.399
| 40098.1112 | 59.978 | 3740.6292 |  |  |  | 17.5995 | 19.127 |  | 0 | 3800.8234 | 3768.8578 | 3787.9175 | 3780.8495 | 3756.7575 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1112 | 59.978 | 3740.6292 | 350 | -164.9734 | 0 | 210.5 | 10 | 0 | -103 | 7638.93 | 17.5995
| 40098.1112 | 59.978 | 3740.6292 |  |  |  | 17.5995 | 18.5924 |  | 0 | 3800.2887 | 3768.7841 | 3787.9498 | 3780.8495 | 3756.8205 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1112 | 59.978 | 3740.6292 | 350 | -164.9734 | 0 | 210.5 | 10 | 0 | -103 | 7638.93 | 17.5995
| 40098.1112 | 59.973 | 3740.7751 |  |  |  | 21.6003 | 19.6452 |  | 0 | 3801.3415 | 3768.7112 | 3787.9847 | 3780.8495 | 3756.8833 | 633 | [6 empty] | 0 | 633 | -917.3881 | [13 empty] | 40098.1112 | 59.973 | 3740.7751 | 350 | -164.9734 | 0 | 211 | 10 | 0 | -103 | 7639.26 | 21.6003
| 40098.1112 | 59.973 | 3740.7751 |  |  |  | 21.6003 | 20.3295 |  | 0 | 3802.0258 | 3768.6386 | 3788.0212 | 3780.8495 | 3756.9457 | 633 | [6 empty] | 0 | 633 | -917.3881 | [13 empty] | 40098.1112 | 59.973 | 3740.7751 | 350 | -164.9734 | 0 | 211 | 10 | 0 | -103 | 7639.26 | 21.6003
| 40098.1113 | 59.977 | 3741.2678 |  |  |  | 18.399 | 19.6538 |  | 0 | 3801.3502 | 3768.5677 | 3788.0557 | 3780.8495 | 3757.0078 | 633 | [6 empty] | 0 | 633 | -973.8667 | [13 empty] | 40098.1113 | 59.977 | 3741.2678 | 350 | -157.6281 | 0 | 211.5 | 10 | 0 | -103 | 7639.59 | 18.399
| 40098.1113 | 59.977 | 3741.2678 |  |  |  | 18.399 | 19.2147 |  | 0 | 3800.911 | 3768.4972 | 3788.0889 | 3780.8495 | 3757.0695 | 633 | [6 empty] | 0 | 633 | -973.8667 | [13 empty] | 40098.1113 | 59.977 | 3741.2678 | 350 | -157.6281 | 0 | 211.5 | 10 | 0 | -103 | 7639.59 | 18.399
| 40098.1113 | 59.978 | 3738.9658 |  |  |  | 17.5995 | 18.6493 |  | 0 | 3800.3457 | 3768.4211 | 3788.1205 | 3780.8495 | 3757.131 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1113 | 59.978 | 3738.9658 | 350 | -157.6281 | 0 | 212 | 10 | 0 | -103 | 7639.92 | 17.5995
| 40098.1113 | 59.978 | 3738.9658 |  |  |  | 17.5995 | 18.2819 |  | 0 | 3799.9783 | 3768.3453 | 3788.151 | 3780.8495 | 3757.1921 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1113 | 59.978 | 3738.9658 | 350 | -157.6281 | 0 | 212 | 10 | 0 | -103 | 7639.92 | 17.5995
| 40098.1114 | 59.981 | 3738.8787 |  |  |  | 15.2008 | 17.2035 |  | 0 | 3798.8999 | 3768.2698 | 3788.1786 | 3780.8495 | 3757.2529 | 633 | [6 empty] | 0 | 633 | -1037.6909 | [13 empty] | 40098.1114 | 59.981 | 3738.8787 | 350 | -157.6281 | 0 | 212.5 | 10 | 0 | -103 | 7640.25 | 15.2008
| 40098.1114 | 59.981 | 3738.8787 |  |  |  | 15.2008 | 16.5026 |  | 0 | 3798.1989 | 3768.1946 | 3788.2042 | 3780.8495 | 3757.3134 | 633 | [6 empty] | 0 | 633 | -1037.6909 | [13 empty] | 40098.1114 | 59.981 | 3738.8787 | 350 | -157.6281 | 0 | 212.5 | 10 | 0 | -103 | 7640.25 | 15.2008
| 40098.1114 | 59.974 | 3738.1016 |  |  |  | 20.8008 | 18.0069 |  | 0 | 3799.7033 | 3768.1179 | 3788.2335 | 3780.8495 | 3757.3736 | 633 | [6 empty] | 0 | 633 | -930.8715 | [13 empty] | 40098.1114 | 59.974 | 3738.1016 | 350 | -157.6281 | 0 | 213 | 10 | 0 | -103 | 7640.58 | 20.8008
| 40098.1114 | 59.974 | 3738.1016 |  |  |  | 20.8008 | 18.9848 |  | 0 | 3800.6811 | 3768.0415 | 3788.2652 | 3780.8495 | 3757.4335 | 633 | [6 empty] | 0 | 633 | -930.8715 | [13 empty] | 40098.1114 | 59.974 | 3738.1016 | 350 | -157.6281 | 0 | 213 | 10 | 0 | -103 | 7640.58 | 20.8008
| 40098.1115 | 59.971 | 3743.5068 |  |  |  | 23.1995 | 20.4599 |  | 0 | 3802.1563 | 3767.9792 | 3788.3004 | 3780.8495 | 3757.4931 | 633 | [6 empty] | 0 | 633 | -891.56 | [13 empty] | 40098.1115 | 59.971 | 3743.5068 | 350 | -157.6281 | 0 | 213.5 | 10 | 0 | -103 | 7640.91 | 23.1995
| 40098.1115 | 59.971 | 3743.5068 |  |  |  | 23.1995 | 21.4188 |  | 0 | 3803.1151 | 3767.9172 | 3788.338 | 3780.8495 | 3757.5524 | 633 | [6 empty] | 0 | 633 | -891.56 | [13 empty] | 40098.1115 | 59.971 | 3743.5068 | 350 | -157.6281 | 0 | 213.5 | 10 | 0 | -103 | 7640.91 | 23.1995
| 40098.1115 | 59.972 | 3745.2507 |  |  |  | 22.3999 | 21.7622 |  | 0 | 3803.4585 | 3767.86 | 3788.3761 | 3780.8495 | 3757.6114 | 633 | [6 empty] | 0 | 633 | -904.2897 | [13 empty] | 40098.1115 | 59.972 | 3745.2507 | 350 | -155.5317 | 0 | 214 | 10 | 0 | -103 | 7641.24 | 22.3999
| 40098.1115 | 59.972 | 3745.2507 |  |  |  | 22.3999 | 21.9854 |  | 0 | 3803.6817 | 3767.8031 | 3788.4147 | 3780.8495 | 3757.67 | 633 | [6 empty] | 0 | 633 | -904.2897 | [13 empty] | 40098.1115 | 59.972 | 3745.2507 | 350 | -155.5317 | 0 | 214 | 10 | 0 | -103 | 7641.24 | 22.3999
| 40098.1116 | 59.966 | 3747.3396 |  |  |  | 27.2003 | 23.8106 |  | 0 | 3805.507 | 3767.7516 | 3788.4576 | 3780.8495 | 3757.7284 | 633 | [6 empty] | 0 | 633 | -832.8924 | [13 empty] | 40098.1116 | 59.966 | 3747.3396 | 350 | -155.5317 | 0 | 214.5 | 10 | 0 | -103 | 7641.57 | 27.2003
| 40098.1116 | 59.966 | 3747.3396 |  |  |  | 27.2003 | 24.997 |  | 0 | 3806.6934 | 3767.7005 | 3788.5033 | 3780.8495 | 3757.7865 | 633 | [6 empty] | 0 | 633 | -832.8924 | [13 empty] | 40098.1116 | 59.966 | 3747.3396 | 350 | -155.5317 | 0 | 214.5 | 10 | 0 | -103 | 7641.57 | 27.2003
| 40098.1116 | 59.971 | 3749.75 |  |  |  | 23.1995 | 24.3679 |  | 0 | 3806.0642 | 3767.6556 | 3788.5472 | 3780.8495 | 3757.8443 | 633 | [6 empty] | 0 | 633 | -891.56 | [13 empty] | 40098.1116 | 59.971 | 3749.75 | 350 | -155.5317 | 0 | 215 | 10 | 0 | -103 | 7641.9 | 23.1995
| 40098.1116 | 59.971 | 3749.75 |  |  |  | 23.1995 | 23.9589 |  | 0 | 3805.6553 | 3767.611 | 3788.5899 | 3780.8495 | 3757.9018 | 633 | [6 empty] | 0 | 633 | -891.56 | [13 empty] | 40098.1116 | 59.971 | 3749.75 | 350 | -155.5317 | 0 | 215 | 10 | 0 | -103 | 7641.9 | 23.1995
| 40098.1116 | 59.972 | 3744.6826 |  |  |  | 22.3999 | 23.4133 |  | 0 | 3805.1096 | 3767.5539 | 3788.631 | 3780.8495 | 3757.9591 | 633 | [6 empty] | 0 | 633 | -904.2897 | [13 empty] | 40098.1116 | 59.972 | 3744.6826 | 350 | -155.5317 | 0 | 215.5 | 10 | 0 | -103 | 7642.23 | 22.3999
| 40098.1117 | 59.972 | 3744.6826 |  |  |  | 22.3999 | 23.0586 |  | 0 | 3804.755 | 3767.4972 | 3788.671 | 3780.8495 | 3758.016 | 633 | [6 empty] | 0 | 633 | -904.2897 | [13 empty] | 40098.1117 | 59.972 | 3744.6826 | 350 | -155.5317 | 0 | 215.5 | 10 | 0 | -103 | 7642.23 | 22.3999
| 40098.1117 | 59.972 | 3743.1489 |  |  |  | 22.3999 | 22.828 |  | 0 | 3804.5244 | 3767.4369 | 3788.7102 | 3780.8495 | 3758.0727 | 633 | [6 empty] | 0 | 633 | -904.2897 | [13 empty] | 40098.1117 | 59.972 | 3743.1489 | 350 | -155.5317 | 0 | 216 | 10 | 0 | -103 | 7642.56 | 22.3999
| 40098.1117 | 59.972 | 3743.1489 |  |  |  | 22.3999 | 22.6782 |  | 0 | 3804.3746 | 3767.3769 | 3788.7489 | 3780.8495 | 3758.129 | 633 | [6 empty] | 0 | 633 | -904.2897 | [13 empty] | 40098.1117 | 59.972 | 3743.1489 | 350 | -155.5317 | 0 | 216 | 10 | 0 | -103 | 7642.56 | 22.3999
| 40098.1117 | 59.973 | 3739.4526 |  |  |  | 21.6003 | 22.3009 |  | 0 | 3803.9973 | 3767.3082 | 3788.7865 | 3780.8495 | 3758.1851 | 633 | [6 empty] | 0 | 633 | -917.3881 | [13 empty] | 40098.1117 | 59.973 | 3739.4526 | 350 | -160.4472 | 0 | 216.5 | 10 | 0 | -103 | 7642.89 | 21.6003
| 40098.1118 | 59.973 | 3739.4526 |  |  |  | 21.6003 | 22.0557 |  | 0 | 3803.7521 | 3767.2397 | 3788.8233 | 3780.8495 | 3758.241 | 633 | [6 empty] | 0 | 633 | -917.3881 | [13 empty] | 40098.1118 | 59.973 | 3739.4526 | 350 | -160.4472 | 0 | 216.5 | 10 | 0 | -103 | 7642.89 | 21.6003
| 40098.1118 | 59.971 | 3731.8296 |  |  |  | 23.1995 | 22.456 |  | 0 | 3804.1524 | 3767.1529 | 3788.8608 | 3780.8495 | 3758.2965 | 633 | [6 empty] | 0 | 633 | -891.56 | [13 empty] | 40098.1118 | 59.971 | 3731.8296 | 350 | -160.4472 | 0 | 217 | 10 | 0 | -103 | 7643.22 | 23.1995
| 40098.1118 | 59.971 | 3731.8296 |  |  |  | 23.1995 | 22.7162 |  | 0 | 3804.4126 | 3767.0666 | 3788.8988 | 3780.8495 | 3758.3518 | 633 | [6 empty] | 0 | 633 | -891.56 | [13 empty] | 40098.1118 | 59.971 | 3731.8296 | 350 | -160.4472 | 0 | 217 | 10 | 0 | -103 | 7643.22 | 23.1995
| 40098.1118 | 59.982 | 3736.2295 |  |  |  | 14.4012 | 19.806 |  | 0 | 3801.5024 | 3766.9913 | 3788.9296 | 3780.8495 | 3758.4068 | 633 | [6 empty] | 0 | 633 | -1054.9759 | [13 empty] | 40098.1118 | 59.982 | 3736.2295 | 350 | -160.4472 | 0 | 217.5 | 10 | 0 | -103 | 7643.55 | 14.4012
| 40098.1119 | 59.982 | 3736.2295 |  |  |  | 14.4012 | 17.9143 |  | 0 | 3799.6107 | 3766.9165 | 3788.9556 | 3780.8495 | 3758.4615 | 633 | [6 empty] | 0 | 633 | -1054.9759 | [13 empty] | 40098.1119 | 59.982 | 3736.2295 | 350 | -160.4472 | 0 | 217.5 | 10 | 0 | -103 | 7643.55 | 14.4012
| 40098.1119 | 59.985 | 3733.4338 |  |  |  | 11.9995 | 15.8441 |  | 0 | 3797.5405 | 3766.8352 | 3788.9764 | 3780.8495 | 3758.516 | 633 | [6 empty] | 0 | 633 | -1110.5418 | [13 empty] | 40098.1119 | 59.985 | 3733.4338 | 350 | -160.4472 | 0 | 218 | 10 | 0 | -103 | 7643.88 | 11.9995
| 40098.1119 | 59.985 | 3733.4338 |  |  |  | 11.9995 | 14.4985 |  | 0 | 3796.1949 | 3766.7544 | 3788.9939 | 3780.8495 | 3758.5702 | 633 | [6 empty] | 0 | 633 | -1110.5418 | [13 empty] | 40098.1119 | 59.985 | 3733.4338 | 350 | -160.4472 | 0 | 218 | 10 | 0 | -103 | 7643.88 | 11.9995
| 40098.1119 | 59.987 | 3730.5098 |  |  |  | 10.4004 | 13.0642 |  | 0 | 3794.7605 | 3766.6668 | 3789.0078 | 3780.8495 | 3758.6242 | 633 | [6 empty] | 0 | 633 | -1150.9027 | [13 empty] | 40098.1119 | 59.987 | 3730.5098 | 350 | -160.4472 | 0 | 218.5 | 10 | 0 | -103 | 7644.21 | 10.4004
| 40098.1119 | 59.987 | 3730.5098 |  |  |  | 10.4004 | 12.1319 |  | 0 | 3793.8282 | 3766.5797 | 3789.0194 | 3780.8495 | 3758.6778 | 633 | [6 empty] | 0 | 633 | -1150.9027 | [13 empty] | 40098.1119 | 59.987 | 3730.5098 | 350 | -160.4472 | 0 | 218.5 | 10 | 0 | -103 | 7644.21 | 10.4004
| 40098.112 | 59.989 | 3725.4587 |  |  |  | 8.8013 | 10.9661 |  | 0 | 3792.6625 | 3766.4808 | 3789.0282 | 3780.8495 | 3758.7313 | 633 | [6 empty] | 0 | 633 | -1194.308 | [13 empty] | 40098.112 | 59.989 | 3725.4587 | 350 | -163.9586 | 0 | 219 | 10 | 0 | -103 | 7644.54 | 8.8013
| 40098.112 | 59.989 | 3725.4587 |  |  |  | 8.8013 | 10.2084 |  | 0 | 3791.9048 | 3766.3825 | 3789.0351 | 3780.8495 | 3758.7844 | 633 | [6 empty] | 0 | 633 | -1194.308 | [13 empty] | 40098.112 | 59.989 | 3725.4587 | 350 | -163.9586 | 0 | 219 | 10 | 0 | -103 | 7644.54 | 8.8013
| 40098.112 | 59.987 | 3720.1079 |  |  |  | 10.4004 | 10.2756 |  | 0 | 3791.972 | 3766.2718 | 3789.0421 | 3780.8495 | 3758.8374 | 633 | [6 empty] | 0 | 633 | -1150.9027 | [13 empty] | 40098.112 | 59.987 | 3720.1079 | 350 | -163.9586 | 0 | 219.5 | 10 | 0 | -103 | 7644.87 | 10.4004
| 40098.112 | 59.987 | 3720.1079 |  |  |  | 10.4004 | 10.3193 |  | 0 | 3792.0157 | 3766.1616 | 3789.0492 | 3780.8495 | 3758.89 | 633 | [6 empty] | 0 | 633 | -1150.9027 | [13 empty] | 40098.112 | 59.987 | 3720.1079 | 350 | -163.9586 | 0 | 219.5 | 10 | 0 | -103 | 7644.87 | 10.4004
| 40098.1121 | 59.994 | 3725.6614 |  |  |  | 4.8004 | 8.3877 |  | 0 | 3790.084 | 3766.0651 | 3789.0517 | 3780.8495 | 3758.9424 | 633 | [6 empty] | 0 | 633 | -1318.7408 | [13 empty] | 40098.1121 | 59.994 | 3725.6614 | 350 | -163.9586 | 0 | 220 | 10 | 0 | -103 | 7645.2 | 4.8004
| 40098.1121 | 59.994 | 3725.6614 |  |  |  | 4.8004 | 7.1321 |  | 0 | 3788.8285 | 3765.9692 | 3789.0511 | 3780.8495 | 3758.9946 | 633 | [6 empty] | 0 | 633 | -1318.7408 | [13 empty] | 40098.1121 | 59.994 | 3725.6614 | 350 | -163.9586 | 0 | 220 | 10 | 0 | -103 | 7645.2 | 4.8004
| 40098.1121 | 60.001 | 3727.7542 |  |  |  | -0.79956 | 4.356 |  | 0 | 3786.0524 | 3765.8786 | 3789.044 | 3780.8495 | 3759.0465 | 633 | [6 empty] | 0 | 633 | -1543.8886 | [13 empty] | 40098.1121 | 60.001 | 3727.7542 | 350 | -163.9586 | 0 | 220.5 | 10 | 0 | -103 | 7645.53 | -0.79956
| 40098.1121 | 60.001 | 3727.7542 |  |  |  | -0.79956 | 2.5516 |  | 0 | 3784.2479 | 3765.7885 | 3789.0327 | 3780.8495 | 3759.0982 | 633 | [6 empty] | 0 | 633 | -1543.8886 | [13 empty] | 40098.1121 | 60.001 | 3727.7542 | 350 | -163.9586 | 0 | 220.5 | 10 | 0 | -103 | 7645.53 | -0.79956
| 40098.1122 | 60.004 | 3727.6833 |  |  |  | -3.2013 | 0.53808 |  | 0 | 3782.2344 | 3765.6986 | 3789.0167 | 3780.8495 | 3759.1496 | 633 | [6 empty] | 0 | 633 | -1665.8684 | [13 empty] | 40098.1122 | 60.004 | 3727.6833 | 350 | -163.9586 | 0 | 221 | 10 | 0 | -103 | 7645.86 | -3.2013
| 40098.1122 | 60.004 | 3727.6833 |  |  |  | -3.2013 | -0.7707 |  | 0 | 3780.9257 | 3765.6092 | 3788.9976 | 3780.8495 | 3759.2008 | 633 | [6 empty] | 0 | 633 | -1665.8684 | [13 empty] | 40098.1122 | 60.004 | 3727.6833 | 350 | -163.9586 | 0 | 221 | 10 | 0 | -103 | 7645.86 | -3.2013
| 40098.1122 | 60.012 | 3725.0122 |  |  |  | -9.6008 | -3.8612 |  | 0 | 3777.8351 | 3765.5139 | 3788.9714 | 3780.8495 | 3759.2517 | 633 | [6 empty] | 0 | 633 | -2110.0859 | [13 empty] | 40098.1122 | 60.012 | 3725.0122 | 350 | -166.0724 | 0 | 221.5 | 10 | 0 | -103 | 7646.19 | -9.6008
| 40098.1122 | 60.012 | 3725.0122 |  |  |  | -9.6008 | -5.8701 |  | 0 | 3775.8263 | 3765.419 | 3788.9406 | 3780.8495 | 3759.3024 | 633 | [6 empty] | 0 | 633 | -2110.0859 | [13 empty] | 40098.1122 | 60.012 | 3725.0122 | 350 | -166.0724 | 0 | 221.5 | 10 | 0 | -103 | 7646.19 | -9.6008
| 40098.1122 | 60.019 | 3726.0156 |  |  |  | -15.2008 | -9.1358 |  | 0 | 3772.5605 | 3765.327 | 3788.9024 | 3780.8495 | 3759.3529 | 633 | [6 empty] | 0 | 633 | -2752.3163 | [13 empty] | 40098.1122 | 60.019 | 3726.0156 | 350 | -166.0724 | 0 | 222 | 10 | 0 | -103 | 7646.52 | -15.2008
| 40098.1123 | 60.019 | 3726.0156 |  |  |  | -15.2008 | -11.2586 |  | 0 | 3770.4378 | 3765.2353 | 3788.8593 | 3780.8495 | 3759.4031 | 633 | [6 empty] | 0 | 633 | -2752.3163 | [13 empty] | 40098.1123 | 60.019 | 3726.0156 | 350 | -166.0724 | 0 | 222 | 10 | 0 | -103 | 7646.52 | -15.2008
| 40098.1123 | 60.025 | 3716.3745 |  |  |  | -20.0012 | -14.3185 |  | 0 | 3767.3779 | 3765.1217 | 3788.8094 | 3780.8495 | 3759.4531 | 633 | [6 empty] | 0 | 633 | -3723.9038 | [13 empty] | 40098.1123 | 60.025 | 3716.3745 | 350 | -166.0724 | 0 | 222.5 | 10 | 0 | -103 | 7646.85 | -20.0012
| 40098.1123 | 60.025 | 3716.3745 |  |  |  | -20.0012 | -16.3075 |  | 0 | 3765.3889 | 3765.0086 | 3788.755 | 3780.8495 | 3759.5028 | 633 | [6 empty] | 0 | 633 | -3723.9038 | [13 empty] | 40098.1123 | 60.025 | 3716.3745 | 350 | -166.0724 | 0 | 222.5 | 10 | 0 | -103 | 7646.85 | -20.0012
| 40098.1123 | 60.027 | 3717.5598 |  |  |  | -21.6003 | -18.16 |  | 0 | 3763.5364 | 3764.8988 | 3788.6967 | 3780.8495 | 3759.5524 | 633 | [6 empty] | 0 | 633 | -4220.1717 | [13 empty] | 40098.1123 | 60.027 | 3717.5598 | 350 | -166.0724 | 0 | 223 | 10 | 0 | -103 | 7647.18 | -21.6003
| 40098.1124 | 60.027 | 3717.5598 |  |  |  | -21.6003 | -19.3641 |  | 0 | 3762.3323 | 3764.7894 | 3788.6358 | 3780.8495 | 3759.6017 | 633 | [6 empty] | 0 | 633 | -4220.1717 | [13 empty] | 40098.1124 | 60.027 | 3717.5598 | 350 | -166.0724 | 0 | 223 | 10 | 0 | -103 | 7647.18 | -21.6003
| 40098.1124 | 60.029 | 3715.166 |  |  |  | -23.1995 | -20.7065 |  | 0 | 3760.9899 | 3764.6751 | 3788.5721 | 3780.8495 | 3759.6507 | 633 | [6 empty] | 0 | 633 | -4869.0479 | [13 empty] | 40098.1124 | 60.029 | 3715.166 | 350 | -166.0724 | 0 | 223.5 | 10 | 0 | -103 | 7647.51 | -23.1995
| 40098.1124 | 60.029 | 3715.166 |  |  |  | -23.1995 | -21.579 |  | 0 | 3760.1173 | 3764.5613 | 3788.5067 | 3780.8495 | 3759.6996 | 633 | [6 empty] | 0 | 633 | -4869.0479 | [13 empty] | 40098.1124 | 60.029 | 3715.166 | 350 | -166.0724 | 0 | 223.5 | 10 | 0 | -103 | 7647.51 | -23.1995
| 40098.1124 | 60.036 | 3710.2834 |  |  |  | -28.7994 | -24.1062 |  | 0 | 3757.5902 | 3764.4368 | 3788.4357 | 3780.8495 | 3759.7482 | 633 | [6 empty] | 0 | 633 | -10549.0879 | [13 empty] | 40098.1124 | 60.036 | 3710.2834 | 350 | -163.7666 | 0 | 224 | 10 | 0 | -103 | 7647.84 | -28.7994
| 40098.1125 | 60.036 | 3710.2834 |  |  |  | -28.7994 | -25.7488 |  | 0 | 3755.9476 | 3764.3129 | 3788.3614 | 3780.8495 | 3759.7966 | 633 | [6 empty] | 0 | 633 | -10549.0879 | [13 empty] | 40098.1125 | 60.036 | 3710.2834 | 350 | -163.7666 | 0 | 224 | 10 | 0 | -103 | 7647.84 | -28.7994
| 40098.1125 | 60.037 | 3699.3557 |  |  |  | -29.599 | -27.0964 |  | 0 | 3754.6 | 3764.1646 | 3788.2843 | 3780.8495 | 3759.8448 | 633 | [6 empty] | 0 | 633 | -12657.2961 | [13 empty] | 40098.1125 | 60.037 | 3699.3557 | 350 | -163.7666 | 0 | 224.5 | 10 | 0 | -103 | 7648.17 | -29.599
| 40098.1125 | 60.037 | 3699.3557 |  |  |  | -29.599 | -27.9723 |  | 0 | 3753.7241 | 3764.0169 | 3788.2056 | 3780.8495 | 3759.8927 | 633 | [6 empty] | 0 | 633 | -12657.2961 | [13 empty] | 40098.1125 | 60.037 | 3699.3557 | 350 | -163.7666 | 0 | 224.5 | 10 | 0 | -103 | 7648.17 | -29.599
| 40098.1125 | 60.041 | 3704.5913 |  |  |  | -32.8003 | -29.6621 |  | 0 | 3752.0343 | 3763.8819 | 3788.1234 | 3780.8495 | 3759.9405 | 633 | [6 empty] | 0 | 633 | -63334.7908 | [13 empty] | 40098.1125 | 60.041 | 3704.5913 | 350 | -163.7666 | 0 | 225 | 10 | 0 | -103 | 7648.5 | -32.8003
| 40098.1125 | 60.041 | 3704.5913 |  |  |  | -32.8003 | -30.7605 |  | 0 | 3750.9359 | 3763.7474 | 3788.0391 | 3780.8495 | 3759.988 | 633 | [6 empty] | 0 | 633 | -63334.7908 | [13 empty] | 40098.1125 | 60.041 | 3704.5913 | 350 | -163.7666 | 0 | 225 | 10 | 0 | -103 | 7648.5 | -32.8003
| 40098.1126 | 60.044 | 3702.4824 |  |  |  | -35.199 | -32.3139 |  | 0 | 3749.3824 | 3763.6088 | 3787.9516 | 3780.8495 | 3760.0353 | 633 | [6 empty] | 0 | 633 | 31667.3954 | [13 empty] | 40098.1126 | 60.044 | 3702.4824 | 350 | -163.7666 | 0 | 225.5 | 10 | 0 | -103 | 7648.83 | -35.199
| 40098.1126 | 60.044 | 3702.4824 |  |  |  | -35.199 | -33.3237 |  | 0 | 3748.3727 | 3763.4708 | 3787.8623 | 3780.8495 | 3760.0824 | 633 | [6 empty] | 0 | 633 | 31667.3954 | [13 empty] | 40098.1126 | 60.044 | 3702.4824 | 350 | -163.7666 | 0 | 225.5 | 10 | 0 | -103 | 7648.83 | -35.199
| 40098.1126 | 60.046 | 3700.8259 |  |  |  | -36.8011 | -34.5408 |  | 0 | 3747.1556 | 3763.3297 | 3787.7706 | 3780.8495 | 3760.1293 | 633 | [6 empty] | 0 | 633 | 15818.6036 | [13 empty] | 40098.1126 | 60.046 | 3700.8259 | 350 | -163.7666 | 0 | 226 | 10 | 0 | -103 | 7649.16 | -36.8011
| 40098.1126 | 60.046 | 3700.8259 |  |  |  | -36.8011 | -35.3319 |  | 0 | 3746.3644 | 3763.1893 | 3787.6775 | 3780.8495 | 3760.1759 | 633 | [6 empty] | 0 | 633 | 15818.6036 | [13 empty] | 40098.1126 | 60.046 | 3700.8259 | 350 | -163.7666 | 0 | 226 | 10 | 0 | -103 | 7649.16 | -36.8011
| 40098.1127 | 60.046 | 3699.7261 |  |  |  | -36.8011 | -35.8462 |  | 0 | 3745.8502 | 3763.047 | 3787.5838 | 3780.8495 | 3760.2224 | 633 | [6 empty] | 0 | 633 | 15818.6036 | [13 empty] | 40098.1127 | 60.046 | 3699.7261 | 350 | -165.1017 | 0 | 226.5 | 10 | 0 | -103 | 7649.49 | -36.8011
| 40098.1127 | 60.046 | 3699.7261 |  |  |  | -36.8011 | -36.1804 |  | 0 | 3745.516 | 3762.9053 | 3787.4896 | 3780.8495 | 3760.2686 | 633 | [6 empty] | 0 | 633 | 15818.6036 | [13 empty] | 40098.1127 | 60.046 | 3699.7261 | 350 | -165.1017 | 0 | 226.5 | 10 | 0 | -103 | 7649.49 | -36.8011
| 40098.1127 | 60.043 | 3690.4773 |  |  |  | -34.3994 | -35.5571 |  | 0 | 3746.1393 | 3762.7437 | 3787.3973 | 3780.8495 | 3760.3147 | 633 | [6 empty] | 0 | 633 | 63334.7908 | [13 empty] | 40098.1127 | 60.043 | 3690.4773 | 350 | -165.1017 | 0 | 227 | 10 | 0 | -103 | 7649.82 | -34.3994
| 40098.1127 | 60.043 | 3690.4773 |  |  |  | -34.3994 | -35.1519 |  | 0 | 3746.5445 | 3762.5827 | 3787.3064 | 3780.8495 | 3760.3605 | 633 | [6 empty] | 0 | 633 | 63334.7908 | [13 empty] | 40098.1127 | 60.043 | 3690.4773 | 350 | -165.1017 | 0 | 227 | 10 | 0 | -103 | 7649.82 | -34.3994
| 40098.1128 | 60.044 | 3696.8772 |  |  |  | -35.199 | -35.1684 |  | 0 | 3746.528 | 3762.4367 | 3787.2157 | 3780.8495 | 3760.4061 | 633 | [6 empty] | 0 | 633 | 31667.3954 | [13 empty] | 40098.1128 | 60.044 | 3696.8772 | 350 | -165.1017 | 0 | 227.5 | 10 | 0 | -103 | 7650.15 | -35.199
| 40098.1128 | 60.044 | 3696.8772 |  |  |  | -35.199 | -35.1791 |  | 0 | 3746.5173 | 3762.2913 | 3787.1255 | 3780.8495 | 3760.4516 | 633 | [6 empty] | 0 | 633 | 31667.3954 | [13 empty] | 40098.1128 | 60.044 | 3696.8772 | 350 | -165.1017 | 0 | 227.5 | 10 | 0 | -103 | 7650.15 | -35.199
Note on L13: TC allowable range 0.050 to 1.000 with 1.0 turning filter off. Beginning Target slope should align with Actual slope.

## Graph 20 to 52s
60.0420

## Form 1 Summary Data
[6 empty] | Interconnection Performance | [9 empty] | Value A Data |  | BA Performance | [8 empty] | Value B |  | 12 to 24 second Average Period Evaluation | [11 empty] | Value B | 18 to 30 second Average Period Evaluation | [12 empty] | Value B | 20 to 40 second Average Period Evaluation | [12 empty] | Value B | 18 to 52 second Average Period Evaluation | [12 empty] | Value B | 20 to 52 second Average Period Evaluation
[18 empty] | JOU | Non- |  |  | Transferred | Contingent | [5 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent
Date | A Point | FPointA | A Value | t(0) Time | C Value | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias
| Time | Hz | Hz |  | Hz | 12 to 24 sec | 12 to 24 sec | 18 to 30 sec | 18 to 30 sec | 20 to 40 sec | 20 to 40 sec | 18 to 52 sec | 18 to 52 sec | 20 to 52 sec | 20 to 52 sec |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting
[6 empty] | Average | Average | Average | Average | Average | Average | Average | Average | Average | Average | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR
[6 empty] | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Hz | MW | MW | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW | Hz | MW | MW | MW | MW | MW | MW | MW | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | P.U. | P.U. | P.U. | MW | MW | MW | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | P.U. | P.U. | P.U. | MW | MW | MW | Hz | MW | MW | MW | MW | MW | MW | MW | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW | Hz | MW | MW | MW | MW | MW | MW | MW | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW
2009-10-12 02:27 | 40098.1023 | 60.041 | 60.042 | 40098.1024 | 59.836 | 59.8823 | -396.9069 | 59.8831 | -398.8954 | 59.8888 | -412.2881 | 59.888 | -411.6043 | 59.8888 | -413.5197 | 60.042 | 3645.3027 | 350 | -165.4764 | 0 | 114.25 | -4.2 | 15 | -103 | 7575.405 | -43.2598 | 59.8823 | 3770.953 | 335 | -207.8297 | 1 | 117.3571 | 11.7714 | 0 | 1.3925 | 0.9834 | 0.89495 | -103 | 7577.4557 | 121.2453 | 59.8831 | 3779.6252 | 335 | -209.8855 | 1.1429 | 118.1429 | 11.6857 | 0 | 1.4778 | 1.0569 | 0.89495 | -103 | 7577.9743 | 120.363 | 59.8883 | 3784.1336 | 335 | -210.82 | 2.0909 | 118.8636 | 11.1727 | 0 | 1.562 | 1.1289 | 0.89495 | -103 | 7578.45 | 115.0787 | 59.888 | 3787.7954 | 335 | -211.7533 | 3.3333 | 119.5 | 11.2 | 0 | 1.5811 | 1.1566 | 0.89495 | -103 | 7578.87 | 115.3599 | 59.8888 | 3788.8466 | 335 | -165.4764 | 3.4706 | 119.6176 | 11.1235 | 0 | 1.5986 | 1.1709 | 0.89495 | -103 | 7578.9476 | 114.5723