## Instructions
Steps | To be completed for each event evaluated.
1 | Set-up Data collection in exact same order as the "Data" sheet of this work book. Data should be in this order:
Column A: Date and Time in this format, mm/dd/yy HH:MM:SS
Column B: Frequency Hz
Column C: Net Actual Interchange
Column D: Joint Owned Unit dynamic schedule
Column E: Non Conforming Load
Column F: Pumped Hydro
Column G: Ramping units
Column H: Transferred Frequency Response
Column I: Contingent BA Lost load or generation
Column J: BA Bias Setting
Column K: BA Load
2 | Note: Columns D, E, F, G and H are optional data. If you choose not to use these, leave the columns blank. Do not delete the columns. Use the sign (+/-) convention defined in FRS Form 1.
3 | Data compression must be turned off for each data point. Quality data will give you quality results in the evaluation.
4 | Data must be at 5 second sample rate for the full 25 minute minimum collection period that starts a minimum of two (2) minutes before the event begins and includes a minimum of 15 minutes after the beginning of the event.
The spreadsheet will work with up to 60 minutes of data. Be sure "Data" worksheet is clear of any old data.
If using PI historian as your data source, use "PasteSpecial/Values" to enter data into the spreadsheet. Do not include historian data collection formulas in the data. The data must be numbers not text.
5 | Once data is in place in the "Data" worksheet, determine when the beginning of the event occurred. This is accomplished by knowing the UTC event time from the master event list.
Convert the UTC event time to your PI data time and then scroll through the Data worksheet column B data of frequency and observe when frequency moves from the normal, pre-event frequency.
This will usually be a single change in frequency of 0.008 to 0.010 Hz more or less. Note the row number in the worksheet that this change occurs. In this sample data spreadsheet this occurs in row 190 of the data.
6 | Edit cell "C8" of the "Entry Data" worksheet, change the formula in the cell "C8" to reference the row number identified in step 5 above. In the sample data of this workbook this formula is: "=Data!A190"
If the correct row is selected, the "Graph 20 to 52s" worksheet will indicate the first change in frequency of the event on the center vertical grid line of the graph (Red Trend).
7 | Determine the end of the event to be evaluated. Use the same rules that are used for DCS only look at frequency instead of ACE. Scroll down the frequency data in column B of the "Data" worksheet until frequency reaches 60 Hz or the
pre-disturbance value. Note the row number in the worksheet that this occurs. In this sample data spreadsheet this occurs in row 258.
8 | Edit cell "C11" of the "Entry Data" worksheet, change the formula in the cell "C11" to reference the row number identified in step 7 above. In the sample data of this workbook this formula is: "=Data!A258"
9 | In cell "R41" of the "Evaluation" spreadsheet, enter the MW value of the unit(s) that tripped (from the Master Event List). This is only necessary for the "Interconnection" evaluation if you're interested.
It is not necessary to do this for the BA evaluation but it will provide a comparison of the BA frequency response as compared to the Interconnection frequency response.
10 | Use the "copy" button provided to copy the evaluation and event specific data for the "FRS Form 1" of this field trial. This data is summarized in the correct order on worksheet "Form 1 Summary Data" of this workbook.
Use PasteSpecial/Values when pasting the data into FRS Form 1 on the appropriate event row.
Steps | To be completed once at the initial setup of the evaluation spreadsheet for your BA.
A | Enter the Balancing Authority name as you want it to appear on the graphs in cell "B1" of the "Entry Data" worksheet. For example: "NYISO".
B | Enter your Balancing Authorities Frequency Response Obligation in cell "B2" of the "Entry Data" worksheet. For example: -80 MW/0.1 Hz (This value could change annually)
C | For informational and educational purposes, a "Sustained" performance evaluation is provided in the "Evaluation" worksheet and in the "Sustained" Graph. This evaluation uses a Time Constant (TC) to model the frequency response of your BA.
The time constant is located in cell "L13" of the "Evaluation" spreadsheet and should be edited for the types of generators in your BA. Presently this time constant is set at 0.35.
The higher the value of the time constant, the faster the delivery of frequency response is expected. Setting the TC to 1.0 effectively turns off the delay and instantaneous frequency response will be modeled. Do not set higher than 1.0.
This time constant is only used in the "Sustained" evaluation and is not used for the Field Trial evaluation of performance to the FRO.
A typical setting for this time constant is 0.08 to 0.15 for hydro units, 0.10 to 0.20 for large steam turbines and 0.20 to 0.40 for combustion turbines.
By observing the slope of your "Interchange Actual" on the "Sustained" Graph, adjust the time constant until the initial slope of the "Target" is similar.
When set appropriately, the "Target" trend on the "Sustained" graph will model what Interchange Actual should have done during the event recovery period based on your minimum FRO.
Note: For ease of use, only the necessary worksheets are displayed. If you are interested in viewing graphs and other hidden worksheets, select the "tab" at the bottom, right click, select unhide and select the worksheet you wish to unhide.

## Data
|  |  | JOU | Non- |  |  | Transferred | Contingent
|  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA
|  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load
|  | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting
Time (T) | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW
2009-10-12 02:12 | 59.98 | 3669.8784 | 350 | 351.3615 | 0 | 0 | 10 | 15 | -103 | 7500
2009-10-12 02:12 | 59.982 | 3670.9492 | 350 | 351.3615 | 0 | 0.5 | 10 | 15 | -103 | 7500.33
2009-10-12 02:12 | 59.981 | 3671.5481 | 350 | 351.3615 | 0 | 1 | 10 | 15 | -103 | 7500.66
2009-10-12 02:12 | 59.979 | 3672.1741 | 350 | 357.9475 | 0 | 1.5 | 10 | 15 | -103 | 7500.99
2009-10-12 02:12 | 59.98 | 3674.2634 | 350 | 357.9475 | 0 | 2 | 10 | 15 | -103 | 7501.32
2009-10-12 02:12 | 59.986 | 3675.0916 | 350 | 357.9475 | 0 | 2.5 | 10 | 15 | -103 | 7501.65
2009-10-12 02:12 | 59.976 | 3669.3303 | 350 | 357.9475 | 0 | 3 | 10 | 15 | -103 | 7501.98
2009-10-12 02:13 | 59.979 | 3673.5603 | 350 | 357.9475 | 0 | 3.5 | 10 | 15 | -103 | 7502.31
2009-10-12 02:13 | 59.987 | 3673.8342 | 350 | 360.2347 | 0 | 4 | 10 | 15 | -103 | 7502.64
2009-10-12 02:13 | 59.993 | 3671.2205 | 350 | 360.2347 | 0 | 4.5 | 10 | 15 | -103 | 7502.97
2009-10-12 02:13 | 59.995 | 3671.2832 | 350 | 360.2347 | 0 | 5 | 10 | 15 | -103 | 7503.3
2009-10-12 02:13 | 59.995 | 3668.1289 | 350 | 360.2347 | 0 | 5.5 | 10 | 15 | -103 | 7503.63
2009-10-12 02:13 | 59.994 | 3669.2913 | 350 | 360.2347 | 0 | 6 | 10 | 15 | -103 | 7503.96
2009-10-12 02:13 | 59.997 | 3670.6833 | 350 | 346.5259 | 0 | 6.5 | 10 | 15 | -103 | 7504.29
2009-10-12 02:13 | 60.001 | 3670.2117 | 350 | 346.5259 | 0 | 7 | 10 | 15 | -103 | 7504.62
2009-10-12 02:13 | 60.003 | 3671.1836 | 350 | 346.5259 | 0 | 7.5 | 10 | 15 | -103 | 7504.95
2009-10-12 02:13 | 60 | 3670.2671 | 350 | 346.5259 | 0 | 8 | 10 | 15 | -103 | 7505.28
2009-10-12 02:13 | 60.003 | 3670.2485 | 350 | 346.5259 | 0 | 8.5 | 10 | 15 | -103 | 7505.61
2009-10-12 02:13 | 60.001 | 3669.8992 | 350 | 296.4434 | 0 | 9 | 10 | 15 | -103 | 7505.94
2009-10-12 02:14 | 60.001 | 3671.6284 | 350 | 296.4434 | 0 | 9.5 | 10 | 15 | -103 | 7506.27
2009-10-12 02:14 | 60.004 | 3671.9683 | 350 | 296.4434 | 0 | 10 | 10 | 15 | -103 | 7506.6
2009-10-12 02:14 | 60.005 | 3671.8752 | 350 | 296.4434 | 0 | 10.5 | 10 | 15 | -103 | 7506.93
2009-10-12 02:14 | 60.003 | 3672.8728 | 350 | 296.4434 | 0 | 11 | 10 | 15 | -103 | 7507.26
2009-10-12 02:14 | 59.999 | 3673.5305 | 350 | 341.0612 | 0 | 11.5 | 10 | 15 | -103 | 7507.59
2009-10-12 02:14 | 59.998 | 3673.1863 | 350 | 341.0612 | 0 | 12 | 10 | 15 | -103 | 7507.92
2009-10-12 02:14 | 59.995 | 3673.365 | 350 | 341.0612 | 0 | 12.5 | 10 | 15 | -103 | 7508.25
2009-10-12 02:14 | 59.996 | 3672.093 | 350 | 341.0612 | 0 | 13 | 10 | 15 | -103 | 7508.58
2009-10-12 02:14 | 60.001 | 3671.0725 | 350 | 341.0612 | 0 | 13.5 | 10 | 15 | -103 | 7508.91
2009-10-12 02:14 | 60.007 | 3671.4414 | 350 | 322.8263 | 0 | 14 | 10 | 15 | -103 | 7509.24
2009-10-12 02:14 | 60.002 | 3670.5129 | 350 | 322.8263 | 0 | 14.5 | 10 | 15 | -103 | 7509.57
2009-10-12 02:14 | 59.999 | 3672.7129 | 350 | 322.8263 | 0 | 15 | 10 | 15 | -103 | 7509.9
2009-10-12 02:15 | 60.007 | 3670.8257 | 350 | 322.8263 | 0 | 15.5 | 10 | 15 | -103 | 7510.23
2009-10-12 02:15 | 60.009 | 3671.8091 | 350 | 322.8263 | 0 | 16 | 10 | 15 | -103 | 7510.56
2009-10-12 02:15 | 59.997 | 3673.2554 | 350 | 321.5444 | 0 | 16.5 | 10 | 15 | -103 | 7510.89
2009-10-12 02:15 | 59.994 | 3675.4258 | 350 | 321.5444 | 0 | 17 | 10 | 15 | -103 | 7511.22
2009-10-12 02:15 | 60.001 | 3675.3105 | 350 | 321.5444 | 0 | 17.5 | 10 | 15 | -103 | 7511.55
2009-10-12 02:15 | 59.995 | 3675.1655 | 350 | 321.5444 | 0 | 18 | 10 | 15 | -103 | 7511.88
2009-10-12 02:15 | 59.986 | 3674.9065 | 350 | 321.5444 | 0 | 18.5 | 10 | 15 | -103 | 7512.21
2009-10-12 02:15 | 59.988 | 3676.7144 | 350 | 362.1363 | 0 | 19 | 10 | 15 | -103 | 7512.54
2009-10-12 02:15 | 59.988 | 3675.543 | 350 | 362.1363 | 0 | 19.5 | 10 | 15 | -103 | 7512.87
2009-10-12 02:15 | 59.984 | 3676.9314 | 350 | 362.1363 | 0 | 20 | 10 | 15 | -103 | 7513.2
2009-10-12 02:15 | 59.982 | 3677.3611 | 350 | 362.1363 | 0 | 20.5 | 10 | 15 | -103 | 7513.53
2009-10-12 02:16 | 59.985 | 3679.2278 | 350 | 362.1363 | 0 | 21 | 10 | 15 | -103 | 7513.86
2009-10-12 02:16 | 59.987 | 3677.627 | 350 | 336.3118 | 0 | 21.5 | 10 | 15 | -103 | 7514.19
2009-10-12 02:16 | 59.987 | 3676.4094 | 350 | 336.3118 | 0 | 22 | 10 | 15 | -103 | 7514.52
2009-10-12 02:16 | 59.98 | 3676.9148 | 350 | 336.3118 | 0 | 22.5 | 10 | 15 | -103 | 7514.85
2009-10-12 02:16 | 59.987 | 3679.2329 | 350 | 336.3118 | 0 | 23 | 10 | 15 | -103 | 7515.18
2009-10-12 02:16 | 59.988 | 3678.3442 | 350 | 336.3118 | 0 | 23.5 | 10 | 15 | -103 | 7515.51
2009-10-12 02:16 | 59.978 | 3677.6777 | 350 | 316.4431 | 0 | 24 | 10 | 15 | -103 | 7515.84
2009-10-12 02:16 | 59.979 | 3678.7295 | 350 | 316.4431 | 0 | 24.5 | 10 | 15 | -103 | 7516.17
2009-10-12 02:16 | 59.988 | 3680.2869 | 350 | 316.4431 | 0 | 25 | 10 | 15 | -103 | 7516.5
2009-10-12 02:16 | 59.989 | 3678.4885 | 350 | 316.4431 | 0 | 25.5 | 10 | 15 | -103 | 7516.83
2009-10-12 02:16 | 59.992 | 3678.7402 | 350 | 316.4431 | 0 | 26 | 10 | 15 | -103 | 7517.16
2009-10-12 02:16 | 59.995 | 3677.0625 | 350 | 325.4643 | 0 | 26.5 | 10 | 15 | -103 | 7517.49
2009-10-12 02:17 | 59.998 | 3678.4905 | 350 | 325.4643 | 0 | 27 | 10 | 15 | -103 | 7517.82
2009-10-12 02:17 | 59.999 | 3678.9509 | 350 | 325.4643 | 0 | 27.5 | 10 | 15 | -103 | 7518.15
2009-10-12 02:17 | 59.992 | 3679.1484 | 350 | 325.4643 | 0 | 28 | 10 | 15 | -103 | 7518.48
2009-10-12 02:17 | 59.998 | 3678.9966 | 350 | 325.4643 | 0 | 28.5 | 10 | 15 | -103 | 7518.81
2009-10-12 02:17 | 60.006 | 3678.4934 | 350 | 336.6142 | 0 | 29 | 10 | 15 | -103 | 7519.14
2009-10-12 02:17 | 60.009 | 3677.8987 | 350 | 336.6142 | 0 | 29.5 | 10 | 15 | -103 | 7519.47
2009-10-12 02:17 | 60.011 | 3679.2087 | 350 | 336.6142 | 0 | 30 | 10 | 15 | -103 | 7519.8
2009-10-12 02:17 | 60.008 | 3679.0566 | 350 | 336.6142 | 0 | 30.5 | 10 | 15 | -103 | 7520.13
2009-10-12 02:17 | 60.012 | 3680.6042 | 350 | 336.6142 | 0 | 31 | 10 | 15 | -103 | 7520.46
2009-10-12 02:17 | 60.01 | 3680.2627 | 350 | 316.7262 | 0 | 31.5 | 10 | 15 | -103 | 7520.79
2009-10-12 02:17 | 60.009 | 3679.5608 | 350 | 316.7262 | 0 | 32 | 10 | 15 | -103 | 7521.12
2009-10-12 02:17 | 60.006 | 3679.9119 | 350 | 316.7262 | 0 | 32.5 | 10 | 15 | -103 | 7521.45
2009-10-12 02:18 | 60.009 | 3679.8879 | 350 | 316.7262 | 0 | 33 | 10 | 15 | -103 | 7521.78
2009-10-12 02:18 | 60.009 | 3679.2607 | 350 | 316.7262 | 0 | 33.5 | 10 | 15 | -103 | 7522.11
2009-10-12 02:18 | 60.004 | 3679.0247 | 350 | 320.1955 | 0 | 34 | 10 | 15 | -103 | 7522.44
2009-10-12 02:18 | 59.999 | 3678.2952 | 350 | 320.1955 | 0 | 34.5 | 10 | 15 | -103 | 7522.77
2009-10-12 02:18 | 59.994 | 3678.2358 | 350 | 320.1955 | 0 | 35 | 10 | 15 | -103 | 7523.1
2009-10-12 02:18 | 59.994 | 3677.7722 | 350 | 320.1955 | 0 | 35.5 | 10 | 15 | -103 | 7523.43
2009-10-12 02:18 | 59.995 | 3677.0933 | 350 | 320.1955 | 0 | 36 | 10 | 15 | -103 | 7523.76
2009-10-12 02:18 | 59.99 | 3678.5156 | 350 | 341.8661 | 0 | 36.5 | 10 | 15 | -103 | 7524.09
2009-10-12 02:18 | 59.983 | 3680.1965 | 350 | 341.8661 | 0 | 37 | 10 | 15 | -103 | 7524.42
2009-10-12 02:18 | 59.977 | 3677.9211 | 350 | 341.8661 | 0 | 37.5 | 10 | 15 | -103 | 7524.75
2009-10-12 02:18 | 59.999 | 3682.0701 | 350 | 341.8661 | 0 | 38 | 10 | 15 | -103 | 7525.08
2009-10-12 02:18 | 59.989 | 3678.0767 | 350 | 341.8661 | 0 | 38.5 | 10 | 15 | -103 | 7525.41
2009-10-12 02:18 | 59.984 | 3678.4268 | 350 | 348.5978 | 0 | 39 | 10 | 15 | -103 | 7525.74
2009-10-12 02:19 | 59.985 | 3677.8223 | 350 | 348.5978 | 0 | 39.5 | 10 | 15 | -103 | 7526.07
2009-10-12 02:19 | 59.986 | 3677.3975 | 350 | 348.5978 | 0 | 40 | 10 | 15 | -103 | 7526.4
2009-10-12 02:19 | 59.981 | 3678.6167 | 350 | 348.5978 | 0 | 40.5 | 10 | 15 | -103 | 7526.73
2009-10-12 02:19 | 59.998 | 3681.2522 | 350 | 348.5978 | 0 | 41 | 10 | 15 | -103 | 7527.06
2009-10-12 02:19 | 60.007 | 3678.1614 | 350 | 329.085 | 0 | 41.5 | 10 | 15 | -103 | 7527.39
2009-10-12 02:19 | 59.981 | 3676.2222 | 350 | 329.085 | 0 | 42 | 10 | 15 | -103 | 7527.72
2009-10-12 02:19 | 59.974 | 3677.49 | 350 | 329.085 | 0 | 42.5 | 10 | 15 | -103 | 7528.05
2009-10-12 02:19 | 59.974 | 3675.437 | 350 | 329.085 | 0 | 43 | 10 | 15 | -103 | 7528.38
2009-10-12 02:19 | 59.979 | 3683.8286 | 350 | 329.085 | 0 | 43.5 | 10 | 15 | -103 | 7528.71
2009-10-12 02:19 | 59.984 | 3681.1084 | 350 | 342.4182 | 0 | 44 | 10 | 15 | -103 | 7529.04
2009-10-12 02:19 | 59.988 | 3676.752 | 350 | 342.4182 | 0 | 44.5 | 10 | 15 | -103 | 7529.37
2009-10-12 02:20 | 59.987 | 3671.9424 | 350 | 342.4182 | 0 | 45 | 10 | 15 | -103 | 7529.7
2009-10-12 02:20 | 59.985 | 3670.1287 | 350 | 342.4182 | 0 | 45.5 | 10 | 15 | -103 | 7530.03
2009-10-12 02:20 | 59.983 | 3672.0479 | 350 | 342.4182 | 0 | 46 | 10 | 15 | -103 | 7530.36
2009-10-12 02:20 | 59.989 | 3672.4136 | 350 | 338.7946 | 0 | 46.5 | 10 | 15 | -103 | 7530.69
2009-10-12 02:20 | 59.982 | 3671.8372 | 350 | 338.7946 | 0 | 47 | 10 | 15 | -103 | 7531.02
2009-10-12 02:20 | 59.981 | 3670.3721 | 350 | 338.7946 | 0 | 47.5 | 10 | 15 | -103 | 7531.35
2009-10-12 02:20 | 59.986 | 3671.4009 | 350 | 338.7946 | 0 | 48 | 10 | 15 | -103 | 7531.68
2009-10-12 02:20 | 59.987 | 3670.2964 | 350 | 338.7946 | 0 | 48.5 | 10 | 15 | -103 | 7532.01
2009-10-12 02:20 | 59.98 | 3668.5896 | 350 | 335.931 | 0 | 49 | 10 | 15 | -103 | 7532.34
2009-10-12 02:20 | 59.98 | 3670.2627 | 350 | 335.931 | 0 | 49.5 | 10 | 15 | -103 | 7532.67
2009-10-12 02:20 | 59.981 | 3670.1021 | 350 | 335.931 | 0 | 50 | 10 | 15 | -103 | 7533
2009-10-12 02:20 | 59.98 | 3672.4424 | 350 | 335.931 | 0 | 50.5 | 10 | 15 | -103 | 7533.33
2009-10-12 02:20 | 59.98 | 3671.947 | 350 | 335.931 | 0 | 51 | 10 | 15 | -103 | 7533.66
2009-10-12 02:21 | 59.977 | 3670.1372 | 350 | 339.7124 | 0 | 51.5 | 10 | 15 | -103 | 7533.99
2009-10-12 02:21 | 59.979 | 3672.3909 | 350 | 339.7124 | 0 | 52 | 10 | 15 | -103 | 7534.32
2009-10-12 02:21 | 59.977 | 3672.6265 | 350 | 339.7124 | 0 | 52.5 | 10 | 15 | -103 | 7534.65
2009-10-12 02:21 | 59.973 | 3673.1829 | 350 | 339.7124 | 0 | 53 | 10 | 15 | -103 | 7534.98
2009-10-12 02:21 | 59.973 | 3676.6233 | 350 | 339.7124 | 0 | 53.5 | 10 | 15 | -103 | 7535.31
2009-10-12 02:21 | 59.975 | 3676.543 | 350 | 332.0247 | 0 | 54 | 10 | 15 | -103 | 7535.64
2009-10-12 02:21 | 59.977 | 3675.2559 | 350 | 332.0247 | 0 | 54.5 | 10 | 15 | -103 | 7535.97
2009-10-12 02:21 | 59.98 | 3671.2769 | 350 | 332.0247 | 0 | 55 | 10 | 15 | -103 | 7536.3
2009-10-12 02:21 | 59.981 | 3669.9629 | 350 | 332.0247 | 0 | 55.5 | 10 | 15 | -103 | 7536.63
2009-10-12 02:21 | 59.982 | 3669.4968 | 350 | 332.0247 | 0 | 56 | 10 | 15 | -103 | 7536.96
2009-10-12 02:21 | 59.981 | 3666.4817 | 350 | 330.759 | 0 | 56.5 | 10 | 15 | -103 | 7537.29
2009-10-12 02:22 | 59.985 | 3666.9106 | 350 | 330.759 | 0 | 57 | 10 | 15 | -103 | 7537.62
2009-10-12 02:22 | 59.989 | 3667.4563 | 350 | 330.759 | 0 | 57.5 | 10 | 15 | -103 | 7537.95
2009-10-12 02:22 | 59.998 | 3665.2617 | 350 | 330.759 | 0 | 58 | 10 | 15 | -103 | 7538.28
2009-10-12 02:22 | 60.004 | 3663.2288 | 350 | 330.759 | 0 | 58.5 | 10 | 15 | -103 | 7538.61
2009-10-12 02:22 | 60.013 | 3661.6953 | 350 | 323.42 | 0 | 59 | 10 | 15 | -103 | 7538.94
2009-10-12 02:22 | 60.013 | 3662.9595 | 350 | 323.42 | 0 | 59.5 | 10 | 15 | -103 | 7539.27
2009-10-12 02:22 | 60.01 | 3664.1392 | 350 | 323.42 | 0 | 60 | 10 | 15 | -103 | 7539.6
2009-10-12 02:22 | 60.019 | 3663.2646 | 350 | 323.42 | 0 | 60.5 | 10 | 15 | -103 | 7539.93
2009-10-12 02:22 | 60.02 | 3661.9292 | 350 | 323.42 | 0 | 61 | 10 | 15 | -103 | 7540.26
2009-10-12 02:22 | 60.021 | 3658.6614 | 350 | 342.3509 | 0 | 61.5 | 10 | 15 | -103 | 7540.59
2009-10-12 02:22 | 60.019 | 3657.571 | 350 | 342.3509 | 0 | 62 | 10 | 15 | -103 | 7540.92
2009-10-12 02:22 | 60.025 | 3658.0146 | 350 | 342.3509 | 0 | 62.5 | 10 | 15 | -103 | 7541.25
2009-10-12 02:22 | 60.02 | 3659.2236 | 350 | 342.3509 | 0 | 63 | 10 | 15 | -103 | 7541.58
2009-10-12 02:23 | 60.018 | 3658.1545 | 350 | 342.3509 | 0 | 63.5 | 10 | 15 | -103 | 7541.91
2009-10-12 02:23 | 60.019 | 3659.7776 | 350 | 345.0818 | 0 | 64 | 10 | 15 | -103 | 7542.24
2009-10-12 02:23 | 60.023 | 3662.3872 | 350 | 345.0818 | 0 | 64.5 | 10 | 15 | -103 | 7542.57
2009-10-12 02:23 | 60.025 | 3662.3901 | 350 | 345.0818 | 0 | 65 | 10 | 15 | -103 | 7542.9
2009-10-12 02:23 | 60.02 | 3663.5386 | 350 | 345.0818 | 0 | 65.5 | 10 | 15 | -103 | 7543.23
2009-10-12 02:23 | 60.02 | 3662.5525 | 350 | 345.0818 | 0 | 66 | 10 | 15 | -103 | 7543.56
2009-10-12 02:23 | 60.021 | 3663.9097 | 350 | 346.5374 | 0 | 66.5 | 10 | 15 | -103 | 7543.89
2009-10-12 02:23 | 60.014 | 3662.7913 | 350 | 346.5374 | 0 | 67 | 10 | 15 | -103 | 7544.22
2009-10-12 02:23 | 60.013 | 3664.3154 | 350 | 346.5374 | 0 | 67.5 | 10 | 15 | -103 | 7544.55
2009-10-12 02:23 | 60.008 | 3665.7976 | 350 | 346.5374 | 0 | 68 | 10 | 15 | -103 | 7544.88
2009-10-12 02:23 | 60.011 | 3667.6768 | 350 | 346.5374 | 0 | 68.5 | 10 | 15 | -103 | 7545.21
2009-10-12 02:24 | 60.009 | 3666.6882 | 350 | 342.9058 | 0 | 69 | 10 | 15 | -103 | 7545.54
2009-10-12 02:24 | 60.009 | 3667.696 | 350 | 342.9058 | 0 | 69.5 | 10 | 15 | -103 | 7545.87
2009-10-12 02:24 | 60.002 | 3667.043 | 350 | 342.9058 | 0 | 70 | 10 | 15 | -103 | 7546.2
2009-10-12 02:24 | 59.996 | 3665.8796 | 350 | 342.9058 | 0 | 70.5 | 10 | 15 | -103 | 7546.53
2009-10-12 02:24 | 59.998 | 3665.8015 | 350 | 342.9058 | 0 | 71 | 10 | 15 | -103 | 7546.86
2009-10-12 02:24 | 59.998 | 3664.9475 | 350 | 340.0944 | 0 | 71.5 | 10 | 15 | -103 | 7547.19
2009-10-12 02:24 | 59.995 | 3666.1333 | 350 | 340.0944 | 0 | 72 | 10 | 15 | -103 | 7547.52
2009-10-12 02:24 | 59.993 | 3667.084 | 350 | 340.0944 | 0 | 72.5 | 10 | 15 | -103 | 7547.85
2009-10-12 02:24 | 59.982 | 3667.3367 | 350 | 340.0944 | 0 | 73 | 10 | 15 | -103 | 7548.18
2009-10-12 02:24 | 59.982 | 3668.6909 | 350 | 340.0944 | 0 | 73.5 | 10 | 15 | -103 | 7548.51
2009-10-12 02:24 | 59.982 | 3669.6062 | 350 | 342.7712 | 0 | 74 | 10 | 15 | -103 | 7548.84
2009-10-12 02:24 | 59.978 | 3670.2646 | 350 | 342.7712 | 0 | 74.5 | 10 | 15 | -103 | 7549.17
2009-10-12 02:24 | 59.974 | 3673.2432 | 350 | 342.7712 | 0 | 75 | 10 | 15 | -103 | 7549.5
2009-10-12 02:25 | 59.979 | 3676.4182 | 350 | 342.7712 | 0 | 75.5 | 10 | 15 | -103 | 7549.83
2009-10-12 02:25 | 59.98 | 3674.6375 | 350 | 342.7712 | 0 | 76 | 10 | 15 | -103 | 7550.16
2009-10-12 02:25 | 59.987 | 3674.7681 | 350 | 342.9099 | 0 | 76.5 | 10 | 15 | -103 | 7550.49
2009-10-12 02:25 | 59.99 | 3673.5142 | 350 | 342.9099 | 0 | 77 | 10 | 15 | -103 | 7550.82
2009-10-12 02:25 | 59.991 | 3673.0564 | 350 | 342.9099 | 0 | 77.5 | 10 | 15 | -103 | 7551.15
2009-10-12 02:25 | 59.993 | 3671.4932 | 350 | 342.9099 | 0 | 78 | 10 | 15 | -103 | 7551.48
2009-10-12 02:25 | 59.996 | 3670.0278 | 350 | 342.9099 | 0 | 78.5 | 10 | 15 | -103 | 7551.81
2009-10-12 02:25 | 60.003 | 3671.5781 | 350 | 343.286 | 0 | 79 | 10 | 15 | -103 | 7552.14
2009-10-12 02:25 | 60.005 | 3673.8186 | 350 | 343.286 | 0 | 79.5 | 10 | 15 | -103 | 7552.47
2009-10-12 02:25 | 60.004 | 3673.1821 | 350 | 343.286 | 0 | 80 | 10 | 15 | -103 | 7552.8
2009-10-12 02:25 | 60.01 | 3672.363 | 350 | 343.286 | 0 | 80.5 | 10 | 15 | -103 | 7553.13
2009-10-12 02:26 | 60.011 | 3672.2607 | 350 | 343.286 | 0 | 81 | 10 | 15 | -103 | 7553.46
2009-10-12 02:26 | 60.014 | 3673.5535 | 350 | 331.853 | 0 | 81.5 | 10 | 15 | -103 | 7553.79
2009-10-12 02:26 | 60.011 | 3674.5371 | 350 | 331.853 | 0 | 82 | 10 | 15 | -103 | 7554.12
2009-10-12 02:26 | 60.017 | 3672.5632 | 350 | 331.853 | 0 | 82.5 | 10 | 15 | -103 | 7554.45
2009-10-12 02:26 | 60.014 | 3672.3882 | 350 | 331.853 | 0 | 83 | 10 | 15 | -103 | 7554.78
2009-10-12 02:26 | 60.014 | 3671.2881 | 350 | 331.853 | 0 | 83.5 | 10 | 15 | -103 | 7555.11
2009-10-12 02:26 | 60.019 | 3672.9817 | 350 | 329.9882 | 0 | 84 | 10 | 15 | -103 | 7555.44
2009-10-12 02:26 | 60.019 | 3671.1931 | 350 | 329.9882 | 0 | 84.5 | 10 | 15 | -103 | 7555.77
2009-10-12 02:26 | 60.026 | 3671.189 | 350 | 329.9882 | 0 | 85 | 10 | 15 | -103 | 7556.1
2009-10-12 02:26 | 60.019 | 3664.4951 | 350 | 329.9882 | 0 | 85.5 | 10 | 15 | -103 | 7556.43
2009-10-12 02:26 | 60.02 | 3666.8208 | 350 | 329.9882 | 0 | 86 | 10 | 15 | -103 | 7556.76
2009-10-12 02:26 | 60.021 | 3670.2668 | 350 | 255.4442 | 0 | 86.5 | 10 | 15 | -103 | 7557.09
2009-10-12 02:26 | 60.019 | 3672.4932 | 350 | 165.1017 | 0 | 87 | 10 | 15 | -103 | 7557.42
2009-10-12 02:27 | 60.022 | 3672.1641 | 350 | 165.1017 | 0 | 87.5 | 10 | 15 | -103 | 7557.75
2009-10-12 02:27 | 60.037 | 3669.9829 | 350 | 165.1017 | 0 | 88 | 10 | 15 | -103 | 7558.08
2009-10-12 02:27 | 60.037 | 3661.5991 | 350 | 165.1017 | 0 | 88.5 | 10 | 15 | -103 | 7558.41
2009-10-12 02:27 | 60.048 | 3651.4917 | 350 | 165.1017 | 0 | 89 | 10 | 15 | -103 | 7558.74
2009-10-12 02:27 | 60.041 | 3648.2463 | 350 | 165.4764 | 0 | 89.5 | 10 | 15 | -103 | 7559.07
2009-10-12 02:27 | 60.039 | 3654.2944 | 350 | 165.4764 | 0 | 90 | 10 | 15 | -103 | 7559.4
2009-10-12 02:27 | 60.043 | 3651.0593 | 350 | 165.4764 | 0 | 90.5 | 10 | 15 | -103 | 7559.73
2009-10-12 02:27 | 60.041 | 3648.2363 | 350 | 165.4764 | 0 | 91 | 10 | 15 | -103 | 7560.06
2009-10-12 02:27 | 60.041 | 3645.4458 | 350 | 165.4764 | 0 | 91.5 | 10 | 15 | -103 | 7560.39
2009-10-12 02:27 | 59.852 | 3641.1912 | 335 | 206.4591 | 1 | 92 | 10 | 0 | -103 | 7560.72
2009-10-12 02:27 | 59.869 | 3734.9043 | 335 | 206.4591 | 1 | 92.5 | 10 | 0 | -103 | 7561.05
2009-10-12 02:28 | 59.88 | 3737.1567 | 335 | 206.4591 | 1 | 93 | 10 | 0 | -103 | 7561.38
2009-10-12 02:28 | 59.875 | 3766.1938 | 335 | 206.4591 | 1 | 93.5 | 10 | 0 | -103 | 7561.71
2009-10-12 02:28 | 59.886 | 3769.925 | 335 | 206.4591 | 1 | 94 | 10 | 0 | -103 | 7562.04
2009-10-12 02:28 | 59.887 | 3782.4995 | 335 | 211.256 | 1 | 94.5 | 10 | 0 | -103 | 7562.37
2009-10-12 02:28 | 59.895 | 3784.7297 | 335 | 211.256 | 1 | 95 | 10 | 0 | -103 | 7562.7
2009-10-12 02:28 | 59.893 | 3788.3276 | 335 | 211.256 | 2 | 95.5 | 10 | 0 | -103 | 7563.03
2009-10-12 02:28 | 59.891 | 3788.4719 | 335 | 211.256 | 3 | 96 | 10 | 0 | -103 | 7563.36
2009-10-12 02:28 | 59.885 | 3794.3743 | 335 | 211.256 | 4 | 96.5 | 10 | 0 | -103 | 7563.69
2009-10-12 02:28 | 59.887 | 3800.4275 | 335 | 214.3467 | 5 | 97 | 10 | 0 | -103 | 7564.02
2009-10-12 02:28 | 59.888 | 3802.925 | 335 | 214.3467 | 6 | 97.5 | 10 | 0 | -103 | 7564.35
2009-10-12 02:28 | 59.882 | 3804.3879 | 335 | 214.3467 | 7 | 98 | 10 | 0 | -103 | 7564.68
2009-10-12 02:28 | 59.857 | 3809.2373 | 335 | 214.3467 | 8 | 98.5 | 10 | 0 | -103 | 7565.01
2009-10-12 02:28 | 59.858 | 3814.8623 | 335 | 214.3467 | 9 | 99 | 10 | 0 | -103 | 7565.34
2009-10-12 02:29 | 59.866 | 3826.0532 | 335 | 212.1727 | 10 | 99.5 | 10 | 0 | -103 | 7565.67
2009-10-12 02:29 | 59.866 | 3827.5239 | 335 | 212.1727 | 11 | 100 | 10 | 0 | -103 | 7566
2009-10-12 02:29 | 59.874 | 3826.4536 | 335 | 212.1727 | 12 | 100.5 | 10 | 0 | -103 | 7566.33
2009-10-12 02:29 | 59.883 | 3823.8257 | 335 | 212.1727 | 13 | 101 | 10 | 0 | -103 | 7566.66
2009-10-12 02:29 | 59.89 | 3818.0552 | 335 | 212.1727 | 14 | 101.5 | 10 | 0 | -103 | 7566.99
2009-10-12 02:29 | 59.893 | 3815.0098 | 335 | 215.5982 | 15 | 102 | 10 | 0 | -103 | 7567.32
2009-10-12 02:29 | 59.903 | 3809.6519 | 335 | 215.5982 | 16 | 102.5 | 10 | 0 | -103 | 7567.65
2009-10-12 02:29 | 59.904 | 3805.5933 | 335 | 215.5982 | 16 | 103 | 10 | 0 | -103 | 7567.98
2009-10-12 02:29 | 59.911 | 3793.9751 | 335 | 215.5982 | 16 | 103.5 | 10 | 0 | -103 | 7568.31
2009-10-12 02:29 | 59.917 | 3791.502 | 335 | 215.5982 | 16 | 104 | 10 | 0 | -103 | 7568.64
2009-10-12 02:29 | 59.92 | 3784.5635 | 335 | 218.3273 | 16 | 104.5 | 10 | 0 | -103 | 7568.97
2009-10-12 02:29 | 59.917 | 3781.7012 | 335 | 218.3273 | 16 | 105 | 10 | 0 | -103 | 7569.3
2009-10-12 02:30 | 59.921 | 3774.6042 | 335 | 218.3273 | 16 | 105.5 | 10 | 0 | -103 | 7569.63
2009-10-12 02:30 | 59.925 | 3773.9578 | 335 | 218.3273 | 16 | 106 | 10 | 0 | -103 | 7569.96
2009-10-12 02:30 | 59.927 | 3769.6296 | 335 | 218.3273 | 16 | 106.5 | 10 | 0 | -103 | 7570.29
2009-10-12 02:30 | 59.928 | 3767.6428 | 335 | 217.3794 | 0 | 107 | 10 | 0 | -103 | 7570.62
2009-10-12 02:30 | 59.929 | 3766.7881 | 335 | 217.3794 | 0 | 107.5 | 10 | 0 | -103 | 7570.95
2009-10-12 02:30 | 59.937 | 3765.6716 | 335 | 217.3794 | 0 | 108 | 10 | 0 | -103 | 7571.28
2009-10-12 02:30 | 59.945 | 3765.105 | 335 | 217.3794 | 0 | 108.5 | 10 | 0 | -103 | 7571.61
2009-10-12 02:30 | 59.942 | 3758.3872 | 335 | 217.3794 | 0 | 109 | 10 | 0 | -103 | 7571.94
2009-10-12 02:30 | 59.942 | 3746.8887 | 335 | 214.8304 | 0 | 109.5 | 10 | 0 | -103 | 7572.27
2009-10-12 02:30 | 59.947 | 3749.5933 | 335 | 214.8304 | 0 | 110 | 10 | 0 | -103 | 7572.6
2009-10-12 02:30 | 59.951 | 3749.0769 | 335 | 214.8304 | 0 | 110.5 | 10 | 0 | -103 | 7572.93
2009-10-12 02:30 | 59.951 | 3740.259 | 335 | 214.8304 | 0 | 111 | 10 | 0 | -103 | 7573.26
2009-10-12 02:31 | 59.952 | 3727.8384 | 335 | 214.8304 | 0 | 111.5 | 10 | 0 | -103 | 7573.59
2009-10-12 02:31 | 59.952 | 3722.6489 | 335 | 227.6559 | 0 | 112 | 10 | 0 | -103 | 7573.92
2009-10-12 02:31 | 59.952 | 3718.1418 | 335 | 227.6559 | 0 | 112.5 | 10 | 0 | -103 | 7574.25
2009-10-12 02:31 | 59.952 | 3713.6938 | 335 | 227.6559 | 0 | 113 | 10 | 0 | -103 | 7574.58
2009-10-12 02:31 | 59.954 | 3710.8101 | 335 | 227.6559 | 0 | 113.5 | 10 | 0 | -103 | 7574.91
2009-10-12 02:31 | 59.956 | 3714.6226 | 335 | 227.6559 | 0 | 114 | 10 | 0 | -103 | 7575.24
2009-10-12 02:31 | 59.956 | 3716.4614 | 335 | 225.0181 | 0 | 114.5 | 10 | 0 | -103 | 7575.57
2009-10-12 02:31 | 59.961 | 3717.759 | 335 | 225.0181 | 0 | 115 | 10 | 0 | -103 | 7575.9
2009-10-12 02:31 | 59.962 | 3722.658 | 335 | 225.0181 | 0 | 115.5 | 10 | 0 | -103 | 7576.23
2009-10-12 02:31 | 59.966 | 3722.2776 | 335 | 225.0181 | 0 | 116 | 10 | 0 | -103 | 7576.56
2009-10-12 02:31 | 59.97 | 3723.9839 | 335 | 225.0181 | 0 | 116.5 | 10 | 0 | -103 | 7576.89
2009-10-12 02:32 | 59.969 | 3723.8931 | 335 | 228.3652 | 0 | 117 | 10 | 0 | -103 | 7577.22
2009-10-12 02:32 | 59.97 | 3728.053 | 335 | 228.3652 | 0 | 117.5 | 10 | 0 | -103 | 7577.55
2009-10-12 02:32 | 59.973 | 3732.53 | 335 | 228.3652 | 0 | 118 | 10 | 0 | -103 | 7577.88
2009-10-12 02:32 | 59.978 | 3736.9075 | 335 | 228.3652 | 0 | 118.5 | 10 | 0 | -103 | 7578.21
2009-10-12 02:32 | 59.978 | 3738.6992 | 335 | 228.3652 | 0 | 119 | 10 | 0 | -103 | 7578.54
2009-10-12 02:32 | 59.978 | 3741.7937 | 335 | 234.0753 | 0 | 119.5 | 10 | 0 | -103 | 7578.87
2009-10-12 02:32 | 59.982 | 3746.6079 | 335 | 234.0753 | 0 | 120 | 10 | 0 | -103 | 7579.2
2009-10-12 02:32 | 59.98 | 3751.5576 | 335 | 234.0753 | 0 | 120.5 | 10 | 0 | -103 | 7579.53
2009-10-12 02:32 | 59.979 | 3755.5986 | 335 | 234.0753 | 0 | 121 | 10 | 0 | -103 | 7579.86
2009-10-12 02:32 | 59.983 | 3760.4053 | 335 | 234.0753 | 0 | 121.5 | 10 | 0 | -103 | 7580.19
2009-10-12 02:32 | 59.989 | 3761.407 | 335 | 228.7982 | 0 | 122 | 10 | 0 | -103 | 7580.52
2009-10-12 02:32 | 59.987 | 3764.9575 | 335 | 228.7982 | 0 | 122.5 | 10 | 0 | -103 | 7580.85
2009-10-12 02:33 | 59.992 | 3766.4331 | 335 | 354.8957 | 0 | 123 | 10 | 0 | -103 | 7581.18
2009-10-12 02:33 | 59.989 | 3768.6335 | 335 | 354.8957 | 0 | 123.5 | 10 | 0 | -103 | 7581.51
2009-10-12 02:33 | 59.983 | 3772.4446 | 335 | 340.4694 | 0 | 124 | 10 | 0 | -103 | 7581.84
2009-10-12 02:33 | 59.993 | 3775.8408 | 335 | 340.4694 | 0 | 124.5 | 10 | 0 | -103 | 7582.17
2009-10-12 02:33 | 59.999 | 3774.8662 | 335 | 340.4694 | 0 | 125 | 10 | 0 | -103 | 7582.5
2009-10-12 02:33 | 59.999 | 3778.5537 | 335 | 340.4694 | 0 | 125.5 | 10 | 0 | -103 | 7582.83
2009-10-12 02:33 | 60.002 | 3781.2559 | 335 | 340.4694 | 0 | 126 | 10 | 0 | -103 | 7583.16
2009-10-12 02:33 | 60.007 | 3783.8955 | 335 | 337.6429 | 0 | 126.5 | 10 | 0 | -103 | 7583.49
2009-10-12 02:33 | 60.014 | 3785.7681 | 335 | 337.6429 | 0 | 127 | 10 | 0 | -103 | 7583.82
2009-10-12 02:33 | 60.019 | 3786.3042 | 335 | 337.6429 | 0 | 127.5 | 10 | 0 | -103 | 7584.15
2009-10-12 02:33 | 60.017 | 3787.5159 | 335 | 337.6429 | 0 | 128 | 10 | 0 | -103 | 7584.48
2009-10-12 02:33 | 60.023 | 3788.6067 | 335 | 337.6429 | 0 | 128.5 | 10 | 0 | -103 | 7584.81
2009-10-12 02:34 | 60.021 | 3787.5366 | 335 | 284.3608 | 0 | 129 | 10 | 0 | -103 | 7585.14
2009-10-12 02:34 | 60.024 | 3787.9304 | 335 | 284.3608 | 0 | 129.5 | 10 | 0 | -103 | 7585.47
2009-10-12 02:34 | 60.02 | 3786.8748 | 350 | 284.3608 | 0 | 130 | 10 | 0 | -103 | 7585.8
2009-10-12 02:34 | 60.024 | 3785.0181 | 350 | 284.3608 | 0 | 130.5 | 10 | 0 | -103 | 7586.13
2009-10-12 02:34 | 60.022 | 3785.9492 | 350 | 284.3608 | 0 | 131 | 10 | 0 | -103 | 7586.46
2009-10-12 02:34 | 60.022 | 3786.8772 | 350 | 260.468 | 0 | 131.5 | 10 | 0 | -103 | 7586.79
2009-10-12 02:34 | 60.023 | 3785.7261 | 350 | 260.468 | 0 | 132 | 10 | 0 | -103 | 7587.12
2009-10-12 02:34 | 60.022 | 3785.7983 | 350 | 260.468 | 0 | 132.5 | 10 | 0 | -103 | 7587.45
2009-10-12 02:34 | 60.018 | 3786.9392 | 350 | 260.468 | 0 | 133 | 10 | 0 | -103 | 7587.78
2009-10-12 02:34 | 60.018 | 3789.6733 | 350 | 260.468 | 0 | 133.5 | 10 | 0 | -103 | 7588.11
2009-10-12 02:34 | 60.016 | 3788.4788 | 350 | 253.1415 | 0 | 134 | 10 | 0 | -103 | 7588.44
2009-10-12 02:34 | 60.016 | 3789.0049 | 350 | 253.1415 | 0 | 134.5 | 10 | 0 | -103 | 7588.77
2009-10-12 02:34 | 60.012 | 3788.9329 | 350 | 253.1415 | 0 | 135 | 10 | 0 | -103 | 7589.1
2009-10-12 02:35 | 60.01 | 3790.4111 | 350 | 253.1415 | 0 | 135.5 | 10 | 0 | -103 | 7589.43
2009-10-12 02:35 | 60.009 | 3791.5398 | 350 | 253.1415 | 0 | 136 | 10 | 0 | -103 | 7589.76
2009-10-12 02:35 | 60.01 | 3791.4431 | 350 | 251.9299 | 0 | 136.5 | 10 | 0 | -103 | 7590.09
2009-10-12 02:35 | 59.995 | 3790.603 | 350 | 251.9299 | 0 | 137 | 10 | 0 | -103 | 7590.42
2009-10-12 02:35 | 59.991 | 3789.585 | 350 | 251.9299 | 0 | 137.5 | 10 | 0 | -103 | 7590.75
2009-10-12 02:35 | 59.988 | 3788.105 | 350 | 251.9299 | 0 | 138 | 10 | 0 | -103 | 7591.08
2009-10-12 02:35 | 59.985 | 3788.4973 | 350 | 251.9299 | 0 | 138.5 | 10 | 0 | -103 | 7591.41
2009-10-12 02:35 | 59.984 | 3788.5708 | 350 | 250.6742 | 0 | 139 | 10 | 0 | -103 | 7591.74
2009-10-12 02:35 | 59.981 | 3786.4529 | 350 | 250.6742 | 0 | 139.5 | 10 | 0 | -103 | 7592.07
2009-10-12 02:35 | 59.977 | 3788.8135 | 350 | 250.6742 | 0 | 140 | 10 | 0 | -103 | 7592.4
2009-10-12 02:35 | 59.976 | 3788.4097 | 350 | 250.6742 | 0 | 140.5 | 10 | 0 | -103 | 7592.73
2009-10-12 02:36 | 59.978 | 3790.6646 | 350 | 250.6742 | 0 | 141 | 10 | 0 | -103 | 7593.06
2009-10-12 02:36 | 59.974 | 3789.2671 | 350 | 253.6319 | 0 | 141.5 | 10 | 0 | -103 | 7593.39
2009-10-12 02:36 | 59.977 | 3790.4304 | 350 | 253.6319 | 0 | 142 | 10 | 0 | -103 | 7593.72
2009-10-12 02:36 | 59.973 | 3787.4421 | 350 | 253.6319 | 0 | 142.5 | 10 | 0 | -103 | 7594.05
2009-10-12 02:36 | 59.971 | 3790.6016 | 350 | 253.6319 | 0 | 143 | 10 | 0 | -103 | 7594.38
2009-10-12 02:36 | 59.978 | 3792.3113 | 350 | 253.6319 | 0 | 143.5 | 10 | 0 | -103 | 7594.71
2009-10-12 02:36 | 59.975 | 3788.0796 | 350 | 246.9573 | 0 | 144 | 10 | 15 | -103 | 7595.04
2009-10-12 02:36 | 59.976 | 3787.1643 | 350 | 246.9573 | 0 | 144.5 | 10 | 15 | -103 | 7595.37
2009-10-12 02:36 | 59.969 | 3787.4048 | 350 | 246.9573 | 0 | 145 | 10 | 15 | -103 | 7595.7
2009-10-12 02:36 | 59.965 | 3789.2139 | 350 | 246.9573 | 0 | 145.5 | 10 | 15 | -103 | 7596.03
2009-10-12 02:36 | 59.97 | 3791.2212 | 350 | 246.9573 | 0 | 146 | 10 | 15 | -103 | 7596.36
2009-10-12 02:36 | 59.965 | 3788.8242 | 350 | 254.5418 | 0 | 146.5 | 10 | 15 | -103 | 7596.69
2009-10-12 02:36 | 59.972 | 3789.1675 | 350 | 254.5418 | 0 | 147 | 10 | 15 | -103 | 7597.02
2009-10-12 02:37 | 59.967 | 3784.8306 | 350 | 254.5418 | 0 | 147.5 | 10 | 15 | -103 | 7597.35
2009-10-12 02:37 | 59.969 | 3784.3203 | 350 | 254.5418 | 0 | 148 | 10 | 15 | -103 | 7597.68
2009-10-12 02:37 | 59.967 | 3779.3516 | 350 | 254.5418 | 0 | 148.5 | 10 | 15 | -103 | 7598.01
2009-10-12 02:37 | 59.971 | 3778.6333 | 350 | 256.5716 | 0 | 149 | 10 | 15 | -103 | 7598.34
2009-10-12 02:37 | 59.965 | 3776.4292 | 350 | 256.5716 | 0 | 149.5 | 10 | 15 | -103 | 7598.67
2009-10-12 02:37 | 59.97 | 3776.5967 | 350 | 256.5716 | 0 | 150 | 10 | 15 | -103 | 7599
2009-10-12 02:37 | 59.969 | 3773.1699 | 350 | 256.5716 | 0 | 150.5 | 10 | 15 | -103 | 7599.33
2009-10-12 02:37 | 59.965 | 3768.793 | 350 | 256.5716 | 0 | 151 | 10 | 15 | -103 | 7599.66
2009-10-12 02:37 | 59.973 | 3767.3662 | 350 | 258.3726 | 0 | 151.5 | 10 | 15 | -103 | 7599.99
2009-10-12 02:37 | 59.968 | 3760.2954 | 350 | 258.3726 | 0 | 152 | 10 | 15 | -103 | 7600.32
2009-10-12 02:37 | 59.967 | 3761.7766 | 350 | 258.3726 | 0 | 152.5 | 10 | 15 | -103 | 7600.65
2009-10-12 02:38 | 59.979 | 3760.1575 | 350 | 258.3726 | 0 | 153 | 10 | 15 | -103 | 7600.98
2009-10-12 02:38 | 59.983 | 3757.7729 | 350 | 258.3726 | 0 | 153.5 | 10 | 15 | -103 | 7601.31
2009-10-12 02:38 | 59.965 | 3753.0874 | 350 | 263.0474 | 0 | 154 | 10 | 15 | -103 | 7601.64
2009-10-12 02:38 | 59.962 | 3758.2246 | 350 | 263.0474 | 0 | 154.5 | 10 | 15 | -103 | 7601.97
2009-10-12 02:38 | 59.96 | 3758.041 | 350 | 263.0474 | 0 | 155 | 10 | 15 | -103 | 7602.3
2009-10-12 02:38 | 59.959 | 3763.8223 | 350 | 263.0474 | 0 | 155.5 | 10 | 15 | -103 | 7602.63
2009-10-12 02:38 | 59.953 | 3763.8582 | 350 | 263.0474 | 0 | 156 | 10 | 15 | -103 | 7602.96
2009-10-12 02:38 | 59.957 | 3768.3389 | 350 | 260.9844 | 0 | 156.5 | 10 | 15 | -103 | 7603.29
2009-10-12 02:38 | 59.963 | 3767.4375 | 350 | 260.9844 | 0 | 157 | 10 | 15 | -103 | 7603.62
2009-10-12 02:38 | 59.959 | 3761.5703 | 350 | 260.9844 | 0 | 157.5 | 10 | 15 | -103 | 7603.95
2009-10-12 02:38 | 59.965 | 3759.627 | 350 | 260.9844 | 0 | 158 | 10 | 15 | -103 | 7604.28
2009-10-12 02:38 | 59.968 | 3750.1016 | 350 | 260.9844 | 0 | 158.5 | 10 | 15 | -103 | 7604.61
2009-10-12 02:38 | 59.973 | 3753.5103 | 350 | 261.3183 | 0 | 159 | 10 | 15 | -103 | 7604.94
2009-10-12 02:39 | 59.965 | 3753.1782 | 350 | 261.3183 | 0 | 159.5 | 10 | 15 | -103 | 7605.27
2009-10-12 02:39 | 59.972 | 3753.2905 | 350 | 261.3183 | 0 | 160 | 10 | 15 | -103 | 7605.6
2009-10-12 02:39 | 59.975 | 3749.3979 | 350 | 261.3183 | 0 | 160.5 | 10 | 15 | -103 | 7605.93
2009-10-12 02:39 | 59.974 | 3740.3704 | 350 | 261.3183 | 0 | 161 | 10 | 15 | -103 | 7606.26
2009-10-12 02:39 | 59.981 | 3745.7383 | 350 | 262.1026 | 0 | 161.5 | 10 | 15 | -103 | 7606.59
2009-10-12 02:39 | 59.982 | 3741.6182 | 350 | 262.1026 | 0 | 162 | 10 | 15 | -103 | 7606.92
2009-10-12 02:39 | 59.984 | 3738.9014 | 350 | 262.1026 | 0 | 162.5 | 10 | 15 | -103 | 7607.25
2009-10-12 02:39 | 59.979 | 3737.2732 | 350 | 262.1026 | 0 | 163 | 10 | 15 | -103 | 7607.58
2009-10-12 02:39 | 59.978 | 3735.4482 | 350 | 262.1026 | 0 | 163.5 | 10 | 15 | -103 | 7607.91
2009-10-12 02:39 | 59.981 | 3737.5405 | 350 | 262.717 | 0 | 164 | 10 | 15 | -103 | 7608.24
2009-10-12 02:39 | 59.978 | 3736.6931 | 350 | 262.717 | 0 | 164.5 | 10 | 15 | -103 | 7608.57
2009-10-12 02:40 | 59.971 | 3736.0942 | 350 | 262.717 | 0 | 165 | 10 | 15 | -103 | 7608.9
2009-10-12 02:40 | 59.974 | 3738.8748 | 350 | 262.717 | 0 | 165.5 | 10 | 15 | -103 | 7609.23
2009-10-12 02:40 | 59.972 | 3738.647 | 350 | 262.717 | 0 | 166 | 10 | 15 | -103 | 7609.56
2009-10-12 02:40 | 59.971 | 3737.8921 | 350 | 260.0165 | 0 | 166.5 | 10 | 15 | -103 | 7609.89
2009-10-12 02:40 | 59.972 | 3740.3289 | 350 | 260.0165 | 0 | 167 | 10 | 15 | -103 | 7610.22
2009-10-12 02:40 | 59.977 | 3742.5244 | 350 | 260.0165 | 0 | 167.5 | 10 | 15 | -103 | 7610.55
2009-10-12 02:40 | 59.976 | 3741.7231 | 350 | 260.0165 | 0 | 168 | 10 | 15 | -103 | 7610.88
2009-10-12 02:40 | 59.974 | 3739.9644 | 350 | 260.0165 | 0 | 168.5 | 10 | 15 | -103 | 7611.21
2009-10-12 02:40 | 59.978 | 3742.8325 | 350 | 263.8732 | 0 | 169 | 10 | 15 | -103 | 7611.54
2009-10-12 02:40 | 59.981 | 3738.9658 | 350 | 263.8732 | 0 | 169.5 | 10 | 15 | -103 | 7611.87
2009-10-12 02:40 | 59.971 | 3738.8787 | 350 | 263.8732 | 0 | 170 | 10 | 15 | -103 | 7612.2
2009-10-12 02:40 | 59.971 | 3738.5579 | 350 | 263.8732 | 0 | 170.5 | 10 | 15 | -103 | 7612.53
2009-10-12 02:40 | 59.966 | 3743.4187 | 350 | 263.8732 | 0 | 171 | 10 | 15 | -103 | 7612.86
2009-10-12 02:41 | 59.971 | 3747.3396 | 350 | 264.5979 | 0 | 171.5 | 10 | 15 | -103 | 7613.19
2009-10-12 02:41 | 59.969 | 3749.75 | 350 | 264.5979 | 0 | 172 | 10 | 15 | -103 | 7613.52
2009-10-12 02:41 | 59.974 | 3743.7451 | 350 | 264.5979 | 0 | 172.5 | 10 | 15 | -103 | 7613.85
2009-10-12 02:41 | 59.971 | 3740.2986 | 350 | 264.5979 | 0 | 173 | 10 | 15 | -103 | 7614.18
2009-10-12 02:41 | 59.982 | 3731.8296 | 350 | 264.5979 | 0 | 173.5 | 10 | 15 | -103 | 7614.51
2009-10-12 02:41 | 59.985 | 3736.2295 | 350 | 262.4159 | 0 | 174 | 10 | 15 | -103 | 7614.84
2009-10-12 02:41 | 59.989 | 3733.1152 | 350 | 262.4159 | 0 | 174.5 | 10 | 15 | -103 | 7615.17
2009-10-12 02:41 | 59.987 | 3729.1802 | 350 | 262.4159 | 0 | 175 | 10 | 15 | -103 | 7615.5
2009-10-12 02:41 | 59.994 | 3720.1079 | 350 | 262.4159 | 0 | 175.5 | 10 | 15 | -103 | 7615.83
2009-10-12 02:41 | 60.003 | 3725.6614 | 350 | 262.4159 | 0 | 176 | 10 | 15 | -103 | 7616.16
2009-10-12 02:41 | 60.006 | 3727.8247 | 350 | 259.6852 | 0 | 176.5 | 10 | 15 | -103 | 7616.49
2009-10-12 02:42 | 60.019 | 3727.2314 | 350 | 259.6852 | 0 | 177 | 10 | 15 | -103 | 7616.82
2009-10-12 02:42 | 60.025 | 3726.0156 | 350 | 259.6852 | 0 | 177.5 | 10 | 15 | -103 | 7617.15
2009-10-12 02:42 | 60.029 | 3716.3745 | 350 | 259.6852 | 0 | 178 | 10 | 15 | -103 | 7617.48
2009-10-12 02:42 | 60.037 | 3717.1421 | 350 | 259.6852 | 0 | 178.5 | 10 | 15 | -103 | 7617.81
2009-10-12 02:42 | 60.037 | 3713.6318 | 350 | 255.911 | 0 | 179 | 10 | 15 | -103 | 7618.14
2009-10-12 02:42 | 60.041 | 3699.3557 | 350 | 255.911 | 0 | 179.5 | 10 | 15 | -103 | 7618.47
2009-10-12 02:42 | 60.043 | 3704.5913 | 350 | 255.911 | 0 | 180 | 10 | 15 | -103 | 7618.8
2009-10-12 02:42 | 60.048 | 3701.3164 | 350 | 255.911 | 0 | 180.5 | 10 | 15 | -103 | 7619.13
2009-10-12 02:42 | 60.043 | 3699.5286 | 350 | 255.911 | 0 | 181 | 10 | 15 | -103 | 7619.46
2009-10-12 02:42 | 60.044 | 3690.4773 | 350 | 258.1482 | 0 | 181.5 | 10 | 15 | -103 | 7619.79
2009-10-12 02:42 | 60.045 | 3696.8772 | 350 | 258.1482 | 0 | 182 | 10 | 15 | -103 | 7620.12
2009-10-12 02:42 | 60.041 | 3696.9678 | 350 | 258.1482 | 0 | 182.5 | 10 | 15 | -103 | 7620.45
2009-10-12 02:42 | 60.036 | 3699.6306 | 350 | 258.1482 | 0 | 183 | 10 | 15 | -103 | 7620.78
2009-10-12 02:43 | 60.033 | 3700.1057 | 350 | 258.1482 | 0 | 183.5 | 10 | 15 | -103 | 7621.11
2009-10-12 02:43 | 60.037 | 3701.1218 | 350 | 258.8736 | 0 | 184 | 10 | 15 | -103 | 7621.44
2009-10-12 02:43 | 60.03 | 3701.9978 | 350 | 258.8736 | 0 | 184.5 | 10 | 15 | -103 | 7621.77
2009-10-12 02:43 | 60.033 | 3703.9092 | 350 | 258.8736 | 0 | 185 | 10 | 15 | -103 | 7622.1
2009-10-12 02:43 | 60.032 | 3704.0874 | 350 | 258.8736 | 0 | 185.5 | 10 | 15 | -103 | 7622.43
2009-10-12 02:43 | 60.033 | 3703.7063 | 350 | 258.8736 | 0 | 186 | 10 | 15 | -103 | 7622.76
2009-10-12 02:43 | 60.035 | 3704.3601 | 350 | 249.3376 | 0 | 186.5 | 10 | 15 | -103 | 7623.09
2009-10-12 02:43 | 60.039 | 3702.2043 | 350 | 249.3376 | 0 | 187 | 10 | 15 | -103 | 7623.42
2009-10-12 02:43 | 60.039 | 3703.3179 | 350 | 249.3376 | 0 | 187.5 | 10 | 15 | -103 | 7623.75
2009-10-12 02:43 | 60.038 | 3702.5249 | 350 | 249.3376 | 0 | 188 | 10 | 15 | -103 | 7624.08
2009-10-12 02:43 | 60.037 | 3702.8652 | 350 | 249.3376 | 0 | 188.5 | 10 | 15 | -103 | 7624.41
2009-10-12 02:44 | 60.04 | 3702.2795 | 350 | 258.2782 | 0 | 189 | 10 | 15 | -103 | 7624.74
2009-10-12 02:44 | 60.045 | 3700.2759 | 350 | 258.2782 | 0 | 189.5 | 10 | 15 | -103 | 7625.07
2009-10-12 02:44 | 60.043 | 3697.7285 | 350 | 258.2782 | 0 | 190 | 10 | 15 | -103 | 7625.4
2009-10-12 02:44 | 60.044 | 3697.3459 | 350 | 258.2782 | 0 | 190.5 | 10 | 15 | -103 | 7625.73
2009-10-12 02:44 | 60.034 | 3694.7629 | 350 | 258.2782 | 0 | 191 | 10 | 15 | -103 | 7626.06
2009-10-12 02:44 | 60.039 | 3696.7983 | 350 | 258.4064 | 0 | 191.5 | 10 | 15 | -103 | 7626.39
2009-10-12 02:44 | 60.034 | 3701.791 | 350 | 258.4064 | 0 | 192 | 10 | 15 | -103 | 7626.72
2009-10-12 02:44 | 60.032 | 3702.1479 | 350 | 258.4064 | 0 | 192.5 | 10 | 15 | -103 | 7627.05
2009-10-12 02:44 | 60.027 | 3707.521 | 350 | 258.4064 | 0 | 193 | 10 | 15 | -103 | 7627.38
2009-10-12 02:44 | 60.032 | 3707.3403 | 350 | 258.4064 | 0 | 193.5 | 10 | 15 | -103 | 7627.71
2009-10-12 02:44 | 60.033 | 3707.3838 | 350 | 260.5389 | 0 | 194 | 10 | 15 | -103 | 7628.04
2009-10-12 02:44 | 60.039 | 3706.8232 | 350 | 260.5389 | 0 | 194.5 | 10 | 15 | -103 | 7628.37
2009-10-12 02:44 | 60.035 | 3701.582 | 350 | 260.5389 | 0 | 195 | 10 | 15 | -103 | 7628.7
2009-10-12 02:45 | 60.04 | 3702.2122 | 350 | 260.5389 | 0 | 195.5 | 10 | 15 | -103 | 7629.03
2009-10-12 02:45 | 60.036 | 3700.3975 | 350 | 260.5389 | 0 | 196 | 10 | 15 | -103 | 7629.36
2009-10-12 02:45 | 60.045 | 3700.8271 | 350 | 257.8821 | 0 | 196.5 | 10 | 15 | -103 | 7629.69
2009-10-12 02:45 | 60.042 | 3696.9351 | 350 | 257.8821 | 0 | 197 | 10 | 15 | -103 | 7630.02
2009-10-12 02:45 | 60.044 | 3693.8242 | 350 | 257.8821 | 0 | 197.5 | 10 | 15 | -103 | 7630.35
2009-10-12 02:45 | 60.041 | 3696.897 | 350 | 257.8821 | 0 | 198 | 10 | 15 | -103 | 7630.68
2009-10-12 02:45 | 60.045 | 3697.5024 | 350 | 257.8821 | 0 | 198.5 | 10 | 15 | -103 | 7631.01
2009-10-12 02:45 | 60.039 | 3700.1768 | 350 | 258.5887 | 0 | 199 | 10 | 15 | -103 | 7631.34
2009-10-12 02:45 | 60.042 | 3697.6807 | 350 | 258.5887 | 0 | 199.5 | 10 | 15 | -103 | 7631.67
2009-10-12 02:45 | 60.036 | 3698.3589 | 350 | 258.5887 | 0 | 200 | 10 | 15 | -103 | 7632
2009-10-12 02:45 | 60.039 | 3700.2622 | 350 | 258.5887 | 0 | 200.5 | 10 | 15 | -103 | 7632.33
2009-10-12 02:46 | 60.039 | 3700.9023 | 350 | 258.5887 | 0 | 201 | 10 | 15 | -103 | 7632.66
2009-10-12 02:46 | 60.038 | 3701.1394 | 350 | 261.9062 | 0 | 201.5 | 10 | 15 | -103 | 7632.99
2009-10-12 02:46 | 60.037 | 3700.2644 | 350 | 261.9062 | 0 | 202 | 10 | 15 | -103 | 7633.32
2009-10-12 02:46 | 60.037 | 3700.4575 | 350 | 261.9062 | 0 | 202.5 | 10 | 15 | -103 | 7633.65
2009-10-12 02:46 | 60.036 | 3698.7944 | 350 | 261.9062 | 0 | 203 | 10 | 15 | -103 | 7633.98
2009-10-12 02:46 | 60.033 | 3700.6614 | 350 | 261.9062 | 0 | 203.5 | 10 | 15 | -103 | 7634.31
2009-10-12 02:46 | 60.032 | 3702.9675 | 350 | 256.7478 | 0 | 204 | 10 | 15 | -103 | 7634.64
2009-10-12 02:46 | 60.037 | 3705.7751 | 350 | 256.7478 | 0 | 204.5 | 10 | 15 | -103 | 7634.97
2009-10-12 02:46 | 60.036 | 3703.7441 | 350 | 256.7478 | 0 | 205 | 10 | 15 | -103 | 7635.3
2009-10-12 02:46 | 60.032 | 3700.7471 | 350 | 256.7478 | 0 | 205.5 | 10 | 15 | -103 | 7635.63
2009-10-12 02:46 | 60.034 | 3705.0593 | 350 | 256.7478 | 0 | 206 | 10 | 15 | -103 | 7635.96
2009-10-12 02:46 | 60.038 | 3703.8308 | 350 | 167.432 | 0 | 206.5 | 10 | 15 | -103 | 7636.29
2009-10-12 02:46 | 60.042 | 3702.7954 | 350 | 167.432 | 0 | 207 | 10 | 15 | -103 | 7636.62
2009-10-12 02:47 | 60.04 | 3696.2495 | 350 | 167.432 | 0 | 207.5 | 10 | 15 | -103 | 7636.95
2009-10-12 02:47 | 60.043 | 3693.5181 | 350 | 167.432 | 0 | 208 | 10 | 15 | -103 | 7637.28
2009-10-12 02:47 | 60.04 | 3695.1855 | 350 | 167.432 | 0 | 208.5 | 10 | 15 | -103 | 7637.61
2009-10-12 02:47 | 60.044 | 3694.7534 | 350 | 164.9734 | 0 | 209 | 10 | 15 | -103 | 7637.94
2009-10-12 02:47 | 60.036 | 3694.1594 | 350 | 164.9734 | 0 | 209.5 | 10 | 15 | -103 | 7638.27
2009-10-12 02:47 | 60.042 | 3692.6863 | 350 | 164.9734 | 0 | 210 | 10 | 15 | -103 | 7638.6
2009-10-12 02:47 | 60.043 | 3692.3569 | 350 | 164.9734 | 0 | 210.5 | 10 | 15 | -103 | 7638.93
2009-10-12 02:47 | 60.039 | 3690.8362 | 350 | 164.9734 | 0 | 211 | 10 | 15 | -103 | 7639.26
2009-10-12 02:47 | 60.034 | 3694.1172 | 350 | 157.6281 | 0 | 211.5 | 10 | 15 | -103 | 7639.59
2009-10-12 02:47 | 60.035 | 3695.5808 | 350 | 157.6281 | 0 | 212 | 10 | 15 | -103 | 7639.92
2009-10-12 02:47 | 60.03 | 3696.3049 | 350 | 157.6281 | 0 | 212.5 | 10 | 15 | -103 | 7640.25
2009-10-12 02:48 | 60.031 | 3697.3357 | 350 | 157.6281 | 0 | 213 | 10 | 15 | -103 | 7640.58
2009-10-12 02:48 | 60.032 | 3699.2512 | 350 | 157.6281 | 0 | 213.5 | 10 | 15 | -103 | 7640.91
2009-10-12 02:48 | 60.032 | 3699.1052 | 350 | 155.5317 | 0 | 214 | 10 | 15 | -103 | 7641.24
2009-10-12 02:48 | 60.033 | 3698.136 | 350 | 155.5317 | 0 | 214.5 | 10 | 15 | -103 | 7641.57
2009-10-12 02:48 | 60.039 | 3697.4119 | 350 | 155.5317 | 0 | 215 | 10 | 15 | -103 | 7641.9
2009-10-12 02:48 | 60.036 | 3693.2236 | 350 | 155.5317 | 0 | 215.5 | 10 | 15 | -103 | 7642.23
2009-10-12 02:48 | 60.04 | 3691.9189 | 350 | 155.5317 | 0 | 216 | 10 | 15 | -103 | 7642.56
2009-10-12 02:48 | 60.036 | 3692.3735 | 350 | 160.4472 | 0 | 216.5 | 10 | 15 | -103 | 7642.89
2009-10-12 02:48 | 60.041 | 3694.7102 | 350 | 160.4472 | 0 | 217 | 10 | 15 | -103 | 7643.22
2009-10-12 02:48 | 60.036 | 3693.6172 | 350 | 160.4472 | 0 | 217.5 | 10 | 15 | -103 | 7643.55
2009-10-12 02:48 | 60.038 | 3694.27 | 350 | 160.4472 | 0 | 218 | 10 | 15 | -103 | 7643.88
2009-10-12 02:48 | 60.041 | 3692.5322 | 350 | 160.4472 | 0 | 218.5 | 10 | 15 | -103 | 7644.21
2009-10-12 02:49 | 60.036 | 3691.0117 | 350 | 163.9586 | 0 | 219 | 10 | 15 | -103 | 7644.54
2009-10-12 02:49 | 60.038 | 3693.7271 | 350 | 163.9586 | 0 | 219.5 | 10 | 15 | -103 | 7644.87
2009-10-12 02:49 | 60.034 | 3692.6406 | 350 | 163.9586 | 0 | 220 | 10 | 15 | -103 | 7645.2
2009-10-12 02:49 | 60.031 | 3688.2085 | 350 | 163.9586 | 0 | 220.5 | 10 | 15 | -103 | 7645.53
2009-10-12 02:49 | 60.029 | 3693.1724 | 350 | 163.9586 | 0 | 221 | 10 | 15 | -103 | 7645.86
2009-10-12 02:49 | 60.03 | 3695.2249 | 350 | 166.0724 | 0 | 221.5 | 10 | 15 | -103 | 7646.19
2009-10-12 02:49 | 60.022 | 3693.4116 | 350 | 166.0724 | 0 | 222 | 10 | 15 | -103 | 7646.52
2009-10-12 02:49 | 60.024 | 3698.0122 | 350 | 166.0724 | 0 | 222.5 | 10 | 15 | -103 | 7646.85
2009-10-12 02:49 | 60.021 | 3699.4143 | 350 | 166.0724 | 0 | 223 | 10 | 15 | -103 | 7647.18
2009-10-12 02:49 | 60.025 | 3700.5442 | 350 | 166.0724 | 0 | 223.5 | 10 | 15 | -103 | 7647.51
2009-10-12 02:49 | 60.025 | 3698.5957 | 350 | 163.7666 | 0 | 224 | 10 | 15 | -103 | 7647.84
2009-10-12 02:49 | 60.024 | 3700.8025 | 350 | 163.7666 | 0 | 224.5 | 10 | 15 | -103 | 7648.17
2009-10-12 02:50 | 60.023 | 3701.4502 | 350 | 163.7666 | 0 | 225 | 10 | 15 | -103 | 7648.5
2009-10-12 02:50 | 60.026 | 3701.7017 | 350 | 163.7666 | 0 | 225.5 | 10 | 15 | -103 | 7648.83
2009-10-12 02:50 | 60.024 | 3701.9648 | 350 | 163.7666 | 0 | 226 | 10 | 15 | -103 | 7649.16
2009-10-12 02:50 | 60.025 | 3701.0898 | 350 | 165.1017 | 0 | 226.5 | 10 | 15 | -103 | 7649.49
2009-10-12 02:50 | 60.023 | 3701.2046 | 350 | 165.1017 | 0 | 227 | 10 | 15 | -103 | 7649.82
2009-10-12 02:50 | 60.024 | 3700.1768 | 350 | 165.1017 | 0 | 227.5 | 10 | 15 | -103 | 7650.15
2009-10-12 02:50 | 60.026 | 3700.2773 | 350 | 165.1017 | 0 | 228 | 10 | 15 | -103 | 7650.48
2009-10-12 02:50 | 60.02 | 3700.2603 | 350 | 165.1017 | 0 | 228.5 | 10 | 15 | -103 | 7650.81
2009-10-12 02:50 | 60.015 | 3699.9255 | 350 | 165.4764 | 0 | 229 | 10 | 15 | -103 | 7651.14
2009-10-12 02:50 | 60.017 | 3703.5161 | 350 | 165.4764 | 0 | 229.5 | 10 | 15 | -103 | 7651.47
2009-10-12 02:50 | 60.017 | 3703.6724 | 350 | 165.4764 | 0 | 230 | 10 | 15 | -103 | 7651.8
2009-10-12 02:50 | 60.012 | 3702.9214 | 350 | 165.4764 | 0 | 230.5 | 10 | 15 | -103 | 7652.13
2009-10-12 02:50 | 60.002 | 3703.1667 | 350 | 165.4764 | 0 | 231 | 10 | 15 | -103 | 7652.46
2009-10-12 02:51 | 59.999 | 3703.7754 | 350 | 206.4591 | 0 | 231.5 | 10 | 15 | -103 | 7652.79
2009-10-12 02:51 | 60.004 | 3701.5337 | 350 | 206.4591 | 0 | 232 | 10 | 0 | -103 | 7616
2009-10-12 02:51 | 59.996 | 3700.6252 | 335 | 206.4591 | 0 | 232.5 | 10 | 0 | -103 | 7626
2009-10-12 02:51 | 59.989 | 3701.7366 | 335 | 206.4591 | 0 | 233 | 10 | 0 | -103 | 7632
2009-10-12 02:51 | 59.985 | 3700.9771 | 335 | 206.4591 | 0 | 233.5 | 10 | 0 | -103 | 7632
2009-10-12 02:51 | 59.984 | 3699.8538 | 335 | 211.256 | 0 | 234 | 10 | 0 | -103 | 7632
2009-10-12 02:51 | 59.98 | 3700.7698 | 335 | 211.256 | 1 | 234.5 | 10 | 0 | -103 | 7632
2009-10-12 02:51 | 59.976 | 3701.6252 | 335 | 211.256 | 1 | 235 | 10 | 0 | -103 | 7632
2009-10-12 02:51 | 59.974 | 3704.7847 | 335 | 211.256 | 1 | 235.5 | 10 | 0 | -103 | 7632
2009-10-12 02:51 | 59.973 | 3706.958 | 335 | 211.256 | 1 | 236 | 10 | 0 | -103 | 7632
2009-10-12 02:51 | 59.971 | 3706.2571 | 335 | 214.3467 | 1 | 236.5 | 10 | 0 | -103 | 7632
2009-10-12 02:52 | 59.98 | 3710.1182 | 335 | 214.3467 | 1 | 237 | 10 | 0 | -103 | 7632
2009-10-12 02:52 | 59.982 | 3708.0181 | 335 | 214.3467 | 1 | 237.5 | 10 | 0 | -103 | 7632
2009-10-12 02:52 | 59.981 | 3706.3425 | 335 | 214.3467 | 2 | 238 | 10 | 0 | -103 | 7632
2009-10-12 02:52 | 59.978 | 3706.1187 | 335 | 214.3467 | 3 | 238.5 | 10 | 0 | -103 | 7632
2009-10-12 02:52 | 59.977 | 3707.7209 | 335 | 212.1727 | 4 | 239 | 10 | 0 | -103 | 7632
2009-10-12 02:52 | 59.978 | 3708.5305 | 335 | 212.1727 | 5 | 239.5 | 10 | 0 | -103 | 7632
2009-10-12 02:52 | 59.97 | 3707.24 | 335 | 212.1727 | 6 | 240 | 10 | 0 | -103 | 7632
2009-10-12 02:52 | 59.971 | 3711.75 | 335 | 212.1727 | 7 | 240.5 | 10 | 0 | -103 | 7632
2009-10-12 02:52 | 59.999 | 3710.6953 | 335 | 212.1727 | 8 | 241 | 10 | 0 | -103 | 7632
2009-10-12 02:52 | 59.998 | 3705.6392 | 335 | 215.5982 | 9 | 241.5 | 10 | 0 | -103 | 7632
2009-10-12 02:52 | 60.005 | 3703.1909 | 335 | 215.5982 | 10 | 242 | 10 | 0 | -103 | 7632
2009-10-12 02:52 | 60.01 | 3698.658 | 335 | 215.5982 | 11 | 242.5 | 10 | 0 | -103 | 7632
2009-10-12 02:52 | 60.022 | 3697.8821 | 335 | 215.5982 | 12 | 243 | 10 | 0 | -103 | 7632
2009-10-12 02:53 | 60.025 | 3697.8684 | 335 | 215.5982 | 13 | 243.5 | 10 | 0 | -103 | 7632
2009-10-12 02:53 | 60.023 | 3693.9121 | 335 | 218.3273 | 14 | 244 | 10 | 0 | -103 | 7632
2009-10-12 02:53 | 60.029 | 3688.021 | 335 | 218.3273 | 15 | 244.5 | 10 | 0 | -103 | 7632
2009-10-12 02:53 | 60.028 | 3688.2368 | 335 | 218.3273 | 16 | 245 | 10 | 0 | -103 | 7632
2009-10-12 02:53 | 60.032 | 3686.6831 | 335 | 218.3273 | 16 | 245.5 | 10 | 0 | -103 | 7632
2009-10-12 02:53 | 60.031 | 3685.5762 | 335 | 218.3273 | 16 | 246 | 10 | 0 | -103 | 7632
2009-10-12 02:53 | 60.021 | 3686.418 | 335 | 217.3794 | 16 | 246.5 | 10 | 0 | -103 | 7632
2009-10-12 02:53 | 60.017 | 3688.9971 | 335 | 217.3794 | 16 | 247 | 10 | 0 | -103 | 7632
2009-10-12 02:53 | 60.016 | 3692.7153 | 335 | 217.3794 | 16 | 247.5 | 10 | 0 | -103 | 7631
2009-10-12 02:53 | 60.012 | 3692.4617 | 335 | 217.3794 | 16 | 248 | 10 | 0 | -103 | 7625
2009-10-12 02:53 | 60.008 | 3693.7434 | 335 | 217.3794 | 16 | 248.5 | 10 | 0 | -103 | 7623
2009-10-12 02:54 | 60.005 | 3694.6807 | 335 | 214.8304 | 16 | 249 | 10 | 0 | -103 | 7621
2009-10-12 02:54 | 59.999 | 3693.7495 | 335 | 214.8304 | 16 | 249.5 | 10 | 0 | -103 | 7623
2009-10-12 02:54 | 60 | 3692.8062 | 335 | 214.8304 | 16 | 250 | 10 | 0 | -103 | 7625
2009-10-12 02:54 | 59.995 | 3691.0769 | 335 | 214.8304 | 16 | 250.5 | 10 | 0 | -103 | 7627
2009-10-12 02:54 | 59.993 | 3689.7974 | 335 | 214.8304 | 16 | 251 | 10 | 0 | -103 | 7628
2009-10-12 02:54 | 59.985 | 3689.5535 | 335 | 227.6559 | 16 | 251.5 | 10 | 0 | -103 | 7628
2009-10-12 02:54 | 59.988 | 3689.7356 | 335 | 227.6559 | 16 | 252 | 10 | 0 | -103 | 7629
2009-10-12 02:54 | 59.983 | 3687.4937 | 335 | 227.6559 | 16 | 252.5 | 10 | 0 | -103 | 7630
2009-10-12 02:54 | 59.986 | 3686.7073 | 335 | 227.6559 | 16 | 253 | 10 | 0 | -103 | 7631
2009-10-12 02:54 | 59.99 | 3684.3335 | 335 | 227.6559 | 16 | 253.5 | 10 | 0 | -103 | 7635
2009-10-12 02:54 | 59.984 | 3683.7349 | 335 | 225.0181 | 16 | 254 | 10 | 0 | -103 | 7638
2009-10-12 02:54 | 59.982 | 3683.4731 | 335 | 225.0181 | 16 | 254.5 | 10 | 0 | -103 | 7639
2009-10-12 02:54 | 59.978 | 3684.8843 | 335 | 225.0181 | 16 | 255 | 10 | 0 | -103 | 7642
2009-10-12 02:55 | 59.975 | 3685.0869 | 335 | 225.0181 | 16 | 255.5 | 10 | 0 | -103 | 7644
2009-10-12 02:55 | 59.976 | 3685.196 | 335 | 225.0181 | 16 | 256 | 10 | 0 | -103 | 7645
2009-10-12 02:55 | 59.979 | 3688.5986 | 335 | 228.3652 | 16 | 256.5 | 10 | 0 | -103 | 7647
2009-10-12 02:55 | 59.979 | 3686.6782 | 335 | 228.3652 | 16 | 257 | 10 | 0 | -103 | 7648
2009-10-12 02:55 | 59.977 | 3685.1426 | 335 | 228.3652 | 16 | 257.5 | 10 | 0 | -103 | 7649
2009-10-12 02:55 | 59.978 | 3684.0933 | 335 | 228.3652 | 16 | 258 | 10 | 0 | -103 | 7650
2009-10-12 02:55 | 59.983 | 3682.3176 | 335 | 228.3652 | 16 | 258.5 | 10 | 0 | -103 | 7651
2009-10-12 02:55 | 59.978 | 3682.6475 | 335 | 234.0753 | 16 | 259 | 10 | 0 | -103 | 7652
2009-10-12 02:55 | 59.978 | 3684.0518 | 335 | 234.0753 | 16 | 259.5 | 10 | 0 | -103 | 7653
2009-10-12 02:55 | 59.987 | 3686.0488 | 335 | 234.0753 | 16 | 260 | 10 | 0 | -103 | 7654
2009-10-12 02:55 | 59.992 | 3683.4146 | 335 | 234.0753 | 16 | 260.5 | 10 | 0 | -103 | 7655
2009-10-12 02:55 | 59.988 | 3681.4026 | 335 | 234.0753 | 16 | 261 | 10 | 0 | -103 | 7655
2009-10-12 02:56 | 59.99 | 3671.7612 | 335 | 228.7982 | 16 | 261.5 | 10 | 0 | -103 | 7656
2009-10-12 02:56 | 59.993 | 3670.1594 | 335 | 228.7982 | 16 | 262 | 10 | 0 | -103 | 7656
2009-10-12 02:56 | 59.994 | 3681.7988 | 335 | 228.7982 | 16 | 262.5 | 10 | 0 | -103 | 7657
2009-10-12 02:56 | 59.984 | 3684.1157 | 335 | 228.7982 | 16 | 263 | 10 | 0 | -103 | 7657
2009-10-12 02:56 | 59.985 | 3684.165 | 335 | 228.7982 | 16 | 263.5 | 10 | 0 | -103 | 7658
2009-10-12 02:56 | 59.986 | 3685.5837 | 335 | 229.467 | 16 | 264 | 10 | 0 | -103 | 7658
2009-10-12 02:56 | 59.985 | 3684.9761 | 335 | 229.467 | 16 | 264.5 | 10 | 0 | -103 | 7659
2009-10-12 02:56 | 59.982 | 3684.8721 | 335 | 229.467 | 16 | 265 | 10 | 0 | -103 | 7659
2009-10-12 02:56 | 59.992 | 3685.5891 | 335 | 229.467 | 16 | 265.5 | 10 | 0 | -103 | 7659
2009-10-12 02:56 | 60.003 | 3682.5789 | 335 | 229.467 | 16 | 266 | 10 | 0 | -103 | 7660
2009-10-12 02:56 | 60.003 | 3682.2239 | 335 | 228.9802 | 16 | 266.5 | 10 | 0 | -103 | 7660
2009-10-12 02:56 | 60.002 | 3681.4585 | 335 | 228.9802 | 16 | 267 | 10 | 0 | -103 | 7661
2009-10-12 02:57 | 60.004 | 3680.167 | 335 | 228.9802 | 16 | 267.5 | 10 | 0 | -103 | 7661
2009-10-12 02:57 | 60.009 | 3679.4292 | 335 | 228.9802 | 16 | 268 | 10 | 0 | -103 | 7662
2009-10-12 02:57 | 60.017 | 3678.2673 | 335 | 228.9802 | 16 | 268.5 | 10 | 0 | -103 | 7662
2009-10-12 02:57 | 60.021 | 3676.8096 | 335 | 219.9756 | 16 | 269 | 10 | 0 | -103 | 7663
2009-10-12 02:57 | 60.018 | 3671.145 | 335 | 219.9756 | 16 | 269.5 | 10 | 0 | -103 | 7663
2009-10-12 02:57 | 60.02 | 3673.6479 | 335 | 219.9756 | 16 | 270 | 10 | 0 | -103 | 7664
2009-10-12 02:57 | 60.018 | 3676.6758 | 335 | 219.9756 | 16 | 270.5 | 10 | 0 | -103 | 7664
2009-10-12 02:57 | 60.018 | 3676.437 | 335 | 219.9756 | 16 | 271 | 10 | 0 | -103 | 7665
2009-10-12 02:57 | 60.016 | 3678.8284 | 335 | 229.0892 | 16 | 271.5 | 10 | 0 | -103 | 7666
2009-10-12 02:57 | 60.015 | 3678.9146 | 335 | 229.0892 | 16 | 272 | 10 | 0 | -103 | 7666
2009-10-12 02:57 | 60.014 | 3678.3669 | 335 | 229.0892 | 16 | 272.5 | 10 | 0 | -103 | 7667
2009-10-12 02:58 | 60.015 | 3678.5894 | 335 | 229.0892 | 16 | 273 | 10 | 0 | -103 | 7668
2009-10-12 02:58 | 60.016 | 3674.6694 | 335 | 229.0892 | 16 | 273.5 | 10 | 0 | -103 | 7668
2009-10-12 02:58 | 60.021 | 3674.4019 | 335 | 229.6633 | 16 | 274 | 10 | 0 | -103 | 7669
2009-10-12 02:58 | 60.022 | 3671.9136 | 335 | 229.6633 | 16 | 274.5 | 10 | 0 | -103 | 7669
2009-10-12 02:58 | 60.025 | 3670.9456 | 335 | 229.6633 | 16 | 275 | 10 | 0 | -103 | 7670
2009-10-12 02:58 | 60.022 | 3671.5386 | 335 | 229.6633 | 16 | 275.5 | 10 | 0 | -103 | 7670
2009-10-12 02:58 | 60.024 | 3674.0095 | 335 | 229.6633 | 16 | 276 | 10 | 0 | -103 | 7671
2009-10-12 02:58 | 60.029 | 3676.0513 | 335 | 229.2339 | 16 | 276.5 | 10 | 0 | -103 | 7671
2009-10-12 02:58 | 60.032 | 3672.5835 | 335 | 229.2339 | 16 | 277 | 10 | 0 | -103 | 7672
2009-10-12 02:58 | 60.03 | 3668.6538 | 335 | 229.2339 | 16 | 277.5 | 10 | 0 | -103 | 7673
2009-10-12 02:58 | 60.021 | 3666.3123 | 335 | 229.2339 | 16 | 278 | 10 | 0 | -103 | 7673
2009-10-12 02:58 | 60.025 | 3657.7141 | 350 | 229.2339 | 16 | 278.5 | 10 | 0 | -103 | 7673
2009-10-12 02:58 | 60.023 | 3669.3088 | 350 | 231.4099 | 16 | 279 | 10 | 0 | -103 | 7673
2009-10-12 02:59 | 60.02 | 3671.332 | 350 | 231.4099 | 16 | 279.5 | 10 | 0 | -103 | 7673
2009-10-12 02:59 | 60.02 | 3672.6831 | 350 | 231.4099 | 16 | 280 | 10 | 0 | -103 | 7673
2009-10-12 02:59 | 60.014 | 3675.6406 | 350 | 231.4099 | 16 | 280.5 | 10 | 0 | -103 | 7673
2009-10-12 02:59 | 60.011 | 3677.0093 | 350 | 231.4099 | 16 | 281 | 10 | 0 | -103 | 7673
2009-10-12 02:59 | 60.01 | 3680.0203 | 350 | 218.6223 | 16 | 281.5 | 10 | 0 | -103 | 7673
2009-10-12 02:59 | 60.012 | 3679.5967 | 350 | 218.6223 | 16 | 282 | 10 | 0 | -103 | 7673
2009-10-12 02:59 | 60.014 | 3679.0615 | 350 | 218.6223 | 16 | 282.5 | 10 | 0 | -103 | 7673
2009-10-12 02:59 | 60.011 | 3679.5869 | 350 | 218.6223 | 16 | 283 | 10 | 0 | -103 | 7673
2009-10-12 02:59 | 60.008 | 3678.4177 | 350 | 218.6223 | 16 | 283.5 | 10 | 0 | -103 | 7673
2009-10-12 02:59 | 60.013 | 3679.6809 | 350 | 213.5359 | 16 | 284 | 10 | 0 | -103 | 7673
2009-10-12 02:59 | 60.018 | 3678.4688 | 350 | 213.5359 | 16 | 284.5 | 10 | 0 | -103 | 7673
2009-10-12 03:00 | 60.019 | 3678.4556 | 350 | 213.5359 | 16 | 285 | 10 | 0 | -103 | 7673
2009-10-12 03:00 | 60.02 | 3677.4314 | 350 | 213.5359 | 16 | 285.5 | 10 | 0 | -103 | 7674
2009-10-12 03:00 | 60.016 | 3677.3154 | 350 | 213.5359 | 16 | 286 | 10 | 0 | -103 | 7675
2009-10-12 03:00 | 60.019 | 3678.8735 | 350 | 225.6519 | 16 | 286.5 | 10 | 0 | -103 | 7676
2009-10-12 03:00 | 60.018 | 3681.0581 | 350 | 225.6519 | 16 | 287 | 10 | 0 | -103 | 7677
2009-10-12 03:00 | 60.016 | 3679.5532 | 350 | 225.6519 | 16 | 287.5 | 10 | 0 | -103 | 7678
2009-10-12 03:00 | 60.015 | 3682.7297 | 350 | 225.6519 | 16 | 288 | 10 | 0 | -103 | 7679
2009-10-12 03:00 | 59.999 | 3681.9146 | 350 | 225.6519 | 16 | 288.5 | 10 | 0 | -103 | 7680
2009-10-12 03:00 | 59.982 | 3683.8135 | 350 | 212.5736 | 16 | 289 | 10 | 0 | -103 | 7681
2009-10-12 03:00 | 59.97 | 3684.6426 | 350 | 212.5736 | 16 | 289.5 | 10 | 0 | -103 | 7682
2009-10-12 03:00 | 59.968 | 3689.4038 | 350 | 212.5736 | 16 | 290 | 10 | 0 | -103 | 7684
2009-10-12 03:00 | 59.972 | 3693.7932 | 350 | 212.5736 | 16 | 290.5 | 10 | 0 | -103 | 7685
2009-10-12 03:00 | 59.964 | 3694.9736 | 350 | 212.5736 | 16 | 291 | 10 | 0 | -103 | 7687
2009-10-12 03:01 | 59.966 | 3698.6169 | 350 | 219.8973 | 16 | 291.5 | 10 | 0 | -103 | 7689
2009-10-12 03:01 | 59.965 | 3699.8501 | 350 | 219.8973 | 16 | 292 | 10 | 0 | -103 | 7690
2009-10-12 03:01 | 59.97 | 3702.218 | 350 | 219.8973 | 16 | 292.5 | 10 | 0 | -103 | 7692
2009-10-12 03:01 | 59.973 | 3703.3655 | 350 | 219.8973 | 16 | 293 | 10 | 0 | -103 | 7692
2009-10-12 03:01 | 59.976 | 3704.8994 | 350 | 219.8973 | 16 | 293.5 | 10 | 0 | -103 | 7693
2009-10-12 03:01 | 59.977 | 3704.2935 | 350 | 231.1754 | 16 | 294 | 10 | 0 | -103 | 7693
2009-10-12 03:01 | 59.976 | 3703.1421 | 350 | 231.1754 | 16 | 294.5 | 10 | 0 | -103 | 7694
2009-10-12 03:01 | 59.974 | 3705.3757 | 350 | 231.1754 | 16 | 295 | 10 | 0 | -103 | 7694
2009-10-12 03:01 | 59.976 | 3706.7764 | 350 | 231.1754 | 16 | 295.5 | 10 | 0 | -103 | 7695
2009-10-12 03:01 | 59.981 | 3706.9282 | 350 | 231.1754 | 16 | 296 | 10 | 0 | -103 | 7695
2009-10-12 03:01 | 59.985 | 3706.771 | 350 | 226.6341 | 16 | 296.5 | 10 | 0 | -103 | 7695
2009-10-12 03:02 | 59.979 | 3704.1272 | 350 | 226.6341 | 16 | 297 | 10 | 0 | -103 | 7696
2009-10-12 03:02 | 59.987 | 3705.9675 | 350 | 226.6341 | 16 | 297.5 | 10 | 0 | -103 | 7696
2009-10-12 03:02 | 59.98 | 3704.6831 | 350 | 226.6341 | 16 | 298 | 10 | 0 | -103 | 7697
2009-10-12 03:02 | 59.984 | 3704.9883 | 350 | 226.6341 | 16 | 298.5 | 10 | 0 | -103 | 7697
2009-10-12 03:02 | 59.989 | 3704.8928 | 350 | 227.2551 | 16 | 299 | 10 | 0 | -103 | 7697
2009-10-12 03:02 | 59.996 | 3701.7952 | 350 | 227.2551 | 16 | 299.5 | 10 | 0 | -103 | 7698
2009-10-12 03:02 | 59.997 | 3701.3081 | 350 | 227.2551 | 16 | 300 | 10 | 0 | -103 | 7698
2009-10-12 03:02 | 59.997 | 3700.541 | 350 | 227.2551 | 16 | 300.5 | 10 | 0 | -103 | 7698.33
2009-10-12 03:02 | 59.996 | 3700.8582 | 350 | 227.2551 | 16 | 301 | 10 | 0 | -103 | 7698.66
2009-10-12 03:02 | 60.003 | 3700.2239 | 350 | 229.2902 | 16 | 301.5 | 10 | 0 | -103 | 7698.99
2009-10-12 03:02 | 60.008 | 3698.0317 | 350 | 229.2902 | 16 | 302 | 10 | 0 | -103 | 7699.32
2009-10-12 03:02 | 60.004 | 3699.2407 | 350 | 229.2902 | 16 | 302.5 | 10 | 0 | -103 | 7699.65
2009-10-12 03:02 | 60.001 | 3701.1099 | 350 | 229.2902 | 16 | 303 | 10 | 0 | -103 | 7699.98
2009-10-12 03:03 | 60.004 | 3700.2202 | 350 | 229.2902 | 16 | 303.5 | 10 | 0 | -103 | 7700.31
2009-10-12 03:03 | 60.008 | 3702.5542 | 350 | 221.4614 | 16 | 304 | 10 | 0 | -103 | 7700.64
2009-10-12 03:03 | 60.006 | 3701.9229 | 350 | 221.4614 | 16 | 304.5 | 10 | 0 | -103 | 7700.97
2009-10-12 03:03 | 60.005 | 3704.0928 | 350 | 221.4614 | 16 | 305 | 10 | 0 | -103 | 7701.3
2009-10-12 03:03 | 59.999 | 3704.4551 | 350 | 221.4614 | 16 | 305.5 | 10 | 0 | -103 | 7701.63
2009-10-12 03:03 | 60.004 | 3705.3291 | 350 | 221.4614 | 16 | 306 | 10 | 0 | -103 | 7701.96
2009-10-12 03:03 | 60.013 | 3703.6753 | 350 | 241.2744 | 16 | 306.5 | 10 | 0 | -103 | 7702.29
2009-10-12 03:03 | 60.012 | 3702.6692 | 350 | 241.2744 | 16 | 307 | 10 | 0 | -103 | 7702.62
2009-10-12 03:03 | 60.005 | 3703.2974 | 350 | 241.2744 | 16 | 307.5 | 10 | 0 | -103 | 7702.95
2009-10-12 03:03 | 60.011 | 3705.2791 | 350 | 241.2744 | 16 | 308 | 10 | 0 | -103 | 7703.28
2009-10-12 03:03 | 60.016 | 3703.438 | 350 | 241.2744 | 16 | 308.5 | 10 | 0 | -103 | 7703.61
2009-10-12 03:04 | 60.019 | 3703.7075 | 350 | 243.0719 | 16 | 309 | 10 | 0 | -103 | 7703.94
2009-10-12 03:04 | 60.013 | 3704.1392 | 350 | 243.0719 | 16 | 309.5 | 10 | 0 | -103 | 7704.27
2009-10-12 03:04 | 60.009 | 3705.4294 | 350 | 243.0719 | 16 | 310 | 10 | 0 | -103 | 7704.6
2009-10-12 03:04 | 60.009 | 3705.634 | 350 | 243.0719 | 16 | 310.5 | 10 | 0 | -103 | 7704.93
2009-10-12 03:04 | 60.02 | 3707.2673 | 350 | 243.0719 | 16 | 311 | 10 | 0 | -103 | 7705.26
2009-10-12 03:04 | 60.018 | 3705.6545 | 350 | 241.6702 | 16 | 311.5 | 10 | 0 | -103 | 7705.59
2009-10-12 03:04 | 60.019 | 3704.2239 | 350 | 241.6702 | 16 | 312 | 10 | 0 | -103 | 7705.92
2009-10-12 03:04 | 60.022 | 3704.7954 | 350 | 241.6702 | 16 | 312.5 | 10 | 0 | -103 | 7706.25
2009-10-12 03:04 | 60.03 | 3702.7642 | 350 | 241.6702 | 16 | 313 | 10 | 0 | -103 | 7706.58
2009-10-12 03:04 | 60.023 | 3701.063 | 350 | 241.6702 | 16 | 313.5 | 10 | 0 | -103 | 7706.91
2009-10-12 03:04 | 60.023 | 3699.3694 | 350 | 228.1493 | 16 | 314 | 10 | 0 | -103 | 7707.24
2009-10-12 03:04 | 60.024 | 3704.2495 | 350 | 228.1493 | 16 | 314.5 | 10 | 0 | -103 | 7707.57
2009-10-12 03:05 | 60.022 | 3703.374 | 350 | 228.1493 | 16 | 315 | 10 | 0 | -103 | 7707.9
2009-10-12 03:05 | 60.025 | 3704.9473 | 350 | 228.1493 | 16 | 315.5 | 10 | 0 | -103 | 7708.23
2009-10-12 03:05 | 60.02 | 3703.5413 | 350 | 228.1493 | 16 | 316 | 10 | 0 | -103 | 7708.56
2009-10-12 03:05 | 60.013 | 3704.3765 | 350 | 235.129 | 16 | 316.5 | 10 | 0 | -103 | 7708.89
2009-10-12 03:05 | 60.017 | 3706.9949 | 350 | 235.129 | 16 | 317 | 10 | 0 | -103 | 7709.22
2009-10-12 03:05 | 60.019 | 3707.7671 | 350 | 235.129 | 16 | 317.5 | 10 | 0 | -103 | 7709.55
2009-10-12 03:05 | 60.015 | 3708.8311 | 350 | 235.129 | 16 | 318 | 10 | 0 | -103 | 7709.88
2009-10-12 03:05 | 60.014 | 3709.8169 | 350 | 235.129 | 16 | 318.5 | 10 | 0 | -103 | 7710.21
2009-10-12 03:05 | 60.019 | 3709.0938 | 350 | 246.4331 | 16 | 319 | 10 | 0 | -103 | 7710.54
2009-10-12 03:05 | 60.014 | 3709.9331 | 350 | 246.4331 | 16 | 319.5 | 10 | 0 | -103 | 7710.87
2009-10-12 03:05 | 60.022 | 3710.5911 | 350 | 246.4331 | 16 | 320 | 10 | 0 | -103 | 7711.2
2009-10-12 03:05 | 60.024 | 3707.3804 | 350 | 246.4331 | 16 | 320.5 | 10 | 0 | -103 | 7711.53
2009-10-12 03:06 | 60.024 | 3706.99 | 350 | 246.4331 | 16 | 321 | 10 | 0 | -103 | 7711.86
2009-10-12 03:06 | 60.02 | 3704.4058 | 350 | 236.5535 | 16 | 321.5 | 10 | 0 | -103 | 7712.19
2009-10-12 03:06 | 60.025 | 3706.5674 | 350 | 236.5535 | 16 | 322 | 10 | 0 | -103 | 7712.52
2009-10-12 03:06 | 60.03 | 3704.4285 | 350 | 236.5535 | 16 | 322.5 | 10 | 0 | -103 | 7712.85
2009-10-12 03:06 | 60.026 | 3703.5317 | 350 | 236.5535 | 16 | 323 | 10 | 0 | -103 | 7713.18
2009-10-12 03:06 | 60.029 | 3703.1692 | 350 | 236.5535 | 16 | 323.5 | 10 | 0 | -103 | 7713.51
2009-10-12 03:06 | 60.03 | 3701.5195 | 350 | 230.2976 | 16 | 324 | 10 | 0 | -103 | 7713.84
2009-10-12 03:06 | 60.016 | 3698.0088 | 350 | 230.2976 | 16 | 324.5 | 10 | 0 | -103 | 7714.17
2009-10-12 03:06 | 60.028 | 3703.1924 | 350 | 230.2976 | 16 | 325 | 10 | 0 | -103 | 7714.5
2009-10-12 03:06 | 60.015 | 3699.9561 | 350 | 230.2976 | 16 | 325.5 | 10 | 0 | -103 | 7714.83
2009-10-12 03:06 | 60.011 | 3703.8022 | 350 | 230.2976 | 16 | 326 | 10 | 0 | -103 | 7715.16
2009-10-12 03:06 | 60.013 | 3707.4895 | 350 | 231.1755 | 16 | 326.5 | 10 | 0 | -103 | 7715.49
2009-10-12 03:06 | 60.016 | 3706.9912 | 350 | 231.1755 | 16 | 327 | 10 | 0 | -103 | 7715.82
2009-10-12 03:07 | 60.013 | 3705.3979 | 350 | 231.1755 | 16 | 327.5 | 10 | 0 | -103 | 7716.15
2009-10-12 03:07 | 59.994 | 3709.144 | 350 | 231.1755 | 16 | 328 | 10 | 0 | -103 | 7716.48
2009-10-12 03:07 | 59.99 | 3706.1926 | 350 | 231.1755 | 16 | 328.5 | 10 | 0 | -103 | 7716.81
2009-10-12 03:07 | 59.993 | 3707.9033 | 350 | 225.6176 | 16 | 329 | 10 | 0 | -103 | 7717.14
2009-10-12 03:07 | 59.993 | 3706.6831 | 350 | 225.6176 | 16 | 329.5 | 10 | 0 | -103 | 7717.47
2009-10-12 03:07 | 59.985 | 3704.9336 | 350 | 225.6176 | 16 | 330 | 10 | 0 | -103 | 7717.8
2009-10-12 03:07 | 59.982 | 3707.0713 | 350 | 225.6176 | 16 | 330.5 | 10 | 0 | -103 | 7718.13
2009-10-12 03:07 | 59.981 | 3707.4785 | 350 | 225.6176 | 16 | 331 | 10 | 0 | -103 | 7718.46
2009-10-12 03:07 | 59.978 | 3710.4194 | 350 | 230.7344 | 16 | 331.5 | 10 | 0 | -103 | 7718.79
2009-10-12 03:07 | 59.977 | 3708.7078 | 350 | 230.7344 | 16 | 332 | 10 | 0 | -103 | 7719.12
2009-10-12 03:07 | 59.983 | 3708.3354 | 350 | 230.7344 | 16 | 332.5 | 10 | 0 | -103 | 7719.45
2009-10-12 03:08 | 59.981 | 3707.9114 | 350 | 230.7344 | 16 | 333 | 10 | 0 | -103 | 7719.78
2009-10-12 03:08 | 59.981 | 3709.689 | 350 | 230.7344 | 16 | 333.5 | 10 | 0 | -103 | 7720.11
2009-10-12 03:08 | 59.98 | 3706.541 | 350 | 234.8471 | 16 | 334 | 10 | 0 | -103 | 7720.44
2009-10-12 03:08 | 59.978 | 3712.3032 | 350 | 234.8471 | 16 | 334.5 | 10 | 0 | -103 | 7720.77
2009-10-12 03:08 | 59.976 | 3711.7034 | 350 | 234.8471 | 16 | 335 | 10 | 0 | -103 | 7721.1
2009-10-12 03:08 | 59.975 | 3714.6121 | 350 | 234.8471 | 16 | 335.5 | 10 | 0 | -103 | 7721.43
2009-10-12 03:08 | 59.975 | 3715.3228 | 350 | 234.8471 | 16 | 336 | 10 | 0 | -103 | 7721.76
2009-10-12 03:08 | 59.975 | 3714.7173 | 350 | 228.9609 | 16 | 336.5 | 10 | 0 | -103 | 7722.09
2009-10-12 03:08 | 59.977 | 3713.9963 | 350 | 228.9609 | 16 | 337 | 10 | 0 | -103 | 7722.42
2009-10-12 03:08 | 59.976 | 3715.6311 | 350 | 228.9609 | 16 | 337.5 | 10 | 0 | -103 | 7722.75
2009-10-12 03:08 | 59.979 | 3715.5674 | 350 | 228.9609 | 16 | 338 | 10 | 0 | -103 | 7723.08
2009-10-12 03:08 | 59.979 | 3713.1416 | 350 | 228.9609 | 16 | 338.5 | 10 | 0 | -103 | 7723.41
2009-10-12 03:08 | 59.987 | 3712.2747 | 350 | 231.1779 | 16 | 339 | 10 | 0 | -103 | 7723.74
2009-10-12 03:09 | 59.984 | 3710.0503 | 350 | 231.1779 | 16 | 339.5 | 10 | 0 | -103 | 7724.07
2009-10-12 03:09 | 59.98 | 3710.4719 | 350 | 231.1779 | 16 | 340 | 10 | 0 | -103 | 7724.4
2009-10-12 03:09 | 59.978 | 3710.1997 | 350 | 231.1779 | 16 | 340.5 | 10 | 0 | -103 | 7724.73
2009-10-12 03:09 | 59.982 | 3709.4622 | 350 | 231.1779 | 16 | 341 | 10 | 0 | -103 | 7725.06
2009-10-12 03:09 | 59.983 | 3710.573 | 350 | 236.4893 | 16 | 341.5 | 10 | 0 | -103 | 7725.39
2009-10-12 03:09 | 59.987 | 3708.3711 | 350 | 236.4893 | 16 | 342 | 10 | 0 | -103 | 7725.72
2009-10-12 03:09 | 59.976 | 3707.4905 | 350 | 236.4893 | 16 | 342.5 | 10 | 0 | -103 | 7726.05
2009-10-12 03:09 | 59.983 | 3709.894 | 350 | 236.4893 | 16 | 343 | 10 | 0 | -103 | 7726.38
2009-10-12 03:09 | 59.981 | 3711.6272 | 350 | 236.4893 | 16 | 343.5 | 10 | 0 | -103 | 7726.71
2009-10-12 03:09 | 59.978 | 3712.3926 | 350 | 245.0389 | 16 | 344 | 10 | 0 | -103 | 7727.04
2009-10-12 03:09 | 59.999 | 3716.6257 | 350 | 245.0389 | 16 | 344.5 | 10 | 0 | -103 | 7727.37
2009-10-12 03:10 | 59.986 | 3712.0918 | 350 | 245.0389 | 16 | 345 | 10 | 0 | -103 | 7727.7
2009-10-12 03:10 | 59.983 | 3714.9531 | 350 | 245.0389 | 16 | 345.5 | 10 | 0 | -103 | 7728.03
2009-10-12 03:10 | 59.99 | 3716.3083 | 350 | 245.0389 | 16 | 346 | 10 | 0 | -103 | 7728.36
2009-10-12 03:10 | 59.995 | 3714.7141 | 350 | 223.6057 | 16 | 346.5 | 10 | 0 | -103 | 7728.69
2009-10-12 03:10 | 59.991 | 3715.9268 | 350 | 223.6057 | 16 | 347 | 10 | 0 | -103 | 7729.02
2009-10-12 03:10 | 60 | 3715.3245 | 350 | 223.6057 | 16 | 347.5 | 10 | 0 | -103 | 7729.35
2009-10-12 03:10 | 60.004 | 3711.7085 | 350 | 223.6057 | 16 | 348 | 10 | 0 | -103 | 7729.68
2009-10-12 03:10 | 59.999 | 3713.3616 | 350 | 223.6057 | 16 | 348.5 | 10 | 0 | -103 | 7730.01
2009-10-12 03:10 | 59.996 | 3718.2925 | 350 | 231.1194 | 16 | 349 | 10 | 0 | -103 | 7730.34
2009-10-12 03:10 | 60.002 | 3717.8152 | 350 | 231.1194 | 16 | 349.5 | 10 | 0 | -103 | 7730.67
2009-10-12 03:10 | 60.005 | 3718.5603 | 350 | 231.1194 | 16 | 350 | 10 | 0 | -103 | 7731
2009-10-12 03:10 | 60.004 | 3718.8213 | 350 | 231.1194 | 16 | 350.5 | 10 | 0 | -103 | 7731.33
2009-10-12 03:10 | 60.003 | 3719.2993 | 350 | 231.1194 | 16 | 351 | 10 | 0 | -103 | 7731.66
2009-10-12 03:11 | 60.006 | 3719.731 | 350 | 237.2066 | 16 | 351.5 | 10 | 0 | -103 | 7731.99
2009-10-12 03:11 | 60.01 | 3718.5796 | 350 | 237.2066 | 16 | 352 | 10 | 0 | -103 | 7732.32
2009-10-12 03:11 | 60.013 | 3720.0337 | 350 | 237.2066 | 16 | 352.5 | 10 | 0 | -103 | 7732.65
2009-10-12 03:11 | 60.009 | 3720.8105 | 350 | 237.2066 | 16 | 353 | 10 | 0 | -103 | 7732.98
2009-10-12 03:11 | 60.008 | 3719.4473 | 350 | 237.2066 | 16 | 353.5 | 10 | 0 | -103 | 7733.31
2009-10-12 03:11 | 60.009 | 3721.2722 | 350 | 240.5164 | 16 | 354 | 10 | 0 | -103 | 7733.64
2009-10-12 03:11 | 60.013 | 3721.5938 | 350 | 240.5164 | 16 | 354.5 | 10 | 0 | -103 | 7733.97
2009-10-12 03:11 | 60.012 | 3721.999 | 350 | 240.5164 | 16 | 355 | 10 | 0 | -103 | 7734.3
2009-10-12 03:11 | 60.011 | 3720.8596 | 350 | 240.5164 | 16 | 355.5 | 10 | 0 | -103 | 7734.63
2009-10-12 03:11 | 60.001 | 3723.8157 | 350 | 240.5164 | 16 | 356 | 10 | 0 | -103 | 7734.96
2009-10-12 03:11 | 59.998 | 3724.8694 | 350 | 237.5661 | 16 | 356.5 | 10 | 0 | -103 | 7735.29
2009-10-12 03:11 | 60.002 | 3723.696 | 350 | 237.5661 | 16 | 357 | 10 | 0 | -103 | 7735.62
2009-10-12 03:12 | 60.003 | 3721.8789 | 350 | 237.5661 | 16 | 357.5 | 10 | 0 | -103 | 7735.95
2009-10-12 03:12 | 60.001 | 3722.9065 | 350 | 237.5661 | 16 | 358 | 10 | 0 | -103 | 7736.28
2009-10-12 03:12 | 59.989 | 3723.2012 | 350 | 237.5661 | 16 | 358.5 | 10 | 0 | -103 | 7736.61
2009-10-12 03:12 | 59.988 | 3723.8813 | 350 | 231.5814 | 16 | 359 | 10 | 0 | -103 | 7736.94
2009-10-12 03:12 | 59.992 | 3724.9438 | 350 | 231.5814 | 16 | 359.5 | 10 | 0 | -103 | 7737.27
2009-10-12 03:12 | 60.04 | 3723.6926 | 350 | 231.5814 | 16 | 360 | 10 | 0 | -103 | 7737.6

## Entry Data
Balancing Authority Name: | My BA
Balancing Authority Frequency Response Obligation (FRO from FRS Form 1) | -80
Note: See "Instruction" tab for more detailed instructions.
Step 1. | Copy and Paste Event Data into the appropriate cells of the "Data" worksheet.
Maintain date and time format of mm/dd/yy hh:mm:ss.
Step 2. | Determine Time of T(0) and edit formula in cell "C8" to reference the correct row of the "Data" worksheet. | 40098.1023
T(0) is the first change in frequency of about 0.010 Hz (10 mHz) which should be the first scan of frequency data of the event.
Step 3. | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062
Step 4. | Enter MW output of generator or load that caused event (+ for gen loss, - for load loss) | 633 | MW
(Value from NERC Event List. If multiple units, enter total MW loss.)
If MW loss value is not known, enter a default 1000 MW.
Step 5. | Hit the big blue button to copy your data for pasting into FRS Form 1 "BA Event Data" worksheet.
Step 6. | Paste data into "FRS Form 1" in the appropriate row on the "BA Event Data" worksheet.
Step 7. | Save this workbook using the following file name format:MyBA_yymmdd_hhmm_FRS_Form2.xlsm
| 2009-10-12 02:27 | Date yymmdd
| 40098.1023 | Time hh:ss of T(0)
Where "MyBA" = your BA mnemonic
Note on C8: Cell "C8": Observe the first change in frequency that identifies the beginning of the event. Look in column "B" of the "Data" worksheet. Select and edit the formula in this cell ("=Data!Axxx") to reference that row number in the "Data" sheet of this first change in frequency where xxx is that row number.
Note on C11: Cell "C11": Similar to identifying the end of a DCS event but only looking at frequency, observe frequency following the beginning of the event. When actual frequency recovers to 60.00 Hz or to the pre-event frequency, edit the formula in this cell to reference that row number in the "Data" worksheet that this occurs. ("=Data!Axxx")
Copy Form 2 Data for Pasting into Form 1

## IPFR (hidden)
IPFR = Interconnection Primary Frequency Response

## Evaluation
scan rate | 2 | seconds |  |  | Date: | 2009-10-12 02:27 |  |  | Balancing Authority | My BA | [10 empty] | A Point | 40098.1023 |  |  |  |  | A Point | 40098.1023 | [13 empty] | Non-Conforming Load sign convention | + | (Data is positive for Load then enter "+" else "-" | [11 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27
[5 empty] | Time of T(0) | 40098.1023 |  |  | Grid Nominal Frequency | 60 | Hz | [9 empty] | FPointA | 60.041 | 40098.1023 |  |  |  | FPointA | 60.041 | 40098.1023 | [26 empty] | Time of T(0) | 40098.1023 | [12 empty] | Time of T(0) | 40098.1023 | [12 empty] | Time of T(0) | 40098.1023 | [12 empty] | Time of T(0) | 40098.1023 | [12 empty] | Time of T(0) | 40098.1023
[5 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062 |  |  | Capacity @ Droop for Minimum Performance | 2400 | MW | [9 empty] | A Value | 60.0413 |  |  |  |  | A Value | 60.0413 | [27 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062
[5 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0413 | Hz |  | Droop Setting | 5% | 3 | Hz | [8 empty] | C Value | 59.852 | 40098.1024 |  |  |  | C Value | 59.852 | #N/A | [26 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0413 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0413 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0413 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0413 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0413 | Hz
[5 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+52)] | 59.8883 | Hz |  | Deadband Setting | 0 | Hz | [9 empty] | Delta FCA | -0.18925 |  |  |  |  | Delta FC | [28 empty] | Value B Post-Perturbation Average Frequency [T(+12 to T(+24)] | 59.8796 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+18 to T(+30)] | 59.8833 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+40)] | 59.8888 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+18 to T(+52)] | 59.8876 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+52)] | 59.8883 | Hz
[5 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15296 | Hz |  | Hz Span | 3 | Hz | [9 empty] | FR C | -334.4799 | MW/0.1 Hz | [32 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.16168 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15796 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15243 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15369 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15296 | Hz
[5 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3649.0017 | MW |  | Frequency Response Obligation (FRO) | -80 | MW/0.1 Hz | [9 empty] | Slope A-C dF/dT | -0.0315 | Hz/second |  |  |  |  | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | [18 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3649.0017 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3649.0017 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3649.0017 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3649.0017 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3649.0017 | MW
[5 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+52)] | 3785.2046 | MW | [13 empty] | C Value Maximum Resource Loss | 633 | [5 empty] | 12 to 24 sec | 12 to 24 sec | 18 to 30 sec | 18 to 30 sec | 20 to 40 sec | 20 to 40 sec | 18 to 52 sec | 18 to 52 sec | 20 to 52 sec | 20 to 52 sec | [18 empty] | Value B Post-Perturbation Average Interchange MW [T(+12 to T(+24)] | 3758.9636 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+18 to T(+30)] | 3774.248 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+40)] | 3780.7259 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+18 to T(+52)] | 3784.1485 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+52)] | 3785.2046 | MW
[5 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 136.2029 | MW | [13 empty] | Secondary C Value | No | n/a | Time |  |  | B Frequency Value | 59.8796 |  | 59.8833 |  | 59.8883 |  | 59.8876 |  | 59.8883 | [19 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 109.9619 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 125.2463 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 131.7242 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 135.1468 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 136.2029 | MW
[5 empty] | Initial Performance Ramp Magnitude Adjustment | -12.6113 | MW | [19 empty] | Delta FB | -0.16168 | -391.8344 | -0.15796 | -401.1562 | -0.15296 | -415.8128 | -0.15369 | -412.3889 | -0.15296 | -414.2499 | [18 empty] | Net Total Adjustments | -51.1899 | MW | [11 empty] | Net Total Adjustments | -53.0458 | MW | [11 empty] | Net Total Adjustments | -54.1488 | MW | [11 empty] | Net Total Adjustments | -53.0854 | MW | [11 empty] | Net Total Adjustments | -53.2238 | MW
[5 empty] | EPFR Pre-Perturbation Average | -33.0002 | MW | [19 empty] | Slope B dF/dT | -0.0080839 |  | -0.0078982 |  | -0.0076478 |  | -0.0076847 |  | -0.0076478 | [19 empty] | EPFR for FRO Pre-Perturbation Average | -33.0002 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -33.0002 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -33.0002 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -33.0002 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -33.0002 | MW
[5 empty] | EPFR Post-Perturbation Average | 89.3644 | MW | [19 empty] | RatioB-C | 85.4314 |  | 83.4686 |  | 80.8225 |  | 81.2128 |  | 80.8225 | [19 empty] | EPFR for FRO Post-Perturbation Average | 96.3423 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 93.3707 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 88.9446 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 89.9553 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 89.3644 | MW
[5 empty] | EPFR Delta | 122.3646 | MW |  | TC (frequency response filter constant) | 0.35 | Time Constant for delayed delivery of PFR during Sustained Measure | [15 empty] | Sustainability Index | -0.014672 |  | -0.018386 |  | -0.023394 |  | -0.022656 |  | -0.023394 | [19 empty] | EPFR for FRO Delta | 129.3424 | MW | [11 empty] | EPFR for FRO Delta | 126.3709 | MW | [11 empty] | EPFR for FRO Delta | 121.9448 | MW | [11 empty] | EPFR for FRO Delta | 122.9555 | MW | [11 empty] | EPFR for FRO Delta | 122.3646 | MW
[21 empty] | Tzero | 40098.1023 | [33 empty] | EPFR for FRO Adjusted | 78.1525 | MW | [11 empty] | EPFR for FRO Adjusted | 73.3251 | MW | [11 empty] | EPFR for FRO Adjusted | 67.796 | MW | [11 empty] | EPFR for FRO Adjusted | 69.8701 | MW | [11 empty] | EPFR for FRO Adjusted | 69.1409 | MW
[21 empty] | FT+4 | 59.852 | [33 empty] | Pre JOU Dynamic Schedules MW | 350 |  |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 350 |  |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 350 | MW |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 350 | MW |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 350 | MW |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz
[9 empty] | Low Hz | Delta Hz Event | [10 empty] | FT+10 | 59.869 | [33 empty] | Pre Non-Conforming Load MW | -165.4764 |  |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | -165.4764 |  |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | -165.4764 | MW |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | -165.4764 | MW |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | -165.4764 | MW |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz
[9 empty] | 3763.5059 | Actual Interchange MW Average during frequency recovery period | [10 empty] | FT+20 | 59.875 | [33 empty] | Pre Pumped Hydro MW | 0 |  |  |  | EPFR for Bias Setting Pre-Perturbation Average | -42.4877 | MW | [6 empty] | Pre Pumped Hydro MW | 0 |  |  |  | EPFR for Bias Setting Pre-Perturbation Average | -42.4877 | MW | [6 empty] | Pre Pumped Hydro MW | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | -42.4877 | MW | [6 empty] | Pre Pumped Hydro MW | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | -42.4877 | MW | [6 empty] | Pre Pumped Hydro MW | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | -42.4877 | MW
[9 empty] | 3781.519 | Target Interchange MW Average during frequency recovery period | [10 empty] | FT+60 | 59.888 | [33 empty] | Pre Ramping Units MW | 90.875 |  |  |  | EPFR for Bias Setting Post-Perturbation Average | 124.0406 | MW | [6 empty] | Pre Ramping Units MW | 90.875 |  |  |  | EPFR for Bias Setting Post-Perturbation Average | 120.2148 | MW | [6 empty] | Pre Ramping Units MW | 90.875 | MW |  |  | EPFR for Bias Setting Post-Perturbation Average | 114.5162 | MW | [6 empty] | Pre Ramping Units MW | 90.875 | MW |  |  | EPFR for Bias Setting Post-Perturbation Average | 115.8175 | MW | [6 empty] | Pre Ramping Units MW | 90.875 | MW |  |  | EPFR for Bias Setting Post-Perturbation Average | 115.0567 | MW
|  |  | EPFR = Expected Primary Frequency Response |  | EPFR(Final) | 109.7534 | MW |  | 3727.2376 | Interchange Average Ramp MW during frequency recovery period | [8 empty] | Interconnection Evaluation | [36 empty] | Pre Transferred Frequency Response MW | -4.125 |  |  |  | EPFR for Bias Setting Delta | 166.5284 | MW | [6 empty] | Pre Transferred Frequency Response MW | -4.125 |  |  |  | EPFR for Bias Setting Delta | 162.7025 | MW | [6 empty] | Pre Transferred Frequency Response MW | -4.125 | MW |  |  | EPFR for Bias Setting Delta | 157.0039 | MW | [6 empty] | Pre Transferred Frequency Response MW | -4.125 | MW |  |  | EPFR for Bias Setting Delta | 158.3052 | MW | [6 empty] | Pre Transferred Frequency Response MW | -4.125 | MW |  |  | EPFR for Bias Setting Delta | 157.5445 | MW
[5 empty] | MW Response in right direction for frequency delta | Yes |  |  | 3645.4458 | Actual MW @ T(-4) | [45 empty] | Pre Contingent BA Lost Generation MW | 15 |  |  |  | Primary Frequency Response Delivery of Bias | 66.03% | [7 empty] | Pre Contingent BA Lost Generation MW | 15 |  |  |  | Primary Frequency Response Delivery of Bias | 76.98% | [7 empty] | Pre Contingent BA Lost Generation MW | 15 | MW |  |  | Primary Frequency Response Delivery of Bias | 83.9% | [7 empty] | Pre Contingent BA Lost Generation MW | 15 | MW |  |  | Primary Frequency Response Delivery of Bias | 85.37% | [7 empty] | Pre Contingent BA Lost Generation MW | 15 | MW |  |  | Primary Frequency Response Delivery of Bias | 86.45%
[9 empty] | 98.6615 | Starting and Ending Difference in Interchange MW during frequency recovery period (indicates ramp direction during recovery period) | [45 empty] | Sum of Pre Perturbation Adjustments | 286.2736 | [12 empty] | Sum of Pre Perturbation Adjustments | 286.2736 | [12 empty] | Sum of Pre Perturbation Adjustments | 286.2736 | MW | [11 empty] | Sum of Pre Perturbation Adjustments | 286.2736 | MW | [11 empty] | Sum of Pre Perturbation Adjustments | 286.2736 | MW
[9 empty] | 0:06 | Event Duration (h:mm:ss)
[9 empty] | No | Target MW Average minus MW @ T(-4) less than zero | [10 empty] | B Value Average Resource Loss | 633 | [33 empty] | Post JOU Dynamic Schedules MW | 335 |  |  |  | Pre-Perturbation BA Load | 7559.9775 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 335 |  |  |  | Pre-Perturbation BA Load | 7559.9775 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 335 | MW |  |  | Pre-Perturbation BA Load | 7559.9775 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 335 | MW |  |  | Pre-Perturbation BA Load | 7559.9775 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 335 | MW |  |  | Pre-Perturbation BA Load | 7559.9775 | MW
[9 empty] | 136.0732 | Interchange Target Relative Average Change - MW (Low Frequency Event) | [10 empty] | B Value Average LaaR Loss | 0 | [33 empty] | Post Non-Conforming Load MW | -206.4591 |  |  |  | Post-Perturbation BA Load | 7561.71 | MW | [6 empty] | Post Non-Conforming Load MW | -208.5149 |  |  |  | Post-Perturbation BA Load | 7562.0871 | MW | [6 empty] | Post Non-Conforming Load MW | -209.9478 | MW |  |  | Post-Perturbation BA Load | 7562.49 | MW | [6 empty] | Post Non-Conforming Load MW | -210.3618 | MW |  |  | Post-Perturbation BA Load | 7562.8283 | MW | [6 empty] | Post Non-Conforming Load MW | -210.5913 | MW |  |  | Post-Perturbation BA Load | 7562.8941 | MW
[9 empty] | 118.0601 | Interchange Actual Relative Average Change - MW (Low Frequency Event) | [10 empty] | B Value Average Net Loss | 633 | [33 empty] | Post Pumped Hydro MW | 1 |  |  |  | Pre to Post Perturbation BA Load Change | 1.7325 | MW | [6 empty] | Post Pumped Hydro MW | 1 |  |  |  | Pre to Post Perturbation BA Load Change | 2.1096 | MW | [6 empty] | Post Pumped Hydro MW | 1.2727 | MW |  |  | Pre to Post Perturbation BA Load Change | 2.5125 | MW | [6 empty] | Post Pumped Hydro MW | 2.1111 | MW |  |  | Pre to Post Perturbation BA Load Change | 2.8508 | MW | [6 empty] | Post Pumped Hydro MW | 2.1765 | MW |  |  | Pre to Post Perturbation BA Load Change | 2.9166 | MW
[9 empty] | No | Interchange Actual Average minus MW @ T(-4) less than zero | [45 empty] | Post Ramping Units MW | 93.5 |  |  |  | Load Dampening Frequency Response | 1.0716 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 94.0714 |  |  |  | Load Dampening Frequency Response | 1.3355 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 94.6818 | MW |  |  | Load Dampening Frequency Response | 1.6483 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 95.1944 | MW |  |  | Load Dampening Frequency Response | 1.8549 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 95.2941 | MW |  |  | Load Dampening Frequency Response | 1.9068 | MW/0.1 Hz
[9 empty] | Yes | Interchange Average MW minus MW @ T(-4) greater than zero | [13 empty] | Interconnection Bias Total | [31 empty] | Post Transferred Frequency Response MW | 12.0428 |  |  |  | Load Dampening % of Total BA Frequency Response | -1.576% | [7 empty] | Post Transferred Frequency Response MW | 11.6713 |  |  |  | Load Dampening % of Total BA Frequency Response | -1.684% | [7 empty] | Post Transferred Frequency Response MW | 11.1181 | MW |  |  | Load Dampening % of Total BA Frequency Response | -1.907% | [7 empty] | Post Transferred Frequency Response MW | 11.2444 | MW |  |  | Load Dampening % of Total BA Frequency Response | -2.109% | [7 empty] | Post Transferred Frequency Response MW | 11.1706 | MW |  |  | Load Dampening % of Total BA Frequency Response | -2.141%
[9 empty] | Yes | Interchange Target MW Average minus MW @ T(-4) greater than zero | [13 empty] | EI | ERCOT | WECC | [29 empty] | Post Contingent BA Lost Generation MW | 0 | [12 empty] | Post Contingent BA Lost Generation MW | 0 | [12 empty] | Post Contingent BA Lost Generation MW | 0 | MW | [11 empty] | Post Contingent BA Lost Generation MW | 0 | MW | [11 empty] | Post Contingent BA Lost Generation MW | 0 | MW
[9 empty] | 37.4117 | Interchange Target Relative Average Change - MW (High Frequency Event) | [10 empty] | Interconnection Bias Setting | -660 |  | -6349 | -660 | -2024 | [29 empty] | Sum of Post Perturbation Adjustments | 235.0837 | [12 empty] | Sum of Post Perturbation Adjustments | 233.2278 | [12 empty] | Sum of Post Perturbation Adjustments | 232.1248 | MW | [11 empty] | Sum of Post Perturbation Adjustments | 233.1882 | MW | [11 empty] | Sum of Post Perturbation Adjustments | 233.0498 | MW
[9 empty] | 19.3986 | Interchange Actual Relative Average Change - MW (High Frequency Event) | [10 empty] | IPFR as a % of Bias Setting | 0% | [33 empty] | Net Total Adjustments MW | -51.1899 | [12 empty] | Net Total Adjustments MW | -53.0458 | [12 empty] | Net Total Adjustments MW | -54.1488 | MW | [11 empty] | Net Total Adjustments MW | -53.0854 | MW | [11 empty] | Net Total Adjustments MW | -53.2238 | MW
[9 empty] | Up | Ramp Direction during frequency recovery period | [10 empty] | Interconnection Total Energy | 37446 | 60.07%
[21 empty] | Interconnection Peak Energy | 62339 |  |  |  |  | Frequency and Interconnection Frequency Response @ different Average periods of B | [11 empty] | Frequency, Actual Interchange, Adjustment Data, Bias and Load used in the evaluation | [12 empty] | 12 to 24 second Average Period Evaluation | [13 empty] | 18 to 30 second Average Period Evaluation | [13 empty] | 20 to 40 second Average Period Evaluation | [13 empty] | 18 to 52 second Average Period Evaluation | [13 empty] | 20 to 52 second Average Period Evaluation
[5 empty] | Initial Response P.U. Performance | 1.241 | P.U. |  | 0.86762 | P.U. Sustianed Response P.U. Performance | [45 empty] | Initial P.U. Performance for FRO | 0.85016 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 0.9911 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.0802 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.0992 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.1131 | P.U.
[56 empty] | Initial P.U. Performance Adjusted for FRO | 1.2459 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 1.4109 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 1.5242 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 1.5309 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 1.5481 | P.U.
[9 empty] | Initial | [6 empty] | Generator | Generator | Generator | Generator | Generator | Generator | Generator | LaaR | Total | Interconnection | FR B | [15 empty] | JOU | Non- |  |  | Transferred | Contingent | [7 empty] | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected
[7 empty] | FRO |  | Measure |  |  | Average | Average |  | Average | Trip | Trip | Trip | Trip | Trip | Trip | Trip | Trip | Generation | Primary | 20 to 52 sec |  | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Expected |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net
[7 empty] | (EPFR) | (TC) | Final |  |  | Output | Target |  | Ramp | MW | MW | MW | MW | MW | MW | MW | MW | Trip | Frequency | Average |  | 12 to 24 sec | 12 to 24 sec | 18 to 30 sec | 18 to 30 sec | 20 to 40 sec | 20 to 40 sec | 18 to 52 sec | 18 to 52 sec | 20 to 52 sec | 20 to 52 sec |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Primary |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual
|  |  |  | Value B |  |  | Expected | Delayed | Expected |  | Recovery | During | During | Recovery | During | [8 empty] | MW | Response | MW |  | Average | Average | Average | Average | Average | Average | Average | Average | Average | Average |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | Freq Response |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange
|  |  |  | 20 to 52 sec |  |  | Primary | Delivery | Primary | Average | Period | Recovery | Recovery | Period | Recovery | [12 empty] | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW
|  | Frequency | Interchange | Average | Average |  | Frequency | Frequency | Frequency | Ramp | Target | Period | Period | Ramp | Period
| T | Hz | MW | Frequency | MW |  | Response | Response | Response | MW/scan | MW | MW | MW | MW | MW | 633 | [8 empty] | MW/0.1 Hz
0
T-72 sec | 40098.1015 | 60.019 | 3671.1931 |  |  |  | -15.2008 | -5.3203 | [15 empty] | 0 |  |  | T-72 sec | [10 empty] | T-72 sec | 40098.1015 | 60.019 | 3671.1931 | 350 | -329.9882 | 0 | 84.5 | 10 | 15 | -103 | 7555.77 | -15.2008 | T-72 sec | 40098.1015 | [12 empty] | T-72 sec | 40098.1015 | [12 empty] | T-72 sec | 40098.1015 | [12 empty] | T-72 sec | 40098.1015 | [12 empty] | T-72 sec | 40098.1015
T-70 sec | 40098.1015 | 60.026 | 3671.189 |  |  |  | -20.8008 | -10.7385 | [15 empty] | 0 |  |  | T-70 sec | [10 empty] | T-70 sec | 40098.1015 | 60.026 | 3671.189 | 350 | -329.9882 | 0 | 85 | 10 | 15 | -103 | 7556.1 | -20.8008 | T-70 sec | 40098.1015 | [12 empty] | T-70 sec | 40098.1015 | [12 empty] | T-70 sec | 40098.1015 | [12 empty] | T-70 sec | 40098.1015 | [12 empty] | T-70 sec | 40098.1015
T-68 sec | 40098.1015 | 60.026 | 3671.189 |  |  |  | -20.8008 | -14.2603 | [15 empty] | 0 |  |  | T-68 sec | [10 empty] | T-68 sec | 40098.1015 | 60.026 | 3671.189 | 350 | -329.9882 | 0 | 85 | 10 | 15 | -103 | 7556.1 | -20.8008 | T-68 sec | 40098.1015 | [12 empty] | T-68 sec | 40098.1015 | [12 empty] | T-68 sec | 40098.1015 | [12 empty] | T-68 sec | 40098.1015 | [12 empty] | T-68 sec | 40098.1015
T-66 sec | 40098.1016 | 60.026 | 3671.189 |  |  |  | -20.8008 | -16.5494 | [15 empty] | 0 |  |  | T-66 sec | [10 empty] | T-66 sec | 40098.1016 | 60.026 | 3671.189 | 350 | -329.9882 | 0 | 85 | 10 | 15 | -103 | 7556.1 | -20.8008 | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016
T-64 sec | 40098.1016 | 60.019 | 3664.4951 |  |  |  | -15.2008 | -16.0774 | [15 empty] | 0 |  |  | T-64 sec | [10 empty] | T-64 sec | 40098.1016 | 60.019 | 3664.4951 | 350 | -329.9882 | 0 | 85.5 | 10 | 15 | -103 | 7556.43 | -15.2008 | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016
T-62 sec | 40098.1016 | 60.019 | 3664.4951 |  |  |  | -15.2008 | -15.7706 | [15 empty] | 0 |  |  | T-62 sec | [10 empty] | T-62 sec | 40098.1016 | 60.019 | 3664.4951 | 350 | -329.9882 | 0 | 85.5 | 10 | 15 | -103 | 7556.43 | -15.2008 | T-62 sec | 40098.1016 | [12 empty] | T-62 sec | 40098.1016 | [12 empty] | T-62 sec | 40098.1016 | [12 empty] | T-62 sec | 40098.1016 | [12 empty] | T-62 sec | 40098.1016
T-60 sec | 40098.1016 | 60.02 | 3666.8208 |  |  |  | -16.0004 | -15.851 |  | -0.15033 | 3666.8208 | [12 empty] | 0 |  |  | T-60 sec | [10 empty] | T-60 sec | 40098.1016 | 60.02 | 3666.8208 | 350 | -329.9882 | 0 | 86 | 10 | 15 | -103 | 7556.76 | -16.0004 | T-60 sec | 40098.1016 | [12 empty] | T-60 sec | 40098.1016 | [12 empty] | T-60 sec | 40098.1016 | [12 empty] | T-60 sec | 40098.1016 | [12 empty] | T-60 sec | 40098.1016
T-58 sec | 40098.1016 | 60.02 | 3666.8208 |  |  |  | -16.0004 | -15.9033 |  | -0.15033 | 3666.6182 | [12 empty] | 0 |  |  | T-58 sec | [10 empty] | T-58 sec | 40098.1016 | 60.02 | 3666.8208 | 350 | -329.9882 | 0 | 86 | 10 | 15 | -103 | 7556.76 | -16.0004 | T-58 sec | 40098.1016 | [12 empty] | T-58 sec | 40098.1016 | [12 empty] | T-58 sec | 40098.1016 | [12 empty] | T-58 sec | 40098.1016 | [12 empty] | T-58 sec | 40098.1016
T-56 sec | 40098.1017 | 60.02 | 3666.8208 |  |  |  | -16.0004 | -15.9373 |  | -0.15033 | 3666.4339 | [12 empty] | 0 |  |  | T-56 sec | [10 empty] | T-56 sec | 40098.1017 | 60.02 | 3666.8208 | 350 | -329.9882 | 0 | 86 | 10 | 15 | -103 | 7556.76 | -16.0004 | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017
T-54 sec | 40098.1017 | 60.021 | 3670.2668 |  |  |  | -16.7999 | -16.2392 |  | -0.15033 | 3665.9816 | [12 empty] | 0 |  |  | T-54 sec | [10 empty] | T-54 sec | 40098.1017 | 60.021 | 3670.2668 | 350 | -255.4442 | 0 | 86.5 | 10 | 15 | -103 | 7557.09 | -16.7999 | T-54 sec | 40098.1017 | [12 empty] | T-54 sec | 40098.1017 | [12 empty] | T-54 sec | 40098.1017 | [12 empty] | T-54 sec | 40098.1017 | [12 empty] | T-54 sec | 40098.1017
T-52 sec | 40098.1017 | 60.021 | 3670.2668 |  |  |  | -16.7999 | -16.4355 |  | -0.15033 | 3665.635 | [12 empty] | 0 |  |  | T-52 sec | [10 empty] | T-52 sec | 40098.1017 | 60.021 | 3670.2668 | 350 | -255.4442 | 0 | 86.5 | 10 | 15 | -103 | 7557.09 | -16.7999 | T-52 sec | 40098.1017 | [12 empty] | T-52 sec | 40098.1017 | [12 empty] | T-52 sec | 40098.1017 | [12 empty] | T-52 sec | 40098.1017 | [12 empty] | T-52 sec | 40098.1017
T-50 sec | 40098.1017 | 60.019 | 3672.4932 |  |  |  | -15.2008 | -16.0033 |  | -0.15033 | 3665.9168 | [12 empty] | 0 |  |  | T-50 sec | [10 empty] | T-50 sec | 40098.1017 | 60.019 | 3672.4932 | 350 | -165.1017 | 0 | 87 | 10 | 15 | -103 | 7557.42 | -15.2008 | T-50 sec | 40098.1017 | [12 empty] | T-50 sec | 40098.1017 | [12 empty] | T-50 sec | 40098.1017 | [12 empty] | T-50 sec | 40098.1017 | [12 empty] | T-50 sec | 40098.1017
T-48 sec | 40098.1018 | 60.019 | 3672.4932 |  |  |  | -15.2008 | -15.7224 |  | -0.15033 | 3666.0474 | [12 empty] | 0 |  |  | T-48 sec | [10 empty] | T-48 sec | 40098.1018 | 60.019 | 3672.4932 | 350 | -165.1017 | 0 | 87 | 10 | 15 | -103 | 7557.42 | -15.2008 | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018
T-46 sec | 40098.1018 | 60.019 | 3672.4932 |  |  |  | -15.2008 | -15.5399 |  | -0.15033 | 3666.0796 | [12 empty] | 0 |  |  | T-46 sec | [10 empty] | T-46 sec | 40098.1018 | 60.019 | 3672.4932 | 350 | -165.1017 | 0 | 87 | 10 | 15 | -103 | 7557.42 | -15.2008 | T-46 sec | 40098.1018 | [12 empty] | T-46 sec | 40098.1018 | [12 empty] | T-46 sec | 40098.1018 | [12 empty] | T-46 sec | 40098.1018 | [12 empty] | T-46 sec | 40098.1018
T-44 sec | 40098.1018 | 60.022 | 3672.1641 |  |  |  | -17.5995 | -16.2607 |  | -0.15033 | 3665.2084 | [12 empty] | 0 |  |  | T-44 sec | [10 empty] | T-44 sec | 40098.1018 | 60.022 | 3672.1641 | 350 | -165.1017 | 0 | 87.5 | 10 | 15 | -103 | 7557.75 | -17.5995 | T-44 sec | 40098.1018 | [12 empty] | T-44 sec | 40098.1018 | [12 empty] | T-44 sec | 40098.1018 | [12 empty] | T-44 sec | 40098.1018 | [12 empty] | T-44 sec | 40098.1018
T-42 sec | 40098.1018 | 60.022 | 3672.1641 |  |  |  | -17.5995 | -16.7293 |  | -0.15033 | 3664.5895 | [12 empty] | 0 |  |  | T-42 sec | [10 empty] | T-42 sec | 40098.1018 | 60.022 | 3672.1641 | 350 | -165.1017 | 0 | 87.5 | 10 | 15 | -103 | 7557.75 | -17.5995 | T-42 sec | 40098.1018 | [12 empty] | T-42 sec | 40098.1018 | [12 empty] | T-42 sec | 40098.1018 | [12 empty] | T-42 sec | 40098.1018 | [12 empty] | T-42 sec | 40098.1018
T-40 sec | 40098.1019 | 60.037 | 3669.9829 |  |  |  | -29.599 | -21.2337 |  | -0.15033 | 3659.9348 | [12 empty] | 0 |  |  | T-40 sec | [10 empty] | T-40 sec | 40098.1019 | 60.037 | 3669.9829 | 350 | -165.1017 | 0 | 88 | 10 | 15 | -103 | 7558.08 | -29.599 | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019
T-38 sec | 40098.1019 | 60.037 | 3669.9829 |  |  |  | -29.599 | -24.1616 |  | -0.15033 | 3656.8566 | [12 empty] | 0 |  |  | T-38 sec | [10 empty] | T-38 sec | 40098.1019 | 60.037 | 3669.9829 | 350 | -165.1017 | 0 | 88 | 10 | 15 | -103 | 7558.08 | -29.599 | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019
T-36 sec | 40098.1019 | 60.037 | 3669.9829 |  |  |  | -29.599 | -26.0647 |  | -0.15033 | 3654.8032 | [12 empty] | 0 |  |  | T-36 sec | [10 empty] | T-36 sec | 40098.1019 | 60.037 | 3669.9829 | 350 | -165.1017 | 0 | 88 | 10 | 15 | -103 | 7558.08 | -29.599 | T-36 sec | 40098.1019 | [12 empty] | T-36 sec | 40098.1019 | [12 empty] | T-36 sec | 40098.1019 | [12 empty] | T-36 sec | 40098.1019 | [12 empty] | T-36 sec | 40098.1019
T-34 sec | 40098.1019 | 60.037 | 3661.5991 |  |  |  | -29.599 | -27.3017 |  | -0.15033 | 3653.4158 | [12 empty] | 0 |  |  | T-34 sec | [10 empty] | T-34 sec | 40098.1019 | 60.037 | 3661.5991 | 350 | -165.1017 | 0 | 88.5 | 10 | 15 | -103 | 7558.41 | -29.599 | T-34 sec | 40098.1019 | [12 empty] | T-34 sec | 40098.1019 | [12 empty] | T-34 sec | 40098.1019 | [12 empty] | T-34 sec | 40098.1019 | [12 empty] | T-34 sec | 40098.1019
T-32 sec | 40098.1019 | 60.037 | 3661.5991 |  |  |  | -29.599 | -28.1057 |  | -0.15033 | 3652.4614 | [12 empty] | 0 |  |  | T-32 sec | [10 empty] | T-32 sec | 40098.1019 | 60.037 | 3661.5991 | 350 | -165.1017 | 0 | 88.5 | 10 | 15 | -103 | 7558.41 | -29.599 | T-32 sec | 40098.1019 | [12 empty] | T-32 sec | 40098.1019 | [12 empty] | T-32 sec | 40098.1019 | [12 empty] | T-32 sec | 40098.1019 | [12 empty] | T-32 sec | 40098.1019
T-30 sec | 40098.102 | 60.048 | 3651.4917 |  |  |  | -38.4003 | -31.7088 |  | -0.15033 | 3648.708 | [12 empty] | 0 |  |  | T-30 sec | [10 empty] | T-30 sec | 40098.102 | 60.048 | 3651.4917 | 350 | -165.1017 | 0 | 89 | 10 | 15 | -103 | 7558.74 | -38.4003 | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102
T-28 sec | 40098.102 | 60.048 | 3651.4917 |  |  |  | -38.4003 | -34.0508 |  | -0.15033 | 3646.2157 | [12 empty] | 0 |  |  | T-28 sec | [10 empty] | T-28 sec | 40098.102 | 60.048 | 3651.4917 | 350 | -165.1017 | 0 | 89 | 10 | 15 | -103 | 7558.74 | -38.4003 | T-28 sec | 40098.102 | [12 empty] | T-28 sec | 40098.102 | [12 empty] | T-28 sec | 40098.102 | [12 empty] | T-28 sec | 40098.102 | [12 empty] | T-28 sec | 40098.102
T-26 sec | 40098.102 | 60.048 | 3651.4917 |  |  |  | -38.4003 | -35.5731 |  | -0.15033 | 3644.543 | [12 empty] | 0 |  |  | T-26 sec | [10 empty] | T-26 sec | 40098.102 | 60.048 | 3651.4917 | 350 | -165.1017 | 0 | 89 | 10 | 15 | -103 | 7558.74 | -38.4003 | T-26 sec | 40098.102 | [12 empty] | T-26 sec | 40098.102 | [12 empty] | T-26 sec | 40098.102 | [12 empty] | T-26 sec | 40098.102 | [12 empty] | T-26 sec | 40098.102
T-24 sec | 40098.102 | 60.041 | 3648.2463 |  |  |  | -32.8003 | -34.6026 |  | -0.15033 | 3645.3632 | [12 empty] | 0 |  |  | T-24 sec | [10 empty] | T-24 sec | 40098.102 | 60.041 | 3648.2463 | 350 | -165.4764 | 0 | 89.5 | 10 | 15 | -103 | 7559.07 | -32.8003 | T-24 sec | 40098.102 | [12 empty] | T-24 sec | 40098.102 | [12 empty] | T-24 sec | 40098.102 | [12 empty] | T-24 sec | 40098.102 | [12 empty] | T-24 sec | 40098.102
T-22 sec | 40098.1021 | 60.041 | 3648.2463 |  |  |  | -32.8003 | -33.9718 |  | -0.15033 | 3645.8437 | [12 empty] | 0 |  |  | T-22 sec | [10 empty] | T-22 sec | 40098.1021 | 60.041 | 3648.2463 | 350 | -165.4764 | 0 | 89.5 | 10 | 15 | -103 | 7559.07 | -32.8003 | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021
T-20 sec | 40098.1021 | 60.039 | 3654.2944 |  |  |  | -31.2012 | -33.0021 |  | -0.15033 | 3646.6631 | [12 empty] | 0 |  |  | T-20 sec | [10 empty] | T-20 sec | 40098.1021 | 60.039 | 3654.2944 | 350 | -165.4764 | 0 | 90 | 10 | 15 | -103 | 7559.4 | -31.2012 | T-20 sec | 40098.1021 | [12 empty] | T-20 sec | 40098.1021 | [12 empty] | T-20 sec | 40098.1021 | [12 empty] | T-20 sec | 40098.1021 | [12 empty] | T-20 sec | 40098.1021
T-18 sec | 40098.1021 | 60.039 | 3654.2944 |  |  |  | -31.2012 | -32.3718 |  | -0.15033 | 3647.1431 | [12 empty] | 0 |  |  | T-18 sec | [10 empty] | T-18 sec | 40098.1021 | 60.039 | 3654.2944 | 350 | -165.4764 | 0 | 90 | 10 | 15 | -103 | 7559.4 | -31.2012 | T-18 sec | 40098.1021 | [12 empty] | T-18 sec | 40098.1021 | [12 empty] | T-18 sec | 40098.1021 | [12 empty] | T-18 sec | 40098.1021 | [12 empty] | T-18 sec | 40098.1021
T-16 sec | 40098.1021 | 60.039 | 3654.2944 | 60.0413 | 3649.0017 |  | -31.2012 | -31.9621 |  | -0.15033 | 3647.4024 | [12 empty] | 0 |  |  | T-16 sec | 60.0413 | [9 empty] | T-16 sec | 40098.1021 | 60.039 | 3654.2944 | 350 | -165.4764 | 0 | 90 | 10 | 15 | -103 | 7559.4 | -31.2012 | T-16 sec | 40098.1021 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-16 sec | 40098.1021 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-16 sec | 40098.1021 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-16 sec | 40098.1021 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-16 sec | 40098.1021 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002
T-14 sec | 40098.1022 | 60.043 | 3651.0593 | 60.0413 | 3649.0017 |  | -34.3994 | -32.8151 |  | -0.15033 | 3646.399 | [12 empty] | 0 |  |  | T-14 sec | 60.0413 | [9 empty] | T-14 sec | 40098.1022 | 60.043 | 3651.0593 | 350 | -165.4764 | 0 | 90.5 | 10 | 15 | -103 | 7559.73 | -34.3994 | T-14 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-14 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-14 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-14 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-14 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002
T-12 sec | 40098.1022 | 60.043 | 3651.0593 | 60.0413 | 3649.0017 |  | -34.3994 | -33.3696 |  | -0.15033 | 3645.6942 | [12 empty] | 0 |  |  | T-12 sec | 60.0413 | [9 empty] | T-12 sec | 40098.1022 | 60.043 | 3651.0593 | 350 | -165.4764 | 0 | 90.5 | 10 | 15 | -103 | 7559.73 | -34.3994 | T-12 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-12 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-12 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-12 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-12 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002
T-10 sec | 40098.1022 | 60.041 | 3648.2363 | 60.0413 | 3649.0017 |  | -32.8003 | -33.1704 |  | -0.15033 | 3645.7431 | [12 empty] | 0 |  |  | T-10 sec | 60.0413 | [9 empty] | T-10 sec | 40098.1022 | 60.041 | 3648.2363 | 350 | -165.4764 | 0 | 91 | 10 | 15 | -103 | 7560.06 | -32.8003 | T-10 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-10 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-10 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-10 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-10 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002
T-08 sec | 40098.1022 | 60.041 | 3648.2363 | 60.0413 | 3649.0017 |  | -32.8003 | -33.0408 |  | -0.15033 | 3645.7223 | [12 empty] | 0 |  |  | T-08 sec | 60.0413 | [9 empty] | T-08 sec | 40098.1022 | 60.041 | 3648.2363 | 350 | -165.4764 | 0 | 91 | 10 | 15 | -103 | 7560.06 | -32.8003 | T-08 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-08 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-08 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-08 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-08 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002
T-06 sec | 40098.1022 | 60.041 | 3648.2363 | 60.0413 | 3649.0017 |  | -32.8003 | -32.9566 |  | -0.15033 | 3645.6562 | [12 empty] | 0 |  |  | T-06 sec | 60.0413 | [9 empty] | T-06 sec | 40098.1022 | 60.041 | 3648.2363 | 350 | -165.4764 | 0 | 91 | 10 | 15 | -103 | 7560.06 | -32.8003 | T-06 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-06 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-06 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-06 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-06 sec | 40098.1022 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002
T-04 sec | 40098.1023 | 60.041 | 3645.4458 | 60.0413 | 3649.0017 |  | -32.8003 | -32.9019 |  | -0.15033 | 3645.5606 | [12 empty] | 0 |  |  | T-04 sec | 60.0413 | [9 empty] | T-04 sec | 40098.1023 | 60.041 | 3645.4458 | 350 | -165.4764 | 0 | 91.5 | 10 | 15 | -103 | 7560.39 | -32.8003 | T-04 sec | 40098.1023 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-04 sec | 40098.1023 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-04 sec | 40098.1023 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-04 sec | 40098.1023 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-04 sec | 40098.1023 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002
T-02 sec | 40098.1023 | 60.041 | 3645.4458 | 60.0413 | 3649.0017 |  | -32.8003 | -32.8664 |  | -0.15033 | 3645.4458 | [12 empty] | 0 |  |  | T-02 sec | 60.0413 | [9 empty] | T-02 sec | 40098.1023 | 60.041 | 3645.4458 | 350 | -165.4764 | 0 | 91.5 | 10 | 15 | -103 | 7560.39 | -32.8003 | T-02 sec | 40098.1023 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-02 sec | 40098.1023 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-02 sec | 40098.1023 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-02 sec | 40098.1023 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002 |  | T-02 sec | 40098.1023 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | 10 | 15 | -103 | 7559.9775 | -33.0002
T+0 sec | 40098.1023 | 59.852 | 3641.1912 |  |  |  | 118.399 | 20.0765 |  | 0 | 3698.3887 |  |  |  |  | 633 | [7 empty] | 633 | -334.4799 |  | T+0 sec | [10 empty] | T+0 sec | 40098.1023 | 59.852 | 3641.1912 | 335 | -206.4591 | 1 | 92 | 10 | 0 | -103 | 7560.72 | 118.399 | T+0 sec | 40098.1023 | [12 empty] | T+0 sec | 40098.1023 | [12 empty] | T+0 sec | 40098.1023 | [12 empty] | T+0 sec | 40098.1023 | [12 empty] | T+0 sec | 40098.1023
T+02 sec | 40098.1023 | 59.852 | 3641.1912 |  |  |  | 118.399 | 54.4894 |  | 0.58036 | 3733.3819 | 3641.1912 | 3715.8853 | 3678.1974 | 3678.1974 | 633 | [7 empty] | 633 | -334.4799 |  | T+02 sec | [10 empty] | T+02 sec | 40098.1023 | 59.852 | 3641.1912 | 335 | -206.4591 | 1 | 92 | 10 | 0 | -103 | 7560.72 | 118.399 | T+02 sec | 40098.1023 | [12 empty] | T+02 sec | 40098.1023 | [12 empty] | T+02 sec | 40098.1023 | [12 empty] | T+02 sec | 40098.1023 | [12 empty] | T+02 sec | 40098.1023
T+04 sec | 40098.1024 | 59.852 | 3641.1912 |  |  |  | 118.399 | 76.8578 |  | 0.58036 | 3756.3307 | 3641.1912 | 3729.3671 | 3678.7777 | 3678.4876 | 633 | [7 empty] | 633 | -334.4799 |  | T+04 sec | [10 empty] | T+04 sec | 40098.1024 | 59.852 | 3641.1912 | 335 | -206.4591 | 1 | 92 | 10 | 0 | -103 | 7560.72 | 118.399 | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024
T+06 sec | 40098.1024 | 59.869 | 3734.9043 |  |  |  | 104.8004 | 86.6377 |  | 0.58036 | 3766.6909 | 3664.6194 | 3738.6981 | 3679.3581 | 3678.7777 | 633 | [6 empty] | 0 | 633 | -367.4875 |  | T+06 sec | [10 empty] | T+06 sec | 40098.1024 | 59.869 | 3734.9043 | 335 | -206.4591 | 1 | 92.5 | 10 | 0 | -103 | 7561.05 | 104.8004 | T+06 sec | 40098.1024 | [12 empty] | T+06 sec | 40098.1024 | [12 empty] | T+06 sec | 40098.1024 | [12 empty] | T+06 sec | 40098.1024 | [12 empty] | T+06 sec | 40098.1024
T+08 sec | 40098.1024 | 59.869 | 3734.9043 |  |  |  | 104.8004 | 92.9947 |  | 0.58036 | 3773.6282 | 3678.6764 | 3745.6841 | 3679.9385 | 3679.0679 | 633 | [6 empty] | 0 | 633 | -367.4875 |  | T+08 sec | [10 empty] | T+08 sec | 40098.1024 | 59.869 | 3734.9043 | 335 | -206.4591 | 1 | 92.5 | 10 | 0 | -103 | 7561.05 | 104.8004 | T+08 sec | 40098.1024 | [12 empty] | T+08 sec | 40098.1024 | [12 empty] | T+08 sec | 40098.1024 | [12 empty] | T+08 sec | 40098.1024 | [12 empty] | T+08 sec | 40098.1024
T+10 sec | 40098.1024 | 59.869 | 3734.9043 |  |  |  | 104.8004 | 97.1267 |  | 0.58036 | 3778.3406 | 3688.0477 | 3751.1268 | 3680.5188 | 3679.3581 | 633 | [6 empty] | 0 | 633 | -367.4875 |  | T+10 sec | [10 empty] | T+10 sec | 40098.1024 | 59.869 | 3734.9043 | 335 | -206.4591 | 1 | 92.5 | 10 | 0 | -103 | 7561.05 | 104.8004 | T+10 sec | 40098.1024 | [12 empty] | T+10 sec | 40098.1024 | [12 empty] | T+10 sec | 40098.1024 | [12 empty] | T+10 sec | 40098.1024 | [12 empty] | T+10 sec | 40098.1024
T+12 sec | 40098.1025 | 59.88 | 3737.1567 |  |  |  | 95.9991 | 96.732 |  | 0.58036 | 3778.5263 | 3695.0633 | 3755.0411 | 3681.0992 | 3679.6483 | 633 | [6 empty] | 0 | 633 | -392.5602 |  | T+12 sec | 59.8796 | -391.8344 | [8 empty] | T+12 sec | 40098.1025 | 59.88 | 3737.1567 | 335 | -206.4591 | 1 | 93 | 10 | 0 | -103 | 7561.38 | 95.9991 | T+12 sec | 40098.1025 | 59.8796 | 3758.9636 | 335 | -206.4591 | 1 | 93.5 | 10 | 0 | -103 | 7561.71 | 96.3423 | 3727.1542 | T+12 sec | 40098.1025 | [12 empty] | T+12 sec | 40098.1025 | [12 empty] | T+12 sec | 40098.1025 | [12 empty] | T+12 sec | 40098.1025
T+14 sec | 40098.1025 | 59.88 | 3737.1567 |  |  |  | 95.9991 | 96.4755 |  | 0.58036 | 3778.8502 | 3700.325 | 3758.0172 | 3681.6795 | 3679.9385 | 633 | [6 empty] | 0 | 633 | -392.5602 |  | T+14 sec | 59.8796 | -391.8344 | [8 empty] | T+14 sec | 40098.1025 | 59.88 | 3737.1567 | 335 | -206.4591 | 1 | 93 | 10 | 0 | -103 | 7561.38 | 95.9991 | T+14 sec | 40098.1025 | 59.8796 | 3758.9636 | 335 | -206.4591 | 1 | 93.5 | 10 | 0 | -103 | 7561.71 | 96.3423 | 3727.1542 | T+14 sec | 40098.1025 | [12 empty] | T+14 sec | 40098.1025 | [12 empty] | T+14 sec | 40098.1025 | [12 empty] | T+14 sec | 40098.1025
T+16 sec | 40098.1025 | 59.875 | 3766.1938 |  |  |  | 100 | 97.7091 |  | 0.58036 | 3780.6641 | 3707.6437 | 3760.5335 | 3682.2599 | 3680.2286 | 633 | [6 empty] | 0 | 633 | -380.7514 |  | T+16 sec | 59.8796 | -391.8344 | [8 empty] | T+16 sec | 40098.1025 | 59.875 | 3766.1938 | 335 | -206.4591 | 1 | 93.5 | 10 | 0 | -103 | 7561.71 | 100 | T+16 sec | 40098.1025 | 59.8796 | 3758.9636 | 335 | -206.4591 | 1 | 93.5 | 10 | 0 | -103 | 7561.71 | 96.3423 | 3727.1542 | T+16 sec | 40098.1025 | [12 empty] | T+16 sec | 40098.1025 | [12 empty] | T+16 sec | 40098.1025 | [12 empty] | T+16 sec | 40098.1025
T+18 sec | 40098.1025 | 59.875 | 3766.1938 |  |  |  | 100 | 98.5109 |  | 0.58036 | 3782.0463 | 3713.4988 | 3762.6848 | 3682.8403 | 3680.5188 | 633 | [6 empty] | 0 | 633 | -380.7514 |  | T+18 sec | 59.8796 | -391.8344 | 59.8833 | -401.1562 |  |  | 59.8876 | -412.3889 |  |  | T+18 sec | 40098.1025 | 59.875 | 3766.1938 | 335 | -206.4591 | 1 | 93.5 | 10 | 0 | -103 | 7561.71 | 100 | T+18 sec | 40098.1025 | 59.8796 | 3758.9636 | 335 | -206.4591 | 1 | 93.5 | 10 | 0 | -103 | 7561.71 | 96.3423 | 3727.1542 | T+18 sec | 40098.1025 | 59.8833 | 3774.248 | 335 | -208.5149 | 1 | 94.0714 | 10 | 0 | -103 | 7562.0871 | 93.3707 | 3722.3269 | T+18 sec | 40098.1025 | [12 empty] | T+18 sec | 40098.1025 | 59.8876 | 3784.1485 | 335 | -210.3618 | 2.1111 | 95.1944 | 10 | 0 | -103 | 7562.8283 | 89.9553 | 3718.8718 | T+18 sec | 40098.1025
T+20 sec | 40098.1025 | 59.875 | 3766.1938 | 59.8883 | 3785.2046 |  | 100 | 99.0321 | 3758.7551 | 0.58036 | 3783.1478 | 3718.2892 | 3764.5451 | 3683.4206 | 3680.809 | 633 | [6 empty] | 0 | 633 | -380.7514 | -414.2499 | T+20 sec | 59.8796 | -391.8344 | 59.8833 | -401.1562 | 59.8883 | -415.8128 | 59.8876 | -412.3889 | 59.8883 | -414.2499 | T+20 sec | 40098.1025 | 59.875 | 3766.1938 | 335 | -206.4591 | 1 | 93.5 | 10 | 0 | -103 | 7561.71 | 100 | T+20 sec | 40098.1025 | 59.8796 | 3758.9636 | 335 | -206.4591 | 1 | 93.5 | 10 | 0 | -103 | 7561.71 | 96.3423 | 3727.1542 | T+20 sec | 40098.1025 | 59.8833 | 3774.248 | 335 | -208.5149 | 1 | 94.0714 | 10 | 0 | -103 | 7562.0871 | 93.3707 | 3722.3269 | T+20 sec | 40098.1025 | 59.8888 | 3780.7259 | 335 | -209.9478 | 1.2727 | 94.6818 | 10 | 0 | -103 | 7562.49 | 88.9446 | 3716.7977 | T+20 sec | 40098.1025 | 59.8876 | 3784.1485 | 335 | -210.3618 | 2.1111 | 95.1944 | 10 | 0 | -103 | 7562.8283 | 89.9553 | 3718.8718 | T+20 sec | 40098.1025 | 59.8883 | 3785.2046 | 335 | -210.5913 | 2.1765 | 95.2941 | 10 | 0 | -103 | 7562.8941 | 89.3644 | 3718.1426
T+22 sec | 40098.1026 | 59.886 | 3769.925 | 59.8883 | 3785.2046 |  | 91.1987 | 96.2904 | 3758.7551 | 0.58036 | 3780.9865 | 3722.5922 | 3765.9152 | 3684.001 | 3681.0992 | 633 | [6 empty] | 0 | 633 | -407.733 | -414.2499 | T+22 sec | 59.8796 | -391.8344 | 59.8833 | -401.1562 | 59.8883 | -415.8128 | 59.8876 | -412.3889 | 59.8883 | -414.2499 | T+22 sec | 40098.1026 | 59.886 | 3769.925 | 335 | -206.4591 | 1 | 94 | 10 | 0 | -103 | 7562.04 | 91.1987 | T+22 sec | 40098.1026 | 59.8796 | 3758.9636 | 335 | -206.4591 | 1 | 93.5 | 10 | 0 | -103 | 7561.71 | 96.3423 | 3727.1542 | T+22 sec | 40098.1026 | 59.8833 | 3774.248 | 335 | -208.5149 | 1 | 94.0714 | 10 | 0 | -103 | 7562.0871 | 93.3707 | 3722.3269 | T+22 sec | 40098.1026 | 59.8888 | 3780.7259 | 335 | -209.9478 | 1.2727 | 94.6818 | 10 | 0 | -103 | 7562.49 | 88.9446 | 3716.7977 | T+22 sec | 40098.1026 | 59.8876 | 3784.1485 | 335 | -210.3618 | 2.1111 | 95.1944 | 10 | 0 | -103 | 7562.8283 | 89.9553 | 3718.8718 | T+22 sec | 40098.1026 | 59.8883 | 3785.2046 | 335 | -210.5913 | 2.1765 | 95.2941 | 10 | 0 | -103 | 7562.8941 | 89.3644 | 3718.1426
T+24 sec | 40098.1026 | 59.886 | 3769.925 | 59.8883 | 3785.2046 |  | 91.1987 | 94.5083 | 3758.7551 | 0.58036 | 3779.7848 | 3726.2332 | 3766.9821 | 3684.5813 | 3681.3894 | 633 | [6 empty] | 0 | 633 | -407.733 | -414.2499 | T+24 sec | 59.8796 | -391.8344 | 59.8833 | -401.1562 | 59.8883 | -415.8128 | 59.8876 | -412.3889 | 59.8883 | -414.2499 | T+24 sec | 40098.1026 | 59.886 | 3769.925 | 335 | -206.4591 | 1 | 94 | 10 | 0 | -103 | 7562.04 | 91.1987 | T+24 sec | 40098.1026 | 59.8796 | 3758.9636 | 335 | -206.4591 | 1 | 93.5 | 10 | 0 | -103 | 7561.71 | 96.3423 | 3727.1542 | T+24 sec | 40098.1026 | 59.8833 | 3774.248 | 335 | -208.5149 | 1 | 94.0714 | 10 | 0 | -103 | 7562.0871 | 93.3707 | 3722.3269 | T+24 sec | 40098.1026 | 59.8888 | 3780.7259 | 335 | -209.9478 | 1.2727 | 94.6818 | 10 | 0 | -103 | 7562.49 | 88.9446 | 3716.7977 | T+24 sec | 40098.1026 | 59.8876 | 3784.1485 | 335 | -210.3618 | 2.1111 | 95.1944 | 10 | 0 | -103 | 7562.8283 | 89.9553 | 3718.8718 | T+24 sec | 40098.1026 | 59.8883 | 3785.2046 | 335 | -210.5913 | 2.1765 | 95.2941 | 10 | 0 | -103 | 7562.8941 | 89.3644 | 3718.1426
T+26 sec | 40098.1026 | 59.887 | 3782.4995 | 59.8883 | 3785.2046 |  | 90.3992 | 93.0701 | 3758.7551 | 0.58036 | 3778.9269 | 3730.2522 | 3767.8353 | 3685.1617 | 3681.6795 | 633 | [6 empty] | 0 | 633 | -410.3749 | -414.2499 | T+26 sec |  |  | 59.8833 | -401.1562 | 59.8883 | -415.8128 | 59.8876 | -412.3889 | 59.8883 | -414.2499 | T+26 sec | 40098.1026 | 59.887 | 3782.4995 | 335 | -211.256 | 1 | 94.5 | 10 | 0 | -103 | 7562.37 | 90.3992 | T+26 sec | 40098.1026 | [12 empty] | T+26 sec | 40098.1026 | 59.8833 | 3774.248 | 335 | -208.5149 | 1 | 94.0714 | 10 | 0 | -103 | 7562.0871 | 93.3707 | 3722.3269 | T+26 sec | 40098.1026 | 59.8888 | 3780.7259 | 335 | -209.9478 | 1.2727 | 94.6818 | 10 | 0 | -103 | 7562.49 | 88.9446 | 3716.7977 | T+26 sec | 40098.1026 | 59.8876 | 3784.1485 | 335 | -210.3618 | 2.1111 | 95.1944 | 10 | 0 | -103 | 7562.8283 | 89.9553 | 3718.8718 | T+26 sec | 40098.1026 | 59.8883 | 3785.2046 | 335 | -210.5913 | 2.1765 | 95.2941 | 10 | 0 | -103 | 7562.8941 | 89.3644 | 3718.1426
T+28 sec | 40098.1026 | 59.887 | 3782.4995 | 59.8883 | 3785.2046 |  | 90.3992 | 92.1353 | 3758.7551 | 0.58036 | 3778.5725 | 3733.7354 | 3768.5511 | 3685.742 | 3681.9697 | 633 | [6 empty] | 0 | 633 | -410.3749 | -414.2499 | T+28 sec |  |  | 59.8833 | -401.1562 | 59.8883 | -415.8128 | 59.8876 | -412.3889 | 59.8883 | -414.2499 | T+28 sec | 40098.1026 | 59.887 | 3782.4995 | 335 | -211.256 | 1 | 94.5 | 10 | 0 | -103 | 7562.37 | 90.3992 | T+28 sec | 40098.1026 | [12 empty] | T+28 sec | 40098.1026 | 59.8833 | 3774.248 | 335 | -208.5149 | 1 | 94.0714 | 10 | 0 | -103 | 7562.0871 | 93.3707 | 3722.3269 | T+28 sec | 40098.1026 | 59.8888 | 3780.7259 | 335 | -209.9478 | 1.2727 | 94.6818 | 10 | 0 | -103 | 7562.49 | 88.9446 | 3716.7977 | T+28 sec | 40098.1026 | 59.8876 | 3784.1485 | 335 | -210.3618 | 2.1111 | 95.1944 | 10 | 0 | -103 | 7562.8283 | 89.9553 | 3718.8718 | T+28 sec | 40098.1026 | 59.8883 | 3785.2046 | 335 | -210.5913 | 2.1765 | 95.2941 | 10 | 0 | -103 | 7562.8941 | 89.3644 | 3718.1426
T+30 sec | 40098.1027 | 59.887 | 3782.4995 | 59.8883 | 3785.2046 |  | 90.3992 | 91.5276 | 3758.7551 | 0.58036 | 3778.5452 | 3736.7831 | 3769.1757 | 3686.3224 | 3682.2599 | 633 | [6 empty] | 0 | 633 | -410.3749 | -414.2499 | T+30 sec |  |  | 59.8833 | -401.1562 | 59.8883 | -415.8128 | 59.8876 | -412.3889 | 59.8883 | -414.2499 | T+30 sec | 40098.1027 | 59.887 | 3782.4995 | 335 | -211.256 | 1 | 94.5 | 10 | 0 | -103 | 7562.37 | 90.3992 | T+30 sec | 40098.1027 | [12 empty] | T+30 sec | 40098.1027 | 59.8833 | 3774.248 | 335 | -208.5149 | 1 | 94.0714 | 10 | 0 | -103 | 7562.0871 | 93.3707 | 3722.3269 | T+30 sec | 40098.1027 | 59.8888 | 3780.7259 | 335 | -209.9478 | 1.2727 | 94.6818 | 10 | 0 | -103 | 7562.49 | 88.9446 | 3716.7977 | T+30 sec | 40098.1027 | 59.8876 | 3784.1485 | 335 | -210.3618 | 2.1111 | 95.1944 | 10 | 0 | -103 | 7562.8283 | 89.9553 | 3718.8718 | T+30 sec | 40098.1027 | 59.8883 | 3785.2046 | 335 | -210.5913 | 2.1765 | 95.2941 | 10 | 0 | -103 | 7562.8941 | 89.3644 | 3718.1426
T+32 sec | 40098.1027 | 59.895 | 3784.7297 | 59.8883 | 3785.2046 |  | 83.9996 | 88.8928 | 3758.7551 | 0.58036 | 3776.4907 | 3739.6035 | 3769.606 | 3686.9028 | 3682.5501 | 633 | [6 empty] | 0 | 633 | -432.8212 | -414.2499 | T+32 sec |  |  |  |  | 59.8883 | -415.8128 | 59.8876 | -412.3889 | 59.8883 | -414.2499 | T+32 sec | 40098.1027 | 59.895 | 3784.7297 | 335 | -211.256 | 1 | 95 | 10 | 0 | -103 | 7562.7 | 83.9996 | T+32 sec | 40098.1027 | [12 empty] | T+32 sec | 40098.1027 | [12 empty] | T+32 sec | 40098.1027 | 59.8888 | 3780.7259 | 335 | -209.9478 | 1.2727 | 94.6818 | 10 | 0 | -103 | 7562.49 | 88.9446 | 3716.7977 | T+32 sec | 40098.1027 | 59.8876 | 3784.1485 | 335 | -210.3618 | 2.1111 | 95.1944 | 10 | 0 | -103 | 7562.8283 | 89.9553 | 3718.8718 | T+32 sec | 40098.1027 | 59.8883 | 3785.2046 | 335 | -210.5913 | 2.1765 | 95.2941 | 10 | 0 | -103 | 7562.8941 | 89.3644 | 3718.1426
T+34 sec | 40098.1027 | 59.895 | 3784.7297 | 59.8883 | 3785.2046 |  | 83.9996 | 87.1802 | 3758.7551 | 0.58036 | 3775.3585 | 3742.1105 | 3769.9256 | 3687.4831 | 3682.8403 | 633 | [6 empty] | 0 | 633 | -432.8212 | -414.2499 | T+34 sec |  |  |  |  | 59.8883 | -415.8128 | 59.8876 | -412.3889 | 59.8883 | -414.2499 | T+34 sec | 40098.1027 | 59.895 | 3784.7297 | 335 | -211.256 | 1 | 95 | 10 | 0 | -103 | 7562.7 | 83.9996 | T+34 sec | 40098.1027 | [12 empty] | T+34 sec | 40098.1027 | [12 empty] | T+34 sec | 40098.1027 | 59.8888 | 3780.7259 | 335 | -209.9478 | 1.2727 | 94.6818 | 10 | 0 | -103 | 7562.49 | 88.9446 | 3716.7977 | T+34 sec | 40098.1027 | 59.8876 | 3784.1485 | 335 | -210.3618 | 2.1111 | 95.1944 | 10 | 0 | -103 | 7562.8283 | 89.9553 | 3718.8718 | T+34 sec | 40098.1027 | 59.8883 | 3785.2046 | 335 | -210.5913 | 2.1765 | 95.2941 | 10 | 0 | -103 | 7562.8941 | 89.3644 | 3718.1426
T+36 sec | 40098.1027 | 59.893 | 3788.3276 | 59.8883 | 3785.2046 |  | 85.5988 | 86.6267 | 3758.7551 | 0.58036 | 3775.3853 | 3744.543 | 3770.213 | 3688.0635 | 3683.1304 | 633 | [6 empty] | 0 | 633 | -426.9853 | -414.2499 | T+36 sec |  |  |  |  | 59.8883 | -415.8128 | 59.8876 | -412.3889 | 59.8883 | -414.2499 | T+36 sec | 40098.1027 | 59.893 | 3788.3276 | 335 | -211.256 | 2 | 95.5 | 10 | 0 | -103 | 7563.03 | 85.5988 | T+36 sec | 40098.1027 | [12 empty] | T+36 sec | 40098.1027 | [12 empty] | T+36 sec | 40098.1027 | 59.8888 | 3780.7259 | 335 | -209.9478 | 1.2727 | 94.6818 | 10 | 0 | -103 | 7562.49 | 88.9446 | 3716.7977 | T+36 sec | 40098.1027 | 59.8876 | 3784.1485 | 335 | -210.3618 | 2.1111 | 95.1944 | 10 | 0 | -103 | 7562.8283 | 89.9553 | 3718.8718 | T+36 sec | 40098.1027 | 59.8883 | 3785.2046 | 335 | -210.5913 | 2.1765 | 95.2941 | 10 | 0 | -103 | 7562.8941 | 89.3644 | 3718.1426
T+38 sec | 40098.1028 | 59.893 | 3788.3276 | 59.8883 | 3785.2046 |  | 85.5988 | 86.2669 | 3758.7551 | 0.58036 | 3775.6059 | 3746.7322 | 3770.4826 | 3688.6438 | 3683.4206 | 633 | [6 empty] | 0 | 633 | -426.9853 | -414.2499 | T+38 sec |  |  |  |  | 59.8883 | -415.8128 | 59.8876 | -412.3889 | 59.8883 | -414.2499 | T+38 sec | 40098.1028 | 59.893 | 3788.3276 | 335 | -211.256 | 2 | 95.5 | 10 | 0 | -103 | 7563.03 | 85.5988 | T+38 sec | 40098.1028 | [12 empty] | T+38 sec | 40098.1028 | [12 empty] | T+38 sec | 40098.1028 | 59.8888 | 3780.7259 | 335 | -209.9478 | 1.2727 | 94.6818 | 10 | 0 | -103 | 7562.49 | 88.9446 | 3716.7977 | T+38 sec | 40098.1028 | 59.8876 | 3784.1485 | 335 | -210.3618 | 2.1111 | 95.1944 | 10 | 0 | -103 | 7562.8283 | 89.9553 | 3718.8718 | T+38 sec | 40098.1028 | 59.8883 | 3785.2046 | 335 | -210.5913 | 2.1765 | 95.2941 | 10 | 0 | -103 | 7562.8941 | 89.3644 | 3718.1426
T+40 sec | 40098.1028 | 59.893 | 3788.3276 | 59.8883 | 3785.2046 |  | 85.5988 | 86.0331 | 3758.7551 | 0.58036 | 3775.9524 | 3748.713 | 3770.7431 | 3689.2242 | 3683.7108 | 633 | [6 empty] | 0 | 633 | -426.9853 | -414.2499 | T+40 sec |  |  |  |  | 59.8883 | -415.8128 | 59.8876 | -412.3889 | 59.8883 | -414.2499 | T+40 sec | 40098.1028 | 59.893 | 3788.3276 | 335 | -211.256 | 2 | 95.5 | 10 | 0 | -103 | 7563.03 | 85.5988 | T+40 sec | 40098.1028 | [12 empty] | T+40 sec | 40098.1028 | [12 empty] | T+40 sec | 40098.1028 | 59.8888 | 3780.7259 | 335 | -209.9478 | 1.2727 | 94.6818 | 10 | 0 | -103 | 7562.49 | 88.9446 | 3716.7977 | T+40 sec | 40098.1028 | 59.8876 | 3784.1485 | 335 | -210.3618 | 2.1111 | 95.1944 | 10 | 0 | -103 | 7562.8283 | 89.9553 | 3718.8718 | T+40 sec | 40098.1028 | 59.8883 | 3785.2046 | 335 | -210.5913 | 2.1765 | 95.2941 | 10 | 0 | -103 | 7562.8941 | 89.3644 | 3718.1426
T+42 sec | 40098.1028 | 59.891 | 3788.4719 | 59.8883 | 3785.2046 |  | 87.2009 | 86.4418 | 3758.7551 | 0.58036 | 3776.9415 | 3750.5202 | 3771.0248 | 3689.8045 | 3684.001 | 633 | [6 empty] | 0 | 633 | -421.2939 | -414.2499 | T+42 sec | [6 empty] | 59.8876 | -412.3889 | 59.8883 | -414.2499 | T+42 sec | 40098.1028 | 59.891 | 3788.4719 | 335 | -211.256 | 3 | 96 | 10 | 0 | -103 | 7563.36 | 87.2009 | T+42 sec | 40098.1028 | [12 empty] | T+42 sec | 40098.1028 | [12 empty] | T+42 sec | 40098.1028 | [12 empty] | T+42 sec | 40098.1028 | 59.8876 | 3784.1485 | 335 | -210.3618 | 2.1111 | 95.1944 | 10 | 0 | -103 | 7562.8283 | 89.9553 | 3718.8718 | T+42 sec | 40098.1028 | 59.8883 | 3785.2046 | 335 | -210.5913 | 2.1765 | 95.2941 | 10 | 0 | -103 | 7562.8941 | 89.3644 | 3718.1426
T+44 sec | 40098.1028 | 59.891 | 3788.4719 | 59.8883 | 3785.2046 |  | 87.2009 | 86.7075 | 3758.7551 | 0.58036 | 3777.7875 | 3752.1703 | 3771.3188 | 3690.3849 | 3684.2911 | 633 | [6 empty] | 0 | 633 | -421.2939 | -414.2499 | T+44 sec | [6 empty] | 59.8876 | -412.3889 | 59.8883 | -414.2499 | T+44 sec | 40098.1028 | 59.891 | 3788.4719 | 335 | -211.256 | 3 | 96 | 10 | 0 | -103 | 7563.36 | 87.2009 | T+44 sec | 40098.1028 | [12 empty] | T+44 sec | 40098.1028 | [12 empty] | T+44 sec | 40098.1028 | [12 empty] | T+44 sec | 40098.1028 | 59.8876 | 3784.1485 | 335 | -210.3618 | 2.1111 | 95.1944 | 10 | 0 | -103 | 7562.8283 | 89.9553 | 3718.8718 | T+44 sec | 40098.1028 | 59.8883 | 3785.2046 | 335 | -210.5913 | 2.1765 | 95.2941 | 10 | 0 | -103 | 7562.8941 | 89.3644 | 3718.1426
T+46 sec | 40098.1028 | 59.885 | 3794.3743 | 59.8883 | 3785.2046 |  | 92.0013 | 88.5603 | 3758.7551 | 0.58036 | 3780.2207 | 3753.9288 | 3771.6898 | 3690.9653 | 3684.5813 | 633 | [6 empty] | 0 | 633 | -405.1151 | -414.2499 | T+46 sec | [6 empty] | 59.8876 | -412.3889 | 59.8883 | -414.2499 | T+46 sec | 40098.1028 | 59.885 | 3794.3743 | 335 | -211.256 | 4 | 96.5 | 10 | 0 | -103 | 7563.69 | 92.0013 | T+46 sec | 40098.1028 | [12 empty] | T+46 sec | 40098.1028 | [12 empty] | T+46 sec | 40098.1028 | [12 empty] | T+46 sec | 40098.1028 | 59.8876 | 3784.1485 | 335 | -210.3618 | 2.1111 | 95.1944 | 10 | 0 | -103 | 7562.8283 | 89.9553 | 3718.8718 | T+46 sec | 40098.1028 | 59.8883 | 3785.2046 | 335 | -210.5913 | 2.1765 | 95.2941 | 10 | 0 | -103 | 7562.8941 | 89.3644 | 3718.1426
T+48 sec | 40098.1029 | 59.885 | 3794.3743 | 59.8883 | 3785.2046 |  | 92.0013 | 89.7647 | 3758.7551 | 0.58036 | 3782.0054 | 3755.5466 | 3772.1024 | 3691.5456 | 3684.8715 | 633 | [6 empty] | 0 | 633 | -405.1151 | -414.2499 | T+48 sec | [6 empty] | 59.8876 | -412.3889 | 59.8883 | -414.2499 | T+48 sec | 40098.1029 | 59.885 | 3794.3743 | 335 | -211.256 | 4 | 96.5 | 10 | 0 | -103 | 7563.69 | 92.0013 | T+48 sec | 40098.1029 | [12 empty] | T+48 sec | 40098.1029 | [12 empty] | T+48 sec | 40098.1029 | [12 empty] | T+48 sec | 40098.1029 | 59.8876 | 3784.1485 | 335 | -210.3618 | 2.1111 | 95.1944 | 10 | 0 | -103 | 7562.8283 | 89.9553 | 3718.8718 | T+48 sec | 40098.1029 | 59.8883 | 3785.2046 | 335 | -210.5913 | 2.1765 | 95.2941 | 10 | 0 | -103 | 7562.8941 | 89.3644 | 3718.1426
T+50 sec | 40098.1029 | 59.885 | 3794.3743 | 59.8883 | 3785.2046 |  | 92.0013 | 90.5475 | 3758.7551 | 0.58036 | 3783.3686 | 3757.04 | 3772.5357 | 3692.126 | 3685.1617 | 633 | [6 empty] | 0 | 633 | -405.1151 | -414.2499 | T+50 sec | [6 empty] | 59.8876 | -412.3889 | 59.8883 | -414.2499 | T+50 sec | 40098.1029 | 59.885 | 3794.3743 | 335 | -211.256 | 4 | 96.5 | 10 | 0 | -103 | 7563.69 | 92.0013 | T+50 sec | 40098.1029 | [12 empty] | T+50 sec | 40098.1029 | [12 empty] | T+50 sec | 40098.1029 | [12 empty] | T+50 sec | 40098.1029 | 59.8876 | 3784.1485 | 335 | -210.3618 | 2.1111 | 95.1944 | 10 | 0 | -103 | 7562.8283 | 89.9553 | 3718.8718 | T+50 sec | 40098.1029 | 59.8883 | 3785.2046 | 335 | -210.5913 | 2.1765 | 95.2941 | 10 | 0 | -103 | 7562.8941 | 89.3644 | 3718.1426
T+52 sec | 40098.1029 | 59.887 | 3800.4275 | 59.8883 | 3785.2046 |  | 90.3992 | 90.4956 | 3758.7551 | 0.58036 | 3783.8971 | 3758.6469 | 3772.9565 | 3692.7063 | 3685.4519 | 633 | [6 empty] | 0 | 633 | -410.3749 | -414.2499 | T+52 sec | [6 empty] | 59.8876 | -412.3889 | 59.8883 | -414.2499 | T+52 sec | 40098.1029 | 59.887 | 3800.4275 | 335 | -214.3467 | 5 | 97 | 10 | 0 | -103 | 7564.02 | 90.3992 | T+52 sec | 40098.1029 | [12 empty] | T+52 sec | 40098.1029 | [12 empty] | T+52 sec | 40098.1029 | [12 empty] | T+52 sec | 40098.1029 | 59.8876 | 3784.1485 | 335 | -210.3618 | 2.1111 | 95.1944 | 10 | 0 | -103 | 7562.8283 | 89.9553 | 3718.8718 | T+52 sec | 40098.1029 | 59.8883 | 3785.2046 | 335 | -210.5913 | 2.1765 | 95.2941 | 10 | 0 | -103 | 7562.8941 | 89.3644 | 3718.1426
T+54 sec | 40098.1029 | 59.887 | 3800.4275 |  |  |  | 90.3992 | 90.4618 |  | 0.58036 | 3784.4437 | 3760.1391 | 3773.3667 | 3693.2867 | 3685.742 | 633 | [6 empty] | 0 | 633 | -410.3749 |  | T+54 sec | [10 empty] | T+54 sec | 40098.1029 | 59.887 | 3800.4275 | 335 | -214.3467 | 5 | 97 | 10 | 0 | -103 | 7564.02 | 90.3992 | T+54 sec | 40098.1029 | [12 empty] | T+54 sec | 40098.1029 | [12 empty] | T+54 sec | 40098.1029 | [12 empty] | T+54 sec | 40098.1029 | [12 empty] | T+54 sec | 40098.1029
T+56 sec | 40098.103 | 59.888 | 3802.925 |  |  |  | 89.5996 | 90.1601 |  | 0.58036 | 3784.7222 | 3761.6145 | 3773.7583 | 3693.8671 | 3686.0322 | 633 | [6 empty] | 0 | 633 | -413.0513 |  | T+56 sec | [10 empty] | T+56 sec | 40098.103 | 59.888 | 3802.925 | 335 | -214.3467 | 6 | 97.5 | 10 | 0 | -103 | 7564.35 | 89.5996 | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103
T+58 sec | 40098.103 | 59.888 | 3802.925 |  |  |  | 89.5996 | 89.9639 |  | 0.58036 | 3785.1064 | 3762.9915 | 3774.1366 | 3694.4474 | 3686.3224 | 633 | [6 empty] | 0 | 633 | -413.0513 |  | T+58 sec | [10 empty] | T+58 sec | 40098.103 | 59.888 | 3802.925 | 335 | -214.3467 | 6 | 97.5 | 10 | 0 | -103 | 7564.35 | 89.5996 | T+58 sec | 40098.103 | [12 empty] | T+58 sec | 40098.103 | [12 empty] | T+58 sec | 40098.103 | [12 empty] | T+58 sec | 40098.103 | [12 empty] | T+58 sec | 40098.103
T+60 sec | 40098.103 | 59.888 | 3802.925 |  |  |  | 89.5996 | 89.8364 |  | 0.58036 | 3785.5593 | 3764.2797 | 3774.5051 | 3695.0278 | 3686.6126 | 633 | [6 empty] | 0 | 633 | -413.0513 |  | T+60 sec | [10 empty] | T+60 sec | 40098.103 | 59.888 | 3802.925 | 335 | -214.3467 | 6 | 97.5 | 10 | 0 | -103 | 7564.35 | 89.5996 | T+60 sec | 40098.103 | [12 empty] | T+60 sec | 40098.103 | [12 empty] | T+60 sec | 40098.103 | [12 empty] | T+60 sec | 40098.103 | [12 empty] | T+60 sec | 40098.103
T+62 sec | 40098.103 | 59.882 | 3804.3879 |  |  |  | 94.4 | 91.4337 |  | 0.58036 | 3787.7369 | 3765.533 | 3774.9186 | 3695.6081 | 3686.9028 | 633 | [6 empty] | 0 | 633 | -397.4876 |  | T+62 sec | [10 empty] | T+62 sec | 40098.103 | 59.882 | 3804.3879 | 335 | -214.3467 | 7 | 98 | 10 | 0 | -103 | 7564.68 | 94.4 | T+62 sec | 40098.103 | [12 empty] | T+62 sec | 40098.103 | [12 empty] | T+62 sec | 40098.103 | [12 empty] | T+62 sec | 40098.103 | [12 empty] | T+62 sec | 40098.103
T+64 sec | 40098.1031 | 59.882 | 3804.3879 |  |  |  | 94.4 | 92.4719 |  | 0.58036 | 3789.3555 | 3766.7105 | 3775.356 | 3696.1885 | 3687.1929 | 633 | [6 empty] | 0 | 633 | -397.4876 |  | T+64 sec | [10 empty] | T+64 sec | 40098.1031 | 59.882 | 3804.3879 | 335 | -214.3467 | 7 | 98 | 10 | 0 | -103 | 7564.68 | 94.4 | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031
T+66 sec | 40098.1031 | 59.857 | 3809.2373 |  |  |  | 114.4012 | 100.1472 |  | 0.58036 | 3797.6111 | 3767.9612 | 3776.0106 | 3696.7688 | 3687.4831 | 633 | [6 empty] | 0 | 633 | -343.5516 |  | T+66 sec | [10 empty] | T+66 sec | 40098.1031 | 59.857 | 3809.2373 | 335 | -214.3467 | 8 | 98.5 | 10 | 0 | -103 | 7565.01 | 114.4012 | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031
T+68 sec | 40098.1031 | 59.857 | 3809.2373 |  |  |  | 114.4012 | 105.1361 |  | 0.58036 | 3803.1804 | 3769.1406 | 3776.7869 | 3697.3492 | 3687.7733 | 633 | [6 empty] | 0 | 633 | -343.5516 |  | T+68 sec | [10 empty] | T+68 sec | 40098.1031 | 59.857 | 3809.2373 | 335 | -214.3467 | 8 | 98.5 | 10 | 0 | -103 | 7565.01 | 114.4012 | T+68 sec | 40098.1031 | [12 empty] | T+68 sec | 40098.1031 | [12 empty] | T+68 sec | 40098.1031 | [12 empty] | T+68 sec | 40098.1031 | [12 empty] | T+68 sec | 40098.1031
T+70 sec | 40098.1031 | 59.857 | 3809.2373 |  |  |  | 114.4012 | 108.3789 |  | 0.58036 | 3807.0036 | 3770.2544 | 3777.6262 | 3697.9296 | 3688.0635 | 633 | [6 empty] | 0 | 633 | -343.5516 |  | T+70 sec | [10 empty] | T+70 sec | 40098.1031 | 59.857 | 3809.2373 | 335 | -214.3467 | 8 | 98.5 | 10 | 0 | -103 | 7565.01 | 114.4012 | T+70 sec | 40098.1031 | [12 empty] | T+70 sec | 40098.1031 | [12 empty] | T+70 sec | 40098.1031 | [12 empty] | T+70 sec | 40098.1031 | [12 empty] | T+70 sec | 40098.1031
T+72 sec | 40098.1031 | 59.858 | 3814.8623 |  |  |  | 113.5986 | 110.2058 |  | 0.58036 | 3809.4108 | 3771.46 | 3778.4853 | 3698.5099 | 3688.3537 | 633 | [6 empty] | 0 | 633 | -345.4325 |  | T+72 sec | [10 empty] | T+72 sec | 40098.1031 | 59.858 | 3814.8623 | 335 | -214.3467 | 9 | 99 | 10 | 0 | -103 | 7565.34 | 113.5986 | T+72 sec | 40098.1031 | [12 empty] | T+72 sec | 40098.1031 | [12 empty] | T+72 sec | 40098.1031 | [12 empty] | T+72 sec | 40098.1031 | [12 empty] | T+72 sec | 40098.1031
T+74 sec | 40098.1032 | 59.858 | 3814.8623 |  |  |  | 113.5986 | 111.3933 |  | 0.58036 | 3811.1787 | 3772.6021 | 3779.3456 | 3699.0903 | 3688.6438 | 633 | [6 empty] | 0 | 633 | -345.4325 |  | T+74 sec | [10 empty] | T+74 sec | 40098.1032 | 59.858 | 3814.8623 | 335 | -214.3467 | 9 | 99 | 10 | 0 | -103 | 7565.34 | 113.5986 | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032
T+76 sec | 40098.1032 | 59.866 | 3826.0532 |  |  |  | 107.1991 | 109.9253 |  | 0.58036 | 3810.2911 | 3773.9727 | 3780.1391 | 3699.6706 | 3688.934 | 633 | [6 empty] | 0 | 633 | -361.2001 |  | T+76 sec | [10 empty] | T+76 sec | 40098.1032 | 59.866 | 3826.0532 | 335 | -212.1727 | 10 | 99.5 | 10 | 0 | -103 | 7565.67 | 107.1991 | T+76 sec | 40098.1032 | [12 empty] | T+76 sec | 40098.1032 | [12 empty] | T+76 sec | 40098.1032 | [12 empty] | T+76 sec | 40098.1032 | [12 empty] | T+76 sec | 40098.1032
T+78 sec | 40098.1032 | 59.866 | 3826.0532 |  |  |  | 107.1991 | 108.9711 |  | 0.58036 | 3809.9173 | 3775.2747 | 3780.8836 | 3700.251 | 3689.2242 | 633 | [6 empty] | 0 | 633 | -361.2001 |  | T+78 sec | [10 empty] | T+78 sec | 40098.1032 | 59.866 | 3826.0532 | 335 | -212.1727 | 10 | 99.5 | 10 | 0 | -103 | 7565.67 | 107.1991 | T+78 sec | 40098.1032 | [12 empty] | T+78 sec | 40098.1032 | [12 empty] | T+78 sec | 40098.1032 | [12 empty] | T+78 sec | 40098.1032 | [12 empty] | T+78 sec | 40098.1032
T+80 sec | 40098.1032 | 59.866 | 3826.0532 |  |  |  | 107.1991 | 108.3509 |  | 0.58036 | 3809.8774 | 3776.5132 | 3781.5907 | 3700.8313 | 3689.5144 | 633 | [6 empty] | 0 | 633 | -361.2001 |  | T+80 sec | [10 empty] | T+80 sec | 40098.1032 | 59.866 | 3826.0532 | 335 | -212.1727 | 10 | 99.5 | 10 | 0 | -103 | 7565.67 | 107.1991 | T+80 sec | 40098.1032 | [12 empty] | T+80 sec | 40098.1032 | [12 empty] | T+80 sec | 40098.1032 | [12 empty] | T+80 sec | 40098.1032 | [12 empty] | T+80 sec | 40098.1032
| 40098.1033 | 59.866 | 3827.5239 |  |  |  | 107.1991 | 107.9478 |  | 0.58036 | 3810.0546 | 3777.7277 | 3782.2684 | 3701.4117 | 3689.8045 | 633 | [6 empty] | 0 | 633 | -361.2001 | [13 empty] | 40098.1033 | 59.866 | 3827.5239 | 335 | -212.1727 | 11 | 100 | 10 | 0 | -103 | 7566 | 107.1991
| 40098.1033 | 59.866 | 3827.5239 |  |  |  | 107.1991 | 107.6857 |  | 0.58036 | 3810.3729 | 3778.8858 | 3782.922 | 3701.9921 | 3690.0947 | 633 | [6 empty] | 0 | 633 | -361.2001 | [13 empty] | 40098.1033 | 59.866 | 3827.5239 | 335 | -212.1727 | 11 | 100 | 10 | 0 | -103 | 7566 | 107.1991
| 40098.1033 | 59.874 | 3826.4536 |  |  |  | 100.7996 | 105.2756 |  | 0.58036 | 3808.5431 | 3779.9669 | 3783.5043 | 3702.5724 | 3690.3849 | 633 | [6 empty] | 0 | 633 | -378.4761 | [13 empty] | 40098.1033 | 59.874 | 3826.4536 | 335 | -212.1727 | 12 | 100.5 | 10 | 0 | -103 | 7566.33 | 100.7996
| 40098.1033 | 59.874 | 3826.4536 |  |  |  | 100.7996 | 103.709 |  | 0.58036 | 3807.5569 | 3780.9999 | 3784.0388 | 3703.1528 | 3690.6751 | 633 | [6 empty] | 0 | 633 | -378.4761 | [13 empty] | 40098.1033 | 59.874 | 3826.4536 | 335 | -212.1727 | 12 | 100.5 | 10 | 0 | -103 | 7566.33 | 100.7996
| 40098.1034 | 59.874 | 3826.4536 |  |  |  | 100.7996 | 102.6907 |  | 0.58036 | 3807.1189 | 3781.988 | 3784.5406 | 3703.7331 | 3690.9653 | 633 | [6 empty] | 0 | 633 | -378.4761 | [13 empty] | 40098.1034 | 59.874 | 3826.4536 | 335 | -212.1727 | 12 | 100.5 | 10 | 0 | -103 | 7566.33 | 100.7996
| 40098.1034 | 59.883 | 3823.8257 |  |  |  | 93.6005 | 99.5091 |  | 0.58036 | 3804.5177 | 3782.8782 | 3784.9656 | 3704.3135 | 3691.2554 | 633 | [6 empty] | 0 | 633 | -399.998 | [13 empty] | 40098.1034 | 59.883 | 3823.8257 | 335 | -212.1727 | 13 | 101 | 10 | 0 | -103 | 7566.66 | 93.6005
| 40098.1034 | 59.883 | 3823.8257 |  |  |  | 93.6005 | 97.4411 |  | 0.58036 | 3803.03 | 3783.7313 | 3785.342 | 3704.8938 | 3691.5456 | 633 | [6 empty] | 0 | 633 | -399.998 | [13 empty] | 40098.1034 | 59.883 | 3823.8257 | 335 | -212.1727 | 13 | 101 | 10 | 0 | -103 | 7566.66 | 93.6005
| 40098.1034 | 59.89 | 3818.0552 |  |  |  | 88.0005 | 94.1369 |  | 0.58036 | 3800.3062 | 3784.4318 | 3785.6473 | 3705.4742 | 3691.8358 | 633 | [6 empty] | 0 | 633 | -418.5101 | [13 empty] | 40098.1034 | 59.89 | 3818.0552 | 335 | -212.1727 | 14 | 101.5 | 10 | 0 | -103 | 7566.99 | 88.0005
| 40098.1034 | 59.89 | 3818.0552 |  |  |  | 88.0005 | 91.9891 |  | 0.58036 | 3798.7388 | 3785.1042 | 3785.9092 | 3706.0546 | 3692.126 | 633 | [6 empty] | 0 | 633 | -418.5101 | [13 empty] | 40098.1034 | 59.89 | 3818.0552 | 335 | -212.1727 | 14 | 101.5 | 10 | 0 | -103 | 7566.99 | 88.0005
| 40098.1035 | 59.89 | 3818.0552 |  |  |  | 88.0005 | 90.5931 |  | 0.58036 | 3797.9232 | 3785.7503 | 3786.1447 | 3706.6349 | 3692.4162 | 633 | [6 empty] | 0 | 633 | -418.5101 | [13 empty] | 40098.1035 | 59.89 | 3818.0552 | 335 | -212.1727 | 14 | 101.5 | 10 | 0 | -103 | 7566.99 | 88.0005
| 40098.1035 | 59.893 | 3815.0098 |  |  |  | 85.5988 | 88.8451 |  | 0.58036 | 3796.7555 | 3786.313 | 3786.3488 | 3707.2153 | 3692.7063 | 633 | [6 empty] | 0 | 633 | -426.9853 | [13 empty] | 40098.1035 | 59.893 | 3815.0098 | 335 | -215.5982 | 15 | 102 | 10 | 0 | -103 | 7567.32 | 85.5988
| 40098.1035 | 59.893 | 3815.0098 |  |  |  | 85.5988 | 87.7089 |  | 0.58036 | 3796.1996 | 3786.8545 | 3786.5347 | 3707.7956 | 3692.9965 | 633 | [6 empty] | 0 | 633 | -426.9853 | [13 empty] | 40098.1035 | 59.893 | 3815.0098 | 335 | -215.5982 | 15 | 102 | 10 | 0 | -103 | 7567.32 | 85.5988
| 40098.1035 | 59.903 | 3809.6519 |  |  |  | 77.6001 | 84.1708 |  | 0.58036 | 3793.2419 | 3787.2766 | 3786.6589 | 3708.376 | 3693.2867 | 633 | [6 empty] | 0 | 633 | -457.865 | [13 empty] | 40098.1035 | 59.903 | 3809.6519 | 335 | -215.5982 | 16 | 102.5 | 10 | 0 | -103 | 7567.65 | 77.6001
| 40098.1036 | 59.903 | 3809.6519 |  |  |  | 77.6001 | 81.8711 |  | 0.58036 | 3791.5225 | 3787.6835 | 3786.7473 | 3708.9564 | 3693.5769 | 633 | [6 empty] | 0 | 633 | -457.865 | [13 empty] | 40098.1036 | 59.903 | 3809.6519 | 335 | -215.5982 | 16 | 102.5 | 10 | 0 | -103 | 7567.65 | 77.6001
| 40098.1036 | 59.903 | 3809.6519 |  |  |  | 77.6001 | 80.3762 |  | 0.58036 | 3790.6081 | 3788.0757 | 3786.8162 | 3709.5367 | 3693.8671 | 633 | [6 empty] | 0 | 633 | -457.865 | [13 empty] | 40098.1036 | 59.903 | 3809.6519 | 335 | -215.5982 | 16 | 102.5 | 10 | 0 | -103 | 7567.65 | 77.6001
| 40098.1036 | 59.904 | 3805.5933 |  |  |  | 76.8005 | 79.1247 |  | 0.58036 | 3789.9369 | 3788.3831 | 3786.871 | 3710.1171 | 3694.1572 | 633 | [6 empty] | 0 | 633 | -461.1992 | [13 empty] | 40098.1036 | 59.904 | 3805.5933 | 335 | -215.5982 | 16 | 103 | 10 | 0 | -103 | 7567.98 | 76.8005
| 40098.1036 | 59.904 | 3805.5933 |  |  |  | 76.8005 | 78.3113 |  | 0.58036 | 3789.7038 | 3788.6798 | 3786.9198 | 3710.6974 | 3694.4474 | 633 | [6 empty] | 0 | 633 | -461.1992 | [13 empty] | 40098.1036 | 59.904 | 3805.5933 | 335 | -215.5982 | 16 | 103 | 10 | 0 | -103 | 7567.98 | 76.8005
| 40098.1037 | 59.911 | 3793.9751 |  |  |  | 71.2006 | 75.8225 |  | 0.58036 | 3787.7954 | 3788.7696 | 3786.9347 | 3711.2778 | 3694.7376 | 633 | [6 empty] | 0 | 633 | -485.985 | [13 empty] | 40098.1037 | 59.911 | 3793.9751 | 335 | -215.5982 | 16 | 103.5 | 10 | 0 | -103 | 7568.31 | 71.2006
| 40098.1037 | 59.911 | 3793.9751 |  |  |  | 71.2006 | 74.2048 |  | 0.58036 | 3786.7581 | 3788.8563 | 3786.9317 | 3711.8581 | 3695.0278 | 633 | [6 empty] | 0 | 633 | -485.985 | [13 empty] | 40098.1037 | 59.911 | 3793.9751 | 335 | -215.5982 | 16 | 103.5 | 10 | 0 | -103 | 7568.31 | 71.2006
| 40098.1037 | 59.911 | 3793.9751 |  |  |  | 71.2006 | 73.1533 |  | 0.58036 | 3786.287 | 3788.9402 | 3786.9212 | 3712.4385 | 3695.3179 | 633 | [6 empty] | 0 | 633 | -485.985 | [13 empty] | 40098.1037 | 59.911 | 3793.9751 | 335 | -215.5982 | 16 | 103.5 | 10 | 0 | -103 | 7568.31 | 71.2006
| 40098.1037 | 59.917 | 3791.502 |  |  |  | 66.4001 | 70.7897 |  | 0.58036 | 3784.5037 | 3788.9815 | 3786.8822 | 3713.0189 | 3695.6081 | 633 | [6 empty] | 0 | 633 | -509.4551 | [13 empty] | 40098.1037 | 59.917 | 3791.502 | 335 | -215.5982 | 16 | 104 | 10 | 0 | -103 | 7568.64 | 66.4001
| 40098.1037 | 59.917 | 3791.502 |  |  |  | 66.4001 | 69.2534 |  | 0.58036 | 3783.5477 | 3789.0216 | 3786.8292 | 3713.5992 | 3695.8983 | 633 | [6 empty] | 0 | 633 | -509.4551 | [13 empty] | 40098.1037 | 59.917 | 3791.502 | 335 | -215.5982 | 16 | 104 | 10 | 0 | -103 | 7568.64 | 66.4001
| 40098.1038 | 59.92 | 3784.5635 |  |  |  | 64.0015 | 67.4152 |  | 0.58036 | 3782.2899 | 3788.9519 | 3786.7583 | 3714.1796 | 3696.1885 | 633 | [6 empty] | 0 | 633 | -522.053 | [13 empty] | 40098.1038 | 59.92 | 3784.5635 | 335 | -218.3273 | 16 | 104.5 | 10 | 0 | -103 | 7568.97 | 64.0015
| 40098.1038 | 59.92 | 3784.5635 |  |  |  | 64.0015 | 66.2204 |  | 0.58036 | 3781.6754 | 3788.8844 | 3786.6801 | 3714.7599 | 3696.4787 | 633 | [6 empty] | 0 | 633 | -522.053 | [13 empty] | 40098.1038 | 59.92 | 3784.5635 | 335 | -218.3273 | 16 | 104.5 | 10 | 0 | -103 | 7568.97 | 64.0015
| 40098.1038 | 59.92 | 3784.5635 |  |  |  | 64.0015 | 65.4438 |  | 0.58036 | 3781.4792 | 3788.8189 | 3786.6013 | 3715.3403 | 3696.7688 | 633 | [6 empty] | 0 | 633 | -522.053 | [13 empty] | 40098.1038 | 59.92 | 3784.5635 | 335 | -218.3273 | 16 | 104.5 | 10 | 0 | -103 | 7568.97 | 64.0015
| 40098.1038 | 59.917 | 3781.7012 |  |  |  | 66.4001 | 65.7785 |  | 0.58036 | 3782.3943 | 3788.7127 | 3786.5385 | 3715.9206 | 3697.059 | 633 | [6 empty] | 0 | 633 | -509.4551 | [13 empty] | 40098.1038 | 59.917 | 3781.7012 | 335 | -218.3273 | 16 | 105 | 10 | 0 | -103 | 7569.3 | 66.4001
| 40098.1039 | 59.917 | 3781.7012 |  |  |  | 66.4001 | 65.9961 |  | 0.58036 | 3783.1922 | 3788.6096 | 3786.4893 | 3716.501 | 3697.3492 | 633 | [6 empty] | 0 | 633 | -509.4551 | [13 empty] | 40098.1039 | 59.917 | 3781.7012 | 335 | -218.3273 | 16 | 105 | 10 | 0 | -103 | 7569.3 | 66.4001
| 40098.1039 | 59.921 | 3774.6042 |  |  |  | 63.1989 | 65.017 |  | 0.58036 | 3782.7935 | 3788.4066 | 3786.4358 | 3717.0814 | 3697.6394 | 633 | [6 empty] | 0 | 633 | -526.4086 | [13 empty] | 40098.1039 | 59.921 | 3774.6042 | 335 | -218.3273 | 16 | 105.5 | 10 | 0 | -103 | 7569.63 | 63.1989
| 40098.1039 | 59.921 | 3774.6042 |  |  |  | 63.1989 | 64.3807 |  | 0.58036 | 3782.7375 | 3788.2094 | 3786.3829 | 3717.6617 | 3697.9296 | 633 | [6 empty] | 0 | 633 | -526.4086 | [13 empty] | 40098.1039 | 59.921 | 3774.6042 | 335 | -218.3273 | 16 | 105.5 | 10 | 0 | -103 | 7569.63 | 63.1989
| 40098.1039 | 59.921 | 3774.6042 |  |  |  | 63.1989 | 63.967 |  | 0.58036 | 3782.9042 | 3788.0178 | 3786.3339 | 3718.2421 | 3698.2197 | 633 | [6 empty] | 0 | 633 | -526.4086 | [13 empty] | 40098.1039 | 59.921 | 3774.6042 | 335 | -218.3273 | 16 | 105.5 | 10 | 0 | -103 | 7569.63 | 63.1989
| 40098.104 | 59.925 | 3773.9578 |  |  |  | 60.0006 | 62.5788 |  | 0.58036 | 3782.0963 | 3787.8225 | 3786.2751 | 3718.8224 | 3698.5099 | 633 | [6 empty] | 0 | 633 | -544.5115 | [13 empty] | 40098.104 | 59.925 | 3773.9578 | 335 | -218.3273 | 16 | 106 | 10 | 0 | -103 | 7569.96 | 60.0006
| 40098.104 | 59.925 | 3773.9578 |  |  |  | 60.0006 | 61.6764 |  | 0.58036 | 3781.7743 | 3787.6326 | 3786.2134 | 3719.4028 | 3698.8001 | 633 | [6 empty] | 0 | 633 | -544.5115 | [13 empty] | 40098.104 | 59.925 | 3773.9578 | 335 | -218.3273 | 16 | 106 | 10 | 0 | -103 | 7569.96 | 60.0006
| 40098.104 | 59.927 | 3769.6296 |  |  |  | 58.4015 | 60.5302 |  | 0.58036 | 3781.2085 | 3787.3893 | 3786.1458 | 3719.9832 | 3699.0903 | 633 | [6 empty] | 0 | 633 | -554.038 | [13 empty] | 40098.104 | 59.927 | 3769.6296 | 335 | -218.3273 | 16 | 106.5 | 10 | 0 | -103 | 7570.29 | 58.4015
| 40098.104 | 59.927 | 3769.6296 |  |  |  | 58.4015 | 59.7852 |  | 0.58036 | 3781.0438 | 3787.1525 | 3786.0778 | 3720.5635 | 3699.3805 | 633 | [6 empty] | 0 | 633 | -554.038 | [13 empty] | 40098.104 | 59.927 | 3769.6296 | 335 | -218.3273 | 16 | 106.5 | 10 | 0 | -103 | 7570.29 | 58.4015
| 40098.1041 | 59.927 | 3769.6296 |  |  |  | 58.4015 | 59.3009 |  | 0.58036 | 3781.1399 | 3786.9219 | 3786.0128 | 3721.1439 | 3699.6706 | 633 | [6 empty] | 0 | 633 | -554.038 | [13 empty] | 40098.1041 | 59.927 | 3769.6296 | 335 | -218.3273 | 16 | 106.5 | 10 | 0 | -103 | 7570.29 | 58.4015
| 40098.1041 | 59.928 | 3767.6428 |  |  |  | 57.5989 | 58.7052 |  | 0.58036 | 3781.1245 | 3786.6716 | 3785.9493 | 3721.7242 | 3699.9608 | 633 | [6 empty] | 0 | 633 | -558.9462 | [13 empty] | 40098.1041 | 59.928 | 3767.6428 | 335 | -217.3794 | 0 | 107 | 10 | 0 | -103 | 7570.62 | 57.5989
| 40098.1041 | 59.928 | 3767.6428 |  |  |  | 57.5989 | 58.318 |  | 0.58036 | 3781.3177 | 3786.4276 | 3785.8899 | 3722.3046 | 3700.251 | 633 | [6 empty] | 0 | 633 | -558.9462 | [13 empty] | 40098.1041 | 59.928 | 3767.6428 | 335 | -217.3794 | 0 | 107 | 10 | 0 | -103 | 7570.62 | 57.5989
| 40098.1041 | 59.929 | 3766.7881 |  |  |  | 56.7993 | 57.7864 |  | 0.58036 | 3781.3665 | 3786.179 | 3785.8327 | 3722.8849 | 3700.5412 | 633 | [6 empty] | 0 | 633 | -563.923 | [13 empty] | 40098.1041 | 59.929 | 3766.7881 | 335 | -217.3794 | 0 | 107.5 | 10 | 0 | -103 | 7570.95 | 56.7993
| 40098.1041 | 59.929 | 3766.7881 |  |  |  | 56.7993 | 57.4409 |  | 0.58036 | 3781.6014 | 3785.9366 | 3785.7798 | 3723.4653 | 3700.8313 | 633 | [6 empty] | 0 | 633 | -563.923 | [13 empty] | 40098.1041 | 59.929 | 3766.7881 | 335 | -217.3794 | 0 | 107.5 | 10 | 0 | -103 | 7570.95 | 56.7993
| 40098.1042 | 59.929 | 3766.7881 |  |  |  | 56.7993 | 57.2164 |  | 0.58036 | 3781.9572 | 3785.7002 | 3785.7326 | 3724.0457 | 3701.1215 | 633 | [6 empty] | 0 | 633 | -563.923 | [13 empty] | 40098.1042 | 59.929 | 3766.7881 | 335 | -217.3794 | 0 | 107.5 | 10 | 0 | -103 | 7570.95 | 56.7993
| 40098.1042 | 59.937 | 3765.6716 |  |  |  | 50.3998 | 54.8306 |  | 0.58036 | 3780.1517 | 3785.456 | 3785.6645 | 3724.626 | 3701.4117 | 633 | [6 empty] | 0 | 633 | -607.1945 | [13 empty] | 40098.1042 | 59.937 | 3765.6716 | 335 | -217.3794 | 0 | 108 | 10 | 0 | -103 | 7571.28 | 50.3998
| 40098.1042 | 59.937 | 3765.6716 |  |  |  | 50.3998 | 53.2798 |  | 0.58036 | 3779.1813 | 3785.2176 | 3785.5864 | 3725.2064 | 3701.7019 | 633 | [6 empty] | 0 | 633 | -607.1945 | [13 empty] | 40098.1042 | 59.937 | 3765.6716 | 335 | -217.3794 | 0 | 108 | 10 | 0 | -103 | 7571.28 | 50.3998
| 40098.1042 | 59.945 | 3765.105 |  |  |  | 44.0002 | 50.032 |  | 0.58036 | 3776.5138 | 3784.9782 | 3785.4784 | 3725.7867 | 3701.9921 | 633 | [6 empty] | 0 | 633 | -657.6587 | [13 empty] | 40098.1042 | 59.945 | 3765.105 | 335 | -217.3794 | 0 | 108.5 | 10 | 0 | -103 | 7571.61 | 44.0002
| 40098.1043 | 59.945 | 3765.105 |  |  |  | 44.0002 | 47.9209 |  | 0.58036 | 3774.9831 | 3784.7444 | 3785.3549 | 3726.3671 | 3702.2822 | 633 | [6 empty] | 0 | 633 | -657.6587 | [13 empty] | 40098.1043 | 59.945 | 3765.105 | 335 | -217.3794 | 0 | 108.5 | 10 | 0 | -103 | 7571.61 | 44.0002
| 40098.1043 | 59.945 | 3765.105 |  |  |  | 44.0002 | 46.5486 |  | 0.58036 | 3774.1912 | 3784.516 | 3785.2251 | 3726.9474 | 3702.5724 | 633 | [6 empty] | 0 | 633 | -657.6587 | [13 empty] | 40098.1043 | 59.945 | 3765.105 | 335 | -217.3794 | 0 | 108.5 | 10 | 0 | -103 | 7571.61 | 44.0002
| 40098.1043 | 59.942 | 3758.3872 |  |  |  | 46.3989 | 46.4962 |  | 0.58036 | 3774.7192 | 3784.2157 | 3785.1044 | 3727.5278 | 3702.8626 | 633 | [6 empty] | 0 | 633 | -637.7905 | [13 empty] | 40098.1043 | 59.942 | 3758.3872 | 335 | -217.3794 | 0 | 109 | 10 | 0 | -103 | 7571.94 | 46.3989
| 40098.1043 | 59.942 | 3758.3872 |  |  |  | 46.3989 | 46.4622 |  | 0.58036 | 3775.2655 | 3783.9222 | 3784.9925 | 3728.1082 | 3703.1528 | 633 | [6 empty] | 0 | 633 | -637.7905 | [13 empty] | 40098.1043 | 59.942 | 3758.3872 | 335 | -217.3794 | 0 | 109 | 10 | 0 | -103 | 7571.94 | 46.3989
| 40098.1044 | 59.942 | 3746.8887 |  |  |  | 46.3989 | 46.44 |  | 0.58036 | 3775.8237 | 3783.5061 | 3784.8895 | 3728.6885 | 3703.443 | 633 | [6 empty] | 0 | 633 | -637.7905 | [13 empty] | 40098.1044 | 59.942 | 3746.8887 | 335 | -214.8304 | 0 | 109.5 | 10 | 0 | -103 | 7572.27 | 46.3989
| 40098.1044 | 59.942 | 3746.8887 |  |  |  | 46.3989 | 46.4257 |  | 0.58036 | 3776.3896 | 3783.0992 | 3784.7951 | 3729.2689 | 3703.7331 | 633 | [6 empty] | 0 | 633 | -637.7905 | [13 empty] | 40098.1044 | 59.942 | 3746.8887 | 335 | -214.8304 | 0 | 109.5 | 10 | 0 | -103 | 7572.27 | 46.3989
| 40098.1044 | 59.942 | 3746.8887 |  |  |  | 46.3989 | 46.4163 |  | 0.58036 | 3776.9607 | 3782.7013 | 3784.709 | 3729.8492 | 3704.0233 | 633 | [6 empty] | 0 | 633 | -637.7905 | [13 empty] | 40098.1044 | 59.942 | 3746.8887 | 335 | -214.8304 | 0 | 109.5 | 10 | 0 | -103 | 7572.27 | 46.3989
| 40098.1044 | 59.947 | 3749.5933 |  |  |  | 42.4011 | 45.011 |  | 0.58036 | 3776.1357 | 3782.3414 | 3784.6158 | 3730.4296 | 3704.3135 | 633 | [6 empty] | 0 | 633 | -671.6064 | [13 empty] | 40098.1044 | 59.947 | 3749.5933 | 335 | -214.8304 | 0 | 110 | 10 | 0 | -103 | 7572.6 | 42.4011
| 40098.1044 | 59.947 | 3749.5933 |  |  |  | 42.4011 | 44.0975 |  | 0.58036 | 3775.8026 | 3781.9893 | 3784.521 | 3731.01 | 3704.6037 | 633 | [6 empty] | 0 | 633 | -671.6064 | [13 empty] | 40098.1044 | 59.947 | 3749.5933 | 335 | -214.8304 | 0 | 110 | 10 | 0 | -103 | 7572.6 | 42.4011
| 40098.1045 | 59.951 | 3749.0769 |  |  |  | 39.1998 | 42.3833 |  | 0.58036 | 3774.6688 | 3781.6391 | 3784.4162 | 3731.5903 | 3704.8938 | 633 | [6 empty] | 0 | 633 | -701.3849 | [13 empty] | 40098.1045 | 59.951 | 3749.0769 | 335 | -214.8304 | 0 | 110.5 | 10 | 0 | -103 | 7572.93 | 39.1998
| 40098.1045 | 59.951 | 3749.0769 |  |  |  | 39.1998 | 41.2691 |  | 0.58036 | 3774.1349 | 3781.2964 | 3784.308 | 3732.1707 | 3705.184 | 633 | [6 empty] | 0 | 633 | -701.3849 | [13 empty] | 40098.1045 | 59.951 | 3749.0769 | 335 | -214.8304 | 0 | 110.5 | 10 | 0 | -103 | 7572.93 | 39.1998
| 40098.1045 | 59.951 | 3749.0769 |  |  |  | 39.1998 | 40.5449 |  | 0.58036 | 3773.991 | 3780.9608 | 3784.2005 | 3732.751 | 3705.4742 | 633 | [6 empty] | 0 | 633 | -701.3849 | [13 empty] | 40098.1045 | 59.951 | 3749.0769 | 335 | -214.8304 | 0 | 110.5 | 10 | 0 | -103 | 7572.93 | 39.1998
| 40098.1045 | 59.951 | 3740.259 |  |  |  | 39.1998 | 40.0741 |  | 0.58036 | 3774.1006 | 3780.5412 | 3784.0964 | 3733.3314 | 3705.7644 | 633 | [6 empty] | 0 | 633 | -701.3849 | [13 empty] | 40098.1045 | 59.951 | 3740.259 | 335 | -214.8304 | 0 | 111 | 10 | 0 | -103 | 7573.26 | 39.1998
| 40098.1046 | 59.951 | 3740.259 |  |  |  | 39.1998 | 39.7681 |  | 0.58036 | 3774.375 | 3780.1301 | 3783.9972 | 3733.9117 | 3706.0546 | 633 | [6 empty] | 0 | 633 | -701.3849 | [13 empty] | 40098.1046 | 59.951 | 3740.259 | 335 | -214.8304 | 0 | 111 | 10 | 0 | -103 | 7573.26 | 39.1998
| 40098.1046 | 59.952 | 3727.8384 |  |  |  | 38.4003 | 39.2894 |  | 0.58036 | 3774.4766 | 3779.6019 | 3783.901 | 3734.4921 | 3706.3447 | 633 | [6 empty] | 0 | 633 | -709.2392 | [13 empty] | 40098.1046 | 59.952 | 3727.8384 | 335 | -214.8304 | 0 | 111.5 | 10 | 0 | -103 | 7573.59 | 38.4003
| 40098.1046 | 59.952 | 3727.8384 |  |  |  | 38.4003 | 38.9782 |  | 0.58036 | 3774.7458 | 3779.0843 | 3783.8095 | 3735.0725 | 3706.6349 | 633 | [6 empty] | 0 | 633 | -709.2392 | [13 empty] | 40098.1046 | 59.952 | 3727.8384 | 335 | -214.8304 | 0 | 111.5 | 10 | 0 | -103 | 7573.59 | 38.4003
| 40098.1046 | 59.952 | 3727.8384 |  |  |  | 38.4003 | 38.7759 |  | 0.58036 | 3775.1238 | 3778.5769 | 3783.7235 | 3735.6528 | 3706.9251 | 633 | [6 empty] | 0 | 633 | -709.2392 | [13 empty] | 40098.1046 | 59.952 | 3727.8384 | 335 | -214.8304 | 0 | 111.5 | 10 | 0 | -103 | 7573.59 | 38.4003
| 40098.1047 | 59.952 | 3722.6489 |  |  |  | 38.4003 | 38.6444 |  | 0.58036 | 3775.5727 | 3778.0286 | 3783.6436 | 3736.2332 | 3707.2153 | 633 | [6 empty] | 0 | 633 | -709.2392 | [13 empty] | 40098.1047 | 59.952 | 3722.6489 | 335 | -227.6559 | 0 | 112 | 10 | 0 | -103 | 7573.92 | 38.4003
| 40098.1047 | 59.952 | 3722.6489 |  |  |  | 38.4003 | 38.559 |  | 0.58036 | 3776.0676 | 3777.4909 | 3783.57 | 3736.8135 | 3707.5055 | 633 | [6 empty] | 0 | 633 | -709.2392 | [13 empty] | 40098.1047 | 59.952 | 3722.6489 | 335 | -227.6559 | 0 | 112 | 10 | 0 | -103 | 7573.92 | 38.4003
| 40098.1047 | 59.952 | 3718.1418 |  |  |  | 38.4003 | 38.5034 |  | 0.58036 | 3776.5924 | 3776.9203 | 3783.5029 | 3737.3939 | 3707.7956 | 633 | [6 empty] | 0 | 633 | -709.2392 | [13 empty] | 40098.1047 | 59.952 | 3718.1418 | 335 | -227.6559 | 0 | 112.5 | 10 | 0 | -103 | 7574.25 | 38.4003
| 40098.1047 | 59.952 | 3718.1418 |  |  |  | 38.4003 | 38.4673 |  | 0.58036 | 3777.1367 | 3776.3605 | 3783.4423 | 3737.9742 | 3708.0858 | 633 | [6 empty] | 0 | 633 | -709.2392 | [13 empty] | 40098.1047 | 59.952 | 3718.1418 | 335 | -227.6559 | 0 | 112.5 | 10 | 0 | -103 | 7574.25 | 38.4003
| 40098.1047 | 59.952 | 3718.1418 |  |  |  | 38.4003 | 38.4439 |  | 0.58036 | 3777.6936 | 3775.8112 | 3783.3881 | 3738.5546 | 3708.376 | 633 | [6 empty] | 0 | 633 | -709.2392 | [13 empty] | 40098.1047 | 59.952 | 3718.1418 | 335 | -227.6559 | 0 | 112.5 | 10 | 0 | -103 | 7574.25 | 38.4003
| 40098.1048 | 59.952 | 3713.6938 |  |  |  | 38.4003 | 38.4286 |  | 0.58036 | 3778.2587 | 3775.2307 | 3783.3401 | 3739.135 | 3708.6662 | 633 | [6 empty] | 0 | 633 | -709.2392 | [13 empty] | 40098.1048 | 59.952 | 3713.6938 | 335 | -227.6559 | 0 | 113 | 10 | 0 | -103 | 7574.58 | 38.4003
| 40098.1048 | 59.952 | 3713.6938 |  |  |  | 38.4003 | 38.4187 |  | 0.58036 | 3778.8291 | 3774.6609 | 3783.2984 | 3739.7153 | 3708.9564 | 633 | [6 empty] | 0 | 633 | -709.2392 | [13 empty] | 40098.1048 | 59.952 | 3713.6938 | 335 | -227.6559 | 0 | 113 | 10 | 0 | -103 | 7574.58 | 38.4003
| 40098.1048 | 59.954 | 3710.8101 |  |  |  | 36.8011 | 37.8525 |  | 0.58036 | 3778.8433 | 3774.0751 | 3783.2575 | 3740.2957 | 3709.2465 | 633 | [6 empty] | 0 | 633 | -725.4876 | [13 empty] | 40098.1048 | 59.954 | 3710.8101 | 335 | -227.6559 | 0 | 113.5 | 10 | 0 | -103 | 7574.91 | 36.8011
| 40098.1048 | 59.954 | 3710.8101 |  |  |  | 36.8011 | 37.4846 |  | 0.58036 | 3779.0557 | 3773.5 | 3783.2193 | 3740.876 | 3709.5367 | 633 | [6 empty] | 0 | 633 | -725.4876 | [13 empty] | 40098.1048 | 59.954 | 3710.8101 | 335 | -227.6559 | 0 | 113.5 | 10 | 0 | -103 | 7574.91 | 36.8011
| 40098.1049 | 59.954 | 3710.8101 |  |  |  | 36.8011 | 37.2454 |  | 0.58036 | 3779.3969 | 3772.9352 | 3783.1849 | 3741.4564 | 3709.8269 | 633 | [6 empty] | 0 | 633 | -725.4876 | [13 empty] | 40098.1049 | 59.954 | 3710.8101 | 335 | -227.6559 | 0 | 113.5 | 10 | 0 | -103 | 7574.91 | 36.8011
| 40098.1049 | 59.956 | 3714.6226 |  |  |  | 35.199 | 36.5291 |  | 0.58036 | 3779.261 | 3772.4146 | 3783.1498 | 3742.0367 | 3710.1171 | 633 | [6 empty] | 0 | 633 | -742.5312 | [13 empty] | 40098.1049 | 59.956 | 3714.6226 | 335 | -227.6559 | 0 | 114 | 10 | 0 | -103 | 7575.24 | 35.199
| 40098.1049 | 59.956 | 3714.6226 |  |  |  | 35.199 | 36.0636 |  | 0.58036 | 3779.3758 | 3771.9031 | 3783.1164 | 3742.6171 | 3710.4072 | 633 | [6 empty] | 0 | 633 | -742.5312 | [13 empty] | 40098.1049 | 59.956 | 3714.6226 | 335 | -227.6559 | 0 | 114 | 10 | 0 | -103 | 7575.24 | 35.199
| 40098.1049 | 59.956 | 3716.4614 |  |  |  | 35.199 | 35.761 |  | 0.58036 | 3779.6535 | 3771.4168 | 3783.0861 | 3743.1975 | 3710.6974 | 633 | [6 empty] | 0 | 633 | -742.5312 | [13 empty] | 40098.1049 | 59.956 | 3716.4614 | 335 | -225.0181 | 0 | 114.5 | 10 | 0 | -103 | 7575.57 | 35.199
| 40098.105 | 59.956 | 3716.4614 |  |  |  | 35.199 | 35.5643 |  | 0.58036 | 3780.0372 | 3770.9389 | 3783.0595 | 3743.7778 | 3710.9876 | 633 | [6 empty] | 0 | 633 | -742.5312 | [13 empty] | 40098.105 | 59.956 | 3716.4614 | 335 | -225.0181 | 0 | 114.5 | 10 | 0 | -103 | 7575.57 | 35.199
| 40098.105 | 59.956 | 3716.4614 |  |  |  | 35.199 | 35.4364 |  | 0.58036 | 3780.4897 | 3770.4693 | 3783.0374 | 3744.3582 | 3711.2778 | 633 | [6 empty] | 0 | 633 | -742.5312 | [13 empty] | 40098.105 | 59.956 | 3716.4614 | 335 | -225.0181 | 0 | 114.5 | 10 | 0 | -103 | 7575.57 | 35.199
| 40098.105 | 59.961 | 3717.759 |  |  |  | 31.2012 | 33.9541 |  | 0.58036 | 3779.5877 | 3770.0188 | 3783.0079 | 3744.9385 | 3711.568 | 633 | [6 empty] | 0 | 633 | -788.7684 | [13 empty] | 40098.105 | 59.961 | 3717.759 | 335 | -225.0181 | 0 | 115 | 10 | 0 | -103 | 7575.9 | 31.2012
| 40098.105 | 59.961 | 3717.759 |  |  |  | 31.2012 | 32.9906 |  | 0.58036 | 3779.2046 | 3769.5759 | 3782.9757 | 3745.5189 | 3711.8581 | 633 | [6 empty] | 0 | 633 | -788.7684 | [13 empty] | 40098.105 | 59.961 | 3717.759 | 335 | -225.0181 | 0 | 115 | 10 | 0 | -103 | 7575.9 | 31.2012
| 40098.105 | 59.962 | 3722.658 |  |  |  | 30.3986 | 32.0834 |  | 0.58036 | 3778.8777 | 3769.1816 | 3782.9412 | 3746.0993 | 3712.1483 | 633 | [6 empty] | 0 | 633 | -798.754 | [13 empty] | 40098.105 | 59.962 | 3722.658 | 335 | -225.0181 | 0 | 115.5 | 10 | 0 | -103 | 7576.23 | 30.3986
| 40098.1051 | 59.962 | 3722.658 |  |  |  | 30.3986 | 31.4937 |  | 0.58036 | 3778.8684 | 3768.7939 | 3782.9073 | 3746.6796 | 3712.4385 | 633 | [6 empty] | 0 | 633 | -798.754 | [13 empty] | 40098.1051 | 59.962 | 3722.658 | 335 | -225.0181 | 0 | 115.5 | 10 | 0 | -103 | 7576.23 | 30.3986
| 40098.1051 | 59.962 | 3722.658 |  |  |  | 30.3986 | 31.1104 |  | 0.58036 | 3779.0655 | 3768.4126 | 3782.8755 | 3747.26 | 3712.7287 | 633 | [6 empty] | 0 | 633 | -798.754 | [13 empty] | 40098.1051 | 59.962 | 3722.658 | 335 | -225.0181 | 0 | 115.5 | 10 | 0 | -103 | 7576.23 | 30.3986
| 40098.1051 | 59.966 | 3722.2776 |  |  |  | 27.2003 | 29.7419 |  | 0.58036 | 3778.2773 | 3768.0345 | 3782.8379 | 3747.8403 | 3713.0189 | 633 | [6 empty] | 0 | 633 | -841.189 | [13 empty] | 40098.1051 | 59.966 | 3722.2776 | 335 | -225.0181 | 0 | 116 | 10 | 0 | -103 | 7576.56 | 27.2003
| 40098.1051 | 59.966 | 3722.2776 |  |  |  | 27.2003 | 28.8523 |  | 0.58036 | 3777.9681 | 3767.6625 | 3782.7983 | 3748.4207 | 3713.309 | 633 | [6 empty] | 0 | 633 | -841.189 | [13 empty] | 40098.1051 | 59.966 | 3722.2776 | 335 | -225.0181 | 0 | 116 | 10 | 0 | -103 | 7576.56 | 27.2003
| 40098.1052 | 59.97 | 3723.9839 |  |  |  | 23.999 | 27.1537 |  | 0.58036 | 3776.8498 | 3767.3102 | 3782.7503 | 3749.001 | 3713.5992 | 633 | [6 empty] | 0 | 633 | -888.4334 | [13 empty] | 40098.1052 | 59.97 | 3723.9839 | 335 | -225.0181 | 0 | 116.5 | 10 | 0 | -103 | 7576.89 | 23.999
| 40098.1052 | 59.97 | 3723.9839 |  |  |  | 23.999 | 26.0495 |  | 0.58036 | 3776.3261 | 3766.9636 | 3782.6989 | 3749.5814 | 3713.8894 | 633 | [6 empty] | 0 | 633 | -888.4334 | [13 empty] | 40098.1052 | 59.97 | 3723.9839 | 335 | -225.0181 | 0 | 116.5 | 10 | 0 | -103 | 7576.89 | 23.999
| 40098.1052 | 59.97 | 3723.9839 |  |  |  | 23.999 | 25.3319 |  | 0.58036 | 3776.1887 | 3766.6225 | 3782.6472 | 3750.1618 | 3714.1796 | 633 | [6 empty] | 0 | 633 | -888.4334 | [13 empty] | 40098.1052 | 59.97 | 3723.9839 | 335 | -225.0181 | 0 | 116.5 | 10 | 0 | -103 | 7576.89 | 23.999
| 40098.1052 | 59.969 | 3723.8931 |  |  |  | 24.7986 | 25.1452 |  | 0.58036 | 3776.5824 | 3766.2861 | 3782.5995 | 3750.7421 | 3714.4698 | 633 | [6 empty] | 0 | 633 | -876.1433 | [13 empty] | 40098.1052 | 59.969 | 3723.8931 | 335 | -228.3652 | 0 | 117 | 10 | 0 | -103 | 7577.22 | 24.7986
| 40098.1053 | 59.969 | 3723.8931 |  |  |  | 24.7986 | 25.0239 |  | 0.58036 | 3777.0415 | 3765.9549 | 3782.5561 | 3751.3225 | 3714.7599 | 633 | [6 empty] | 0 | 633 | -876.1433 | [13 empty] | 40098.1053 | 59.969 | 3723.8931 | 335 | -228.3652 | 0 | 117 | 10 | 0 | -103 | 7577.22 | 24.7986
| 40098.1053 | 59.97 | 3728.053 |  |  |  | 23.999 | 24.6652 |  | 0.58036 | 3777.2631 | 3765.661 | 3782.515 | 3751.9028 | 3715.0501 | 633 | [6 empty] | 0 | 633 | -888.4334 | [13 empty] | 40098.1053 | 59.97 | 3728.053 | 335 | -228.3652 | 0 | 117.5 | 10 | 0 | -103 | 7577.55 | 23.999
| 40098.1053 | 59.97 | 3728.053 |  |  |  | 23.999 | 24.432 |  | 0.58036 | 3777.6103 | 3765.3718 | 3782.4773 | 3752.4832 | 3715.3403 | 633 | [6 empty] | 0 | 633 | -888.4334 | [13 empty] | 40098.1053 | 59.97 | 3728.053 | 335 | -228.3652 | 0 | 117.5 | 10 | 0 | -103 | 7577.55 | 23.999
| 40098.1053 | 59.97 | 3728.053 |  |  |  | 23.999 | 24.2805 |  | 0.58036 | 3778.0391 | 3765.0869 | 3782.4434 | 3753.0635 | 3715.6305 | 633 | [6 empty] | 0 | 633 | -888.4334 | [13 empty] | 40098.1053 | 59.97 | 3728.053 | 335 | -228.3652 | 0 | 117.5 | 10 | 0 | -103 | 7577.55 | 23.999
| 40098.1053 | 59.973 | 3732.53 |  |  |  | 21.6003 | 23.3424 |  | 0.58036 | 3777.6815 | 3764.8402 | 3782.4073 | 3753.6439 | 3715.9206 | 633 | [6 empty] | 0 | 633 | -927.4636 | [13 empty] | 40098.1053 | 59.973 | 3732.53 | 335 | -228.3652 | 0 | 118 | 10 | 0 | -103 | 7577.88 | 21.6003
| 40098.1054 | 59.973 | 3732.53 |  |  |  | 21.6003 | 22.7327 |  | 0.58036 | 3777.6521 | 3764.5973 | 3782.3716 | 3754.2243 | 3716.2108 | 633 | [6 empty] | 0 | 633 | -927.4636 | [13 empty] | 40098.1054 | 59.973 | 3732.53 | 335 | -228.3652 | 0 | 118 | 10 | 0 | -103 | 7577.88 | 21.6003
| 40098.1054 | 59.978 | 3736.9075 |  |  |  | 17.5995 | 20.9361 |  | 0.58036 | 3776.4358 | 3764.3907 | 3782.3273 | 3754.8046 | 3716.501 | 633 | [6 empty] | 0 | 633 | -1000.797 | [13 empty] | 40098.1054 | 59.978 | 3736.9075 | 335 | -228.3652 | 0 | 118.5 | 10 | 0 | -103 | 7578.21 | 17.5995
| 40098.1054 | 59.978 | 3736.9075 |  |  |  | 17.5995 | 19.7683 |  | 0.58036 | 3775.8484 | 3764.1871 | 3782.2793 | 3755.385 | 3716.7912 | 633 | [6 empty] | 0 | 633 | -1000.797 | [13 empty] | 40098.1054 | 59.978 | 3736.9075 | 335 | -228.3652 | 0 | 118.5 | 10 | 0 | -103 | 7578.21 | 17.5995
| 40098.1054 | 59.978 | 3736.9075 |  |  |  | 17.5995 | 19.0092 |  | 0.58036 | 3775.6697 | 3763.9865 | 3782.2307 | 3755.9653 | 3717.0814 | 633 | [6 empty] | 0 | 633 | -1000.797 | [13 empty] | 40098.1054 | 59.978 | 3736.9075 | 335 | -228.3652 | 0 | 118.5 | 10 | 0 | -103 | 7578.21 | 17.5995
| 40098.1055 | 59.978 | 3738.6992 |  |  |  | 17.5995 | 18.5158 |  | 0.58036 | 3775.7566 | 3763.8019 | 3782.1834 | 3756.5457 | 3717.3715 | 633 | [6 empty] | 0 | 633 | -1000.797 | [13 empty] | 40098.1055 | 59.978 | 3738.6992 | 335 | -228.3652 | 0 | 119 | 10 | 0 | -103 | 7578.54 | 17.5995
| 40098.1055 | 59.978 | 3738.6992 |  |  |  | 17.5995 | 18.1951 |  | 0.58036 | 3776.0163 | 3763.62 | 3782.1388 | 3757.1261 | 3717.6617 | 633 | [6 empty] | 0 | 633 | -1000.797 | [13 empty] | 40098.1055 | 59.978 | 3738.6992 | 335 | -228.3652 | 0 | 119 | 10 | 0 | -103 | 7578.54 | 17.5995
| 40098.1055 | 59.978 | 3741.7937 |  |  |  | 17.5995 | 17.9866 |  | 0.58036 | 3776.3882 | 3763.463 | 3782.0974 | 3757.7064 | 3717.9519 | 633 | [6 empty] | 0 | 633 | -1000.797 | [13 empty] | 40098.1055 | 59.978 | 3741.7937 | 335 | -234.0753 | 0 | 119.5 | 10 | 0 | -103 | 7578.87 | 17.5995
| 40098.1055 | 59.978 | 3741.7937 |  |  |  | 17.5995 | 17.8511 |  | 0.58036 | 3776.833 | 3763.3082 | 3782.0598 | 3758.2868 | 3718.2421 | 633 | [6 empty] | 0 | 633 | -1000.797 | [13 empty] | 40098.1055 | 59.978 | 3741.7937 | 335 | -234.0753 | 0 | 119.5 | 10 | 0 | -103 | 7578.87 | 17.5995
| 40098.1056 | 59.978 | 3741.7937 |  |  |  | 17.5995 | 17.7631 |  | 0.58036 | 3777.3253 | 3763.1556 | 3782.0262 | 3758.8671 | 3718.5323 | 633 | [6 empty] | 0 | 633 | -1000.797 | [13 empty] | 40098.1056 | 59.978 | 3741.7937 | 335 | -234.0753 | 0 | 119.5 | 10 | 0 | -103 | 7578.87 | 17.5995
| 40098.1056 | 59.982 | 3746.6079 |  |  |  | 14.4012 | 16.5864 |  | 0.58036 | 3776.729 | 3763.0391 | 3781.9889 | 3759.4475 | 3718.8224 | 633 | [6 empty] | 0 | 633 | -1068.3222 | [13 empty] | 40098.1056 | 59.982 | 3746.6079 | 335 | -234.0753 | 0 | 120 | 10 | 0 | -103 | 7579.2 | 14.4012
| 40098.1056 | 59.982 | 3746.6079 |  |  |  | 14.4012 | 15.8216 |  | 0.58036 | 3776.5446 | 3762.9242 | 3781.9508 | 3760.0278 | 3719.1126 | 633 | [6 empty] | 0 | 633 | -1068.3222 | [13 empty] | 40098.1056 | 59.982 | 3746.6079 | 335 | -234.0753 | 0 | 120 | 10 | 0 | -103 | 7579.2 | 14.4012
| 40098.1056 | 59.98 | 3751.5576 |  |  |  | 16.0004 | 15.8842 |  | 0.58036 | 3777.1875 | 3762.8453 | 3781.9177 | 3760.6082 | 3719.4028 | 633 | [6 empty] | 0 | 633 | -1033.4578 | [13 empty] | 40098.1056 | 59.98 | 3751.5576 | 335 | -234.0753 | 0 | 120.5 | 10 | 0 | -103 | 7579.53 | 16.0004
| 40098.1056 | 59.98 | 3751.5576 |  |  |  | 16.0004 | 15.9248 |  | 0.58036 | 3777.8085 | 3762.7674 | 3781.8894 | 3761.1886 | 3719.693 | 633 | [6 empty] | 0 | 633 | -1033.4578 | [13 empty] | 40098.1056 | 59.98 | 3751.5576 | 335 | -234.0753 | 0 | 120.5 | 10 | 0 | -103 | 7579.53 | 16.0004
| 40098.1057 | 59.98 | 3751.5576 |  |  |  | 16.0004 | 15.9513 |  | 0.58036 | 3778.4153 | 3762.6906 | 3781.8656 | 3761.7689 | 3719.9832 | 633 | [6 empty] | 0 | 633 | -1033.4578 | [13 empty] | 40098.1057 | 59.98 | 3751.5576 | 335 | -234.0753 | 0 | 120.5 | 10 | 0 | -103 | 7579.53 | 16.0004
| 40098.1057 | 59.979 | 3755.5986 |  |  |  | 16.7999 | 16.2483 |  | 0.58036 | 3779.2927 | 3762.6424 | 3781.8481 | 3762.3493 | 3720.2733 | 633 | [6 empty] | 0 | 633 | -1016.8652 | [13 empty] | 40098.1057 | 59.979 | 3755.5986 | 335 | -234.0753 | 0 | 121 | 10 | 0 | -103 | 7579.86 | 16.7999
| 40098.1057 | 59.979 | 3755.5986 |  |  |  | 16.7999 | 16.4414 |  | 0.58036 | 3780.0661 | 3762.5948 | 3781.8361 | 3762.9296 | 3720.5635 | 633 | [6 empty] | 0 | 633 | -1016.8652 | [13 empty] | 40098.1057 | 59.979 | 3755.5986 | 335 | -234.0753 | 0 | 121 | 10 | 0 | -103 | 7579.86 | 16.7999
| 40098.1057 | 59.983 | 3760.4053 |  |  |  | 13.5986 | 15.4464 |  | 0.58036 | 3779.6515 | 3762.5801 | 3781.8214 | 3763.51 | 3720.8537 | 633 | [6 empty] | 0 | 633 | -1086.7229 | [13 empty] | 40098.1057 | 59.983 | 3760.4053 | 335 | -234.0753 | 0 | 121.5 | 10 | 0 | -103 | 7580.19 | 13.5986
| 40098.1058 | 59.983 | 3760.4053 |  |  |  | 13.5986 | 14.7997 |  | 0.58036 | 3779.5852 | 3762.5656 | 3781.8065 | 3764.0903 | 3721.1439 | 633 | [6 empty] | 0 | 633 | -1086.7229 | [13 empty] | 40098.1058 | 59.983 | 3760.4053 | 335 | -234.0753 | 0 | 121.5 | 10 | 0 | -103 | 7580.19 | 13.5986
| 40098.1058 | 59.983 | 3760.4053 |  |  |  | 13.5986 | 14.3793 |  | 0.58036 | 3779.7451 | 3762.5513 | 3781.7928 | 3764.6707 | 3721.434 | 633 | [6 empty] | 0 | 633 | -1086.7229 | [13 empty] | 40098.1058 | 59.983 | 3760.4053 | 335 | -234.0753 | 0 | 121.5 | 10 | 0 | -103 | 7580.19 | 13.5986
| 40098.1058 | 59.989 | 3761.407 |  |  |  | 8.8013 | 12.427 |  | 0.58036 | 3778.3732 | 3762.5438 | 3781.7703 | 3765.2511 | 3721.7242 | 633 | [6 empty] | 0 | 633 | -1211.4412 | [13 empty] | 40098.1058 | 59.989 | 3761.407 | 335 | -228.7982 | 0 | 122 | 10 | 0 | -103 | 7580.52 | 8.8013
| 40098.1058 | 59.989 | 3761.407 |  |  |  | 8.8013 | 11.158 |  | 0.58036 | 3777.6845 | 3762.5363 | 3781.7436 | 3765.8314 | 3722.0144 | 633 | [6 empty] | 0 | 633 | -1211.4412 | [13 empty] | 40098.1058 | 59.989 | 3761.407 | 335 | -228.7982 | 0 | 122 | 10 | 0 | -103 | 7580.52 | 8.8013
| 40098.1059 | 59.987 | 3764.9575 |  |  |  | 10.4004 | 10.8928 |  | 0.58036 | 3777.9997 | 3762.5521 | 3781.7193 | 3766.4118 | 3722.3046 | 633 | [6 empty] | 0 | 633 | -1166.8049 | [13 empty] | 40098.1059 | 59.987 | 3764.9575 | 335 | -228.7982 | 0 | 122.5 | 10 | 0 | -103 | 7580.85 | 10.4004
| 40098.1059 | 59.987 | 3764.9575 |  |  |  | 10.4004 | 10.7205 |  | 0.58036 | 3778.4077 | 3762.5676 | 3781.698 | 3766.9921 | 3722.5948 | 633 | [6 empty] | 0 | 633 | -1166.8049 | [13 empty] | 40098.1059 | 59.987 | 3764.9575 | 335 | -228.7982 | 0 | 122.5 | 10 | 0 | -103 | 7580.85 | 10.4004
| 40098.1059 | 59.987 | 3764.9575 |  |  |  | 10.4004 | 10.6084 |  | 0.58036 | 3778.8761 | 3762.5829 | 3781.6799 | 3767.5725 | 3722.8849 | 633 | [6 empty] | 0 | 633 | -1166.8049 | [13 empty] | 40098.1059 | 59.987 | 3764.9575 | 335 | -228.7982 | 0 | 122.5 | 10 | 0 | -103 | 7580.85 | 10.4004
| 40098.1059 | 59.992 | 3766.4331 |  |  |  | 6.3995 | 9.1353 |  | 0.58036 | 3777.9833 | 3762.6074 | 3781.6563 | 3768.1528 | 3723.1751 | 633 | [6 empty] | 0 | 633 | -1285.2883 | [13 empty] | 40098.1059 | 59.992 | 3766.4331 | 335 | -354.8957 | 0 | 123 | 10 | 0 | -103 | 7581.18 | 6.3995
| 40098.1059 | 59.992 | 3766.4331 |  |  |  | 6.3995 | 8.1778 |  | 0.58036 | 3777.6061 | 3762.6316 | 3781.6307 | 3768.7332 | 3723.4653 | 633 | [6 empty] | 0 | 633 | -1285.2883 | [13 empty] | 40098.1059 | 59.992 | 3766.4331 | 335 | -354.8957 | 0 | 123 | 10 | 0 | -103 | 7581.18 | 6.3995
| 40098.106 | 59.989 | 3768.6335 |  |  |  | 8.8013 | 8.396 |  | 0.58036 | 3778.4047 | 3762.6694 | 3781.6104 | 3769.3136 | 3723.7555 | 633 | [6 empty] | 0 | 633 | -1211.4412 | [13 empty] | 40098.106 | 59.989 | 3768.6335 | 335 | -354.8957 | 0 | 123.5 | 10 | 0 | -103 | 7581.51 | 8.8013
| 40098.106 | 59.989 | 3768.6335 |  |  |  | 8.8013 | 8.5379 |  | 0.58036 | 3779.1269 | 3762.7067 | 3781.5949 | 3769.8939 | 3724.0457 | 633 | [6 empty] | 0 | 633 | -1211.4412 | [13 empty] | 40098.106 | 59.989 | 3768.6335 | 335 | -354.8957 | 0 | 123.5 | 10 | 0 | -103 | 7581.51 | 8.8013
| 40098.106 | 59.989 | 3768.6335 |  |  |  | 8.8013 | 8.63 |  | 0.58036 | 3779.7995 | 3762.7435 | 3781.5837 | 3770.4743 | 3724.3358 | 633 | [6 empty] | 0 | 633 | -1211.4412 | [13 empty] | 40098.106 | 59.989 | 3768.6335 | 335 | -354.8957 | 0 | 123.5 | 10 | 0 | -103 | 7581.51 | 8.8013
| 40098.106 | 59.983 | 3772.4446 |  |  |  | 13.5986 | 10.3691 |  | 0.58036 | 3782.1188 | 3762.8034 | 3781.587 | 3771.0546 | 3724.626 | 633 | [6 empty] | 0 | 633 | -1086.7229 | [13 empty] | 40098.106 | 59.983 | 3772.4446 | 335 | -340.4694 | 0 | 124 | 10 | 0 | -103 | 7581.84 | 13.5986
| 40098.1061 | 59.983 | 3772.4446 |  |  |  | 13.5986 | 11.4994 |  | 0.58036 | 3783.8295 | 3762.8625 | 3781.6008 | 3771.635 | 3724.9162 | 633 | [6 empty] | 0 | 633 | -1086.7229 | [13 empty] | 40098.1061 | 59.983 | 3772.4446 | 335 | -340.4694 | 0 | 124 | 10 | 0 | -103 | 7581.84 | 13.5986
| 40098.1061 | 59.993 | 3775.8408 |  |  |  | 5.6 | 9.4346 |  | 0.58036 | 3782.3451 | 3762.9416 | 3781.6053 | 3772.2154 | 3725.2064 | 633 | [6 empty] | 0 | 633 | -1311.9117 | [13 empty] | 40098.1061 | 59.993 | 3775.8408 | 335 | -340.4694 | 0 | 124.5 | 10 | 0 | -103 | 7582.17 | 5.6
| 40098.1061 | 59.993 | 3775.8408 |  |  |  | 5.6 | 8.0925 |  | 0.58036 | 3781.5833 | 3763.0198 | 3781.6052 | 3772.7957 | 3725.4966 | 633 | [6 empty] | 0 | 633 | -1311.9117 | [13 empty] | 40098.1061 | 59.993 | 3775.8408 | 335 | -340.4694 | 0 | 124.5 | 10 | 0 | -103 | 7582.17 | 5.6
| 40098.1061 | 59.993 | 3775.8408 |  |  |  | 5.6 | 7.2201 |  | 0.58036 | 3781.2913 | 3763.097 | 3781.6033 | 3773.3761 | 3725.7867 | 633 | [6 empty] | 0 | 633 | -1311.9117 | [13 empty] | 40098.1061 | 59.993 | 3775.8408 | 335 | -340.4694 | 0 | 124.5 | 10 | 0 | -103 | 7582.17 | 5.6
| 40098.1062 | 59.999 | 3774.8662 |  |  |  | 0.79956 | 4.9729 |  | 0.58036 | 3779.6245 | 3763.1675 | 3781.5915 | 3773.9564 | 3726.0769 | 633 | [6 empty] | 0 | 633 | -1498.2362 | [13 empty] | 40098.1062 | 59.999 | 3774.8662 | 335 | -340.4694 | 0 | 125 | 10 | 0 | -103 | 7582.5 | 0.79956
| 40098.1062 | 59.999 | 3774.8662 |  |  |  | 0.79956 | 3.5122 |  | 0.58036 | 3778.7441 | 3763.2372 | 3781.5745 | 3774.5368 | 3726.3671 | 633 | [6 empty] | 0 | 633 | -1498.2362 | [13 empty] | 40098.1062 | 59.999 | 3774.8662 | 335 | -340.4694 | 0 | 125 | 10 | 0 | -103 | 7582.5 | 0.79956
| 40098.1062 | 59.999 | 3778.5537 |  |  |  | 0.79956 | 2.5628 |  | 0.58036 | 3778.3751 | 3763.3278 | 3781.5556 | 3775.1171 | 3726.6573 | 633 | [6 empty] | 0 | 633 | -1498.2362 | [13 empty] | 40098.1062 | 59.999 | 3778.5537 | 335 | -340.4694 | 0 | 125.5 | 10 | 0 | -103 | 7582.83 | 0.79956
| 40098.1062 | 59.999 | 3778.5537 |  |  |  | 0.79956 | 1.9457 |  | 0.58036 | 3778.3383 | 3763.4174 | 3781.5367 | 3775.6975 | 3726.9474 | 633 | [6 empty] | 0 | 633 | -1498.2362 | [13 empty] | 40098.1062 | 59.999 | 3778.5537 | 335 | -340.4694 | 0 | 125.5 | 10 | 0 | -103 | 7582.83 | 0.79956
| 40098.1062 | 59.999 | 3778.5537 |  |  |  | 0.79956 | 1.5445 |  | 0.58036 | 3778.5175 | 3763.5059 | 3781.519 | 3776.2779 | 3727.2376 | 633 | [6 empty] | 0 | 633 | -1498.2362 | [13 empty] | 40098.1062 | 59.999 | 3778.5537 | 335 | -340.4694 | 0 | 125.5 | 10 | 0 | -103 | 7582.83 | 0.79956
| 40098.1063 | 60.002 | 3781.2559 |  |  |  | -1.5991 | 0.44425 |  | 0 | 3777.4172 | 3763.6091 | 3781.4952 | 3776.2779 | 3727.5244 | 633 | [6 empty] | 0 | 633 | -1612.6843 | [13 empty] | 40098.1063 | 60.002 | 3781.2559 | 335 | -340.4694 | 0 | 126 | 10 | 0 | -103 | 7583.16 | -1.5991
| 40098.1063 | 60.002 | 3781.2559 |  |  |  | -1.5991 | -0.27093 |  | 0 | 3776.7021 | 3763.7111 | 3781.4674 | 3776.2779 | 3727.8079 | 633 | [6 empty] | 0 | 633 | -1612.6843 | [13 empty] | 40098.1063 | 60.002 | 3781.2559 | 335 | -340.4694 | 0 | 126 | 10 | 0 | -103 | 7583.16 | -1.5991
| 40098.1063 | 60.007 | 3783.8955 |  |  |  | -5.6 | -2.1361 |  | 0 | 3774.8369 | 3763.8271 | 3781.4293 | 3776.2779 | 3728.088 | 633 | [6 empty] | 0 | 633 | -1848.1612 | [13 empty] | 40098.1063 | 60.007 | 3783.8955 | 335 | -337.6429 | 0 | 126.5 | 10 | 0 | -103 | 7583.49 | -5.6
| 40098.1063 | 60.007 | 3783.8955 |  |  |  | -5.6 | -3.3485 |  | 0 | 3773.6245 | 3763.9417 | 3781.3847 | 3776.2779 | 3728.365 | 633 | [6 empty] | 0 | 633 | -1848.1612 | [13 empty] | 40098.1063 | 60.007 | 3783.8955 | 335 | -337.6429 | 0 | 126.5 | 10 | 0 | -103 | 7583.49 | -5.6
| 40098.1064 | 60.007 | 3783.8955 |  |  |  | -5.6 | -4.1365 |  | 0 | 3772.8365 | 3764.0551 | 3781.3362 | 3776.2779 | 3728.6388 | 633 | [6 empty] | 0 | 633 | -1848.1612 | [13 empty] | 40098.1064 | 60.007 | 3783.8955 | 335 | -337.6429 | 0 | 126.5 | 10 | 0 | -103 | 7583.49 | -5.6
| 40098.1064 | 60.014 | 3785.7681 |  |  |  | -11.2 | -6.6087 |  | 0 | 3770.3643 | 3764.1778 | 3781.2742 | 3776.2779 | 3728.9095 | 633 | [6 empty] | 0 | 633 | -2322.9111 | [13 empty] | 40098.1064 | 60.014 | 3785.7681 | 335 | -337.6429 | 0 | 127 | 10 | 0 | -103 | 7583.82 | -11.2
| 40098.1064 | 60.014 | 3785.7681 |  |  |  | -11.2 | -8.2156 |  | 0 | 3768.7573 | 3764.2991 | 3781.2039 | 3776.2779 | 3729.1771 | 633 | [6 empty] | 0 | 633 | -2322.9111 | [13 empty] | 40098.1064 | 60.014 | 3785.7681 | 335 | -337.6429 | 0 | 127 | 10 | 0 | -103 | 7583.82 | -11.2
| 40098.1064 | 60.019 | 3786.3042 |  |  |  | -15.2008 | -10.6604 |  | 0 | 3766.3125 | 3764.422 | 3781.1207 | 3776.2779 | 3729.4417 | 633 | [6 empty] | 0 | 633 | -2845.0433 | [13 empty] | 40098.1064 | 60.019 | 3786.3042 | 335 | -337.6429 | 0 | 127.5 | 10 | 0 | -103 | 7584.15 | -15.2008
| 40098.1065 | 60.019 | 3786.3042 |  |  |  | -15.2008 | -12.2496 |  | 0 | 3764.7234 | 3764.5436 | 3781.0296 | 3776.2779 | 3729.7033 | 633 | [6 empty] | 0 | 633 | -2845.0433 | [13 empty] | 40098.1065 | 60.019 | 3786.3042 | 335 | -337.6429 | 0 | 127.5 | 10 | 0 | -103 | 7584.15 | -15.2008
| 40098.1065 | 60.019 | 3786.3042 |  |  |  | -15.2008 | -13.2825 |  | 0 | 3763.6905 | 3764.6638 | 3780.9338 | 3776.2779 | 3729.9621 | 633 | [6 empty] | 0 | 633 | -2845.0433 | [13 empty] | 40098.1065 | 60.019 | 3786.3042 | 335 | -337.6429 | 0 | 127.5 | 10 | 0 | -103 | 7584.15 | -15.2008
| 40098.1065 | 60.017 | 3787.5159 |  |  |  | -13.5986 | -13.3931 |  | 0 | 3763.5798 | 3764.7894 | 3780.8384 | 3776.2779 | 3730.218 | 633 | [6 empty] | 0 | 633 | -2610.1007 | [13 empty] | 40098.1065 | 60.017 | 3787.5159 | 335 | -337.6429 | 0 | 128 | 10 | 0 | -103 | 7584.48 | -13.5986
| 40098.1065 | 60.017 | 3787.5159 |  |  |  | -13.5986 | -13.4651 |  | 0 | 3763.5079 | 3764.9136 | 3780.7437 | 3776.2779 | 3730.471 | 633 | [6 empty] | 0 | 633 | -2610.1007 | [13 empty] | 40098.1065 | 60.017 | 3787.5159 | 335 | -337.6429 | 0 | 128 | 10 | 0 | -103 | 7584.48 | -13.5986
| 40098.1066 | 60.023 | 3788.6067 |  |  |  | -18.399 | -15.192 |  | 0 | 3761.781 | 3765.0423 | 3780.6407 | 3776.2779 | 3730.7214 | 633 | [6 empty] | 0 | 633 | -3468.2235 | [13 empty] | 40098.1066 | 60.023 | 3788.6067 | 335 | -337.6429 | 0 | 128.5 | 10 | 0 | -103 | 7584.81 | -18.399
| 40098.1066 | 60.023 | 3788.6067 |  |  |  | -18.399 | -16.3144 |  | 0 | 3760.6585 | 3765.1697 | 3780.5327 | 3776.2779 | 3730.9689 | 633 | [6 empty] | 0 | 633 | -3468.2235 | [13 empty] | 40098.1066 | 60.023 | 3788.6067 | 335 | -337.6429 | 0 | 128.5 | 10 | 0 | -103 | 7584.81 | -18.399
| 40098.1066 | 60.023 | 3788.6067 |  |  |  | -18.399 | -17.0441 |  | 0 | 3759.9289 | 3765.2957 | 3780.4219 | 3776.2779 | 3731.2139 | 633 | [6 empty] | 0 | 633 | -3468.2235 | [13 empty] | 40098.1066 | 60.023 | 3788.6067 | 335 | -337.6429 | 0 | 128.5 | 10 | 0 | -103 | 7584.81 | -18.399
| 40098.1066 | 60.021 | 3787.5366 |  |  |  | -16.7999 | -16.9586 |  | 0 | 3760.0144 | 3765.4146 | 3780.3128 | 3776.2779 | 3731.4561 | 633 | [6 empty] | 0 | 633 | -3125.8765 | [13 empty] | 40098.1066 | 60.021 | 3787.5366 | 335 | -284.3608 | 0 | 129 | 10 | 0 | -103 | 7585.14 | -16.7999
| 40098.1066 | 60.021 | 3787.5366 |  |  |  | -16.7999 | -16.9031 |  | 0 | 3760.0699 | 3765.5323 | 3780.2051 | 3776.2779 | 3731.6958 | 633 | [6 empty] | 0 | 633 | -3125.8765 | [13 empty] | 40098.1066 | 60.021 | 3787.5366 | 335 | -284.3608 | 0 | 129 | 10 | 0 | -103 | 7585.14 | -16.7999
| 40098.1067 | 60.024 | 3787.9304 |  |  |  | -19.1986 | -17.7065 |  | 0 | 3759.2665 | 3765.6508 | 3780.0943 | 3776.2779 | 3731.933 | 633 | [6 empty] | 0 | 633 | -3669.1465 | [13 empty] | 40098.1067 | 60.024 | 3787.9304 | 335 | -284.3608 | 0 | 129.5 | 10 | 0 | -103 | 7585.47 | -19.1986
| 40098.1067 | 60.024 | 3787.9304 |  |  |  | -19.1986 | -18.2287 |  | 0 | 3758.7442 | 3765.7681 | 3779.9819 | 3776.2779 | 3732.1676 | 633 | [6 empty] | 0 | 633 | -3669.1465 | [13 empty] | 40098.1067 | 60.024 | 3787.9304 | 335 | -284.3608 | 0 | 129.5 | 10 | 0 | -103 | 7585.47 | -19.1986
| 40098.1067 | 60.024 | 3787.9304 |  |  |  | -19.1986 | -18.5682 |  | 0 | 3758.4048 | 3765.8841 | 3779.869 | 3776.2779 | 3732.3998 | 633 | [6 empty] | 0 | 633 | -3669.1465 | [13 empty] | 40098.1067 | 60.024 | 3787.9304 | 335 | -284.3608 | 0 | 129.5 | 10 | 0 | -103 | 7585.47 | -19.1986
| 40098.1067 | 60.02 | 3786.8748 |  |  |  | -16.0004 | -17.6695 |  | 0 | 3759.3035 | 3765.9934 | 3779.7618 | 3776.2779 | 3732.6295 | 633 | [6 empty] | 0 | 633 | -2978.8556 | [13 empty] | 40098.1067 | 60.02 | 3786.8748 | 350 | -284.3608 | 0 | 130 | 10 | 0 | -103 | 7585.8 | -16.0004
| 40098.1068 | 60.02 | 3786.8748 |  |  |  | -16.0004 | -17.0853 |  | 0 | 3759.8877 | 3766.1016 | 3779.6589 | 3776.2779 | 3732.8568 | 633 | [6 empty] | 0 | 633 | -2978.8556 | [13 empty] | 40098.1068 | 60.02 | 3786.8748 | 350 | -284.3608 | 0 | 130 | 10 | 0 | -103 | 7585.8 | -16.0004
| 40098.1068 | 60.024 | 3785.0181 |  |  |  | -19.1986 | -17.8249 |  | 0 | 3759.148 | 3766.1991 | 3779.5531 | 3776.2779 | 3733.0818 | 633 | [6 empty] | 0 | 633 | -3669.1465 | [13 empty] | 40098.1068 | 60.024 | 3785.0181 | 350 | -284.3608 | 0 | 130.5 | 10 | 0 | -103 | 7586.13 | -19.1986
| 40098.1068 | 60.024 | 3785.0181 |  |  |  | -19.1986 | -18.3057 |  | 0 | 3758.6673 | 3766.2957 | 3779.446 | 3776.2779 | 3733.3045 | 633 | [6 empty] | 0 | 633 | -3669.1465 | [13 empty] | 40098.1068 | 60.024 | 3785.0181 | 350 | -284.3608 | 0 | 130.5 | 10 | 0 | -103 | 7586.13 | -19.1986
| 40098.1068 | 60.024 | 3785.0181 |  |  |  | -19.1986 | -18.6182 |  | 0 | 3758.3547 | 3766.3912 | 3779.3384 | 3776.2779 | 3733.5248 | 633 | [6 empty] | 0 | 633 | -3669.1465 | [13 empty] | 40098.1068 | 60.024 | 3785.0181 | 350 | -284.3608 | 0 | 130.5 | 10 | 0 | -103 | 7586.13 | -19.1986
| 40098.1069 | 60.022 | 3785.9492 |  |  |  | -17.5995 | -18.2617 |  | 0 | 3758.7113 | 3766.4905 | 3779.2337 | 3776.2779 | 3733.743 | 633 | [6 empty] | 0 | 633 | -3288.1631 | [13 empty] | 40098.1069 | 60.022 | 3785.9492 | 350 | -284.3608 | 0 | 131 | 10 | 0 | -103 | 7586.46 | -17.5995
| 40098.1069 | 60.022 | 3785.9492 |  |  |  | -17.5995 | -18.0299 |  | 0 | 3758.9431 | 3766.5887 | 3779.1312 | 3776.2779 | 3733.9589 | 633 | [6 empty] | 0 | 633 | -3288.1631 | [13 empty] | 40098.1069 | 60.022 | 3785.9492 | 350 | -284.3608 | 0 | 131 | 10 | 0 | -103 | 7586.46 | -17.5995
| 40098.1069 | 60.022 | 3786.8772 |  |  |  | -17.5995 | -17.8793 |  | 0 | 3759.0937 | 3766.6907 | 3779.0306 | 3776.2779 | 3734.1726 | 633 | [6 empty] | 0 | 633 | -3288.1631 | [13 empty] | 40098.1069 | 60.022 | 3786.8772 | 350 | -260.468 | 0 | 131.5 | 10 | 0 | -103 | 7586.79 | -17.5995
| 40098.1069 | 60.022 | 3786.8772 |  |  |  | -17.5995 | -17.7813 |  | 0 | 3759.1916 | 3766.7916 | 3778.9314 | 3776.2779 | 3734.3842 | 633 | [6 empty] | 0 | 633 | -3288.1631 | [13 empty] | 40098.1069 | 60.022 | 3786.8772 | 350 | -260.468 | 0 | 131.5 | 10 | 0 | -103 | 7586.79 | -17.5995
| 40098.1069 | 60.022 | 3786.8772 |  |  |  | -17.5995 | -17.7177 |  | 0 | 3759.2553 | 3766.8915 | 3778.8335 | 3776.2779 | 3734.5937 | 633 | [6 empty] | 0 | 633 | -3288.1631 | [13 empty] | 40098.1069 | 60.022 | 3786.8772 | 350 | -260.468 | 0 | 131.5 | 10 | 0 | -103 | 7586.79 | -17.5995
| 40098.107 | 60.023 | 3785.7261 |  |  |  | -18.399 | -17.9562 |  | 0 | 3759.0168 | 3766.9848 | 3778.7354 | 3776.2779 | 3734.801 | 633 | [6 empty] | 0 | 633 | -3468.2235 | [13 empty] | 40098.107 | 60.023 | 3785.7261 | 350 | -260.468 | 0 | 132 | 10 | 0 | -103 | 7587.12 | -18.399
| 40098.107 | 60.023 | 3785.7261 |  |  |  | -18.399 | -18.1112 |  | 0 | 3758.8618 | 3767.0771 | 3778.6375 | 3776.2779 | 3735.0064 | 633 | [6 empty] | 0 | 633 | -3468.2235 | [13 empty] | 40098.107 | 60.023 | 3785.7261 | 350 | -260.468 | 0 | 132 | 10 | 0 | -103 | 7587.12 | -18.399
| 40098.107 | 60.022 | 3785.7983 |  |  |  | -17.5995 | -17.9321 |  | 0 | 3759.0409 | 3767.1689 | 3778.5414 | 3776.2779 | 3735.2097 | 633 | [6 empty] | 0 | 633 | -3288.1631 | [13 empty] | 40098.107 | 60.022 | 3785.7983 | 350 | -260.468 | 0 | 132.5 | 10 | 0 | -103 | 7587.45 | -17.5995
| 40098.107 | 60.022 | 3785.7983 |  |  |  | -17.5995 | -17.8157 |  | 0 | 3759.1573 | 3767.2598 | 3778.4468 | 3776.2779 | 3735.411 | 633 | [6 empty] | 0 | 633 | -3288.1631 | [13 empty] | 40098.107 | 60.022 | 3785.7983 | 350 | -260.468 | 0 | 132.5 | 10 | 0 | -103 | 7587.45 | -17.5995
| 40098.1071 | 60.022 | 3785.7983 |  |  |  | -17.5995 | -17.74 |  | 0 | 3759.233 | 3767.3497 | 3778.3536 | 3776.2779 | 3735.6103 | 633 | [6 empty] | 0 | 633 | -3288.1631 | [13 empty] | 40098.1071 | 60.022 | 3785.7983 | 350 | -260.468 | 0 | 132.5 | 10 | 0 | -103 | 7587.45 | -17.5995
| 40098.1071 | 60.018 | 3786.9392 |  |  |  | -14.4012 | -16.5714 |  | 0 | 3760.4015 | 3767.4444 | 3778.2668 | 3776.2779 | 3735.8078 | 633 | [6 empty] | 0 | 633 | -2722.7361 | [13 empty] | 40098.1071 | 60.018 | 3786.9392 | 350 | -260.468 | 0 | 133 | 10 | 0 | -103 | 7587.78 | -14.4012
| 40098.1071 | 60.018 | 3786.9392 |  |  |  | -14.4012 | -15.8119 |  | 0 | 3761.1611 | 3767.5381 | 3778.1846 | 3776.2779 | 3736.0033 | 633 | [6 empty] | 0 | 633 | -2722.7361 | [13 empty] | 40098.1071 | 60.018 | 3786.9392 | 350 | -260.468 | 0 | 133 | 10 | 0 | -103 | 7587.78 | -14.4012
| 40098.1071 | 60.018 | 3789.6733 |  |  |  | -14.4012 | -15.3182 |  | 0 | 3761.6548 | 3767.644 | 3778.1055 | 3776.2779 | 3736.1969 | 633 | [6 empty] | 0 | 633 | -2722.7361 | [13 empty] | 40098.1071 | 60.018 | 3789.6733 | 350 | -260.468 | 0 | 133.5 | 10 | 0 | -103 | 7588.11 | -14.4012
| 40098.1072 | 60.018 | 3789.6733 |  |  |  | -14.4012 | -14.9972 |  | 0 | 3761.9757 | 3767.7489 | 3778.0287 | 3776.2779 | 3736.3887 | 633 | [6 empty] | 0 | 633 | -2722.7361 | [13 empty] | 40098.1072 | 60.018 | 3789.6733 | 350 | -260.468 | 0 | 133.5 | 10 | 0 | -103 | 7588.11 | -14.4012
| 40098.1072 | 60.018 | 3789.6733 |  |  |  | -14.4012 | -14.7886 |  | 0 | 3762.1843 | 3767.8528 | 3777.9536 | 3776.2779 | 3736.5786 | 633 | [6 empty] | 0 | 633 | -2722.7361 | [13 empty] | 40098.1072 | 60.018 | 3789.6733 | 350 | -260.468 | 0 | 133.5 | 10 | 0 | -103 | 7588.11 | -14.4012
| 40098.1072 | 60.016 | 3788.4788 |  |  |  | -12.7991 | -14.0923 |  | 0 | 3762.8807 | 3767.9501 | 3777.8825 | 3776.2779 | 3736.7668 | 633 | [6 empty] | 0 | 633 | -2506.7928 | [13 empty] | 40098.1072 | 60.016 | 3788.4788 | 350 | -253.1415 | 0 | 134 | 10 | 0 | -103 | 7588.44 | -12.7991
| 40098.1072 | 60.016 | 3788.4788 |  |  |  | -12.7991 | -13.6397 |  | 0 | 3763.3333 | 3768.0465 | 3777.8142 | 3776.2779 | 3736.9531 | 633 | [6 empty] | 0 | 633 | -2506.7928 | [13 empty] | 40098.1072 | 60.016 | 3788.4788 | 350 | -253.1415 | 0 | 134 | 10 | 0 | -103 | 7588.44 | -12.7991
| 40098.1072 | 60.016 | 3789.0049 |  |  |  | -12.7991 | -13.3455 |  | 0 | 3763.6275 | 3768.1444 | 3777.7479 | 3776.2779 | 3737.1378 | 633 | [6 empty] | 0 | 633 | -2506.7928 | [13 empty] | 40098.1072 | 60.016 | 3789.0049 | 350 | -253.1415 | 0 | 134.5 | 10 | 0 | -103 | 7588.77 | -12.7991
| 40098.1073 | 60.016 | 3789.0049 |  |  |  | -12.7991 | -13.1542 |  | 0 | 3763.8188 | 3768.2415 | 3777.6831 | 3776.2779 | 3737.3207 | 633 | [6 empty] | 0 | 633 | -2506.7928 | [13 empty] | 40098.1073 | 60.016 | 3789.0049 | 350 | -253.1415 | 0 | 134.5 | 10 | 0 | -103 | 7588.77 | -12.7991
| 40098.1073 | 60.016 | 3789.0049 |  |  |  | -12.7991 | -13.0299 |  | 0 | 3763.9431 | 3768.3376 | 3777.6195 | 3776.2779 | 3737.5019 | 633 | [6 empty] | 0 | 633 | -2506.7928 | [13 empty] | 40098.1073 | 60.016 | 3789.0049 | 350 | -253.1415 | 0 | 134.5 | 10 | 0 | -103 | 7588.77 | -12.7991
| 40098.1073 | 60.012 | 3788.9329 |  |  |  | -9.6008 | -11.8297 |  | 0 | 3765.1432 | 3768.4325 | 3777.562 | 3776.2779 | 3737.6814 | 633 | [6 empty] | 0 | 633 | -2164.1624 | [13 empty] | 40098.1073 | 60.012 | 3788.9329 | 350 | -253.1415 | 0 | 135 | 10 | 0 | -103 | 7589.1 | -9.6008
| 40098.1073 | 60.012 | 3788.9329 |  |  |  | -9.6008 | -11.0496 |  | 0 | 3765.9234 | 3768.5265 | 3777.5086 | 3776.2779 | 3737.8592 | 633 | [6 empty] | 0 | 633 | -2164.1624 | [13 empty] | 40098.1073 | 60.012 | 3788.9329 | 350 | -253.1415 | 0 | 135 | 10 | 0 | -103 | 7589.1 | -9.6008
| 40098.1074 | 60.01 | 3790.4111 |  |  |  | -7.9987 | -9.9818 |  | 0 | 3766.9912 | 3768.6265 | 3777.4606 | 3776.2779 | 3738.0355 | 633 | [6 empty] | 0 | 633 | -2025.4764 | [13 empty] | 40098.1074 | 60.01 | 3790.4111 | 350 | -253.1415 | 0 | 135.5 | 10 | 0 | -103 | 7589.43 | -7.9987
| 40098.1074 | 60.01 | 3790.4111 |  |  |  | -7.9987 | -9.2877 |  | 0 | 3767.6853 | 3768.7255 | 3777.4162 | 3776.2779 | 3738.2101 | 633 | [6 empty] | 0 | 633 | -2025.4764 | [13 empty] | 40098.1074 | 60.01 | 3790.4111 | 350 | -253.1415 | 0 | 135.5 | 10 | 0 | -103 | 7589.43 | -7.9987
| 40098.1074 | 60.01 | 3790.4111 |  |  |  | -7.9987 | -8.8365 |  | 0 | 3768.1365 | 3768.8236 | 3777.3742 | 3776.2779 | 3738.3831 | 633 | [6 empty] | 0 | 633 | -2025.4764 | [13 empty] | 40098.1074 | 60.01 | 3790.4111 | 350 | -253.1415 | 0 | 135.5 | 10 | 0 | -103 | 7589.43 | -7.9987
| 40098.1074 | 60.009 | 3791.5398 |  |  |  | -7.1991 | -8.2634 |  | 0 | 3768.7096 | 3768.9259 | 3777.3352 | 3776.2779 | 3738.5546 | 633 | [6 empty] | 0 | 633 | -1962.708 | [13 empty] | 40098.1074 | 60.009 | 3791.5398 | 350 | -253.1415 | 0 | 136 | 10 | 0 | -103 | 7589.76 | -7.1991
| 40098.1075 | 60.009 | 3791.5398 |  |  |  | -7.1991 | -7.8909 |  | 0 | 3769.0821 | 3769.0273 | 3777.2982 | 3776.2779 | 3738.7245 | 633 | [6 empty] | 0 | 633 | -1962.708 | [13 empty] | 40098.1075 | 60.009 | 3791.5398 | 350 | -253.1415 | 0 | 136 | 10 | 0 | -103 | 7589.76 | -7.1991
| 40098.1075 | 60.01 | 3791.4431 |  |  |  | -7.9987 | -7.9286 |  | 0 | 3769.0444 | 3769.1274 | 3777.2613 | 3776.2779 | 3738.8929 | 633 | [6 empty] | 0 | 633 | -2025.4764 | [13 empty] | 40098.1075 | 60.01 | 3791.4431 | 350 | -251.9299 | 0 | 136.5 | 10 | 0 | -103 | 7590.09 | -7.9987
| 40098.1075 | 60.01 | 3791.4431 |  |  |  | -7.9987 | -7.9531 |  | 0 | 3769.0198 | 3769.2266 | 3777.2247 | 3776.2779 | 3739.0598 | 633 | [6 empty] | 0 | 633 | -2025.4764 | [13 empty] | 40098.1075 | 60.01 | 3791.4431 | 350 | -251.9299 | 0 | 136.5 | 10 | 0 | -103 | 7590.09 | -7.9987
| 40098.1075 | 60.01 | 3791.4431 |  |  |  | -7.9987 | -7.9691 |  | 0 | 3769.0039 | 3769.3249 | 3777.1883 | 3776.2779 | 3739.2252 | 633 | [6 empty] | 0 | 633 | -2025.4764 | [13 empty] | 40098.1075 | 60.01 | 3791.4431 | 350 | -251.9299 | 0 | 136.5 | 10 | 0 | -103 | 7590.09 | -7.9987
| 40098.1075 | 59.995 | 3790.603 |  |  |  | 4.0009 | -3.7796 |  | 0 | 3773.1934 | 3769.4186 | 3777.1707 | 3776.2779 | 3739.3892 | 633 | [6 empty] | 0 | 633 | -1368.6103 | [13 empty] | 40098.1075 | 59.995 | 3790.603 | 350 | -251.9299 | 0 | 137 | 10 | 0 | -103 | 7590.42 | 4.0009
| 40098.1076 | 59.995 | 3790.603 |  |  |  | 4.0009 | -1.0564 |  | 0 | 3775.9165 | 3769.5115 | 3777.1652 | 3776.2779 | 3739.5517 | 633 | [6 empty] | 0 | 633 | -1368.6103 | [13 empty] | 40098.1076 | 59.995 | 3790.603 | 350 | -251.9299 | 0 | 137 | 10 | 0 | -103 | 7590.42 | 4.0009
| 40098.1076 | 59.991 | 3789.585 |  |  |  | 7.1991 | 1.833 |  | 0 | 3778.806 | 3769.5992 | 3777.1724 | 3776.2779 | 3739.7128 | 633 | [6 empty] | 0 | 633 | -1259.7241 | [13 empty] | 40098.1076 | 59.991 | 3789.585 | 350 | -251.9299 | 0 | 137.5 | 10 | 0 | -103 | 7590.75 | 7.1991
| 40098.1076 | 59.991 | 3789.585 |  |  |  | 7.1991 | 3.7111 |  | 0 | 3780.6841 | 3769.6861 | 3777.1876 | 3776.2779 | 3739.8724 | 633 | [6 empty] | 0 | 633 | -1259.7241 | [13 empty] | 40098.1076 | 59.991 | 3789.585 | 350 | -251.9299 | 0 | 137.5 | 10 | 0 | -103 | 7590.75 | 7.1991
| 40098.1076 | 59.991 | 3789.585 |  |  |  | 7.1991 | 4.9319 |  | 0 | 3781.9049 | 3769.7722 | 3777.2081 | 3776.2779 | 3740.0307 | 633 | [6 empty] | 0 | 633 | -1259.7241 | [13 empty] | 40098.1076 | 59.991 | 3789.585 | 350 | -251.9299 | 0 | 137.5 | 10 | 0 | -103 | 7590.75 | 7.1991
| 40098.1077 | 59.988 | 3788.105 |  |  |  | 9.6008 | 6.566 |  | 0 | 3783.539 | 3769.8513 | 3777.2353 | 3776.2779 | 3740.1876 | 633 | [6 empty] | 0 | 633 | -1188.7041 | [13 empty] | 40098.1077 | 59.988 | 3788.105 | 350 | -251.9299 | 0 | 138 | 10 | 0 | -103 | 7591.08 | 9.6008
| 40098.1077 | 59.988 | 3788.105 |  |  |  | 9.6008 | 7.6282 |  | 0 | 3784.6012 | 3769.9296 | 3777.267 | 3776.2779 | 3740.3432 | 633 | [6 empty] | 0 | 633 | -1188.7041 | [13 empty] | 40098.1077 | 59.988 | 3788.105 | 350 | -251.9299 | 0 | 138 | 10 | 0 | -103 | 7591.08 | 9.6008
| 40098.1077 | 59.985 | 3788.4973 |  |  |  | 11.9995 | 9.1582 |  | 0 | 3786.1311 | 3770.009 | 3777.3048 | 3776.2779 | 3740.4974 | 633 | [6 empty] | 0 | 633 | -1125.341 | [13 empty] | 40098.1077 | 59.985 | 3788.4973 | 350 | -251.9299 | 0 | 138.5 | 10 | 0 | -103 | 7591.41 | 11.9995
| 40098.1077 | 59.985 | 3788.4973 |  |  |  | 11.9995 | 10.1526 |  | 0 | 3787.1256 | 3770.0876 | 3777.3466 | 3776.2779 | 3740.6503 | 633 | [6 empty] | 0 | 633 | -1125.341 | [13 empty] | 40098.1077 | 59.985 | 3788.4973 | 350 | -251.9299 | 0 | 138.5 | 10 | 0 | -103 | 7591.41 | 11.9995
| 40098.1078 | 59.985 | 3788.4973 |  |  |  | 11.9995 | 10.799 |  | 0 | 3787.772 | 3770.1656 | 3777.3908 | 3776.2779 | 3740.8019 | 633 | [6 empty] | 0 | 633 | -1125.341 | [13 empty] | 40098.1078 | 59.985 | 3788.4973 | 350 | -251.9299 | 0 | 138.5 | 10 | 0 | -103 | 7591.41 | 11.9995
| 40098.1078 | 59.984 | 3788.5708 |  |  |  | 12.7991 | 11.4991 |  | 0 | 3788.472 | 3770.2433 | 3777.4376 | 3776.2779 | 3740.9523 | 633 | [6 empty] | 0 | 633 | -1105.6948 | [13 empty] | 40098.1078 | 59.984 | 3788.5708 | 350 | -250.6742 | 0 | 139 | 10 | 0 | -103 | 7591.74 | 12.7991
| 40098.1078 | 59.984 | 3788.5708 |  |  |  | 12.7991 | 11.9541 |  | 0 | 3788.927 | 3770.3203 | 3777.4858 | 3776.2779 | 3741.1013 | 633 | [6 empty] | 0 | 633 | -1105.6948 | [13 empty] | 40098.1078 | 59.984 | 3788.5708 | 350 | -250.6742 | 0 | 139 | 10 | 0 | -103 | 7591.74 | 12.7991
| 40098.1078 | 59.981 | 3786.4529 |  |  |  | 15.2008 | 13.0904 |  | 0 | 3790.0634 | 3770.3878 | 3777.5385 | 3776.2779 | 3741.2491 | 633 | [6 empty] | 0 | 633 | -1050.6009 | [13 empty] | 40098.1078 | 59.981 | 3786.4529 | 350 | -250.6742 | 0 | 139.5 | 10 | 0 | -103 | 7592.07 | 15.2008
| 40098.1078 | 59.981 | 3786.4529 |  |  |  | 15.2008 | 13.8291 |  | 0 | 3790.802 | 3770.4547 | 3777.5937 | 3776.2779 | 3741.3957 | 633 | [6 empty] | 0 | 633 | -1050.6009 | [13 empty] | 40098.1078 | 59.981 | 3786.4529 | 350 | -250.6742 | 0 | 139.5 | 10 | 0 | -103 | 7592.07 | 15.2008
| 40098.1079 | 59.981 | 3786.4529 |  |  |  | 15.2008 | 14.3092 |  | 0 | 3791.2821 | 3770.5211 | 3777.6505 | 3776.2779 | 3741.541 | 633 | [6 empty] | 0 | 633 | -1050.6009 | [13 empty] | 40098.1079 | 59.981 | 3786.4529 | 350 | -250.6742 | 0 | 139.5 | 10 | 0 | -103 | 7592.07 | 15.2008
| 40098.1079 | 59.977 | 3788.8135 |  |  |  | 18.399 | 15.7406 |  | 0 | 3792.7136 | 3770.5967 | 3777.7128 | 3776.2779 | 3741.6852 | 633 | [6 empty] | 0 | 633 | -985.2287 | [13 empty] | 40098.1079 | 59.977 | 3788.8135 | 350 | -250.6742 | 0 | 140 | 10 | 0 | -103 | 7592.4 | 18.399
| 40098.1079 | 59.977 | 3788.8135 |  |  |  | 18.399 | 16.6711 |  | 0 | 3793.6441 | 3770.6717 | 3777.7783 | 3776.2779 | 3741.8281 | 633 | [6 empty] | 0 | 633 | -985.2287 | [13 empty] | 40098.1079 | 59.977 | 3788.8135 | 350 | -250.6742 | 0 | 140 | 10 | 0 | -103 | 7592.4 | 18.399
| 40098.1079 | 59.976 | 3788.4097 |  |  |  | 19.1986 | 17.5557 |  | 0 | 3794.5287 | 3770.7444 | 3777.847 | 3776.2779 | 3741.9699 | 633 | [6 empty] | 0 | 633 | -970.1374 | [13 empty] | 40098.1079 | 59.976 | 3788.4097 | 350 | -250.6742 | 0 | 140.5 | 10 | 0 | -103 | 7592.73 | 19.1986
| 40098.108 | 59.976 | 3788.4097 |  |  |  | 19.1986 | 18.1307 |  | 0 | 3795.1037 | 3770.8165 | 3777.9174 | 3776.2779 | 3742.1105 | 633 | [6 empty] | 0 | 633 | -970.1374 | [13 empty] | 40098.108 | 59.976 | 3788.4097 | 350 | -250.6742 | 0 | 140.5 | 10 | 0 | -103 | 7592.73 | 19.1986
| 40098.108 | 59.976 | 3788.4097 |  |  |  | 19.1986 | 18.5045 |  | 0 | 3795.4775 | 3770.888 | 3777.9888 | 3776.2779 | 3742.2499 | 633 | [6 empty] | 0 | 633 | -970.1374 | [13 empty] | 40098.108 | 59.976 | 3788.4097 | 350 | -250.6742 | 0 | 140.5 | 10 | 0 | -103 | 7592.73 | 19.1986
| 40098.108 | 59.978 | 3790.6646 |  |  |  | 17.5995 | 18.1877 |  | 0 | 3795.1607 | 3770.9681 | 3778.0583 | 3776.2779 | 3742.3883 | 633 | [6 empty] | 0 | 633 | -1000.797 | [13 empty] | 40098.108 | 59.978 | 3790.6646 | 350 | -250.6742 | 0 | 141 | 10 | 0 | -103 | 7593.06 | 17.5995
| 40098.108 | 59.978 | 3790.6646 |  |  |  | 17.5995 | 17.9818 |  | 0 | 3794.9548 | 3771.0475 | 3778.1265 | 3776.2779 | 3742.5255 | 633 | [6 empty] | 0 | 633 | -1000.797 | [13 empty] | 40098.108 | 59.978 | 3790.6646 | 350 | -250.6742 | 0 | 141 | 10 | 0 | -103 | 7593.06 | 17.5995
| 40098.1081 | 59.974 | 3789.2671 |  |  |  | 20.8008 | 18.9685 |  | 0 | 3795.9415 | 3771.1206 | 3778.198 | 3776.2779 | 3742.6616 | 633 | [6 empty] | 0 | 633 | -941.2471 | [13 empty] | 40098.1081 | 59.974 | 3789.2671 | 350 | -253.6319 | 0 | 141.5 | 10 | 0 | -103 | 7593.39 | 20.8008
| 40098.1081 | 59.974 | 3789.2671 |  |  |  | 20.8008 | 19.6098 |  | 0 | 3796.5828 | 3771.1932 | 3778.2715 | 3776.2779 | 3742.7966 | 633 | [6 empty] | 0 | 633 | -941.2471 | [13 empty] | 40098.1081 | 59.974 | 3789.2671 | 350 | -253.6319 | 0 | 141.5 | 10 | 0 | -103 | 7593.39 | 20.8008
| 40098.1081 | 59.974 | 3789.2671 |  |  |  | 20.8008 | 20.0266 |  | 0 | 3796.9996 | 3771.2652 | 3778.3462 | 3776.2779 | 3742.9305 | 633 | [6 empty] | 0 | 633 | -941.2471 | [13 empty] | 40098.1081 | 59.974 | 3789.2671 | 350 | -253.6319 | 0 | 141.5 | 10 | 0 | -103 | 7593.39 | 20.8008
| 40098.1081 | 59.977 | 3790.4304 |  |  |  | 18.399 | 19.457 |  | 0 | 3796.43 | 3771.3413 | 3778.4179 | 3776.2779 | 3743.0634 | 633 | [6 empty] | 0 | 633 | -985.2287 | [13 empty] | 40098.1081 | 59.977 | 3790.4304 | 350 | -253.6319 | 0 | 142 | 10 | 0 | -103 | 7593.72 | 18.399
| 40098.1081 | 59.977 | 3790.4304 |  |  |  | 18.399 | 19.0867 |  | 0 | 3796.0597 | 3771.4167 | 3778.4876 | 3776.2779 | 3743.1952 | 633 | [6 empty] | 0 | 633 | -985.2287 | [13 empty] | 40098.1081 | 59.977 | 3790.4304 | 350 | -253.6319 | 0 | 142 | 10 | 0 | -103 | 7593.72 | 18.399
| 40098.1082 | 59.973 | 3787.4421 |  |  |  | 21.6003 | 19.9665 |  | 0 | 3796.9395 | 3771.4798 | 3778.5603 | 3776.2779 | 3743.3259 | 633 | [6 empty] | 0 | 633 | -927.4636 | [13 empty] | 40098.1082 | 59.973 | 3787.4421 | 350 | -253.6319 | 0 | 142.5 | 10 | 0 | -103 | 7594.05 | 21.6003
| 40098.1082 | 59.973 | 3787.4421 |  |  |  | 21.6003 | 20.5383 |  | 0 | 3797.5113 | 3771.5424 | 3778.6346 | 3776.2779 | 3743.4557 | 633 | [6 empty] | 0 | 633 | -927.4636 | [13 empty] | 40098.1082 | 59.973 | 3787.4421 | 350 | -253.6319 | 0 | 142.5 | 10 | 0 | -103 | 7594.05 | 21.6003
| 40098.1082 | 59.973 | 3787.4421 |  |  |  | 21.6003 | 20.91 |  | 0 | 3797.883 | 3771.6045 | 3778.7098 | 3776.2779 | 3743.5844 | 633 | [6 empty] | 0 | 633 | -927.4636 | [13 empty] | 40098.1082 | 59.973 | 3787.4421 | 350 | -253.6319 | 0 | 142.5 | 10 | 0 | -103 | 7594.05 | 21.6003
| 40098.1082 | 59.971 | 3790.6016 |  |  |  | 23.1995 | 21.7113 |  | 0 | 3798.6843 | 3771.6785 | 3778.7875 | 3776.2779 | 3743.7121 | 633 | [6 empty] | 0 | 633 | -901.0733 | [13 empty] | 40098.1082 | 59.971 | 3790.6016 | 350 | -253.6319 | 0 | 143 | 10 | 0 | -103 | 7594.38 | 23.1995
| 40098.1083 | 59.971 | 3790.6016 |  |  |  | 23.1995 | 22.2322 |  | 0 | 3799.2052 | 3771.7518 | 3778.8667 | 3776.2779 | 3743.8388 | 633 | [6 empty] | 0 | 633 | -901.0733 | [13 empty] | 40098.1083 | 59.971 | 3790.6016 | 350 | -253.6319 | 0 | 143 | 10 | 0 | -103 | 7594.38 | 23.1995
| 40098.1083 | 59.978 | 3792.3113 |  |  |  | 17.5995 | 20.6107 |  | 0 | 3797.5837 | 3771.8312 | 3778.9389 | 3776.2779 | 3743.9645 | 633 | [6 empty] | 0 | 633 | -1000.797 | [13 empty] | 40098.1083 | 59.978 | 3792.3113 | 350 | -253.6319 | 0 | 143.5 | 10 | 0 | -103 | 7594.71 | 17.5995
| 40098.1083 | 59.978 | 3792.3113 |  |  |  | 17.5995 | 19.5568 |  | 0 | 3796.5298 | 3771.91 | 3779.0066 | 3776.2779 | 3744.0893 | 633 | [6 empty] | 0 | 633 | -1000.797 | [13 empty] | 40098.1083 | 59.978 | 3792.3113 | 350 | -253.6319 | 0 | 143.5 | 10 | 0 | -103 | 7594.71 | 17.5995
| 40098.1083 | 59.978 | 3792.3113 |  |  |  | 17.5995 | 18.8717 |  | 0 | 3795.8447 | 3771.9881 | 3779.0711 | 3776.2779 | 3744.2131 | 633 | [6 empty] | 0 | 633 | -1000.797 | [13 empty] | 40098.1083 | 59.978 | 3792.3113 | 350 | -253.6319 | 0 | 143.5 | 10 | 0 | -103 | 7594.71 | 17.5995
| 40098.1084 | 59.975 | 3788.0796 |  |  |  | 20.0012 | 19.2671 |  | 0 | 3796.24 | 3772.0495 | 3779.1366 | 3776.2779 | 3744.3359 | 633 | [6 empty] | 0 | 633 | -955.4464 | [13 empty] | 40098.1084 | 59.975 | 3788.0796 | 350 | -246.9573 | 0 | 144 | 10 | 15 | -103 | 7595.04 | 20.0012
| 40098.1084 | 59.975 | 3788.0796 |  |  |  | 20.0012 | 19.524 |  | 0 | 3796.497 | 3772.1105 | 3779.2026 | 3776.2779 | 3744.4579 | 633 | [6 empty] | 0 | 633 | -955.4464 | [13 empty] | 40098.1084 | 59.975 | 3788.0796 | 350 | -246.9573 | 0 | 144 | 10 | 15 | -103 | 7595.04 | 20.0012
| 40098.1084 | 59.976 | 3787.1643 |  |  |  | 19.1986 | 19.4101 |  | 0 | 3796.3831 | 3772.1675 | 3779.2677 | 3776.2779 | 3744.5788 | 633 | [6 empty] | 0 | 633 | -970.1374 | [13 empty] | 40098.1084 | 59.976 | 3787.1643 | 350 | -246.9573 | 0 | 144.5 | 10 | 15 | -103 | 7595.37 | 19.1986
| 40098.1084 | 59.976 | 3787.1643 |  |  |  | 19.1986 | 19.3361 |  | 0 | 3796.3091 | 3772.2241 | 3779.332 | 3776.2779 | 3744.6989 | 633 | [6 empty] | 0 | 633 | -970.1374 | [13 empty] | 40098.1084 | 59.976 | 3787.1643 | 350 | -246.9573 | 0 | 144.5 | 10 | 15 | -103 | 7595.37 | 19.1986
| 40098.1084 | 59.976 | 3787.1643 |  |  |  | 19.1986 | 19.288 |  | 0 | 3796.261 | 3772.2803 | 3779.3957 | 3776.2779 | 3744.8181 | 633 | [6 empty] | 0 | 633 | -970.1374 | [13 empty] | 40098.1084 | 59.976 | 3787.1643 | 350 | -246.9573 | 0 | 144.5 | 10 | 15 | -103 | 7595.37 | 19.1986
| 40098.1085 | 59.969 | 3787.4048 |  |  |  | 24.7986 | 21.2167 |  | 0 | 3798.1897 | 3772.3369 | 3779.466 | 3776.2779 | 3744.9364 | 633 | [6 empty] | 0 | 633 | -876.1433 | [13 empty] | 40098.1085 | 59.969 | 3787.4048 | 350 | -246.9573 | 0 | 145 | 10 | 15 | -103 | 7595.7 | 24.7986
| 40098.1085 | 59.969 | 3787.4048 |  |  |  | 24.7986 | 22.4704 |  | 0 | 3799.4433 | 3772.3931 | 3779.5406 | 3776.2779 | 3745.0537 | 633 | [6 empty] | 0 | 633 | -876.1433 | [13 empty] | 40098.1085 | 59.969 | 3787.4048 | 350 | -246.9573 | 0 | 145 | 10 | 15 | -103 | 7595.7 | 24.7986
| 40098.1085 | 59.965 | 3789.2139 |  |  |  | 27.9999 | 24.4057 |  | 0 | 3801.3787 | 3772.4557 | 3779.6218 | 3776.2779 | 3745.1702 | 633 | [6 empty] | 0 | 633 | -830.1631 | [13 empty] | 40098.1085 | 59.965 | 3789.2139 | 350 | -246.9573 | 0 | 145.5 | 10 | 15 | -103 | 7596.03 | 27.9999
| 40098.1085 | 59.965 | 3789.2139 |  |  |  | 27.9999 | 25.6637 |  | 0 | 3802.6366 | 3772.5177 | 3779.707 | 3776.2779 | 3745.2859 | 633 | [6 empty] | 0 | 633 | -830.1631 | [13 empty] | 40098.1085 | 59.965 | 3789.2139 | 350 | -246.9573 | 0 | 145.5 | 10 | 15 | -103 | 7596.03 | 27.9999
| 40098.1086 | 59.965 | 3789.2139 |  |  |  | 27.9999 | 26.4813 |  | 0 | 3803.4543 | 3772.5793 | 3779.7946 | 3776.2779 | 3745.4007 | 633 | [6 empty] | 0 | 633 | -830.1631 | [13 empty] | 40098.1086 | 59.965 | 3789.2139 | 350 | -246.9573 | 0 | 145.5 | 10 | 15 | -103 | 7596.03 | 27.9999
| 40098.1086 | 59.97 | 3791.2212 |  |  |  | 23.999 | 25.6125 |  | 0 | 3802.5855 | 3772.6479 | 3779.8784 | 3776.2779 | 3745.5146 | 633 | [6 empty] | 0 | 633 | -888.4334 | [13 empty] | 40098.1086 | 59.97 | 3791.2212 | 350 | -246.9573 | 0 | 146 | 10 | 15 | -103 | 7596.36 | 23.999
| 40098.1086 | 59.97 | 3791.2212 |  |  |  | 23.999 | 25.0478 |  | 0 | 3802.0208 | 3772.7159 | 3779.9595 | 3776.2779 | 3745.6277 | 633 | [6 empty] | 0 | 633 | -888.4334 | [13 empty] | 40098.1086 | 59.97 | 3791.2212 | 350 | -246.9573 | 0 | 146 | 10 | 15 | -103 | 7596.36 | 23.999
| 40098.1086 | 59.965 | 3788.8242 |  |  |  | 27.9999 | 26.081 |  | 0 | 3803.054 | 3772.7747 | 3780.0438 | 3776.2779 | 3745.74 | 633 | [6 empty] | 0 | 633 | -830.1631 | [13 empty] | 40098.1086 | 59.965 | 3788.8242 | 350 | -254.5418 | 0 | 146.5 | 10 | 15 | -103 | 7596.69 | 27.9999
| 40098.1087 | 59.965 | 3788.8242 |  |  |  | 27.9999 | 26.7526 |  | 0 | 3803.7256 | 3772.8331 | 3780.1299 | 3776.2779 | 3745.8514 | 633 | [6 empty] | 0 | 633 | -830.1631 | [13 empty] | 40098.1087 | 59.965 | 3788.8242 | 350 | -254.5418 | 0 | 146.5 | 10 | 15 | -103 | 7596.69 | 27.9999
| 40098.1087 | 59.965 | 3788.8242 |  |  |  | 27.9999 | 27.1892 |  | 0 | 3804.1621 | 3772.891 | 3780.217 | 3776.2779 | 3745.9621 | 633 | [6 empty] | 0 | 633 | -830.1631 | [13 empty] | 40098.1087 | 59.965 | 3788.8242 | 350 | -254.5418 | 0 | 146.5 | 10 | 15 | -103 | 7596.69 | 27.9999
| 40098.1087 | 59.972 | 3789.1675 |  |  |  | 22.3999 | 25.5129 |  | 0 | 3802.4859 | 3772.9498 | 3780.2974 | 3776.2779 | 3746.0719 | 633 | [6 empty] | 0 | 633 | -914.078 | [13 empty] | 40098.1087 | 59.972 | 3789.1675 | 350 | -254.5418 | 0 | 147 | 10 | 15 | -103 | 7597.02 | 22.3999
| 40098.1087 | 59.972 | 3789.1675 |  |  |  | 22.3999 | 24.4234 |  | 0 | 3801.3963 | 3773.0081 | 3780.3733 | 3776.2779 | 3746.181 | 633 | [6 empty] | 0 | 633 | -914.078 | [13 empty] | 40098.1087 | 59.972 | 3789.1675 | 350 | -254.5418 | 0 | 147 | 10 | 15 | -103 | 7597.02 | 22.3999
| 40098.1087 | 59.967 | 3784.8306 |  |  |  | 26.4008 | 25.1155 |  | 0 | 3802.0884 | 3773.0505 | 3780.4511 | 3776.2779 | 3746.2892 | 633 | [6 empty] | 0 | 633 | -852.5118 | [13 empty] | 40098.1087 | 59.967 | 3784.8306 | 350 | -254.5418 | 0 | 147.5 | 10 | 15 | -103 | 7597.35 | 26.4008
| 40098.1088 | 59.967 | 3784.8306 |  |  |  | 26.4008 | 25.5653 |  | 0 | 3802.5383 | 3773.0926 | 3780.53 | 3776.2779 | 3746.3967 | 633 | [6 empty] | 0 | 633 | -852.5118 | [13 empty] | 40098.1088 | 59.967 | 3784.8306 | 350 | -254.5418 | 0 | 147.5 | 10 | 15 | -103 | 7597.35 | 26.4008
| 40098.1088 | 59.967 | 3784.8306 |  |  |  | 26.4008 | 25.8577 |  | 0 | 3802.8307 | 3773.1343 | 3780.6094 | 3776.2779 | 3746.5034 | 633 | [6 empty] | 0 | 633 | -852.5118 | [13 empty] | 40098.1088 | 59.967 | 3784.8306 | 350 | -254.5418 | 0 | 147.5 | 10 | 15 | -103 | 7597.35 | 26.4008
| 40098.1088 | 59.969 | 3784.3203 |  |  |  | 24.7986 | 25.487 |  | 0 | 3802.46 | 3773.174 | 3780.6869 | 3776.2779 | 3746.6094 | 633 | [6 empty] | 0 | 633 | -876.1433 | [13 empty] | 40098.1088 | 59.969 | 3784.3203 | 350 | -254.5418 | 0 | 148 | 10 | 15 | -103 | 7597.68 | 24.7986
| 40098.1088 | 59.969 | 3784.3203 |  |  |  | 24.7986 | 25.2461 |  | 0 | 3802.219 | 3773.2134 | 3780.7629 | 3776.2779 | 3746.7146 | 633 | [6 empty] | 0 | 633 | -876.1433 | [13 empty] | 40098.1088 | 59.969 | 3784.3203 | 350 | -254.5418 | 0 | 148 | 10 | 15 | -103 | 7597.68 | 24.7986
| 40098.1089 | 59.967 | 3779.3516 |  |  |  | 26.4008 | 25.6502 |  | 0 | 3802.6232 | 3773.235 | 3780.8399 | 3776.2779 | 3746.8191 | 633 | [6 empty] | 0 | 633 | -852.5118 | [13 empty] | 40098.1089 | 59.967 | 3779.3516 | 350 | -254.5418 | 0 | 148.5 | 10 | 15 | -103 | 7598.01 | 26.4008
| 40098.1089 | 59.967 | 3779.3516 |  |  |  | 26.4008 | 25.9129 |  | 0 | 3802.8859 | 3773.2565 | 3780.9173 | 3776.2779 | 3746.9228 | 633 | [6 empty] | 0 | 633 | -852.5118 | [13 empty] | 40098.1089 | 59.967 | 3779.3516 | 350 | -254.5418 | 0 | 148.5 | 10 | 15 | -103 | 7598.01 | 26.4008
| 40098.1089 | 59.967 | 3779.3516 |  |  |  | 26.4008 | 26.0837 |  | 0 | 3803.0566 | 3773.2778 | 3780.9947 | 3776.2779 | 3747.0258 | 633 | [6 empty] | 0 | 633 | -852.5118 | [13 empty] | 40098.1089 | 59.967 | 3779.3516 | 350 | -254.5418 | 0 | 148.5 | 10 | 15 | -103 | 7598.01 | 26.4008
| 40098.1089 | 59.971 | 3778.6333 |  |  |  | 23.1995 | 25.0742 |  | 0 | 3802.0472 | 3773.2964 | 3781.068 | 3776.2779 | 3747.1281 | 633 | [6 empty] | 0 | 633 | -901.0733 | [13 empty] | 40098.1089 | 59.971 | 3778.6333 | 350 | -256.5716 | 0 | 149 | 10 | 15 | -103 | 7598.34 | 23.1995
| 40098.109 | 59.971 | 3778.6333 |  |  |  | 23.1995 | 24.418 |  | 0 | 3801.391 | 3773.315 | 3781.1386 | 3776.2779 | 3747.2296 | 633 | [6 empty] | 0 | 633 | -901.0733 | [13 empty] | 40098.109 | 59.971 | 3778.6333 | 350 | -256.5716 | 0 | 149 | 10 | 15 | -103 | 7598.34 | 23.1995
| 40098.109 | 59.965 | 3776.4292 |  |  |  | 27.9999 | 25.6717 |  | 0 | 3802.6447 | 3773.3257 | 3781.213 | 3776.2779 | 3747.3305 | 633 | [6 empty] | 0 | 633 | -830.1631 | [13 empty] | 40098.109 | 59.965 | 3776.4292 | 350 | -256.5716 | 0 | 149.5 | 10 | 15 | -103 | 7598.67 | 27.9999
| 40098.109 | 59.965 | 3776.4292 |  |  |  | 27.9999 | 26.4865 |  | 0 | 3803.4595 | 3773.3364 | 3781.2897 | 3776.2779 | 3747.4307 | 633 | [6 empty] | 0 | 633 | -830.1631 | [13 empty] | 40098.109 | 59.965 | 3776.4292 | 350 | -256.5716 | 0 | 149.5 | 10 | 15 | -103 | 7598.67 | 27.9999
| 40098.109 | 59.965 | 3776.4292 |  |  |  | 27.9999 | 27.0162 |  | 0 | 3803.9892 | 3773.3471 | 3781.3677 | 3776.2779 | 3747.5301 | 633 | [6 empty] | 0 | 633 | -830.1631 | [13 empty] | 40098.109 | 59.965 | 3776.4292 | 350 | -256.5716 | 0 | 149.5 | 10 | 15 | -103 | 7598.67 | 27.9999
| 40098.1091 | 59.97 | 3776.5967 |  |  |  | 23.999 | 25.9602 |  | 0 | 3802.9332 | 3773.3582 | 3781.4416 | 3776.2779 | 3747.6289 | 633 | [6 empty] | 0 | 633 | -888.4334 | [13 empty] | 40098.1091 | 59.97 | 3776.5967 | 350 | -256.5716 | 0 | 150 | 10 | 15 | -103 | 7599 | 23.999
| 40098.1091 | 59.97 | 3776.5967 |  |  |  | 23.999 | 25.2738 |  | 0 | 3802.2468 | 3773.3692 | 3781.5126 | 3776.2779 | 3747.727 | 633 | [6 empty] | 0 | 633 | -888.4334 | [13 empty] | 40098.1091 | 59.97 | 3776.5967 | 350 | -256.5716 | 0 | 150 | 10 | 15 | -103 | 7599 | 23.999
| 40098.1091 | 59.969 | 3773.1699 |  |  |  | 24.7986 | 25.1075 |  | 0 | 3802.0804 | 3773.3686 | 3781.5826 | 3776.2779 | 3747.8245 | 633 | [6 empty] | 0 | 633 | -876.1433 | [13 empty] | 40098.1091 | 59.969 | 3773.1699 | 350 | -256.5716 | 0 | 150.5 | 10 | 15 | -103 | 7599.33 | 24.7986
| 40098.1091 | 59.969 | 3773.1699 |  |  |  | 24.7986 | 24.9994 |  | 0 | 3801.9723 | 3773.3679 | 3781.6517 | 3776.2779 | 3747.9213 | 633 | [6 empty] | 0 | 633 | -876.1433 | [13 empty] | 40098.1091 | 59.969 | 3773.1699 | 350 | -256.5716 | 0 | 150.5 | 10 | 15 | -103 | 7599.33 | 24.7986
| 40098.1091 | 59.969 | 3773.1699 |  |  |  | 24.7986 | 24.9291 |  | 0 | 3801.9021 | 3773.3672 | 3781.7201 | 3776.2779 | 3748.0174 | 633 | [6 empty] | 0 | 633 | -876.1433 | [13 empty] | 40098.1091 | 59.969 | 3773.1699 | 350 | -256.5716 | 0 | 150.5 | 10 | 15 | -103 | 7599.33 | 24.7986
| 40098.1092 | 59.965 | 3768.793 |  |  |  | 27.9999 | 26.0039 |  | 0 | 3802.9768 | 3773.3518 | 3781.7917 | 3776.2779 | 3748.1129 | 633 | [6 empty] | 0 | 633 | -830.1631 | [13 empty] | 40098.1092 | 59.965 | 3768.793 | 350 | -256.5716 | 0 | 151 | 10 | 15 | -103 | 7599.66 | 27.9999
| 40098.1092 | 59.965 | 3768.793 |  |  |  | 27.9999 | 26.7025 |  | 0 | 3803.6754 | 3773.3365 | 3781.8651 | 3776.2779 | 3748.2077 | 633 | [6 empty] | 0 | 633 | -830.1631 | [13 empty] | 40098.1092 | 59.965 | 3768.793 | 350 | -256.5716 | 0 | 151 | 10 | 15 | -103 | 7599.66 | 27.9999
| 40098.1092 | 59.973 | 3767.3662 |  |  |  | 21.6003 | 24.9167 |  | 0 | 3801.8897 | 3773.3166 | 3781.9321 | 3776.2779 | 3748.3019 | 633 | [6 empty] | 0 | 633 | -927.4636 | [13 empty] | 40098.1092 | 59.973 | 3767.3662 | 350 | -258.3726 | 0 | 151.5 | 10 | 15 | -103 | 7599.99 | 21.6003
| 40098.1092 | 59.973 | 3767.3662 |  |  |  | 21.6003 | 23.756 |  | 0 | 3800.729 | 3773.2967 | 3781.9947 | 3776.2779 | 3748.3955 | 633 | [6 empty] | 0 | 633 | -927.4636 | [13 empty] | 40098.1092 | 59.973 | 3767.3662 | 350 | -258.3726 | 0 | 151.5 | 10 | 15 | -103 | 7599.99 | 21.6003
| 40098.1093 | 59.973 | 3767.3662 |  |  |  | 21.6003 | 23.0015 |  | 0 | 3799.9745 | 3773.277 | 3782.0545 | 3776.2779 | 3748.4884 | 633 | [6 empty] | 0 | 633 | -927.4636 | [13 empty] | 40098.1093 | 59.973 | 3767.3662 | 350 | -258.3726 | 0 | 151.5 | 10 | 15 | -103 | 7599.99 | 21.6003
| 40098.1093 | 59.968 | 3760.2954 |  |  |  | 25.6012 | 23.9114 |  | 0 | 3800.8844 | 3773.234 | 3782.1168 | 3776.2779 | 3748.5807 | 633 | [6 empty] | 0 | 633 | -864.1435 | [13 empty] | 40098.1093 | 59.968 | 3760.2954 | 350 | -258.3726 | 0 | 152 | 10 | 15 | -103 | 7600.32 | 25.6012
| 40098.1093 | 59.968 | 3760.2954 |  |  |  | 25.6012 | 24.5028 |  | 0 | 3801.4758 | 3773.1913 | 3782.1807 | 3776.2779 | 3748.6724 | 633 | [6 empty] | 0 | 633 | -864.1435 | [13 empty] | 40098.1093 | 59.968 | 3760.2954 | 350 | -258.3726 | 0 | 152 | 10 | 15 | -103 | 7600.32 | 25.6012
| 40098.1093 | 59.967 | 3761.7766 |  |  |  | 26.4008 | 25.1671 |  | 0 | 3802.1401 | 3773.1538 | 3782.2464 | 3776.2779 | 3748.7635 | 633 | [6 empty] | 0 | 633 | -852.5118 | [13 empty] | 40098.1093 | 59.967 | 3761.7766 | 350 | -258.3726 | 0 | 152.5 | 10 | 15 | -103 | 7600.65 | 26.4008
| 40098.1094 | 59.967 | 3761.7766 |  |  |  | 26.4008 | 25.5989 |  | 0 | 3802.5719 | 3773.1165 | 3782.313 | 3776.2779 | 3748.854 | 633 | [6 empty] | 0 | 633 | -852.5118 | [13 empty] | 40098.1094 | 59.967 | 3761.7766 | 350 | -258.3726 | 0 | 152.5 | 10 | 15 | -103 | 7600.65 | 26.4008
| 40098.1094 | 59.967 | 3761.7766 |  |  |  | 26.4008 | 25.8795 |  | 0 | 3802.8525 | 3773.0794 | 3782.3801 | 3776.2779 | 3748.944 | 633 | [6 empty] | 0 | 633 | -852.5118 | [13 empty] | 40098.1094 | 59.967 | 3761.7766 | 350 | -258.3726 | 0 | 152.5 | 10 | 15 | -103 | 7600.65 | 26.4008
| 40098.1094 | 59.979 | 3760.1575 |  |  |  | 16.7999 | 22.7017 |  | 0 | 3799.6747 | 3773.0373 | 3782.4365 | 3776.2779 | 3749.0333 | 633 | [6 empty] | 0 | 633 | -1016.8652 | [13 empty] | 40098.1094 | 59.979 | 3760.1575 | 350 | -258.3726 | 0 | 153 | 10 | 15 | -103 | 7600.98 | 16.7999
| 40098.1094 | 59.979 | 3760.1575 |  |  |  | 16.7999 | 20.6361 |  | 0 | 3797.609 | 3772.9955 | 3782.4857 | 3776.2779 | 3749.122 | 633 | [6 empty] | 0 | 633 | -1016.8652 | [13 empty] | 40098.1094 | 59.979 | 3760.1575 | 350 | -258.3726 | 0 | 153 | 10 | 15 | -103 | 7600.98 | 16.7999
| 40098.1094 | 59.983 | 3757.7729 |  |  |  | 13.5986 | 18.173 |  | 0 | 3795.1459 | 3772.9462 | 3782.5267 | 3776.2779 | 3749.2102 | 633 | [6 empty] | 0 | 633 | -1086.7229 | [13 empty] | 40098.1094 | 59.983 | 3757.7729 | 350 | -258.3726 | 0 | 153.5 | 10 | 15 | -103 | 7601.31 | 13.5986
| 40098.1095 | 59.983 | 3757.7729 |  |  |  | 13.5986 | 16.5719 |  | 0 | 3793.5449 | 3772.8973 | 3782.5622 | 3776.2779 | 3749.2978 | 633 | [6 empty] | 0 | 633 | -1086.7229 | [13 empty] | 40098.1095 | 59.983 | 3757.7729 | 350 | -258.3726 | 0 | 153.5 | 10 | 15 | -103 | 7601.31 | 13.5986
| 40098.1095 | 59.983 | 3757.7729 |  |  |  | 13.5986 | 15.5313 |  | 0 | 3792.5043 | 3772.8487 | 3782.5942 | 3776.2779 | 3749.3848 | 633 | [6 empty] | 0 | 633 | -1086.7229 | [13 empty] | 40098.1095 | 59.983 | 3757.7729 | 350 | -258.3726 | 0 | 153.5 | 10 | 15 | -103 | 7601.31 | 13.5986
| 40098.1095 | 59.965 | 3753.0874 |  |  |  | 27.9999 | 19.8953 |  | 0 | 3796.8683 | 3772.7853 | 3782.6399 | 3776.2779 | 3749.4713 | 633 | [6 empty] | 0 | 633 | -830.1631 | [13 empty] | 40098.1095 | 59.965 | 3753.0874 | 350 | -263.0474 | 0 | 154 | 10 | 15 | -103 | 7601.64 | 27.9999
| 40098.1095 | 59.965 | 3753.0874 |  |  |  | 27.9999 | 22.7319 |  | 0 | 3799.7049 | 3772.7224 | 3782.6945 | 3776.2779 | 3749.5572 | 633 | [6 empty] | 0 | 633 | -830.1631 | [13 empty] | 40098.1095 | 59.965 | 3753.0874 | 350 | -263.0474 | 0 | 154 | 10 | 15 | -103 | 7601.64 | 27.9999
| 40098.1096 | 59.962 | 3758.2246 |  |  |  | 30.3986 | 25.4152 |  | 0 | 3802.3882 | 3772.6762 | 3782.7572 | 3776.2779 | 3749.6426 | 633 | [6 empty] | 0 | 633 | -798.754 | [13 empty] | 40098.1096 | 59.962 | 3758.2246 | 350 | -263.0474 | 0 | 154.5 | 10 | 15 | -103 | 7601.97 | 30.3986
| 40098.1096 | 59.962 | 3758.2246 |  |  |  | 30.3986 | 27.1594 |  | 0 | 3804.1324 | 3772.6304 | 3782.825 | 3776.2779 | 3749.7274 | 633 | [6 empty] | 0 | 633 | -798.754 | [13 empty] | 40098.1096 | 59.962 | 3758.2246 | 350 | -263.0474 | 0 | 154.5 | 10 | 15 | -103 | 7601.97 | 30.3986
| 40098.1096 | 59.962 | 3758.2246 |  |  |  | 30.3986 | 28.2931 |  | 0 | 3805.2661 | 3772.5848 | 3782.8961 | 3776.2779 | 3749.8117 | 633 | [6 empty] | 0 | 633 | -798.754 | [13 empty] | 40098.1096 | 59.962 | 3758.2246 | 350 | -263.0474 | 0 | 154.5 | 10 | 15 | -103 | 7601.97 | 30.3986
| 40098.1096 | 59.96 | 3758.041 |  |  |  | 32.0007 | 29.5908 |  | 0 | 3806.5638 | 3772.5389 | 3782.9707 | 3776.2779 | 3749.8955 | 633 | [6 empty] | 0 | 633 | -779.0659 | [13 empty] | 40098.1096 | 59.96 | 3758.041 | 350 | -263.0474 | 0 | 155 | 10 | 15 | -103 | 7602.3 | 32.0007
| 40098.1097 | 59.96 | 3758.041 |  |  |  | 32.0007 | 30.4343 |  | 0 | 3807.4072 | 3772.4933 | 3783.0476 | 3776.2779 | 3749.9787 | 633 | [6 empty] | 0 | 633 | -779.0659 | [13 empty] | 40098.1097 | 59.96 | 3758.041 | 350 | -263.0474 | 0 | 155 | 10 | 15 | -103 | 7602.3 | 32.0007
| 40098.1097 | 59.959 | 3763.8223 |  |  |  | 32.8003 | 31.2624 |  | 0 | 3808.2353 | 3772.4661 | 3783.1265 | 3776.2779 | 3750.0614 | 633 | [6 empty] | 0 | 633 | -769.5993 | [13 empty] | 40098.1097 | 59.959 | 3763.8223 | 350 | -263.0474 | 0 | 155.5 | 10 | 15 | -103 | 7602.63 | 32.8003
| 40098.1097 | 59.959 | 3763.8223 |  |  |  | 32.8003 | 31.8006 |  | 0 | 3808.7736 | 3772.4391 | 3783.2067 | 3776.2779 | 3750.1436 | 633 | [6 empty] | 0 | 633 | -769.5993 | [13 empty] | 40098.1097 | 59.959 | 3763.8223 | 350 | -263.0474 | 0 | 155.5 | 10 | 15 | -103 | 7602.63 | 32.8003
| 40098.1097 | 59.959 | 3763.8223 |  |  |  | 32.8003 | 32.1505 |  | 0 | 3809.1235 | 3772.4123 | 3783.2874 | 3776.2779 | 3750.2252 | 633 | [6 empty] | 0 | 633 | -769.5993 | [13 empty] | 40098.1097 | 59.959 | 3763.8223 | 350 | -263.0474 | 0 | 155.5 | 10 | 15 | -103 | 7602.63 | 32.8003
| 40098.1097 | 59.953 | 3763.8582 |  |  |  | 37.6007 | 34.0581 |  | 0 | 3811.0311 | 3772.3857 | 3783.3736 | 3776.2779 | 3750.3064 | 633 | [6 empty] | 0 | 633 | -717.2714 | [13 empty] | 40098.1097 | 59.953 | 3763.8582 | 350 | -263.0474 | 0 | 156 | 10 | 15 | -103 | 7602.96 | 37.6007
| 40098.1098 | 59.953 | 3763.8582 |  |  |  | 37.6007 | 35.298 |  | 0 | 3812.271 | 3772.3593 | 3783.463 | 3776.2779 | 3750.3871 | 633 | [6 empty] | 0 | 633 | -717.2714 | [13 empty] | 40098.1098 | 59.953 | 3763.8582 | 350 | -263.0474 | 0 | 156 | 10 | 15 | -103 | 7602.96 | 37.6007
| 40098.1098 | 59.957 | 3768.3389 |  |  |  | 34.3994 | 34.9835 |  | 0 | 3811.9565 | 3772.3469 | 3783.551 | 3776.2779 | 3750.4672 | 633 | [6 empty] | 0 | 633 | -751.3398 | [13 empty] | 40098.1098 | 59.957 | 3768.3389 | 350 | -260.9844 | 0 | 156.5 | 10 | 15 | -103 | 7603.29 | 34.3994
| 40098.1098 | 59.957 | 3768.3389 |  |  |  | 34.3994 | 34.7791 |  | 0 | 3811.752 | 3772.3345 | 3783.6378 | 3776.2779 | 3750.5469 | 633 | [6 empty] | 0 | 633 | -751.3398 | [13 empty] | 40098.1098 | 59.957 | 3768.3389 | 350 | -260.9844 | 0 | 156.5 | 10 | 15 | -103 | 7603.29 | 34.3994
| 40098.1098 | 59.957 | 3768.3389 |  |  |  | 34.3994 | 34.6462 |  | 0 | 3811.6192 | 3772.3223 | 3783.7236 | 3776.2779 | 3750.626 | 633 | [6 empty] | 0 | 633 | -751.3398 | [13 empty] | 40098.1098 | 59.957 | 3768.3389 | 350 | -260.9844 | 0 | 156.5 | 10 | 15 | -103 | 7603.29 | 34.3994
| 40098.1099 | 59.963 | 3767.4375 |  |  |  | 29.599 | 32.8797 |  | 0 | 3809.8527 | 3772.3074 | 3783.8035 | 3776.2779 | 3750.7047 | 633 | [6 empty] | 0 | 633 | -808.9563 | [13 empty] | 40098.1099 | 59.963 | 3767.4375 | 350 | -260.9844 | 0 | 157 | 10 | 15 | -103 | 7603.62 | 29.599
| 40098.1099 | 59.963 | 3767.4375 |  |  |  | 29.599 | 31.7314 |  | 0 | 3808.7044 | 3772.2925 | 3783.8794 | 3776.2779 | 3750.7829 | 633 | [6 empty] | 0 | 633 | -808.9563 | [13 empty] | 40098.1099 | 59.963 | 3767.4375 | 350 | -260.9844 | 0 | 157 | 10 | 15 | -103 | 7603.62 | 29.599
| 40098.1099 | 59.959 | 3761.5703 |  |  |  | 32.8003 | 32.1055 |  | 0 | 3809.0785 | 3772.2599 | 3783.956 | 3776.2779 | 3750.8607 | 633 | [6 empty] | 0 | 633 | -769.5993 | [13 empty] | 40098.1099 | 59.959 | 3761.5703 | 350 | -260.9844 | 0 | 157.5 | 10 | 15 | -103 | 7603.95 | 32.8003
| 40098.1099 | 59.959 | 3761.5703 |  |  |  | 32.8003 | 32.3487 |  | 0 | 3809.3217 | 3772.2275 | 3784.0329 | 3776.2779 | 3750.9379 | 633 | [6 empty] | 0 | 633 | -769.5993 | [13 empty] | 40098.1099 | 59.959 | 3761.5703 | 350 | -260.9844 | 0 | 157.5 | 10 | 15 | -103 | 7603.95 | 32.8003
| 40098.11 | 59.959 | 3761.5703 |  |  |  | 32.8003 | 32.5068 |  | 0 | 3809.4797 | 3772.1953 | 3784.1097 | 3776.2779 | 3751.0147 | 633 | [6 empty] | 0 | 633 | -769.5993 | [13 empty] | 40098.11 | 59.959 | 3761.5703 | 350 | -260.9844 | 0 | 157.5 | 10 | 15 | -103 | 7603.95 | 32.8003
| 40098.11 | 59.965 | 3759.627 |  |  |  | 27.9999 | 30.9294 |  | 0 | 3807.9023 | 3772.1575 | 3784.1814 | 3776.2779 | 3751.091 | 633 | [6 empty] | 0 | 633 | -830.1631 | [13 empty] | 40098.11 | 59.965 | 3759.627 | 350 | -260.9844 | 0 | 158 | 10 | 15 | -103 | 7604.28 | 27.9999
| 40098.11 | 59.965 | 3759.627 |  |  |  | 27.9999 | 29.904 |  | 0 | 3806.877 | 3772.1198 | 3784.2496 | 3776.2779 | 3751.1669 | 633 | [6 empty] | 0 | 633 | -830.1631 | [13 empty] | 40098.11 | 59.965 | 3759.627 | 350 | -260.9844 | 0 | 158 | 10 | 15 | -103 | 7604.28 | 27.9999
| 40098.11 | 59.968 | 3750.1016 |  |  |  | 25.6012 | 28.398 |  | 0 | 3805.371 | 3772.0539 | 3784.3128 | 3776.2779 | 3751.2423 | 633 | [6 empty] | 0 | 633 | -864.1435 | [13 empty] | 40098.11 | 59.968 | 3750.1016 | 350 | -260.9844 | 0 | 158.5 | 10 | 15 | -103 | 7604.61 | 25.6012
| 40098.11 | 59.968 | 3750.1016 |  |  |  | 25.6012 | 27.4191 |  | 0 | 3804.3921 | 3771.9884 | 3784.3727 | 3776.2779 | 3751.3173 | 633 | [6 empty] | 0 | 633 | -864.1435 | [13 empty] | 40098.11 | 59.968 | 3750.1016 | 350 | -260.9844 | 0 | 158.5 | 10 | 15 | -103 | 7604.61 | 25.6012
| 40098.1101 | 59.968 | 3750.1016 |  |  |  | 25.6012 | 26.7829 |  | 0 | 3803.7558 | 3771.9232 | 3784.4304 | 3776.2779 | 3751.3918 | 633 | [6 empty] | 0 | 633 | -864.1435 | [13 empty] | 40098.1101 | 59.968 | 3750.1016 | 350 | -260.9844 | 0 | 158.5 | 10 | 15 | -103 | 7604.61 | 25.6012
| 40098.1101 | 59.973 | 3753.5103 |  |  |  | 21.6003 | 24.969 |  | 0 | 3801.942 | 3771.8686 | 3784.4824 | 3776.2779 | 3751.4658 | 633 | [6 empty] | 0 | 633 | -927.4636 | [13 empty] | 40098.1101 | 59.973 | 3753.5103 | 350 | -261.3183 | 0 | 159 | 10 | 15 | -103 | 7604.94 | 21.6003
| 40098.1101 | 59.973 | 3753.5103 |  |  |  | 21.6003 | 23.79 |  | 0 | 3800.7629 | 3771.8143 | 3784.5306 | 3776.2779 | 3751.5395 | 633 | [6 empty] | 0 | 633 | -927.4636 | [13 empty] | 40098.1101 | 59.973 | 3753.5103 | 350 | -261.3183 | 0 | 159 | 10 | 15 | -103 | 7604.94 | 21.6003
| 40098.1101 | 59.965 | 3753.1782 |  |  |  | 27.9999 | 25.2634 |  | 0 | 3802.2364 | 3771.7593 | 3784.5828 | 3776.2779 | 3751.6127 | 633 | [6 empty] | 0 | 633 | -830.1631 | [13 empty] | 40098.1101 | 59.965 | 3753.1782 | 350 | -261.3183 | 0 | 159.5 | 10 | 15 | -103 | 7605.27 | 27.9999
| 40098.1102 | 59.965 | 3753.1782 |  |  |  | 27.9999 | 26.2212 |  | 0 | 3803.1942 | 3771.7047 | 3784.6375 | 3776.2779 | 3751.6854 | 633 | [6 empty] | 0 | 633 | -830.1631 | [13 empty] | 40098.1102 | 59.965 | 3753.1782 | 350 | -261.3183 | 0 | 159.5 | 10 | 15 | -103 | 7605.27 | 27.9999
| 40098.1102 | 59.965 | 3753.1782 |  |  |  | 27.9999 | 26.8437 |  | 0 | 3803.8167 | 3771.6503 | 3784.6938 | 3776.2779 | 3751.7577 | 633 | [6 empty] | 0 | 633 | -830.1631 | [13 empty] | 40098.1102 | 59.965 | 3753.1782 | 350 | -261.3183 | 0 | 159.5 | 10 | 15 | -103 | 7605.27 | 27.9999
| 40098.1102 | 59.972 | 3753.2905 |  |  |  | 22.3999 | 25.2884 |  | 0 | 3802.2614 | 3771.5967 | 3784.7451 | 3776.2779 | 3751.8296 | 633 | [6 empty] | 0 | 633 | -914.078 | [13 empty] | 40098.1102 | 59.972 | 3753.2905 | 350 | -261.3183 | 0 | 160 | 10 | 15 | -103 | 7605.6 | 22.3999
| 40098.1102 | 59.972 | 3753.2905 |  |  |  | 22.3999 | 24.2774 |  | 0 | 3801.2504 | 3771.5433 | 3784.7933 | 3776.2779 | 3751.9011 | 633 | [6 empty] | 0 | 633 | -914.078 | [13 empty] | 40098.1102 | 59.972 | 3753.2905 | 350 | -261.3183 | 0 | 160 | 10 | 15 | -103 | 7605.6 | 22.3999
| 40098.1103 | 59.975 | 3749.3979 |  |  |  | 20.0012 | 22.7807 |  | 0 | 3799.7537 | 3771.4789 | 3784.8367 | 3776.2779 | 3751.9722 | 633 | [6 empty] | 0 | 633 | -955.4464 | [13 empty] | 40098.1103 | 59.975 | 3749.3979 | 350 | -261.3183 | 0 | 160.5 | 10 | 15 | -103 | 7605.93 | 20.0012
| 40098.1103 | 59.975 | 3749.3979 |  |  |  | 20.0012 | 21.8079 |  | 0 | 3798.7809 | 3771.4149 | 3784.8772 | 3776.2779 | 3752.0429 | 633 | [6 empty] | 0 | 633 | -955.4464 | [13 empty] | 40098.1103 | 59.975 | 3749.3979 | 350 | -261.3183 | 0 | 160.5 | 10 | 15 | -103 | 7605.93 | 20.0012
| 40098.1103 | 59.975 | 3749.3979 |  |  |  | 20.0012 | 21.1756 |  | 0 | 3798.1486 | 3771.3513 | 3784.9155 | 3776.2779 | 3752.1131 | 633 | [6 empty] | 0 | 633 | -955.4464 | [13 empty] | 40098.1103 | 59.975 | 3749.3979 | 350 | -261.3183 | 0 | 160.5 | 10 | 15 | -103 | 7605.93 | 20.0012
| 40098.1103 | 59.974 | 3740.3704 |  |  |  | 20.8008 | 21.0444 |  | 0 | 3798.0174 | 3771.262 | 3784.9533 | 3776.2779 | 3752.1829 | 633 | [6 empty] | 0 | 633 | -941.2471 | [13 empty] | 40098.1103 | 59.974 | 3740.3704 | 350 | -261.3183 | 0 | 161 | 10 | 15 | -103 | 7606.26 | 20.8008
| 40098.1103 | 59.974 | 3740.3704 |  |  |  | 20.8008 | 20.9591 |  | 0 | 3797.9321 | 3771.1732 | 3784.9906 | 3776.2779 | 3752.2524 | 633 | [6 empty] | 0 | 633 | -941.2471 | [13 empty] | 40098.1103 | 59.974 | 3740.3704 | 350 | -261.3183 | 0 | 161 | 10 | 15 | -103 | 7606.26 | 20.8008
| 40098.1104 | 59.981 | 3745.7383 |  |  |  | 15.2008 | 18.9437 |  | 0 | 3795.9167 | 3771.1003 | 3785.0219 | 3776.2779 | 3752.3214 | 633 | [6 empty] | 0 | 633 | -1050.6009 | [13 empty] | 40098.1104 | 59.981 | 3745.7383 | 350 | -262.1026 | 0 | 161.5 | 10 | 15 | -103 | 7606.59 | 15.2008
| 40098.1104 | 59.981 | 3745.7383 |  |  |  | 15.2008 | 17.6337 |  | 0 | 3794.6067 | 3771.0279 | 3785.0493 | 3776.2779 | 3752.3901 | 633 | [6 empty] | 0 | 633 | -1050.6009 | [13 empty] | 40098.1104 | 59.981 | 3745.7383 | 350 | -262.1026 | 0 | 161.5 | 10 | 15 | -103 | 7606.59 | 15.2008
| 40098.1104 | 59.981 | 3745.7383 |  |  |  | 15.2008 | 16.7822 |  | 0 | 3793.7552 | 3770.9558 | 3785.0741 | 3776.2779 | 3752.4583 | 633 | [6 empty] | 0 | 633 | -1050.6009 | [13 empty] | 40098.1104 | 59.981 | 3745.7383 | 350 | -262.1026 | 0 | 161.5 | 10 | 15 | -103 | 7606.59 | 15.2008
| 40098.1104 | 59.982 | 3741.6182 |  |  |  | 14.4012 | 15.9489 |  | 0 | 3792.9218 | 3770.8725 | 3785.0964 | 3776.2779 | 3752.5262 | 633 | [6 empty] | 0 | 633 | -1068.3222 | [13 empty] | 40098.1104 | 59.982 | 3741.6182 | 350 | -262.1026 | 0 | 162 | 10 | 15 | -103 | 7606.92 | 14.4012
| 40098.1105 | 59.982 | 3741.6182 |  |  |  | 14.4012 | 15.4072 |  | 0 | 3792.3802 | 3770.7896 | 3785.117 | 3776.2779 | 3752.5937 | 633 | [6 empty] | 0 | 633 | -1068.3222 | [13 empty] | 40098.1105 | 59.982 | 3741.6182 | 350 | -262.1026 | 0 | 162 | 10 | 15 | -103 | 7606.92 | 14.4012
| 40098.1105 | 59.984 | 3738.9014 |  |  |  | 12.7991 | 14.4944 |  | 0 | 3791.4673 | 3770.6995 | 3785.1349 | 3776.2779 | 3752.6607 | 633 | [6 empty] | 0 | 633 | -1105.6948 | [13 empty] | 40098.1105 | 59.984 | 3738.9014 | 350 | -262.1026 | 0 | 162.5 | 10 | 15 | -103 | 7607.25 | 12.7991
| 40098.1105 | 59.984 | 3738.9014 |  |  |  | 12.7991 | 13.901 |  | 0 | 3790.874 | 3770.61 | 3785.1511 | 3776.2779 | 3752.7275 | 633 | [6 empty] | 0 | 633 | -1105.6948 | [13 empty] | 40098.1105 | 59.984 | 3738.9014 | 350 | -262.1026 | 0 | 162.5 | 10 | 15 | -103 | 7607.25 | 12.7991
| 40098.1105 | 59.984 | 3738.9014 |  |  |  | 12.7991 | 13.5153 |  | 0 | 3790.4883 | 3770.5209 | 3785.1661 | 3776.2779 | 3752.7938 | 633 | [6 empty] | 0 | 633 | -1105.6948 | [13 empty] | 40098.1105 | 59.984 | 3738.9014 | 350 | -262.1026 | 0 | 162.5 | 10 | 15 | -103 | 7607.25 | 12.7991
| 40098.1106 | 59.979 | 3737.2732 |  |  |  | 16.7999 | 14.6649 |  | 0 | 3791.6379 | 3770.4278 | 3785.1842 | 3776.2779 | 3752.8598 | 633 | [6 empty] | 0 | 633 | -1016.8652 | [13 empty] | 40098.1106 | 59.979 | 3737.2732 | 350 | -262.1026 | 0 | 163 | 10 | 15 | -103 | 7607.58 | 16.7999
| 40098.1106 | 59.979 | 3737.2732 |  |  |  | 16.7999 | 15.4122 |  | 0 | 3792.3852 | 3770.3352 | 3785.2043 | 3776.2779 | 3752.9254 | 633 | [6 empty] | 0 | 633 | -1016.8652 | [13 empty] | 40098.1106 | 59.979 | 3737.2732 | 350 | -262.1026 | 0 | 163 | 10 | 15 | -103 | 7607.58 | 16.7999
| 40098.1106 | 59.978 | 3735.4482 |  |  |  | 17.5995 | 16.1777 |  | 0 | 3793.1507 | 3770.238 | 3785.2265 | 3776.2779 | 3752.9906 | 633 | [6 empty] | 0 | 633 | -1000.797 | [13 empty] | 40098.1106 | 59.978 | 3735.4482 | 350 | -262.1026 | 0 | 163.5 | 10 | 15 | -103 | 7607.91 | 17.5995
| 40098.1106 | 59.978 | 3735.4482 |  |  |  | 17.5995 | 16.6754 |  | 0 | 3793.6483 | 3770.1413 | 3785.2499 | 3776.2779 | 3753.0555 | 633 | [6 empty] | 0 | 633 | -1000.797 | [13 empty] | 40098.1106 | 59.978 | 3735.4482 | 350 | -262.1026 | 0 | 163.5 | 10 | 15 | -103 | 7607.91 | 17.5995
| 40098.1106 | 59.978 | 3735.4482 |  |  |  | 17.5995 | 16.9988 |  | 0 | 3793.9718 | 3770.0452 | 3785.274 | 3776.2779 | 3753.12 | 633 | [6 empty] | 0 | 633 | -1000.797 | [13 empty] | 40098.1106 | 59.978 | 3735.4482 | 350 | -262.1026 | 0 | 163.5 | 10 | 15 | -103 | 7607.91 | 17.5995
| 40098.1107 | 59.981 | 3737.5405 |  |  |  | 15.2008 | 16.3695 |  | 0 | 3793.3425 | 3769.9554 | 3785.2963 | 3776.2779 | 3753.1841 | 633 | [6 empty] | 0 | 633 | -1050.6009 | [13 empty] | 40098.1107 | 59.981 | 3737.5405 | 350 | -262.717 | 0 | 164 | 10 | 15 | -103 | 7608.24 | 15.2008
| 40098.1107 | 59.981 | 3737.5405 |  |  |  | 15.2008 | 15.9605 |  | 0 | 3792.9334 | 3769.8661 | 3785.3174 | 3776.2779 | 3753.2479 | 633 | [6 empty] | 0 | 633 | -1050.6009 | [13 empty] | 40098.1107 | 59.981 | 3737.5405 | 350 | -262.717 | 0 | 164 | 10 | 15 | -103 | 7608.24 | 15.2008
| 40098.1107 | 59.978 | 3736.6931 |  |  |  | 17.5995 | 16.5341 |  | 0 | 3793.5071 | 3769.775 | 3785.3399 | 3776.2779 | 3753.3114 | 633 | [6 empty] | 0 | 633 | -1000.797 | [13 empty] | 40098.1107 | 59.978 | 3736.6931 | 350 | -262.717 | 0 | 164.5 | 10 | 15 | -103 | 7608.57 | 17.5995
| 40098.1107 | 59.978 | 3736.6931 |  |  |  | 17.5995 | 16.907 |  | 0 | 3793.88 | 3769.6844 | 3785.3633 | 3776.2779 | 3753.3745 | 633 | [6 empty] | 0 | 633 | -1000.797 | [13 empty] | 40098.1107 | 59.978 | 3736.6931 | 350 | -262.717 | 0 | 164.5 | 10 | 15 | -103 | 7608.57 | 17.5995
| 40098.1108 | 59.978 | 3736.6931 |  |  |  | 17.5995 | 17.1494 |  | 0 | 3794.1223 | 3769.5942 | 3785.3872 | 3776.2779 | 3753.4372 | 633 | [6 empty] | 0 | 633 | -1000.797 | [13 empty] | 40098.1108 | 59.978 | 3736.6931 | 350 | -262.717 | 0 | 164.5 | 10 | 15 | -103 | 7608.57 | 17.5995
| 40098.1108 | 59.971 | 3736.0942 |  |  |  | 23.1995 | 19.2669 |  | 0 | 3796.2399 | 3769.503 | 3785.4168 | 3776.2779 | 3753.4996 | 633 | [6 empty] | 0 | 633 | -901.0733 | [13 empty] | 40098.1108 | 59.971 | 3736.0942 | 350 | -262.717 | 0 | 165 | 10 | 15 | -103 | 7608.9 | 23.1995
| 40098.1108 | 59.971 | 3736.0942 |  |  |  | 23.1995 | 20.6433 |  | 0 | 3797.6163 | 3769.4122 | 3785.4499 | 3776.2779 | 3753.5617 | 633 | [6 empty] | 0 | 633 | -901.0733 | [13 empty] | 40098.1108 | 59.971 | 3736.0942 | 350 | -262.717 | 0 | 165 | 10 | 15 | -103 | 7608.9 | 23.1995
| 40098.1108 | 59.974 | 3738.8748 |  |  |  | 20.8008 | 20.6984 |  | 0 | 3797.6714 | 3769.3294 | 3785.483 | 3776.2779 | 3753.6234 | 633 | [6 empty] | 0 | 633 | -941.2471 | [13 empty] | 40098.1108 | 59.974 | 3738.8748 | 350 | -262.717 | 0 | 165.5 | 10 | 15 | -103 | 7609.23 | 20.8008
| 40098.1109 | 59.974 | 3738.8748 |  |  |  | 20.8008 | 20.7342 |  | 0 | 3797.7072 | 3769.2471 | 3785.5161 | 3776.2779 | 3753.6848 | 633 | [6 empty] | 0 | 633 | -941.2471 | [13 empty] | 40098.1109 | 59.974 | 3738.8748 | 350 | -262.717 | 0 | 165.5 | 10 | 15 | -103 | 7609.23 | 20.8008
| 40098.1109 | 59.974 | 3738.8748 |  |  |  | 20.8008 | 20.7575 |  | 0 | 3797.7305 | 3769.1652 | 3785.549 | 3776.2779 | 3753.7459 | 633 | [6 empty] | 0 | 633 | -941.2471 | [13 empty] | 40098.1109 | 59.974 | 3738.8748 | 350 | -262.717 | 0 | 165.5 | 10 | 15 | -103 | 7609.23 | 20.8008
| 40098.1109 | 59.972 | 3738.647 |  |  |  | 22.3999 | 21.3324 |  | 0 | 3798.3053 | 3769.0832 | 3785.5833 | 3776.2779 | 3753.8066 | 633 | [6 empty] | 0 | 633 | -914.078 | [13 empty] | 40098.1109 | 59.972 | 3738.647 | 350 | -262.717 | 0 | 166 | 10 | 15 | -103 | 7609.56 | 22.3999
| 40098.1109 | 59.972 | 3738.647 |  |  |  | 22.3999 | 21.706 |  | 0 | 3798.679 | 3769.0016 | 3785.6184 | 3776.2779 | 3753.867 | 633 | [6 empty] | 0 | 633 | -914.078 | [13 empty] | 40098.1109 | 59.972 | 3738.647 | 350 | -262.717 | 0 | 166 | 10 | 15 | -103 | 7609.56 | 22.3999
| 40098.1109 | 59.971 | 3737.8921 |  |  |  | 23.1995 | 22.2287 |  | 0 | 3799.2017 | 3768.9184 | 3785.6547 | 3776.2779 | 3753.9271 | 633 | [6 empty] | 0 | 633 | -901.0733 | [13 empty] | 40098.1109 | 59.971 | 3737.8921 | 350 | -260.0165 | 0 | 166.5 | 10 | 15 | -103 | 7609.89 | 23.1995
| 40098.111 | 59.971 | 3737.8921 |  |  |  | 23.1995 | 22.5685 |  | 0 | 3799.5415 | 3768.8357 | 3785.6917 | 3776.2779 | 3753.9868 | 633 | [6 empty] | 0 | 633 | -901.0733 | [13 empty] | 40098.111 | 59.971 | 3737.8921 | 350 | -260.0165 | 0 | 166.5 | 10 | 15 | -103 | 7609.89 | 23.1995
| 40098.111 | 59.971 | 3737.8921 |  |  |  | 23.1995 | 22.7893 |  | 0 | 3799.7623 | 3768.7534 | 3785.7292 | 3776.2779 | 3754.0463 | 633 | [6 empty] | 0 | 633 | -901.0733 | [13 empty] | 40098.111 | 59.971 | 3737.8921 | 350 | -260.0165 | 0 | 166.5 | 10 | 15 | -103 | 7609.89 | 23.1995
| 40098.111 | 59.972 | 3740.3289 |  |  |  | 22.3999 | 22.653 |  | 0 | 3799.626 | 3768.678 | 3785.766 | 3776.2779 | 3754.1054 | 633 | [6 empty] | 0 | 633 | -914.078 | [13 empty] | 40098.111 | 59.972 | 3740.3289 | 350 | -260.0165 | 0 | 167 | 10 | 15 | -103 | 7610.22 | 22.3999
| 40098.111 | 59.972 | 3740.3289 |  |  |  | 22.3999 | 22.5644 |  | 0 | 3799.5374 | 3768.603 | 3785.8025 | 3776.2779 | 3754.1642 | 633 | [6 empty] | 0 | 633 | -914.078 | [13 empty] | 40098.111 | 59.972 | 3740.3289 | 350 | -260.0165 | 0 | 167 | 10 | 15 | -103 | 7610.22 | 22.3999
| 40098.1111 | 59.977 | 3742.5244 |  |  |  | 18.399 | 21.1065 |  | 0 | 3798.0795 | 3768.5342 | 3785.8348 | 3776.2779 | 3754.2227 | 633 | [6 empty] | 0 | 633 | -985.2287 | [13 empty] | 40098.1111 | 59.977 | 3742.5244 | 350 | -260.0165 | 0 | 167.5 | 10 | 15 | -103 | 7610.55 | 18.399
| 40098.1111 | 59.977 | 3742.5244 |  |  |  | 18.399 | 20.1589 |  | 0 | 3797.1319 | 3768.4657 | 3785.8646 | 3776.2779 | 3754.2809 | 633 | [6 empty] | 0 | 633 | -985.2287 | [13 empty] | 40098.1111 | 59.977 | 3742.5244 | 350 | -260.0165 | 0 | 167.5 | 10 | 15 | -103 | 7610.55 | 18.399
| 40098.1111 | 59.977 | 3742.5244 |  |  |  | 18.399 | 19.543 |  | 0 | 3796.5159 | 3768.3976 | 3785.8925 | 3776.2779 | 3754.3388 | 633 | [6 empty] | 0 | 633 | -985.2287 | [13 empty] | 40098.1111 | 59.977 | 3742.5244 | 350 | -260.0165 | 0 | 167.5 | 10 | 15 | -103 | 7610.55 | 18.399
| 40098.1111 | 59.976 | 3741.7231 |  |  |  | 19.1986 | 19.4224 |  | 0 | 3796.3954 | 3768.3278 | 3785.92 | 3776.2779 | 3754.3964 | 633 | [6 empty] | 0 | 633 | -970.1374 | [13 empty] | 40098.1111 | 59.976 | 3741.7231 | 350 | -260.0165 | 0 | 168 | 10 | 15 | -103 | 7610.88 | 19.1986
| 40098.1112 | 59.976 | 3741.7231 |  |  |  | 19.1986 | 19.3441 |  | 0 | 3796.3171 | 3768.2584 | 3785.9472 | 3776.2779 | 3754.4537 | 633 | [6 empty] | 0 | 633 | -970.1374 | [13 empty] | 40098.1112 | 59.976 | 3741.7231 | 350 | -260.0165 | 0 | 168 | 10 | 15 | -103 | 7610.88 | 19.1986
| 40098.1112 | 59.974 | 3739.9644 |  |  |  | 20.8008 | 19.8539 |  | 0 | 3796.8269 | 3768.1847 | 3785.9755 | 3776.2779 | 3754.5107 | 633 | [6 empty] | 0 | 633 | -941.2471 | [13 empty] | 40098.1112 | 59.974 | 3739.9644 | 350 | -260.0165 | 0 | 168.5 | 10 | 15 | -103 | 7611.21 | 20.8008
| 40098.1112 | 59.974 | 3739.9644 |  |  |  | 20.8008 | 20.1853 |  | 0 | 3797.1583 | 3768.1114 | 3786.0046 | 3776.2779 | 3754.5673 | 633 | [6 empty] | 0 | 633 | -941.2471 | [13 empty] | 40098.1112 | 59.974 | 3739.9644 | 350 | -260.0165 | 0 | 168.5 | 10 | 15 | -103 | 7611.21 | 20.8008
| 40098.1112 | 59.974 | 3739.9644 |  |  |  | 20.8008 | 20.4007 |  | 0 | 3797.3737 | 3768.0385 | 3786.034 | 3776.2779 | 3754.6237 | 633 | [6 empty] | 0 | 633 | -941.2471 | [13 empty] | 40098.1112 | 59.974 | 3739.9644 | 350 | -260.0165 | 0 | 168.5 | 10 | 15 | -103 | 7611.21 | 20.8008
| 40098.1112 | 59.978 | 3742.8325 |  |  |  | 17.5995 | 19.4203 |  | 0 | 3796.3933 | 3767.9733 | 3786.0608 | 3776.2779 | 3754.6798 | 633 | [6 empty] | 0 | 633 | -1000.797 | [13 empty] | 40098.1112 | 59.978 | 3742.8325 | 350 | -263.8732 | 0 | 169 | 10 | 15 | -103 | 7611.54 | 17.5995
| 40098.1113 | 59.978 | 3742.8325 |  |  |  | 17.5995 | 18.783 |  | 0 | 3795.756 | 3767.9085 | 3786.0858 | 3776.2779 | 3754.7356 | 633 | [6 empty] | 0 | 633 | -1000.797 | [13 empty] | 40098.1113 | 59.978 | 3742.8325 | 350 | -263.8732 | 0 | 169 | 10 | 15 | -103 | 7611.54 | 17.5995
| 40098.1113 | 59.981 | 3738.9658 |  |  |  | 15.2008 | 17.5292 |  | 0 | 3794.5022 | 3767.8341 | 3786.1074 | 3776.2779 | 3754.7912 | 633 | [6 empty] | 0 | 633 | -1050.6009 | [13 empty] | 40098.1113 | 59.981 | 3738.9658 | 350 | -263.8732 | 0 | 169.5 | 10 | 15 | -103 | 7611.87 | 15.2008
| 40098.1113 | 59.981 | 3738.9658 |  |  |  | 15.2008 | 16.7143 |  | 0 | 3793.6873 | 3767.7601 | 3786.1268 | 3776.2779 | 3754.8464 | 633 | [6 empty] | 0 | 633 | -1050.6009 | [13 empty] | 40098.1113 | 59.981 | 3738.9658 | 350 | -263.8732 | 0 | 169.5 | 10 | 15 | -103 | 7611.87 | 15.2008
| 40098.1113 | 59.981 | 3738.9658 |  |  |  | 15.2008 | 16.1846 |  | 0 | 3793.1575 | 3767.6865 | 3786.1448 | 3776.2779 | 3754.9013 | 633 | [6 empty] | 0 | 633 | -1050.6009 | [13 empty] | 40098.1113 | 59.981 | 3738.9658 | 350 | -263.8732 | 0 | 169.5 | 10 | 15 | -103 | 7611.87 | 15.2008
| 40098.1114 | 59.971 | 3738.8787 |  |  |  | 23.1995 | 18.6398 |  | 0 | 3795.6128 | 3767.613 | 3786.169 | 3776.2779 | 3754.956 | 633 | [6 empty] | 0 | 633 | -901.0733 | [13 empty] | 40098.1114 | 59.971 | 3738.8787 | 350 | -263.8732 | 0 | 170 | 10 | 15 | -103 | 7612.2 | 23.1995
| 40098.1114 | 59.971 | 3738.8787 |  |  |  | 23.1995 | 20.2357 |  | 0 | 3797.2086 | 3767.5399 | 3786.1971 | 3776.2779 | 3755.0104 | 633 | [6 empty] | 0 | 633 | -901.0733 | [13 empty] | 40098.1114 | 59.971 | 3738.8787 | 350 | -263.8732 | 0 | 170 | 10 | 15 | -103 | 7612.2 | 23.1995
| 40098.1114 | 59.971 | 3738.5579 |  |  |  | 23.1995 | 21.273 |  | 0 | 3798.246 | 3767.4663 | 3786.2276 | 3776.2779 | 3755.0645 | 633 | [6 empty] | 0 | 633 | -901.0733 | [13 empty] | 40098.1114 | 59.971 | 3738.5579 | 350 | -263.8732 | 0 | 170.5 | 10 | 15 | -103 | 7612.53 | 23.1995
| 40098.1114 | 59.971 | 3738.5579 |  |  |  | 23.1995 | 21.9473 |  | 0 | 3798.9202 | 3767.3931 | 3786.2598 | 3776.2779 | 3755.1184 | 633 | [6 empty] | 0 | 633 | -901.0733 | [13 empty] | 40098.1114 | 59.971 | 3738.5579 | 350 | -263.8732 | 0 | 170.5 | 10 | 15 | -103 | 7612.53 | 23.1995
| 40098.1115 | 59.971 | 3738.5579 |  |  |  | 23.1995 | 22.3855 |  | 0 | 3799.3585 | 3767.3203 | 3786.2929 | 3776.2779 | 3755.1719 | 633 | [6 empty] | 0 | 633 | -901.0733 | [13 empty] | 40098.1115 | 59.971 | 3738.5579 | 350 | -263.8732 | 0 | 170.5 | 10 | 15 | -103 | 7612.53 | 23.1995
| 40098.1115 | 59.966 | 3743.4187 |  |  |  | 27.2003 | 24.0707 |  | 0 | 3801.0437 | 3767.2601 | 3786.33 | 3776.2779 | 3755.2252 | 633 | [6 empty] | 0 | 633 | -841.189 | [13 empty] | 40098.1115 | 59.966 | 3743.4187 | 350 | -263.8732 | 0 | 171 | 10 | 15 | -103 | 7612.86 | 27.2003
| 40098.1115 | 59.966 | 3743.4187 |  |  |  | 27.2003 | 25.1661 |  | 0 | 3802.139 | 3767.2002 | 3786.3697 | 3776.2779 | 3755.2783 | 633 | [6 empty] | 0 | 633 | -841.189 | [13 empty] | 40098.1115 | 59.966 | 3743.4187 | 350 | -263.8732 | 0 | 171 | 10 | 15 | -103 | 7612.86 | 27.2003
| 40098.1115 | 59.971 | 3747.3396 |  |  |  | 23.1995 | 24.4778 |  | 0 | 3801.4507 | 3767.1504 | 3786.4075 | 3776.2779 | 3755.331 | 633 | [6 empty] | 0 | 633 | -901.0733 | [13 empty] | 40098.1115 | 59.971 | 3747.3396 | 350 | -264.5979 | 0 | 171.5 | 10 | 15 | -103 | 7613.19 | 23.1995
| 40098.1116 | 59.971 | 3747.3396 |  |  |  | 23.1995 | 24.0304 |  | 0 | 3801.0033 | 3767.1009 | 3786.444 | 3776.2779 | 3755.3835 | 633 | [6 empty] | 0 | 633 | -901.0733 | [13 empty] | 40098.1116 | 59.971 | 3747.3396 | 350 | -264.5979 | 0 | 171.5 | 10 | 15 | -103 | 7613.19 | 23.1995
| 40098.1116 | 59.971 | 3747.3396 |  |  |  | 23.1995 | 23.7395 |  | 0 | 3800.7125 | 3767.0516 | 3786.4796 | 3776.2779 | 3755.4358 | 633 | [6 empty] | 0 | 633 | -901.0733 | [13 empty] | 40098.1116 | 59.971 | 3747.3396 | 350 | -264.5979 | 0 | 171.5 | 10 | 15 | -103 | 7613.19 | 23.1995
| 40098.1116 | 59.969 | 3749.75 |  |  |  | 24.7986 | 24.1102 |  | 0 | 3801.0832 | 3767.0086 | 3786.5159 | 3776.2779 | 3755.4877 | 633 | [6 empty] | 0 | 633 | -876.1433 | [13 empty] | 40098.1116 | 59.969 | 3749.75 | 350 | -264.5979 | 0 | 172 | 10 | 15 | -103 | 7613.52 | 24.7986
| 40098.1116 | 59.969 | 3749.75 |  |  |  | 24.7986 | 24.3511 |  | 0 | 3801.3241 | 3766.9657 | 3786.5527 | 3776.2779 | 3755.5395 | 633 | [6 empty] | 0 | 633 | -876.1433 | [13 empty] | 40098.1116 | 59.969 | 3749.75 | 350 | -264.5979 | 0 | 172 | 10 | 15 | -103 | 7613.52 | 24.7986
| 40098.1116 | 59.974 | 3743.7451 |  |  |  | 20.8008 | 23.1085 |  | 0 | 3800.0815 | 3766.9083 | 3786.5862 | 3776.2779 | 3755.5909 | 633 | [6 empty] | 0 | 633 | -941.2471 | [13 empty] | 40098.1116 | 59.974 | 3743.7451 | 350 | -264.5979 | 0 | 172.5 | 10 | 15 | -103 | 7613.85 | 20.8008
| 40098.1117 | 59.974 | 3743.7451 |  |  |  | 20.8008 | 22.3008 |  | 0 | 3799.2738 | 3766.8511 | 3786.6175 | 3776.2779 | 3755.6421 | 633 | [6 empty] | 0 | 633 | -941.2471 | [13 empty] | 40098.1117 | 59.974 | 3743.7451 | 350 | -264.5979 | 0 | 172.5 | 10 | 15 | -103 | 7613.85 | 20.8008
| 40098.1117 | 59.974 | 3743.7451 |  |  |  | 20.8008 | 21.7758 |  | 0 | 3798.7488 | 3766.7942 | 3786.6474 | 3776.2779 | 3755.6931 | 633 | [6 empty] | 0 | 633 | -941.2471 | [13 empty] | 40098.1117 | 59.974 | 3743.7451 | 350 | -264.5979 | 0 | 172.5 | 10 | 15 | -103 | 7613.85 | 20.8008
| 40098.1117 | 59.971 | 3740.2986 |  |  |  | 23.1995 | 22.2741 |  | 0 | 3799.2471 | 3766.7291 | 3786.6783 | 3776.2779 | 3755.7438 | 633 | [6 empty] | 0 | 633 | -901.0733 | [13 empty] | 40098.1117 | 59.971 | 3740.2986 | 350 | -264.5979 | 0 | 173 | 10 | 15 | -103 | 7614.18 | 23.1995
| 40098.1117 | 59.971 | 3740.2986 |  |  |  | 23.1995 | 22.598 |  | 0 | 3799.5709 | 3766.6643 | 3786.7099 | 3776.2779 | 3755.7942 | 633 | [6 empty] | 0 | 633 | -901.0733 | [13 empty] | 40098.1117 | 59.971 | 3740.2986 | 350 | -264.5979 | 0 | 173 | 10 | 15 | -103 | 7614.18 | 23.1995
| 40098.1118 | 59.982 | 3731.8296 |  |  |  | 14.4012 | 19.7291 |  | 0 | 3796.7021 | 3766.5791 | 3786.7344 | 3776.2779 | 3755.8444 | 633 | [6 empty] | 0 | 633 | -1068.3222 | [13 empty] | 40098.1118 | 59.982 | 3731.8296 | 350 | -264.5979 | 0 | 173.5 | 10 | 15 | -103 | 7614.51 | 14.4012
| 40098.1118 | 59.982 | 3731.8296 |  |  |  | 14.4012 | 17.8644 |  | 0 | 3794.8373 | 3766.4944 | 3786.7541 | 3776.2779 | 3755.8944 | 633 | [6 empty] | 0 | 633 | -1068.3222 | [13 empty] | 40098.1118 | 59.982 | 3731.8296 | 350 | -264.5979 | 0 | 173.5 | 10 | 15 | -103 | 7614.51 | 14.4012
| 40098.1118 | 59.982 | 3731.8296 |  |  |  | 14.4012 | 16.6523 |  | 0 | 3793.6252 | 3766.41 | 3786.7708 | 3776.2779 | 3755.9441 | 633 | [6 empty] | 0 | 633 | -1068.3222 | [13 empty] | 40098.1118 | 59.982 | 3731.8296 | 350 | -264.5979 | 0 | 173.5 | 10 | 15 | -103 | 7614.51 | 14.4012
| 40098.1118 | 59.985 | 3736.2295 |  |  |  | 11.9995 | 15.0238 |  | 0 | 3791.9968 | 3766.3368 | 3786.7835 | 3776.2779 | 3755.9936 | 633 | [6 empty] | 0 | 633 | -1125.341 | [13 empty] | 40098.1118 | 59.985 | 3736.2295 | 350 | -262.4159 | 0 | 174 | 10 | 15 | -103 | 7614.84 | 11.9995
| 40098.1119 | 59.985 | 3736.2295 |  |  |  | 11.9995 | 13.9653 |  | 0 | 3790.9383 | 3766.2639 | 3786.7936 | 3776.2779 | 3756.0428 | 633 | [6 empty] | 0 | 633 | -1125.341 | [13 empty] | 40098.1119 | 59.985 | 3736.2295 | 350 | -262.4159 | 0 | 174 | 10 | 15 | -103 | 7614.84 | 11.9995
| 40098.1119 | 59.989 | 3733.1152 |  |  |  | 8.8013 | 12.1579 |  | 0 | 3789.1309 | 3766.1838 | 3786.7992 | 3776.2779 | 3756.0918 | 633 | [6 empty] | 0 | 633 | -1211.4412 | [13 empty] | 40098.1119 | 59.989 | 3733.1152 | 350 | -262.4159 | 0 | 174.5 | 10 | 15 | -103 | 7615.17 | 8.8013
| 40098.1119 | 59.989 | 3733.1152 |  |  |  | 8.8013 | 10.9831 |  | 0 | 3787.9561 | 3766.1041 | 3786.802 | 3776.2779 | 3756.1406 | 633 | [6 empty] | 0 | 633 | -1211.4412 | [13 empty] | 40098.1119 | 59.989 | 3733.1152 | 350 | -262.4159 | 0 | 174.5 | 10 | 15 | -103 | 7615.17 | 8.8013
| 40098.1119 | 59.989 | 3733.1152 |  |  |  | 8.8013 | 10.2194 |  | 0 | 3787.1924 | 3766.0248 | 3786.8029 | 3776.2779 | 3756.1891 | 633 | [6 empty] | 0 | 633 | -1211.4412 | [13 empty] | 40098.1119 | 59.989 | 3733.1152 | 350 | -262.4159 | 0 | 174.5 | 10 | 15 | -103 | 7615.17 | 8.8013
| 40098.1119 | 59.987 | 3729.1802 |  |  |  | 10.4004 | 10.2828 |  | 0 | 3787.2558 | 3765.9364 | 3786.804 | 3776.2779 | 3756.2374 | 633 | [6 empty] | 0 | 633 | -1166.8049 | [13 empty] | 40098.1119 | 59.987 | 3729.1802 | 350 | -262.4159 | 0 | 175 | 10 | 15 | -103 | 7615.5 | 10.4004
| 40098.112 | 59.987 | 3729.1802 |  |  |  | 10.4004 | 10.3239 |  | 0 | 3787.2969 | 3765.8485 | 3786.8052 | 3776.2779 | 3756.2854 | 633 | [6 empty] | 0 | 633 | -1166.8049 | [13 empty] | 40098.112 | 59.987 | 3729.1802 | 350 | -262.4159 | 0 | 175 | 10 | 15 | -103 | 7615.5 | 10.4004
| 40098.112 | 59.994 | 3720.1079 |  |  |  | 4.8004 | 8.3907 |  | 0 | 3785.3637 | 3765.7393 | 3786.8018 | 3776.2779 | 3756.3333 | 633 | [6 empty] | 0 | 633 | -1339.6613 | [13 empty] | 40098.112 | 59.994 | 3720.1079 | 350 | -262.4159 | 0 | 175.5 | 10 | 15 | -103 | 7615.83 | 4.8004
| 40098.112 | 59.994 | 3720.1079 |  |  |  | 4.8004 | 7.1341 |  | 0 | 3784.1071 | 3765.6307 | 3786.7954 | 3776.2779 | 3756.3809 | 633 | [6 empty] | 0 | 633 | -1339.6613 | [13 empty] | 40098.112 | 59.994 | 3720.1079 | 350 | -262.4159 | 0 | 175.5 | 10 | 15 | -103 | 7615.83 | 4.8004
| 40098.112 | 59.994 | 3720.1079 |  |  |  | 4.8004 | 6.3173 |  | 0 | 3783.2903 | 3765.5226 | 3786.787 | 3776.2779 | 3756.4282 | 633 | [6 empty] | 0 | 633 | -1339.6613 | [13 empty] | 40098.112 | 59.994 | 3720.1079 | 350 | -262.4159 | 0 | 175.5 | 10 | 15 | -103 | 7615.83 | 4.8004
| 40098.1121 | 60.003 | 3725.6614 |  |  |  | -2.3987 | 3.2667 |  | 0 | 3780.2397 | 3765.4281 | 3786.7715 | 3776.2779 | 3756.4754 | 633 | [6 empty] | 0 | 633 | -1654.8208 | [13 empty] | 40098.1121 | 60.003 | 3725.6614 | 350 | -262.4159 | 0 | 176 | 10 | 15 | -103 | 7616.16 | -2.3987
| 40098.1121 | 60.003 | 3725.6614 |  |  |  | -2.3987 | 1.2838 |  | 0 | 3778.2568 | 3765.3341 | 3786.7514 | 3776.2779 | 3756.5223 | 633 | [6 empty] | 0 | 633 | -1654.8208 | [13 empty] | 40098.1121 | 60.003 | 3725.6614 | 350 | -262.4159 | 0 | 176 | 10 | 15 | -103 | 7616.16 | -2.3987
| 40098.1121 | 60.006 | 3727.8247 |  |  |  | -4.8004 | -0.84566 |  | 0 | 3776.1273 | 3765.2456 | 3786.7263 | 3776.2779 | 3756.569 | 633 | [6 empty] | 0 | 633 | -1795.7595 | [13 empty] | 40098.1121 | 60.006 | 3727.8247 | 350 | -259.6852 | 0 | 176.5 | 10 | 15 | -103 | 7616.49 | -4.8004
| 40098.1121 | 60.006 | 3727.8247 |  |  |  | -4.8004 | -2.2298 |  | 0 | 3774.7432 | 3765.1576 | 3786.6981 | 3776.2779 | 3756.6155 | 633 | [6 empty] | 0 | 633 | -1795.7595 | [13 empty] | 40098.1121 | 60.006 | 3727.8247 | 350 | -259.6852 | 0 | 176.5 | 10 | 15 | -103 | 7616.49 | -4.8004
| 40098.1122 | 60.006 | 3727.8247 |  |  |  | -4.8004 | -3.1295 |  | 0 | 3773.8434 | 3765.07 | 3786.668 | 3776.2779 | 3756.6618 | 633 | [6 empty] | 0 | 633 | -1795.7595 | [13 empty] | 40098.1122 | 60.006 | 3727.8247 | 350 | -259.6852 | 0 | 176.5 | 10 | 15 | -103 | 7616.49 | -4.8004
| 40098.1122 | 60.019 | 3727.2314 |  |  |  | -15.2008 | -7.3545 |  | 0 | 3769.6185 | 3764.9813 | 3786.628 | 3776.2779 | 3756.7078 | 633 | [6 empty] | 0 | 633 | -2845.0433 | [13 empty] | 40098.1122 | 60.019 | 3727.2314 | 350 | -259.6852 | 0 | 177 | 10 | 15 | -103 | 7616.82 | -15.2008
| 40098.1122 | 60.019 | 3727.2314 |  |  |  | -15.2008 | -10.1007 |  | 0 | 3766.8723 | 3764.8931 | 3786.5819 | 3776.2779 | 3756.7536 | 633 | [6 empty] | 0 | 633 | -2845.0433 | [13 empty] | 40098.1122 | 60.019 | 3727.2314 | 350 | -259.6852 | 0 | 177 | 10 | 15 | -103 | 7616.82 | -15.2008
| 40098.1122 | 60.025 | 3726.0156 |  |  |  | -20.0012 | -13.5659 |  | 0 | 3763.4071 | 3764.8025 | 3786.5279 | 3776.2779 | 3756.7993 | 633 | [6 empty] | 0 | 633 | -3895.6956 | [13 empty] | 40098.1122 | 60.025 | 3726.0156 | 350 | -259.6852 | 0 | 177.5 | 10 | 15 | -103 | 7617.15 | -20.0012
| 40098.1122 | 60.025 | 3726.0156 |  |  |  | -20.0012 | -15.8182 |  | 0 | 3761.1547 | 3764.7123 | 3786.4688 | 3776.2779 | 3756.8447 | 633 | [6 empty] | 0 | 633 | -3895.6956 | [13 empty] | 40098.1122 | 60.025 | 3726.0156 | 350 | -259.6852 | 0 | 177.5 | 10 | 15 | -103 | 7617.15 | -20.0012
| 40098.1123 | 60.025 | 3726.0156 |  |  |  | -20.0012 | -17.2823 |  | 0 | 3759.6907 | 3764.6225 | 3786.4067 | 3776.2779 | 3756.8899 | 633 | [6 empty] | 0 | 633 | -3895.6956 | [13 empty] | 40098.1123 | 60.025 | 3726.0156 | 350 | -259.6852 | 0 | 177.5 | 10 | 15 | -103 | 7617.15 | -20.0012
| 40098.1123 | 60.029 | 3716.3745 |  |  |  | -23.1995 | -19.3533 |  | 0 | 3757.6197 | 3764.5108 | 3786.3401 | 3776.2779 | 3756.9348 | 633 | [6 empty] | 0 | 633 | -5166.9672 | [13 empty] | 40098.1123 | 60.029 | 3716.3745 | 350 | -259.6852 | 0 | 178 | 10 | 15 | -103 | 7617.48 | -23.1995
| 40098.1123 | 60.029 | 3716.3745 |  |  |  | -23.1995 | -20.6995 |  | 0 | 3756.2735 | 3764.3997 | 3786.2706 | 3776.2779 | 3756.9796 | 633 | [6 empty] | 0 | 633 | -5166.9672 | [13 empty] | 40098.1123 | 60.029 | 3716.3745 | 350 | -259.6852 | 0 | 178 | 10 | 15 | -103 | 7617.48 | -23.1995
| 40098.1123 | 60.037 | 3717.1421 |  |  |  | -29.599 | -23.8143 |  | 0 | 3753.1587 | 3764.2908 | 3786.1943 | 3776.2779 | 3757.0242 | 633 | [6 empty] | 0 | 633 | -14888.9324 | [13 empty] | 40098.1123 | 60.037 | 3717.1421 | 350 | -259.6852 | 0 | 178.5 | 10 | 15 | -103 | 7617.81 | -29.599
| 40098.1124 | 60.037 | 3717.1421 |  |  |  | -29.599 | -25.8389 |  | 0 | 3751.134 | 3764.1824 | 3786.1137 | 3776.2779 | 3757.0685 | 633 | [6 empty] | 0 | 633 | -14888.9324 | [13 empty] | 40098.1124 | 60.037 | 3717.1421 | 350 | -259.6852 | 0 | 178.5 | 10 | 15 | -103 | 7617.81 | -29.599
| 40098.1124 | 60.037 | 3717.1421 |  |  |  | -29.599 | -27.155 |  | 0 | 3749.818 | 3764.0745 | 3786.0305 | 3776.2779 | 3757.1127 | 633 | [6 empty] | 0 | 633 | -14888.9324 | [13 empty] | 40098.1124 | 60.037 | 3717.1421 | 350 | -259.6852 | 0 | 178.5 | 10 | 15 | -103 | 7617.81 | -29.599
| 40098.1124 | 60.037 | 3713.6318 |  |  |  | -29.599 | -28.0104 |  | 0 | 3748.9626 | 3763.9591 | 3785.9457 | 3776.2779 | 3757.1567 | 633 | [6 empty] | 0 | 633 | -14888.9324 | [13 empty] | 40098.1124 | 60.037 | 3713.6318 | 350 | -255.911 | 0 | 179 | 10 | 15 | -103 | 7618.14 | -29.599
| 40098.1124 | 60.037 | 3713.6318 |  |  |  | -29.599 | -28.5664 |  | 0 | 3748.4066 | 3763.8442 | 3785.86 | 3776.2779 | 3757.2004 | 633 | [6 empty] | 0 | 633 | -14888.9324 | [13 empty] | 40098.1124 | 60.037 | 3713.6318 | 350 | -255.911 | 0 | 179 | 10 | 15 | -103 | 7618.14 | -29.599
| 40098.1125 | 60.041 | 3699.3557 |  |  |  | -32.8003 | -30.0483 |  | 0 | 3746.9247 | 3763.6973 | 3785.7713 | 3776.2779 | 3757.244 | 633 | [6 empty] | 0 | 633 | -253339.1634 | [13 empty] | 40098.1125 | 60.041 | 3699.3557 | 350 | -255.911 | 0 | 179.5 | 10 | 15 | -103 | 7618.47 | -32.8003
| 40098.1125 | 60.041 | 3699.3557 |  |  |  | -32.8003 | -31.0115 |  | 0 | 3745.9615 | 3763.551 | 3785.6808 | 3776.2779 | 3757.2873 | 633 | [6 empty] | 0 | 633 | -253339.1634 | [13 empty] | 40098.1125 | 60.041 | 3699.3557 | 350 | -255.911 | 0 | 179.5 | 10 | 15 | -103 | 7618.47 | -32.8003
| 40098.1125 | 60.041 | 3699.3557 |  |  |  | -32.8003 | -31.6376 |  | 0 | 3745.3354 | 3763.4055 | 3785.5893 | 3776.2779 | 3757.3305 | 633 | [6 empty] | 0 | 633 | -253339.1634 | [13 empty] | 40098.1125 | 60.041 | 3699.3557 | 350 | -255.911 | 0 | 179.5 | 10 | 15 | -103 | 7618.47 | -32.8003
| 40098.1125 | 60.043 | 3704.5913 |  |  |  | -34.3994 | -32.6042 |  | 0 | 3744.3688 | 3763.2724 | 3785.4961 | 3776.2779 | 3757.3735 | 633 | [6 empty] | 0 | 633 | 36191.3091 | [13 empty] | 40098.1125 | 60.043 | 3704.5913 | 350 | -255.911 | 0 | 180 | 10 | 15 | -103 | 7618.8 | -34.3994
| 40098.1125 | 60.043 | 3704.5913 |  |  |  | -34.3994 | -33.2325 |  | 0 | 3743.7404 | 3763.1399 | 3785.4018 | 3776.2779 | 3757.4162 | 633 | [6 empty] | 0 | 633 | 36191.3091 | [13 empty] | 40098.1125 | 60.043 | 3704.5913 | 350 | -255.911 | 0 | 180 | 10 | 15 | -103 | 7618.8 | -34.3994
| 40098.1126 | 60.048 | 3701.3164 |  |  |  | -38.4003 | -35.0412 |  | 0 | 3741.9317 | 3763.0007 | 3785.3039 | 3776.2779 | 3757.4588 | 633 | [6 empty] | 0 | 633 | 9377.6294 | [13 empty] | 40098.1126 | 60.048 | 3701.3164 | 350 | -255.911 | 0 | 180.5 | 10 | 15 | -103 | 7619.13 | -38.4003
| 40098.1126 | 60.048 | 3701.3164 |  |  |  | -38.4003 | -36.2169 |  | 0 | 3740.7561 | 3762.8621 | 3785.2038 | 3776.2779 | 3757.5012 | 633 | [6 empty] | 0 | 633 | 9377.6294 | [13 empty] | 40098.1126 | 60.048 | 3701.3164 | 350 | -255.911 | 0 | 180.5 | 10 | 15 | -103 | 7619.13 | -38.4003
| 40098.1126 | 60.048 | 3701.3164 |  |  |  | -38.4003 | -36.9811 |  | 0 | 3739.9919 | 3762.7241 | 3785.1024 | 3776.2779 | 3757.5434 | 633 | [6 empty] | 0 | 633 | 9377.6294 | [13 empty] | 40098.1126 | 60.048 | 3701.3164 | 350 | -255.911 | 0 | 180.5 | 10 | 15 | -103 | 7619.13 | -38.4003
| 40098.1126 | 60.043 | 3699.5286 |  |  |  | -34.3994 | -36.0775 |  | 0 | 3740.8955 | 3762.5827 | 3785.0035 | 3776.2779 | 3757.5854 | 633 | [6 empty] | 0 | 633 | 36191.3091 | [13 empty] | 40098.1126 | 60.043 | 3699.5286 | 350 | -255.911 | 0 | 181 | 10 | 15 | -103 | 7619.46 | -34.3994
| 40098.1127 | 60.043 | 3699.5286 |  |  |  | -34.3994 | -35.4902 |  | 0 | 3741.4828 | 3762.442 | 3784.9064 | 3776.2779 | 3757.6272 | 633 | [6 empty] | 0 | 633 | 36191.3091 | [13 empty] | 40098.1127 | 60.043 | 3699.5286 | 350 | -255.911 | 0 | 181 | 10 | 15 | -103 | 7619.46 | -34.3994
| 40098.1127 | 60.044 | 3690.4773 |  |  |  | -35.199 | -35.3882 |  | 0 | 3741.5847 | 3762.2817 | 3784.8099 | 3776.2779 | 3757.6688 | 633 | [6 empty] | 0 | 633 | 23030.833 | [13 empty] | 40098.1127 | 60.044 | 3690.4773 | 350 | -258.1482 | 0 | 181.5 | 10 | 15 | -103 | 7619.79 | -35.199
| 40098.1127 | 60.044 | 3690.4773 |  |  |  | -35.199 | -35.322 |  | 0 | 3741.651 | 3762.1221 | 3784.714 | 3776.2779 | 3757.7103 | 633 | [6 empty] | 0 | 633 | 23030.833 | [13 empty] | 40098.1127 | 60.044 | 3690.4773 | 350 | -258.1482 | 0 | 181.5 | 10 | 15 | -103 | 7619.79 | -35.199
| 40098.1127 | 60.044 | 3690.4773 |  |  |  | -35.199 | -35.2789 |  | 0 | 3741.694 | 3761.9633 | 3784.6186 | 3776.2779 | 3757.7515 | 633 | [6 empty] | 0 | 633 | 23030.833 | [13 empty] | 40098.1127 | 60.044 | 3690.4773 | 350 | -258.1482 | 0 | 181.5 | 10 | 15 | -103 | 7619.79 | -35.199
Note on L13: TC allowable range 0.050 to 1.000 with 1.0 turning filter off. Beginning Target slope should align with Actual slope.

## Graph 20 to 52s
60.0413

## Form 1 Summary Data
[6 empty] | Interconnection Performance | [9 empty] | Value A Data |  | BA Performance | [8 empty] | Value B |  | 12 to 24 second Average Period Evaluation | [11 empty] | Value B | 18 to 30 second Average Period Evaluation | [12 empty] | Value B | 20 to 40 second Average Period Evaluation | [12 empty] | Value B | 18 to 52 second Average Period Evaluation | [12 empty] | Value B | 20 to 52 second Average Period Evaluation
[18 empty] | JOU | Non- |  |  | Transferred | Contingent | [5 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent
Date | A Point | FPointA | A Value | t(0) Time | C Value | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias
| Time | Hz | Hz |  | Hz | 12 to 24 sec | 12 to 24 sec | 18 to 30 sec | 18 to 30 sec | 20 to 40 sec | 20 to 40 sec | 18 to 52 sec | 18 to 52 sec | 20 to 52 sec | 20 to 52 sec |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting
[6 empty] | Average | Average | Average | Average | Average | Average | Average | Average | Average | Average | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR
[6 empty] | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Hz | MW | MW | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW | Hz | MW | MW | MW | MW | MW | MW | MW | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | P.U. | P.U. | P.U. | MW | MW | MW | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | P.U. | P.U. | P.U. | MW | MW | MW | Hz | MW | MW | MW | MW | MW | MW | MW | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW | Hz | MW | MW | MW | MW | MW | MW | MW | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW
2009-10-12 02:27 | 40098.1023 | 60.041 | 60.0413 | 40098.1023 | 59.852 | 59.8796 | -391.8344 | 59.8833 | -401.1562 | 59.8883 | -415.8128 | 59.8876 | -412.3889 | 59.8883 | -414.2499 | 60.0413 | 3649.0017 | 350 | -165.4764 | 0 | 90.875 | -4.125 | 15 | -103 | 7559.9775 | -42.4877 | 59.8796 | 3758.9636 | 335 | -206.4591 | 1 | 93.5 | 12.0428 | 0 | 1.2459 | 0.85016 | 0.86762 | -103 | 7561.71 | 124.0406 | 59.8833 | 3774.248 | 335 | -208.5149 | 1 | 94.0714 | 11.6713 | 0 | 1.4109 | 0.9911 | 0.86762 | -103 | 7562.0871 | 120.2148 | 59.8888 | 3780.7259 | 335 | -209.9478 | 1.2727 | 94.6818 | 11.1181 | 0 | 1.5242 | 1.0802 | 0.86762 | -103 | 7562.49 | 114.5162 | 59.8876 | 3784.1485 | 335 | -210.3618 | 2.1111 | 95.1944 | 11.2444 | 0 | 1.5309 | 1.0992 | 0.86762 | -103 | 7562.8283 | 115.8175 | 59.8883 | 3785.2046 | 335 | -165.4764 | 2.1765 | 95.2941 | 11.1706 | 0 | 1.5481 | 1.1131 | 0.86762 | -103 | 7562.8941 | 115.0567