## Instructions
Steps | To be completed for each event evaluated.
1 | Set-up Data collection in exact same order as the "Data" sheet of this work book. Data should be in this order:
Column A: Date and Time in this format, mm/dd/yy HH:MM:SS
Column B: Frequency Hz
Column C: Net Actual Interchange
Column D: Joint Owned Unit dynamic schedule
Column E: Non Conforming Load
Column F: Pumped Hydro
Column G: Ramping units
Column H: Transferred Frequency Response
Column I: Contingent BA Lost load or generation
Column J: BA Bias Setting
Column K: BA Load
2 | Note: Columns D, E, F, G and H are optional data. If you choose not to use these, leave the columns blank. Do not delete the columns. Use the sign (+/-) convention defined in FRS Form 1.
3 | Data compression must be turned off for each data point. Quality data will give you quality results in the evaluation.
4 | Data must be at 6 second sample rate for the full 25 minute minimum collection period that starts a minimum of two (2) minutes before the event begins and includes a minimum of 15 minutes after the beginning of the event.
The spreadsheet will work with up to 60 minutes of data. Be sure "Data" worksheet is clear of any old data.
If using PI historian as your data source, use "PasteSpecial/Values" to enter data into the spreadsheet. Do not include historian data collection formulas in the data. The data must be numbers not text.
5 | Once data is in place in the "Data" worksheet, determine when the beginning of the event occurred. This is accomplished by knowing the UTC event time from the master event list.
Convert the UTC event time to your PI data time and then scroll through the Data worksheet column B data of frequency and observe when frequency moves from the normal, pre-event frequency.
This will usually be a single change in frequency of 0.008 to 0.010 Hz more or less. Note the row number in the worksheet that this change occurs. In this sample data spreadsheet this occurs in row 160 of the data.
6 | Edit cell "C8" of the "Entry Data" worksheet, change the formula in the cell "C8" to reference the row number identified in step 5 above. In the sample data of this workbook this formula is: "=Data!A160"
If the correct row is selected, the "Graph 20 to 52s" worksheet will indicate the first change in frequency of the event on the center vertical grid line of the graph (Red Trend).
7 | Determine the end of the event to be evaluated. Use the same rules that are used for DCS only look at frequency instead of ACE. Scroll down the frequency data in column B of the "Data" worksheet until frequency reaches 60 Hz or the
pre-disturbance value. Note the row number in the worksheet that this occurs. In this sample data spreadsheet this occurs in row 217.
8 | Edit cell "C11" of the "Entry Data" worksheet, change the formula in the cell "C11" to reference the row number identified in step 7 above. In the sample data of this workbook this formula is: "=Data!A217"
9 | In cell "R41" of the "Evaluation" spreadsheet, enter the MW value of the unit(s) that tripped (from the Master Event List). This is only necessary for the "Interconnection" evaluation if your interested.
It is not necessary to do this for the BA evaluation but it will provide a comparison of the BA frequency response as compared to the Interconnection frequency response.
10 | Use the "copy" button provided to copy the evaluation and event specific data for the "FRS Form 1" of this field trial. This data is summarized in the correct order on worksheet "Form 1 Summary Data" of this workbook.
Use PasteSpecial/Values when pasting the data into FRS Form 1 on the appropriate event row.
Steps | To be completed once at the initial setup of the evaluation spreadsheet for your BA.
A | Enter the Balancing Authority name as you want it to appear on the graphs in cell "B1" of the "Entry Data" worksheet. For example: "NYISO".
B | Enter your Balancing Authorities Frequency Response Obligation in cell "B2" of the "Entry Data" worksheet. For example: -80 MW/0.1 Hz (This value could change annually)
C | For informational and educational purposes, a "Sustained" performance evaluation is provided in the "Evaluation" worksheet and in the "Sustained" Graph. This evaluation uses a Time Constant (TC) to model the frequency response of your BA.
The time constant is located in cell "L13" of the "Evaluation" spreadsheet and should be edited for the types of generators in your BA. Presently this time constant is set at 0.35.
The higher the value of the time constant, the faster the delivery of frequency response is expected. Setting the TC to 1.0 effectively turns off the delay and instantaneous frequency response will be modeled. Do not set higher than 1.0.
This time constant is only used in the "Sustained" evaluation and is not used for the Field Trial evaluation of performance to the FRO.
A typical setting for this time constant is 0.08 to 0.15 for hydro units, 0.10 to 0.20 for large steam turbines and 0.20 to 0.40 for combustion turbines.
By observing the slope of your "Interchange Actual" on the "Sustained" Graph, adjust the time constant until the initial slope of the "Target" is similar.
When set appropriately, the "Target" trend on the "Sustained" graph will model what Interchange Actual should have done during the event recovery period.
Note: For ease of use, only the necessary worksheets are displayed. If you are interested in viewing graphs and other hidded worksheets, select the "tab" at the bottom, right click, select unhide and select the worksheet you wish to unhide.

## Data
|  |  | JOU | Non- |  |  | Transferred | Contingent
|  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA
|  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load
|  | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting
Time (T) | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW
2009-10-12 02:12 | 59.981 | 3669.8784 | 350 | 351.3615 | 0 | 0 | 10 | 15 | -103 | 7500
2009-10-12 02:12 | 59.98 | 3670.9492 | 350 | 351.3615 | 0 | 0.5 | 10 | 15 | -103 | 7500.99
2009-10-12 02:12 | 59.981 | 3672.3103 | 350 | 351.3615 | 0 | 1 | 10 | 15 | -103 | 7501.98
2009-10-12 02:12 | 59.982 | 3672.2761 | 350 | 357.9475 | 0 | 1.5 | 10 | 15 | -103 | 7502.97
2009-10-12 02:12 | 59.98 | 3673.8438 | 350 | 357.9475 | 0 | 2 | 10 | 15 | -103 | 7503.96
2009-10-12 02:12 | 59.986 | 3669.3303 | 350 | 357.9475 | 0 | 2.5 | 10 | 15 | -103 | 7504.95
2009-10-12 02:13 | 59.976 | 3673.5603 | 350 | 357.9475 | 0 | 3 | 10 | 15 | -103 | 7505.94
2009-10-12 02:13 | 59.981 | 3671.8872 | 350 | 357.9475 | 0 | 3.5 | 10 | 15 | -103 | 7506.93
2009-10-12 02:13 | 59.99 | 3671.5603 | 350 | 360.2347 | 0 | 4 | 10 | 15 | -103 | 7507.92
2009-10-12 02:13 | 59.995 | 3668.3621 | 350 | 360.2347 | 0 | 4.5 | 10 | 15 | -103 | 7508.91
2009-10-12 02:13 | 59.995 | 3669.2913 | 350 | 360.2347 | 0 | 5 | 10 | 15 | -103 | 7509.9
2009-10-12 02:13 | 59.994 | 3670.6833 | 350 | 360.2347 | 0 | 5.5 | 10 | 15 | -103 | 7510.89
2009-10-12 02:13 | 60.001 | 3670.7124 | 350 | 360.2347 | 0 | 6 | 10 | 15 | -103 | 7511.88
2009-10-12 02:13 | 60.003 | 3671.2271 | 350 | 346.5259 | 0 | 6.5 | 10 | 15 | -103 | 7512.87
2009-10-12 02:13 | 60.003 | 3671.0923 | 350 | 346.5259 | 0 | 7 | 10 | 15 | -103 | 7513.86
2009-10-12 02:13 | 60.003 | 3669.8992 | 350 | 346.5259 | 0 | 7.5 | 10 | 15 | -103 | 7514.85
2009-10-12 02:14 | 60.001 | 3671.6284 | 350 | 346.5259 | 0 | 8 | 10 | 15 | -103 | 7515.84
2009-10-12 02:14 | 60.004 | 3671.4443 | 350 | 346.5259 | 0 | 8.5 | 10 | 15 | -103 | 7516.83
2009-10-12 02:14 | 60.004 | 3671.0657 | 350 | 296.4434 | 0 | 9 | 10 | 15 | -103 | 7517.82
2009-10-12 02:14 | 60.002 | 3673.4978 | 350 | 296.4434 | 0 | 9.5 | 10 | 15 | -103 | 7518.81
2009-10-12 02:14 | 59.999 | 3673.1863 | 350 | 296.4434 | 0 | 10 | 10 | 15 | -103 | 7519.8
2009-10-12 02:14 | 59.998 | 3673.365 | 350 | 296.4434 | 0 | 10.5 | 10 | 15 | -103 | 7520.79
2009-10-12 02:14 | 59.993 | 3671.998 | 350 | 296.4434 | 0 | 11 | 10 | 15 | -103 | 7521.78
2009-10-12 02:14 | 59.999 | 3670.9568 | 350 | 341.0612 | 0 | 11.5 | 10 | 15 | -103 | 7522.77
2009-10-12 02:14 | 60.007 | 3670.1619 | 350 | 341.0612 | 0 | 12 | 10 | 15 | -103 | 7523.76
2009-10-12 02:14 | 60.002 | 3672.7129 | 350 | 341.0612 | 0 | 12.5 | 10 | 15 | -103 | 7524.75
2009-10-12 02:15 | 59.999 | 3670.8257 | 350 | 341.0612 | 0 | 13 | 10 | 15 | -103 | 7525.74
2009-10-12 02:15 | 60.01 | 3673.3633 | 350 | 341.0612 | 0 | 13.5 | 10 | 15 | -103 | 7526.73
2009-10-12 02:15 | 60.003 | 3674.4146 | 350 | 322.8263 | 0 | 14 | 10 | 15 | -103 | 7527.72
2009-10-12 02:15 | 59.994 | 3674.29 | 350 | 322.8263 | 0 | 14.5 | 10 | 15 | -103 | 7528.71
2009-10-12 02:15 | 60.001 | 3675.1655 | 350 | 322.8263 | 0 | 15 | 10 | 15 | -103 | 7529.7
2009-10-12 02:15 | 59.995 | 3674.9065 | 350 | 322.8263 | 0 | 15.5 | 10 | 15 | -103 | 7530.69
2009-10-12 02:15 | 59.986 | 3677.791 | 350 | 322.8263 | 0 | 16 | 10 | 15 | -103 | 7531.68
2009-10-12 02:15 | 59.989 | 3676.593 | 350 | 321.5444 | 0 | 16.5 | 10 | 15 | -103 | 7532.67
2009-10-12 02:15 | 59.985 | 3677.0671 | 350 | 321.5444 | 0 | 17 | 10 | 15 | -103 | 7533.66
2009-10-12 02:16 | 59.982 | 3679.2278 | 350 | 321.5444 | 0 | 17.5 | 10 | 15 | -103 | 7534.65
2009-10-12 02:16 | 59.985 | 3677.627 | 350 | 321.5444 | 0 | 18 | 10 | 15 | -103 | 7535.64
2009-10-12 02:16 | 59.99 | 3677.5281 | 350 | 321.5444 | 0 | 18.5 | 10 | 15 | -103 | 7536.63
2009-10-12 02:16 | 59.983 | 3678.0864 | 350 | 362.1363 | 0 | 19 | 10 | 15 | -103 | 7537.62
2009-10-12 02:16 | 59.983 | 3679.2134 | 350 | 362.1363 | 0 | 19.5 | 10 | 15 | -103 | 7538.61
2009-10-12 02:16 | 59.988 | 3677.6777 | 350 | 362.1363 | 0 | 20 | 10 | 15 | -103 | 7539.6
2009-10-12 02:16 | 59.978 | 3678.7295 | 350 | 362.1363 | 0 | 20.5 | 10 | 15 | -103 | 7540.59
2009-10-12 02:16 | 59.989 | 3679.0259 | 350 | 362.1363 | 0 | 21 | 10 | 15 | -103 | 7541.58
2009-10-12 02:16 | 59.983 | 3678.7202 | 350 | 336.3118 | 0 | 21.5 | 10 | 15 | -103 | 7542.57
2009-10-12 02:16 | 59.989 | 3679.3901 | 350 | 336.3118 | 0 | 22 | 10 | 15 | -103 | 7543.56
2009-10-12 02:17 | 59.995 | 3678.4905 | 350 | 336.3118 | 0 | 22.5 | 10 | 15 | -103 | 7544.55
2009-10-12 02:17 | 59.998 | 3678.9509 | 350 | 336.3118 | 0 | 23 | 10 | 15 | -103 | 7545.54
2009-10-12 02:17 | 59.995 | 3679.9033 | 350 | 336.3118 | 0 | 23.5 | 10 | 15 | -103 | 7546.53
2009-10-12 02:17 | 59.995 | 3677.8604 | 350 | 316.4431 | 0 | 24 | 10 | 15 | -103 | 7547.52
2009-10-12 02:17 | 60.003 | 3677.6855 | 350 | 316.4431 | 0 | 24.5 | 10 | 15 | -103 | 7548.51
2009-10-12 02:17 | 60.009 | 3679.2087 | 350 | 316.4431 | 0 | 25 | 10 | 15 | -103 | 7549.5
2009-10-12 02:17 | 60.011 | 3679.0566 | 350 | 316.4431 | 0 | 25.5 | 10 | 15 | -103 | 7550.49
2009-10-12 02:17 | 60.007 | 3679.8059 | 350 | 316.4431 | 0 | 26 | 10 | 15 | -103 | 7551.48
2009-10-12 02:17 | 60.013 | 3679.8511 | 350 | 325.4643 | 0 | 26.5 | 10 | 15 | -103 | 7552.47
2009-10-12 02:17 | 60.007 | 3679.4399 | 350 | 325.4643 | 0 | 27 | 10 | 15 | -103 | 7553.46
2009-10-12 02:18 | 60.006 | 3679.8879 | 350 | 325.4643 | 0 | 27.5 | 10 | 15 | -103 | 7554.45
2009-10-12 02:18 | 60.009 | 3679.2607 | 350 | 325.4643 | 0 | 28 | 10 | 15 | -103 | 7555.44
2009-10-12 02:18 | 60.009 | 3679.1521 | 350 | 325.4643 | 0 | 28.5 | 10 | 15 | -103 | 7556.43
2009-10-12 02:18 | 60.001 | 3678.2488 | 350 | 336.6142 | 0 | 29 | 10 | 15 | -103 | 7557.42
2009-10-12 02:18 | 59.991 | 3677.9548 | 350 | 336.6142 | 0 | 29.5 | 10 | 15 | -103 | 7558.41
2009-10-12 02:18 | 59.994 | 3677.0933 | 350 | 336.6142 | 0 | 30 | 10 | 15 | -103 | 7559.4
2009-10-12 02:18 | 59.995 | 3678.5156 | 350 | 336.6142 | 0 | 30.5 | 10 | 15 | -103 | 7560.39
2009-10-12 02:18 | 59.99 | 3678.7432 | 350 | 336.6142 | 0 | 31 | 10 | 15 | -103 | 7561.38
2009-10-12 02:18 | 59.977 | 3680.2537 | 350 | 316.7262 | 0 | 31.5 | 10 | 15 | -103 | 7562.37
2009-10-12 02:18 | 59.995 | 3678.6555 | 350 | 316.7262 | 0 | 32 | 10 | 15 | -103 | 7563.36
2009-10-12 02:18 | 59.989 | 3678.4268 | 350 | 316.7262 | 0 | 32.5 | 10 | 15 | -103 | 7564.35
2009-10-12 02:19 | 59.984 | 3677.8223 | 350 | 316.7262 | 0 | 33 | 10 | 15 | -103 | 7565.34
2009-10-12 02:19 | 59.986 | 3677.917 | 350 | 316.7262 | 0 | 33.5 | 10 | 15 | -103 | 7566.33
2009-10-12 02:19 | 59.98 | 3678.9626 | 350 | 320.1955 | 0 | 34 | 10 | 15 | -103 | 7567.32
2009-10-12 02:19 | 59.989 | 3680.0449 | 350 | 320.1955 | 0 | 34.5 | 10 | 15 | -103 | 7568.31
2009-10-12 02:19 | 60.007 | 3676.2222 | 350 | 320.1955 | 0 | 35 | 10 | 15 | -103 | 7569.3
2009-10-12 02:19 | 59.981 | 3677.49 | 350 | 320.1955 | 0 | 35.5 | 10 | 15 | -103 | 7570.29
2009-10-12 02:19 | 59.976 | 3680.4509 | 350 | 320.1955 | 0 | 36 | 10 | 15 | -103 | 7571.28
2009-10-12 02:19 | 59.977 | 3682.8433 | 350 | 341.8661 | 0 | 36.5 | 10 | 15 | -103 | 7572.27
2009-10-12 02:19 | 59.982 | 3678.229 | 350 | 341.8661 | 0 | 37 | 10 | 15 | -103 | 7573.26
2009-10-12 02:20 | 59.988 | 3671.9424 | 350 | 341.8661 | 0 | 37.5 | 10 | 15 | -103 | 7574.25
2009-10-12 02:20 | 59.987 | 3670.1287 | 350 | 341.8661 | 0 | 38 | 10 | 15 | -103 | 7575.24
2009-10-12 02:20 | 59.984 | 3671.5757 | 350 | 341.8661 | 0 | 38.5 | 10 | 15 | -103 | 7576.23
2009-10-12 02:20 | 59.989 | 3671.8823 | 350 | 348.5978 | 0 | 39 | 10 | 15 | -103 | 7577.22
2009-10-12 02:20 | 59.984 | 3670.7258 | 350 | 348.5978 | 0 | 39.5 | 10 | 15 | -103 | 7578.21
2009-10-12 02:20 | 59.981 | 3671.4009 | 350 | 348.5978 | 0 | 40 | 10 | 15 | -103 | 7579.2
2009-10-12 02:20 | 59.986 | 3670.2964 | 350 | 348.5978 | 0 | 40.5 | 10 | 15 | -103 | 7580.19
2009-10-12 02:20 | 59.985 | 3669.9082 | 350 | 348.5978 | 0 | 41 | 10 | 15 | -103 | 7581.18
2009-10-12 02:20 | 59.983 | 3669.3823 | 350 | 329.085 | 0 | 41.5 | 10 | 15 | -103 | 7582.17
2009-10-12 02:20 | 59.979 | 3671.4026 | 350 | 329.085 | 0 | 42 | 10 | 15 | -103 | 7583.16
2009-10-12 02:20 | 59.98 | 3671.947 | 350 | 329.085 | 0 | 42.5 | 10 | 15 | -103 | 7584.15
2009-10-12 02:21 | 59.98 | 3670.1372 | 350 | 329.085 | 0 | 43 | 10 | 15 | -103 | 7585.14
2009-10-12 02:21 | 59.979 | 3672.5579 | 350 | 329.085 | 0 | 43.5 | 10 | 15 | -103 | 7586.13
2009-10-12 02:21 | 59.976 | 3671.8003 | 350 | 342.4182 | 0 | 44 | 10 | 15 | -103 | 7587.12
2009-10-12 02:21 | 59.971 | 3676.2627 | 350 | 342.4182 | 0 | 44.5 | 10 | 15 | -103 | 7588.11
2009-10-12 02:21 | 59.973 | 3676.543 | 350 | 342.4182 | 0 | 45 | 10 | 15 | -103 | 7589.1
2009-10-12 02:21 | 59.975 | 3675.2559 | 350 | 342.4182 | 0 | 45.5 | 10 | 15 | -103 | 7590.09
2009-10-12 02:21 | 59.975 | 3671.5933 | 350 | 342.4182 | 0 | 46 | 10 | 15 | -103 | 7591.08
2009-10-12 02:21 | 59.979 | 3669.54 | 350 | 338.7946 | 0 | 46.5 | 10 | 15 | -103 | 7592.07
2009-10-12 02:21 | 59.982 | 3667.6765 | 350 | 338.7946 | 0 | 47 | 10 | 15 | -103 | 7593.06
2009-10-12 02:22 | 59.981 | 3666.9106 | 350 | 338.7946 | 0 | 47.5 | 10 | 15 | -103 | 7594.05
2009-10-12 02:22 | 59.985 | 3667.4563 | 350 | 338.7946 | 0 | 48 | 10 | 15 | -103 | 7595.04
2009-10-12 02:22 | 59.993 | 3664.031 | 350 | 338.7946 | 0 | 48.5 | 10 | 15 | -103 | 7596.03
2009-10-12 02:22 | 59.998 | 3662.0549 | 350 | 335.931 | 0 | 49 | 10 | 15 | -103 | 7597.02
2009-10-12 02:22 | 60.01 | 3662.2239 | 350 | 335.931 | 0 | 49.5 | 10 | 15 | -103 | 7598.01
2009-10-12 02:22 | 60.013 | 3664.1392 | 350 | 335.931 | 0 | 50 | 10 | 15 | -103 | 7599
2009-10-12 02:22 | 60.01 | 3663.2646 | 350 | 335.931 | 0 | 50.5 | 10 | 15 | -103 | 7599.99
2009-10-12 02:22 | 60.023 | 3661.5122 | 350 | 335.931 | 0 | 51 | 10 | 15 | -103 | 7600.98
2009-10-12 02:22 | 60.021 | 3656.7854 | 350 | 339.7124 | 0 | 51.5 | 10 | 15 | -103 | 7601.97
2009-10-12 02:22 | 60.019 | 3657.7104 | 350 | 339.7124 | 0 | 52 | 10 | 15 | -103 | 7602.96
2009-10-12 02:22 | 60.025 | 3659.2236 | 350 | 339.7124 | 0 | 52.5 | 10 | 15 | -103 | 7603.95
2009-10-12 02:23 | 60.02 | 3658.1545 | 350 | 339.7124 | 0 | 53 | 10 | 15 | -103 | 7604.94
2009-10-12 02:23 | 60.018 | 3660.8196 | 350 | 339.7124 | 0 | 53.5 | 10 | 15 | -103 | 7605.93
2009-10-12 02:23 | 60.019 | 3662.0789 | 350 | 332.0247 | 0 | 54 | 10 | 15 | -103 | 7606.92
2009-10-12 02:23 | 60.022 | 3663.5767 | 350 | 332.0247 | 0 | 54.5 | 10 | 15 | -103 | 7607.91
2009-10-12 02:23 | 60.02 | 3662.5525 | 350 | 332.0247 | 0 | 55 | 10 | 15 | -103 | 7608.9
2009-10-12 02:23 | 60.02 | 3663.9097 | 350 | 332.0247 | 0 | 55.5 | 10 | 15 | -103 | 7609.89
2009-10-12 02:23 | 60.018 | 3663.3958 | 350 | 332.0247 | 0 | 56 | 10 | 15 | -103 | 7610.88
2009-10-12 02:23 | 60.014 | 3665.313 | 350 | 330.759 | 0 | 56.5 | 10 | 15 | -103 | 7611.87
2009-10-12 02:23 | 60.01 | 3666.7258 | 350 | 330.759 | 0 | 57 | 10 | 15 | -103 | 7612.86
2009-10-12 02:24 | 60.011 | 3666.6882 | 350 | 330.759 | 0 | 57.5 | 10 | 15 | -103 | 7613.85
2009-10-12 02:24 | 60.009 | 3667.696 | 350 | 330.759 | 0 | 58 | 10 | 15 | -103 | 7614.84
2009-10-12 02:24 | 60.009 | 3666.6235 | 350 | 330.759 | 0 | 58.5 | 10 | 15 | -103 | 7615.83
2009-10-12 02:24 | 59.999 | 3665.4033 | 350 | 323.42 | 0 | 59 | 10 | 15 | -103 | 7616.82
2009-10-12 02:24 | 59.997 | 3665.3521 | 350 | 323.42 | 0 | 59.5 | 10 | 15 | -103 | 7617.81
2009-10-12 02:24 | 59.998 | 3666.1333 | 350 | 323.42 | 0 | 60 | 10 | 15 | -103 | 7618.8
2009-10-12 02:24 | 59.995 | 3667.084 | 350 | 323.42 | 0 | 60.5 | 10 | 15 | -103 | 7619.79
2009-10-12 02:24 | 59.988 | 3667.8533 | 350 | 323.42 | 0 | 61 | 10 | 15 | -103 | 7620.78
2009-10-12 02:24 | 59.982 | 3669.3992 | 350 | 342.3509 | 0 | 61.5 | 10 | 15 | -103 | 7621.77
2009-10-12 02:24 | 59.984 | 3670.25 | 350 | 342.3509 | 0 | 62 | 10 | 15 | -103 | 7622.76
2009-10-12 02:24 | 59.978 | 3673.2432 | 350 | 342.3509 | 0 | 62.5 | 10 | 15 | -103 | 7623.75
2009-10-12 02:25 | 59.974 | 3676.4182 | 350 | 342.3509 | 0 | 63 | 10 | 15 | -103 | 7624.74
2009-10-12 02:25 | 59.98 | 3675.3289 | 350 | 342.3509 | 0 | 63.5 | 10 | 15 | -103 | 7625.73
2009-10-12 02:25 | 59.984 | 3674.3994 | 350 | 345.0818 | 0 | 64 | 10 | 15 | -103 | 7626.72
2009-10-12 02:25 | 59.988 | 3672.4417 | 350 | 345.0818 | 0 | 64.5 | 10 | 15 | -103 | 7627.71
2009-10-12 02:25 | 59.991 | 3671.4932 | 350 | 345.0818 | 0 | 65 | 10 | 15 | -103 | 7628.7
2009-10-12 02:25 | 59.993 | 3670.0278 | 350 | 345.0818 | 0 | 65.5 | 10 | 15 | -103 | 7629.69
2009-10-12 02:25 | 60.002 | 3672.6255 | 350 | 345.0818 | 0 | 66 | 10 | 15 | -103 | 7630.68
2009-10-12 02:25 | 60.004 | 3673.2495 | 350 | 346.5374 | 0 | 66.5 | 10 | 15 | -103 | 7631.67
2009-10-12 02:25 | 60.002 | 3672.418 | 350 | 346.5374 | 0 | 67 | 10 | 15 | -103 | 7632.66
2009-10-12 02:26 | 60.01 | 3672.2607 | 350 | 346.5374 | 0 | 67.5 | 10 | 15 | -103 | 7633.65
2009-10-12 02:26 | 60.011 | 3673.5535 | 350 | 346.5374 | 0 | 68 | 10 | 15 | -103 | 7634.64
2009-10-12 02:26 | 60.013 | 3673.8125 | 350 | 346.5374 | 0 | 68.5 | 10 | 15 | -103 | 7635.63
2009-10-12 02:26 | 60.011 | 3673.0676 | 350 | 342.9058 | 0 | 69 | 10 | 15 | -103 | 7636.62
2009-10-12 02:26 | 60.017 | 3671.25 | 350 | 342.9058 | 0 | 69.5 | 10 | 15 | -103 | 7637.61
2009-10-12 02:26 | 60.014 | 3672.9817 | 350 | 342.9058 | 0 | 70 | 10 | 15 | -103 | 7638.6
2009-10-12 02:26 | 60.019 | 3671.1931 | 350 | 342.9058 | 0 | 70.5 | 10 | 15 | -103 | 7639.59
2009-10-12 02:26 | 60.027 | 3668.6106 | 350 | 165.4764 | 0 | 71 | 10 | 15 | -103 | 7640.58
2009-10-12 02:26 | 60.022 | 3666.0618 | 350 | 165.4764 | 0 | 71.5 | 10 | 15 | -103 | 7641.57
2009-10-12 02:26 | 60.019 | 3670.4536 | 350 | 165.4764 | 0 | 72 | 10 | 15 | -103 | 7642.56
2009-10-12 02:26 | 60.021 | 3672.4932 | 350 | 165.4764 | 0 | 72.5 | 10 | 15 | -103 | 7643.55
2009-10-12 02:27 | 60.019 | 3672.1641 | 350 | 165.4764 | 0 | 73 | 10 | 15 | -103 | 7644.54
2009-10-12 02:27 | 60.031 | 3666.4673 | 350 | 165.4764 | 0 | 73.5 | 10 | 15 | -103 | 7645.53
2009-10-12 02:27 | 60.036 | 3660.6724 | 350 | 165.4764 | 0 | 74 | 10 | 15 | -103 | 7646.52
2009-10-12 02:27 | 60.048 | 3650.0251 | 350 | 165.4764 | 0 | 74.5 | 10 | 15 | -103 | 7647.51
2009-10-12 02:27 | 60.041 | 3654.2944 | 350 | 165.4764 | 0 | 75 | 10 | 15 | -103 | 7648.5
2009-10-12 02:27 | 60.039 | 3651.0593 | 350 | 165.4764 | 0 | 75.5 | 10 | 15 | -103 | 7649.49
2009-10-12 02:27 | 60.045 | 3645.387 | 350 | 165.4764 | 0 | 76 | 10 | 15 | -103 | 7650.48
2009-10-12 02:27 | 60.041 | 3640.6821 | 350 | 165.4764 | 0 | 76.5 | 10 | 15 | -103 | 7651.47
2009-10-12 02:27 | 59.978 | 3696.3623 | 350 | 206.4591 | 0 | 77 | 10 | 15 | -103 | 7645
2009-10-12 02:28 | 59.869 | 3737.1567 | 335 | 206.4591 | 0 | 77.5 | 10 | 0 | -103 | 7639
2009-10-12 02:28 | 59.88 | 3766.1938 | 335 | 206.4591 | 0 | 78 | 10 | 0 | -103 | 7631
2009-10-12 02:28 | 59.883 | 3780.6206 | 335 | 206.4591 | 0 | 78.5 | 10 | 0 | -103 | 7630
2009-10-12 02:28 | 59.885 | 3784.9619 | 335 | 206.4591 | 0 | 79 | 10 | 0 | -103 | 7631
2009-10-12 02:28 | 59.89 | 3788.0723 | 335 | 211.256 | 0 | 79.5 | 10 | 0 | -103 | 7630
2009-10-12 02:28 | 59.893 | 3788.4719 | 335 | 211.256 | 0 | 80 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.891 | 3794.3743 | 335 | 211.256 | 0 | 80.5 | 10 | 0 | -103 | 7633
2009-10-12 02:28 | 59.885 | 3799.9592 | 335 | 211.256 | 0 | 81 | 10 | 0 | -103 | 7634
2009-10-12 02:28 | 59.888 | 3802.9509 | 335 | 211.256 | 0 | 81.5 | 10 | 0 | -103 | 7635
2009-10-12 02:28 | 59.889 | 3805.6167 | 335 | 214.3467 | 0 | 82 | 10 | 0 | -103 | 7636
2009-10-12 02:28 | 59.857 | 3814.8623 | 335 | 214.3467 | 0 | 82.5 | 10 | 0 | -103 | 7637
2009-10-12 02:29 | 59.858 | 3826.0532 | 335 | 214.3467 | 0 | 83 | 10 | 0 | -103 | 7638
2009-10-12 02:29 | 59.865 | 3826.7532 | 335 | 214.3467 | 0 | 83.5 | 10 | 0 | -103 | 7641
2009-10-12 02:29 | 59.871 | 3825.7134 | 335 | 214.3467 | 0 | 84 | 10 | 0 | -103 | 7642
2009-10-12 02:29 | 59.88 | 3819.0811 | 335 | 212.1727 | 0 | 84.5 | 10 | 0 | -103 | 7629
2009-10-12 02:29 | 59.89 | 3815.0098 | 335 | 212.1727 | 0 | 85 | 10 | 0 | -103 | 7630
2009-10-12 02:29 | 59.893 | 3809.6519 | 335 | 212.1727 | 0 | 85.5 | 10 | 0 | -103 | 7630
2009-10-12 02:29 | 59.902 | 3804.1885 | 335 | 329.9882 | 0 | 86 | 10 | 0 | -103 | 7631
2009-10-12 02:29 | 59.907 | 3792.1694 | 335 | 255.4442 | 0 | 86.5 | 10 | 0 | -103 | 7633
2009-10-12 02:29 | 59.916 | 3788.1321 | 335 | 255.4442 | 0 | 87 | 10 | 0 | -103 | 7636
2009-10-12 02:29 | 59.92 | 3781.7012 | 335 | 255.4442 | 0 | 87.5 | 10 | 0 | -103 | 7640
2009-10-12 02:30 | 59.917 | 3774.6042 | 335 | 255.4442 | 0 | 88 | 10 | 0 | -103 | 7644
2009-10-12 02:30 | 59.923 | 3772.7224 | 335 | 255.4442 | 0 | 88.5 | 10 | 0 | -103 | 7648
2009-10-12 02:30 | 59.928 | 3768.707 | 335 | 254.8383 | 0 | 89 | 10 | 0 | -103 | 7652
2009-10-12 02:30 | 59.927 | 3767.408 | 335 | 254.8383 | 0 | 89.5 | 10 | 0 | -103 | 7656
2009-10-12 02:30 | 59.929 | 3765.6716 | 350 | 254.8383 | 0 | 90 | 10 | 0 | -103 | 7662
2009-10-12 02:30 | 59.937 | 3765.105 | 350 | 254.8383 | 0 | 90.5 | 10 | 0 | -103 | 7665
2009-10-12 02:30 | 59.949 | 3753.9224 | 350 | 254.8383 | 0 | 91 | 10 | 0 | -103 | 7670
2009-10-12 02:30 | 59.941 | 3747.8755 | 350 | 257.147 | 0 | 91.5 | 10 | 0 | -103 | 7674
2009-10-12 02:30 | 59.948 | 3746.7061 | 350 | 257.147 | 0 | 92 | 10 | 0 | -103 | 7679
2009-10-12 02:30 | 59.951 | 3740.259 | 350 | 257.147 | 0 | 92.5 | 10 | 0 | -103 | 7682
2009-10-12 02:31 | 59.951 | 3727.8384 | 350 | 257.147 | 0 | 93 | 10 | 0 | -103 | 7684
2009-10-12 02:31 | 59.952 | 3720.5781 | 350 | 257.147 | 0 | 93.5 | 10 | 0 | -103 | 7686
2009-10-12 02:31 | 59.954 | 3715.7527 | 350 | 262.2894 | 0 | 94 | 10 | 0 | -103 | 7688
2009-10-12 02:31 | 59.953 | 3710.8481 | 350 | 262.2894 | 0 | 94.5 | 10 | 0 | -103 | 7689
2009-10-12 02:31 | 59.954 | 3714.6226 | 350 | 262.2894 | 0 | 95 | 10 | 0 | -103 | 7689
2009-10-12 02:31 | 59.956 | 3716.4614 | 350 | 262.2894 | 0 | 95.5 | 10 | 0 | -103 | 7690
2009-10-12 02:31 | 59.955 | 3722.3613 | 350 | 262.2894 | 0 | 96 | 10 | 0 | -103 | 7690.08
2009-10-12 02:31 | 59.962 | 3722.2666 | 350 | 256.6479 | 0 | 96.5 | 10 | 0 | -103 | 7690
2009-10-12 02:31 | 59.966 | 3723.0908 | 350 | 256.6479 | 0 | 97 | 10 | 0 | -103 | 7692.06
2009-10-12 02:32 | 59.97 | 3723.8931 | 350 | 256.6479 | 0 | 97.5 | 10 | 0 | -103 | 7693.05
2009-10-12 02:32 | 59.969 | 3728.053 | 350 | 256.6479 | 0 | 98 | 10 | 0 | -103 | 7694.04
2009-10-12 02:32 | 59.971 | 3733.3271 | 350 | 256.6479 | 0 | 98.5 | 10 | 0 | -103 | 7695.03
2009-10-12 02:32 | 59.976 | 3736.8218 | 350 | 256.3073 | 0 | 99 | 10 | 0 | -103 | 7696.02
2009-10-12 02:32 | 59.976 | 3740.877 | 350 | 256.3073 | 0 | 99.5 | 10 | 0 | -103 | 7697.01
2009-10-12 02:32 | 59.978 | 3746.6079 | 350 | 256.3073 | 0 | 100 | 10 | 0 | -103 | 7698
2009-10-12 02:32 | 59.982 | 3751.5576 | 350 | 256.3073 | 0 | 100.5 | 10 | 0 | -103 | 7699
2009-10-12 02:32 | 59.979 | 3756.4072 | 350 | 256.3073 | 0 | 101 | 10 | 0 | -103 | 7699.98
2009-10-12 02:32 | 59.983 | 3760.9822 | 350 | 249.0864 | 0 | 101.5 | 10 | 0 | -103 | 7700.97
2009-10-12 02:32 | 59.988 | 3763.2122 | 350 | 249.0864 | 0 | 102 | 10 | 0 | -103 | 7701.96
2009-10-12 02:33 | 59.987 | 3766.4331 | 350 | 249.0864 | 0 | 102.5 | 10 | 0 | -103 | 7702.95
2009-10-12 02:33 | 59.992 | 3768.6335 | 350 | 249.0864 | 0 | 103 | 10 | 0 | -103 | 7703.94
2009-10-12 02:33 | 59.986 | 3773.6948 | 350 | 249.0864 | 0 | 103.5 | 10 | 0 | -103 | 7704.93
2009-10-12 02:33 | 59.988 | 3775.3633 | 350 | 253.7425 | 0 | 104 | 10 | 0 | -103 | 7705.92
2009-10-12 02:33 | 59.998 | 3776.4202 | 350 | 253.7425 | 0 | 104.5 | 10 | 0 | -103 | 7706.91
2009-10-12 02:33 | 59.999 | 3781.2559 | 350 | 253.7425 | 0 | 105 | 10 | 0 | -103 | 7707.9
2009-10-12 02:33 | 60.002 | 3783.8955 | 350 | 253.7425 | 0 | 105.5 | 10 | 0 | -103 | 7708.89
2009-10-12 02:33 | 60.008 | 3785.4626 | 350 | 253.7425 | 0 | 106 | 10 | 0 | -103 | 7709.88
2009-10-12 02:33 | 60.017 | 3787.2593 | 350 | 257.4212 | 0 | 106.5 | 10 | 0 | -103 | 7710.87
2009-10-12 02:33 | 60.017 | 3788.0303 | 350 | 257.4212 | 0 | 107 | 10 | 0 | -103 | 7711.86
2009-10-12 02:34 | 60.023 | 3787.5366 | 350 | 257.4212 | 0 | 107.5 | 10 | 0 | -103 | 7712.85
2009-10-12 02:34 | 60.021 | 3787.9304 | 350 | 257.4212 | 0 | 108 | 10 | 0 | -103 | 7713.84
2009-10-12 02:34 | 60.024 | 3786.5498 | 350 | 257.4212 | 0 | 108.5 | 10 | 0 | -103 | 7714.83
2009-10-12 02:34 | 60.025 | 3785.614 | 350 | 261.7382 | 0 | 109 | 10 | 0 | -103 | 7715.82
2009-10-12 02:34 | 60.02 | 3786.8643 | 350 | 261.7382 | 0 | 109.5 | 10 | 0 | -103 | 7716.81
2009-10-12 02:34 | 60.022 | 3785.7261 | 350 | 261.7382 | 0 | 110 | 10 | 0 | -103 | 7717.8
2009-10-12 02:34 | 60.023 | 3785.7983 | 350 | 261.7382 | 0 | 110.5 | 10 | 0 | -103 | 7718.79
2009-10-12 02:34 | 60.019 | 3787.6274 | 350 | 261.7382 | 0 | 111 | 10 | 0 | -103 | 7719.78
2009-10-12 02:34 | 60.018 | 3789.4043 | 350 | 271.876 | 0 | 111.5 | 10 | 0 | -103 | 7720.77
2009-10-12 02:34 | 60.019 | 3789.3689 | 350 | 271.876 | 0 | 112 | 10 | 0 | -103 | 7721.76
2009-10-12 02:34 | 60.016 | 3788.9329 | 350 | 271.876 | 0 | 112.5 | 10 | 0 | -103 | 7722.75
2009-10-12 02:35 | 60.012 | 3790.4111 | 350 | 271.876 | 0 | 113 | 10 | 0 | -103 | 7723.74
2009-10-12 02:35 | 60.007 | 3792.9453 | 350 | 271.876 | 0 | 113.5 | 10 | 0 | -103 | 7724.73
2009-10-12 02:35 | 60.009 | 3791.426 | 350 | 262.0735 | 0 | 114 | 10 | 0 | -103 | 7725.72
2009-10-12 02:35 | 59.999 | 3790.2163 | 350 | 262.0735 | 0 | 114.5 | 10 | 0 | -103 | 7726.71
2009-10-12 02:35 | 59.991 | 3788.105 | 350 | 262.0735 | 0 | 115 | 10 | 0 | -103 | 7727.7
2009-10-12 02:35 | 59.988 | 3788.4973 | 350 | 262.0735 | 0 | 115.5 | 10 | 0 | -103 | 7728.69
2009-10-12 02:35 | 59.984 | 3788.1011 | 350 | 262.0735 | 0 | 116 | 10 | 0 | -103 | 7729.68
2009-10-12 02:35 | 59.982 | 3787.7324 | 350 | 260.3644 | 0 | 116.5 | 10 | 0 | -103 | 7730.67
2009-10-12 02:35 | 59.979 | 3788.2563 | 350 | 260.3644 | 0 | 117 | 10 | 0 | -103 | 7731.66
2009-10-12 02:36 | 59.976 | 3790.6646 | 350 | 260.3644 | 0 | 117.5 | 10 | 0 | -103 | 7732.65
2009-10-12 02:36 | 59.978 | 3789.2671 | 350 | 260.3644 | 0 | 118 | 10 | 0 | -103 | 7733.64
2009-10-12 02:36 | 59.976 | 3789.9143 | 350 | 260.3644 | 0 | 118.5 | 10 | 0 | -103 | 7734.63
2009-10-12 02:36 | 59.975 | 3788.9629 | 350 | 352.6444 | 0 | 119 | 10 | 0 | -103 | 7735.62
2009-10-12 02:36 | 59.97 | 3792.9106 | 350 | 352.6444 | 0 | 119.5 | 10 | 0 | -103 | 7736.61
2009-10-12 02:36 | 59.978 | 3788.0796 | 350 | 352.6444 | 0 | 120 | 10 | 0 | -103 | 7737.6
2009-10-12 02:36 | 59.975 | 3787.1643 | 350 | 352.6444 | 0 | 120.5 | 10 | 0 | -103 | 7738.59
2009-10-12 02:36 | 59.975 | 3786.4868 | 350 | 352.6444 | 0 | 121 | 10 | 0 | -103 | 7739.58
2009-10-12 02:36 | 59.966 | 3790.5117 | 350 | 354.8957 | 0 | 121.5 | 10 | 0 | -103 | 7740.57
2009-10-12 02:36 | 59.969 | 3790.9595 | 350 | 354.8957 | 0 | 122 | 10 | 0 | -103 | 7741.56
2009-10-12 02:36 | 59.965 | 3789.1675 | 350 | 354.8957 | 0 | 122.5 | 10 | 0 | -103 | 7742.55
2009-10-12 02:37 | 59.972 | 3784.8306 | 350 | 354.8957 | 0 | 123 | 10 | 0 | -103 | 7743.54
2009-10-12 02:37 | 59.969 | 3782.8086 | 350 | 354.8957 | 0 | 123.5 | 10 | 0 | -103 | 7744.53
2009-10-12 02:37 | 59.967 | 3779.0562 | 350 | 340.4694 | 0 | 124 | 10 | 0 | -103 | 7745.52
2009-10-12 02:37 | 59.965 | 3779.3347 | 350 | 340.4694 | 0 | 124.5 | 10 | 0 | -103 | 7746.51
2009-10-12 02:37 | 59.965 | 3776.5967 | 350 | 340.4694 | 0 | 125 | 10 | 0 | -103 | 7747.5
2009-10-12 02:37 | 59.97 | 3773.1699 | 350 | 340.4694 | 0 | 125.5 | 10 | 0 | -103 | 7748.49
2009-10-12 02:37 | 59.968 | 3768.5029 | 350 | 340.4694 | 0 | 126 | 10 | 0 | -103 | 7749.48
2009-10-12 02:37 | 59.97 | 3764.7861 | 350 | 337.6429 | 0 | 126.5 | 10 | 0 | -103 | 7750.47
2009-10-12 02:37 | 59.965 | 3761.8938 | 350 | 337.6429 | 0 | 127 | 10 | 0 | -103 | 7751.46
2009-10-12 02:38 | 59.967 | 3760.1575 | 350 | 337.6429 | 0 | 127.5 | 10 | 0 | -103 | 7752.45
2009-10-12 02:38 | 59.979 | 3757.7729 | 350 | 337.6429 | 0 | 128 | 10 | 0 | -103 | 7753.44
2009-10-12 02:38 | 59.974 | 3751.6367 | 350 | 337.6429 | 0 | 128.5 | 10 | 0 | -103 | 7754.43
2009-10-12 02:38 | 59.962 | 3759.2498 | 350 | 284.3608 | 0 | 129 | 10 | 0 | -103 | 7755.42
2009-10-12 02:38 | 59.961 | 3762.0222 | 350 | 284.3608 | 0 | 129.5 | 10 | 0 | -103 | 7756.41
2009-10-12 02:38 | 59.959 | 3763.8582 | 350 | 284.3608 | 0 | 130 | 10 | 0 | -103 | 7757.4
2009-10-12 02:38 | 59.953 | 3768.3389 | 350 | 284.3608 | 0 | 130.5 | 10 | 0 | -103 | 7758.39
2009-10-12 02:38 | 59.956 | 3765.6064 | 350 | 284.3608 | 0 | 131 | 10 | 0 | -103 | 7759.38
2009-10-12 02:38 | 59.961 | 3761.9199 | 350 | 260.468 | 0 | 131.5 | 10 | 0 | -103 | 7760.37
2009-10-12 02:38 | 59.963 | 3752.4287 | 350 | 260.468 | 0 | 132 | 10 | 0 | -103 | 7761.36
2009-10-12 02:38 | 59.968 | 3753.5103 | 350 | 260.468 | 0 | 132.5 | 10 | 0 | -103 | 7762.35
2009-10-12 02:39 | 59.973 | 3753.1782 | 350 | 260.468 | 0 | 133 | 10 | 0 | -103 | 7763.34
2009-10-12 02:39 | 59.967 | 3752.8716 | 350 | 260.468 | 0 | 133.5 | 10 | 0 | -103 | 7764.33
2009-10-12 02:39 | 59.976 | 3747.4758 | 350 | 253.1415 | 0 | 134 | 10 | 0 | -103 | 7765.32
2009-10-12 02:39 | 59.973 | 3746.6509 | 350 | 253.1415 | 0 | 134.5 | 10 | 0 | -103 | 7766.31
2009-10-12 02:39 | 59.981 | 3741.6182 | 350 | 253.1415 | 0 | 135 | 10 | 0 | -103 | 7767.3
2009-10-12 02:39 | 59.982 | 3738.9014 | 350 | 253.1415 | 0 | 135.5 | 10 | 0 | -103 | 7768.29
2009-10-12 02:39 | 59.982 | 3736.3083 | 350 | 253.1415 | 0 | 136 | 10 | 0 | -103 | 7769.28
2009-10-12 02:39 | 59.98 | 3735.6497 | 350 | 251.9299 | 0 | 136.5 | 10 | 0 | -103 | 7770.27
2009-10-12 02:39 | 59.98 | 3736.7476 | 350 | 251.9299 | 0 | 137 | 10 | 0 | -103 | 7771.26
2009-10-12 02:40 | 59.978 | 3736.0942 | 350 | 251.9299 | 0 | 137.5 | 10 | 0 | -103 | 7772.25
2009-10-12 02:40 | 59.971 | 3738.8748 | 350 | 251.9299 | 0 | 138 | 10 | 0 | -103 | 7773.24
2009-10-12 02:40 | 59.975 | 3737.6841 | 350 | 251.9299 | 0 | 138.5 | 10 | 0 | -103 | 7774.23
2009-10-12 02:40 | 59.969 | 3740.0168 | 350 | 250.6742 | 0 | 139 | 10 | 0 | -103 | 7775.22
2009-10-12 02:40 | 59.972 | 3742.4238 | 350 | 250.6742 | 0 | 139.5 | 10 | 0 | -103 | 7776.21
2009-10-12 02:40 | 59.977 | 3741.7231 | 350 | 250.6742 | 0 | 140 | 10 | 0 | -103 | 7777.2
2009-10-12 02:40 | 59.976 | 3739.9644 | 350 | 250.6742 | 0 | 140.5 | 10 | 0 | -103 | 7778.19
2009-10-12 02:40 | 59.977 | 3741.2678 | 350 | 250.6742 | 0 | 141 | 10 | 0 | -103 | 7779.18
2009-10-12 02:40 | 59.979 | 3738.7061 | 350 | 253.6319 | 0 | 141.5 | 10 | 0 | -103 | 7780.17
2009-10-12 02:40 | 59.974 | 3738.1016 | 350 | 253.6319 | 0 | 142 | 10 | 0 | -103 | 7781.16
2009-10-12 02:40 | 59.971 | 3743.4187 | 350 | 253.6319 | 0 | 142.5 | 10 | 0 | -103 | 7782.15
2009-10-12 02:41 | 59.966 | 3747.3396 | 350 | 253.6319 | 0 | 143 | 10 | 0 | -103 | 7783.14
2009-10-12 02:41 | 59.973 | 3746.2166 | 350 | 253.6319 | 0 | 143.5 | 10 | 0 | -103 | 7784.13
2009-10-12 02:41 | 59.972 | 3743.1489 | 350 | 246.9573 | 0 | 144 | 10 | 0 | -103 | 7785.12
2009-10-12 02:41 | 59.97 | 3733.376 | 350 | 246.9573 | 0 | 144.5 | 10 | 0 | -103 | 7786.11
2009-10-12 02:41 | 59.982 | 3736.2295 | 350 | 246.9573 | 0 | 145 | 10 | 0 | -103 | 7787.1
2009-10-12 02:41 | 59.985 | 3733.1152 | 350 | 246.9573 | 0 | 145.5 | 10 | 0 | -103 | 7788.09
2009-10-12 02:41 | 59.989 | 3725.4587 | 350 | 246.9573 | 0 | 146 | 10 | 0 | -103 | 7789.08
2009-10-12 02:41 | 59.99 | 3720.9382 | 350 | 254.5418 | 0 | 146.5 | 10 | 0 | -103 | 7790.07
2009-10-12 02:41 | 60.001 | 3727.7542 | 350 | 254.5418 | 0 | 147 | 10 | 0 | -103 | 7791.06
2009-10-12 02:42 | 60.006 | 3727.2314 | 350 | 254.5418 | 0 | 147.5 | 10 | 0 | -103 | 7792.05
2009-10-12 02:42 | 60.019 | 3726.0156 | 350 | 254.5418 | 0 | 148 | 10 | 0 | -103 | 7793.04
2009-10-12 02:42 | 60.026 | 3717.3325 | 350 | 254.5418 | 0 | 148.5 | 10 | 0 | -103 | 7794.03
2009-10-12 02:42 | 60.029 | 3715.166 | 350 | 256.5716 | 0 | 149 | 10 | 0 | -103 | 7795.02
2009-10-12 02:42 | 60.037 | 3710.1577 | 350 | 256.5716 | 0 | 149.5 | 10 | 0 | -103 | 7796.01
2009-10-12 02:42 | 60.041 | 3704.5913 | 350 | 256.5716 | 0 | 150 | 10 | 0 | -103 | 7797
2009-10-12 02:42 | 60.043 | 3701.3164 | 350 | 256.5716 | 0 | 150.5 | 10 | 0 | -103 | 7797.99
2009-10-12 02:42 | 60.046 | 3699.7261 | 350 | 256.5716 | 0 | 151 | 10 | 0 | -103 | 7798.98
2009-10-12 02:42 | 60.043 | 3696.8645 | 350 | 258.3726 | 0 | 151.5 | 10 | 0 | -103 | 7799.97
2009-10-12 02:42 | 60.043 | 3696.5413 | 350 | 258.3726 | 0 | 152 | 10 | 0 | -103 | 7800.96
2009-10-12 02:42 | 60.041 | 3699.6306 | 350 | 258.3726 | 0 | 152.5 | 10 | 0 | -103 | 7801.95
2009-10-12 02:43 | 60.036 | 3700.1057 | 350 | 258.3726 | 0 | 153 | 10 | 0 | -103 | 7802.94
2009-10-12 02:43 | 60.034 | 3701.8652 | 350 | 258.3726 | 0 | 153.5 | 10 | 0 | -103 | 7803.93
2009-10-12 02:43 | 60.035 | 3702.9126 | 350 | 263.0474 | 0 | 154 | 10 | 0 | -103 | 7804.92
2009-10-12 02:43 | 60.036 | 3704.9668 | 350 | 263.0474 | 0 | 154.5 | 10 | 0 | -103 | 7805.91
2009-10-12 02:43 | 60.032 | 3703.7063 | 350 | 263.0474 | 0 | 155 | 10 | 0 | -103 | 7806.9
2009-10-12 02:43 | 60.033 | 3704.3601 | 350 | 263.0474 | 0 | 155.5 | 10 | 0 | -103 | 7807.89
2009-10-12 02:43 | 60.035 | 3701.9419 | 350 | 263.0474 | 0 | 156 | 10 | 0 | -103 | 7808.88
2009-10-12 02:43 | 60.037 | 3702.457 | 350 | 260.9844 | 0 | 156.5 | 10 | 0 | -103 | 7809.87
2009-10-12 02:43 | 60.034 | 3703.8435 | 350 | 260.9844 | 0 | 157 | 10 | 0 | -103 | 7810.86
2009-10-12 02:44 | 60.037 | 3702.2795 | 350 | 260.9844 | 0 | 157.5 | 10 | 0 | -103 | 7811.85
2009-10-12 02:44 | 60.04 | 3700.2759 | 350 | 260.9844 | 0 | 158 | 10 | 0 | -103 | 7812.84
2009-10-12 02:44 | 60.045 | 3696.916 | 350 | 260.9844 | 0 | 158.5 | 10 | 0 | -103 | 7813.83
2009-10-12 02:44 | 60.04 | 3698.4292 | 350 | 261.3183 | 0 | 159 | 10 | 0 | -103 | 7814.82
2009-10-12 02:44 | 60.042 | 3693.2407 | 350 | 261.3183 | 0 | 159.5 | 10 | 0 | -103 | 7815.81
2009-10-12 02:44 | 60.039 | 3701.791 | 350 | 261.3183 | 0 | 160 | 10 | 0 | -103 | 7816.8
2009-10-12 02:44 | 60.034 | 3702.1479 | 350 | 261.3183 | 0 | 160.5 | 10 | 0 | -103 | 7817.79
2009-10-12 02:44 | 60.031 | 3707.2866 | 350 | 261.3183 | 0 | 161 | 10 | 0 | -103 | 7818.78
2009-10-12 02:44 | 60.031 | 3707.9165 | 350 | 262.1026 | 0 | 161.5 | 10 | 0 | -103 | 7819.77
2009-10-12 02:44 | 60.031 | 3707.6152 | 350 | 262.1026 | 0 | 162 | 10 | 0 | -103 | 7820.76
2009-10-12 02:44 | 60.039 | 3701.582 | 350 | 262.1026 | 0 | 162.5 | 10 | 0 | -103 | 7821.75
2009-10-12 02:45 | 60.035 | 3702.2122 | 350 | 262.1026 | 0 | 163 | 10 | 0 | -103 | 7822.74
2009-10-12 02:45 | 60.042 | 3699.6897 | 350 | 262.1026 | 0 | 163.5 | 10 | 0 | -103 | 7823.73
2009-10-12 02:45 | 60.04 | 3700.6616 | 350 | 262.717 | 0 | 164 | 10 | 0 | -103 | 7824.72
2009-10-12 02:45 | 60.048 | 3695.8186 | 350 | 262.717 | 0 | 164.5 | 10 | 0 | -103 | 7825.71
2009-10-12 02:45 | 60.044 | 3696.897 | 350 | 262.717 | 0 | 165 | 10 | 0 | -103 | 7826.7
2009-10-12 02:45 | 60.04 | 3698.4243 | 350 | 262.717 | 0 | 165.5 | 10 | 0 | -103 | 7827.69
2009-10-12 02:45 | 60.044 | 3699.8064 | 350 | 262.717 | 0 | 166 | 10 | 0 | -103 | 7828.68
2009-10-12 02:45 | 60.042 | 3698.5073 | 350 | 260.0165 | 0 | 166.5 | 10 | 0 | -103 | 7829.67
2009-10-12 02:45 | 60.038 | 3699.0771 | 350 | 260.0165 | 0 | 167 | 10 | 0 | -103 | 7830.66
2009-10-12 02:46 | 60.039 | 3700.9023 | 350 | 260.0165 | 0 | 167.5 | 10 | 0 | -103 | 7831.65
2009-10-12 02:46 | 60.039 | 3701.1394 | 350 | 260.0165 | 0 | 168 | 10 | 0 | -103 | 7832.64
2009-10-12 02:46 | 60.039 | 3699.4585 | 350 | 260.0165 | 0 | 168.5 | 10 | 0 | -103 | 7833.63
2009-10-12 02:46 | 60.037 | 3699.5051 | 350 | 263.8732 | 0 | 169 | 10 | 0 | -103 | 7834.62
2009-10-12 02:46 | 60.038 | 3699.4004 | 350 | 263.8732 | 0 | 169.5 | 10 | 0 | -103 | 7835.61
2009-10-12 02:46 | 60.033 | 3702.9675 | 350 | 263.8732 | 0 | 170 | 10 | 0 | -103 | 7836.6
2009-10-12 02:46 | 60.032 | 3705.7751 | 350 | 263.8732 | 0 | 170.5 | 10 | 0 | -103 | 7837.59
2009-10-12 02:46 | 60.042 | 3701.9812 | 350 | 263.8732 | 0 | 171 | 10 | 0 | -103 | 7838.58
2009-10-12 02:46 | 60.031 | 3702.2126 | 350 | 264.5979 | 0 | 171.5 | 10 | 0 | -103 | 7839.57
2009-10-12 02:46 | 60.034 | 3704.4487 | 350 | 264.5979 | 0 | 172 | 10 | 0 | -103 | 7840.56
2009-10-12 02:46 | 60.038 | 3702.7954 | 350 | 264.5979 | 0 | 172.5 | 10 | 0 | -103 | 7841.55
2009-10-12 02:47 | 60.042 | 3696.2495 | 350 | 264.5979 | 0 | 173 | 10 | 0 | -103 | 7842.54
2009-10-12 02:47 | 60.04 | 3693.5771 | 350 | 264.5979 | 0 | 173.5 | 10 | 0 | -103 | 7843.53
2009-10-12 02:47 | 60.041 | 3693.7861 | 350 | 262.4159 | 0 | 174 | 10 | 0 | -103 | 7844.52
2009-10-12 02:47 | 60.043 | 3694.9377 | 350 | 262.4159 | 0 | 174.5 | 10 | 0 | -103 | 7845.51
2009-10-12 02:47 | 60.036 | 3692.6863 | 350 | 262.4159 | 0 | 175 | 10 | 0 | -103 | 7846.5
2009-10-12 02:47 | 60.042 | 3692.3569 | 350 | 262.4159 | 0 | 175.5 | 10 | 0 | -103 | 7847.49
2009-10-12 02:47 | 60.036 | 3692.0422 | 350 | 262.4159 | 0 | 176 | 10 | 0 | -103 | 7848.48
2009-10-12 02:47 | 60.037 | 3695.2583 | 350 | 259.6852 | 0 | 176.5 | 10 | 0 | -103 | 7849.47
2009-10-12 02:47 | 60.035 | 3695.4912 | 350 | 259.6852 | 0 | 177 | 10 | 0 | -103 | 7850.46
2009-10-12 02:48 | 60.03 | 3697.3357 | 350 | 259.6852 | 0 | 177.5 | 10 | 0 | -103 | 7851.45
2009-10-12 02:48 | 60.031 | 3699.2512 | 350 | 259.6852 | 0 | 178 | 10 | 0 | -103 | 7852.44
2009-10-12 02:48 | 60.031 | 3699.1265 | 350 | 259.6852 | 0 | 178.5 | 10 | 0 | -103 | 7853.43
2009-10-12 02:48 | 60.032 | 3698.2773 | 350 | 255.911 | 0 | 179 | 10 | 0 | -103 | 7854.42
2009-10-12 02:48 | 60.04 | 3693.7358 | 350 | 255.911 | 0 | 179.5 | 10 | 0 | -103 | 7855.41
2009-10-12 02:48 | 60.036 | 3691.9189 | 350 | 255.911 | 0 | 180 | 10 | 0 | -103 | 7856.4
2009-10-12 02:48 | 60.04 | 3692.3735 | 350 | 255.911 | 0 | 180.5 | 10 | 0 | -103 | 7857.39
2009-10-12 02:48 | 60.038 | 3694.3313 | 350 | 255.911 | 0 | 181 | 10 | 0 | -103 | 7858.38
2009-10-12 02:48 | 60.04 | 3694.324 | 350 | 258.1482 | 0 | 181.5 | 10 | 0 | -103 | 7859.37
2009-10-12 02:48 | 60.034 | 3693.7476 | 350 | 258.1482 | 0 | 182 | 10 | 0 | -103 | 7860.36
2009-10-12 02:49 | 60.041 | 3691.0117 | 350 | 258.1482 | 0 | 182.5 | 10 | 0 | -103 | 7861.35
2009-10-12 02:49 | 60.036 | 3693.7271 | 350 | 258.1482 | 0 | 183 | 10 | 0 | -103 | 7862.34
2009-10-12 02:49 | 60.039 | 3688.1594 | 350 | 258.1482 | 0 | 183.5 | 10 | 0 | -103 | 7863.33
2009-10-12 02:49 | 60.033 | 3690.0918 | 350 | 258.8736 | 0 | 184 | 10 | 0 | -103 | 7864.32
2009-10-12 02:49 | 60.029 | 3694.5933 | 350 | 258.8736 | 0 | 184.5 | 10 | 0 | -103 | 7865.31
2009-10-12 02:49 | 60.03 | 3693.4116 | 350 | 258.8736 | 0 | 185 | 10 | 0 | -103 | 7866.3
2009-10-12 02:49 | 60.022 | 3698.0122 | 350 | 258.8736 | 0 | 185.5 | 10 | 0 | -103 | 7867.29
2009-10-12 02:49 | 60.023 | 3698.9351 | 350 | 258.8736 | 0 | 186 | 10 | 0 | -103 | 7868.28
2009-10-12 02:49 | 60.023 | 3700.4858 | 350 | 249.3376 | 0 | 186.5 | 10 | 0 | -103 | 7869.27
2009-10-12 02:49 | 60.026 | 3699.9138 | 350 | 249.3376 | 0 | 187 | 10 | 0 | -103 | 7870.26
2009-10-12 02:50 | 60.024 | 3701.4502 | 350 | 249.3376 | 0 | 187.5 | 10 | 0 | -103 | 7871.25
2009-10-12 02:50 | 60.023 | 3701.7017 | 350 | 249.3376 | 0 | 188 | 10 | 0 | -103 | 7872.24
2009-10-12 02:50 | 60.029 | 3700.2688 | 350 | 249.3376 | 0 | 188.5 | 10 | 0 | -103 | 7873.23
2009-10-12 02:50 | 60.021 | 3701.2681 | 350 | 258.2782 | 0 | 189 | 10 | 0 | -103 | 7874.22
2009-10-12 02:50 | 60.025 | 3700.5317 | 350 | 258.2782 | 0 | 189.5 | 10 | 0 | -103 | 7875.21
2009-10-12 02:50 | 60.024 | 3700.2773 | 350 | 258.2782 | 0 | 190 | 10 | 0 | -103 | 7876.2
2009-10-12 02:50 | 60.026 | 3700.2603 | 350 | 258.2782 | 0 | 190.5 | 10 | 0 | -103 | 7877.19
2009-10-12 02:50 | 60.02 | 3700.9648 | 350 | 258.2782 | 0 | 191 | 10 | 0 | -103 | 7878.18
2009-10-12 02:50 | 60.016 | 3703.8237 | 350 | 258.4064 | 0 | 191.5 | 10 | 0 | -103 | 7879.17
2009-10-12 02:50 | 60.015 | 3703.0034 | 350 | 258.4064 | 0 | 192 | 10 | 0 | -103 | 7880.16
2009-10-12 02:50 | 60.012 | 3703.1667 | 350 | 258.4064 | 0 | 192.5 | 10 | 0 | -103 | 7881.15
2009-10-12 02:51 | 60.002 | 3703.7754 | 350 | 258.4064 | 0 | 193 | 10 | 0 | -103 | 7882.14
2009-10-12 02:51 | 60.002 | 3700.6167 | 350 | 258.4064 | 0 | 193.5 | 10 | 0 | -103 | 7883.13
2009-10-12 02:51 | 60.001 | 3701.3889 | 350 | 260.5389 | 0 | 194 | 10 | 0 | -103 | 7884.12
2009-10-12 02:51 | 59.992 | 3700.8264 | 350 | 260.5389 | 0 | 194.5 | 10 | 0 | -103 | 7885.11
2009-10-12 02:51 | 59.985 | 3699.8538 | 350 | 260.5389 | 0 | 195 | 10 | 0 | -103 | 7886.1
2009-10-12 02:51 | 59.984 | 3700.7698 | 350 | 260.5389 | 0 | 195.5 | 10 | 0 | -103 | 7887.09
2009-10-12 02:51 | 59.977 | 3703.1658 | 350 | 260.5389 | 0 | 196 | 10 | 0 | -103 | 7888.08
2009-10-12 02:51 | 59.972 | 3705.8105 | 350 | 257.8821 | 0 | 196.5 | 10 | 0 | -103 | 7889.07
2009-10-12 02:51 | 59.975 | 3706.543 | 350 | 257.8821 | 0 | 197 | 10 | 0 | -103 | 7890.06
2009-10-12 02:52 | 59.971 | 3710.1182 | 350 | 257.8821 | 0 | 197.5 | 10 | 0 | -103 | 7891.05
2009-10-12 02:52 | 59.98 | 3708.0181 | 350 | 257.8821 | 0 | 198 | 10 | 0 | -103 | 7892.04
2009-10-12 02:52 | 59.982 | 3706.1255 | 350 | 257.8821 | 0 | 198.5 | 10 | 0 | -103 | 7893.03
2009-10-12 02:52 | 59.979 | 3706.1904 | 350 | 258.5887 | 0 | 199 | 10 | 0 | -103 | 7894.02
2009-10-12 02:52 | 59.978 | 3708.9714 | 350 | 258.5887 | 0 | 199.5 | 10 | 0 | -103 | 7895.01
2009-10-12 02:52 | 59.978 | 3707.24 | 350 | 258.5887 | 0 | 200 | 10 | 0 | -103 | 7896
2009-10-12 02:52 | 59.97 | 3711.75 | 350 | 258.5887 | 0 | 200.5 | 10 | 0 | -103 | 7896.99
2009-10-12 02:52 | 59.99 | 3707.8667 | 350 | 258.5887 | 0 | 201 | 10 | 0 | -103 | 7897.98
2009-10-12 02:52 | 59.999 | 3703.7869 | 350 | 261.9062 | 0 | 201.5 | 10 | 0 | -103 | 7898.97
2009-10-12 02:52 | 60.003 | 3699.51 | 350 | 261.9062 | 0 | 202 | 10 | 0 | -103 | 7899.96
2009-10-12 02:52 | 60.01 | 3697.8821 | 350 | 261.9062 | 0 | 202.5 | 10 | 0 | -103 | 7900.95
2009-10-12 02:53 | 60.022 | 3697.8684 | 350 | 261.9062 | 0 | 203 | 10 | 0 | -103 | 7901.94
2009-10-12 02:53 | 60.025 | 3693.4177 | 350 | 261.9062 | 0 | 203.5 | 10 | 0 | -103 | 7902.93
2009-10-12 02:53 | 60.029 | 3689.1431 | 350 | 256.7478 | 0 | 204 | 10 | 0 | -103 | 7903.92
2009-10-12 02:53 | 60.028 | 3687.0264 | 350 | 256.7478 | 0 | 204.5 | 10 | 0 | -103 | 7904.91
2009-10-12 02:53 | 60.032 | 3685.5762 | 350 | 256.7478 | 0 | 205 | 10 | 0 | -103 | 7905.9
2009-10-12 02:53 | 60.03 | 3687.1589 | 350 | 256.7478 | 0 | 205.5 | 10 | 0 | -103 | 7906.89
2009-10-12 02:53 | 60.019 | 3690.4258 | 350 | 256.7478 | 0 | 206 | 10 | 0 | -103 | 7907.88
2009-10-12 02:53 | 60.017 | 3692.5776 | 350 | 167.432 | 0 | 206.5 | 10 | 0 | -103 | 7908.87
2009-10-12 02:53 | 60.015 | 3693.2488 | 350 | 167.432 | 0 | 207 | 10 | 0 | -103 | 7909.86
2009-10-12 02:54 | 60.008 | 3694.6807 | 350 | 167.432 | 0 | 207.5 | 10 | 0 | -103 | 7910.85
2009-10-12 02:54 | 60.005 | 3693.7495 | 350 | 167.432 | 0 | 208 | 10 | 0 | -103 | 7911.84
2009-10-12 02:54 | 59.997 | 3691.1499 | 350 | 167.432 | 0 | 208.5 | 10 | 0 | -103 | 7912.83
2009-10-12 02:54 | 59.998 | 3690.5876 | 350 | 164.9734 | 0 | 209 | 10 | 0 | -103 | 7913.82
2009-10-12 02:54 | 59.992 | 3689.4453 | 350 | 164.9734 | 0 | 209.5 | 10 | 0 | -103 | 7914.81
2009-10-12 02:54 | 59.985 | 3689.7356 | 350 | 164.9734 | 0 | 210 | 10 | 0 | -103 | 7915.8
2009-10-12 02:54 | 59.988 | 3687.4937 | 350 | 164.9734 | 0 | 210.5 | 10 | 0 | -103 | 7916.79
2009-10-12 02:54 | 59.983 | 3685.6597 | 350 | 164.9734 | 0 | 211 | 10 | 0 | -103 | 7917.78
2009-10-12 02:54 | 59.987 | 3683.9109 | 350 | 157.6281 | 0 | 211.5 | 10 | 0 | -103 | 7918.77
2009-10-12 02:54 | 59.985 | 3683.811 | 350 | 157.6281 | 0 | 212 | 10 | 0 | -103 | 7919.76
2009-10-12 02:54 | 59.982 | 3684.8843 | 350 | 157.6281 | 0 | 212.5 | 10 | 0 | -103 | 7920.75
2009-10-12 02:55 | 59.978 | 3685.0869 | 350 | 157.6281 | 0 | 213 | 10 | 0 | -103 | 7921.74
2009-10-12 02:55 | 59.973 | 3687.4124 | 350 | 157.6281 | 0 | 213.5 | 10 | 0 | -103 | 7922.73
2009-10-12 02:55 | 59.976 | 3687.8477 | 350 | 155.5317 | 0 | 214 | 10 | 0 | -103 | 7923.72
2009-10-12 02:55 | 59.979 | 3684.8901 | 350 | 155.5317 | 0 | 214.5 | 10 | 0 | -103 | 7924.71
2009-10-12 02:55 | 59.977 | 3684.0933 | 350 | 155.5317 | 0 | 215 | 10 | 0 | -103 | 7925.7
2009-10-12 02:55 | 59.978 | 3682.3176 | 350 | 155.5317 | 0 | 215.5 | 10 | 0 | -103 | 7926.69
2009-10-12 02:55 | 59.981 | 3682.8555 | 350 | 155.5317 | 0 | 216 | 10 | 0 | -103 | 7927.68
2009-10-12 02:55 | 59.979 | 3684.3184 | 350 | 160.4472 | 0 | 216.5 | 10 | 0 | -103 | 7928.67
2009-10-12 02:55 | 59.983 | 3685.2864 | 350 | 160.4472 | 0 | 217 | 10 | 0 | -103 | 7929.66
2009-10-12 02:55 | 59.992 | 3681.4026 | 350 | 160.4472 | 0 | 217.5 | 10 | 0 | -103 | 7930.65
2009-10-12 02:56 | 59.988 | 3671.7612 | 350 | 160.4472 | 0 | 218 | 10 | 0 | -103 | 7931.64
2009-10-12 02:56 | 59.993 | 3679.0005 | 350 | 160.4472 | 0 | 218.5 | 10 | 0 | -103 | 7932.63
2009-10-12 02:56 | 59.994 | 3682.7004 | 350 | 163.9586 | 0 | 219 | 10 | 0 | -103 | 7933.62
2009-10-12 02:56 | 59.989 | 3684.8784 | 350 | 163.9586 | 0 | 219.5 | 10 | 0 | -103 | 7934.61
2009-10-12 02:56 | 59.985 | 3685.5837 | 350 | 163.9586 | 0 | 220 | 10 | 0 | -103 | 7935.6
2009-10-12 02:56 | 59.986 | 3684.9761 | 350 | 163.9586 | 0 | 220.5 | 10 | 0 | -103 | 7936.59
2009-10-12 02:56 | 59.982 | 3684.2446 | 350 | 163.9586 | 0 | 221 | 10 | 0 | -103 | 7937.58
2009-10-12 02:56 | 59.987 | 3683.7358 | 350 | 166.0724 | 0 | 221.5 | 10 | 0 | -103 | 7938.57
2009-10-12 02:56 | 60 | 3682.1377 | 350 | 166.0724 | 0 | 222 | 10 | 0 | -103 | 7939.56
2009-10-12 02:56 | 60.003 | 3681.4585 | 350 | 166.0724 | 0 | 222.5 | 10 | 0 | -103 | 7940.55
2009-10-12 02:57 | 60.002 | 3680.167 | 350 | 166.0724 | 0 | 223 | 10 | 0 | -103 | 7941.54
2009-10-12 02:57 | 60.005 | 3679.6692 | 350 | 166.0724 | 0 | 223.5 | 10 | 0 | -103 | 7942.53
2009-10-12 02:57 | 60.012 | 3676.7961 | 350 | 163.7666 | 0 | 224 | 10 | 0 | -103 | 7943.52
2009-10-12 02:57 | 60.022 | 3673.906 | 350 | 163.7666 | 0 | 224.5 | 10 | 0 | -103 | 7944.51
2009-10-12 02:57 | 60.018 | 3673.6479 | 350 | 163.7666 | 0 | 225 | 10 | 0 | -103 | 7945.5
2009-10-12 02:57 | 60.02 | 3676.6758 | 350 | 163.7666 | 0 | 225.5 | 10 | 0 | -103 | 7946.49
2009-10-12 02:57 | 60.019 | 3677.1848 | 350 | 163.7666 | 0 | 226 | 10 | 0 | -103 | 7947.48
2009-10-12 02:57 | 60.017 | 3679.2888 | 350 | 165.1017 | 0 | 226.5 | 10 | 0 | -103 | 7948.47
2009-10-12 02:57 | 60.016 | 3678.5986 | 350 | 165.1017 | 0 | 227 | 10 | 0 | -103 | 7949.46
2009-10-12 02:58 | 60.014 | 3678.5894 | 350 | 165.1017 | 0 | 227.5 | 10 | 0 | -103 | 7950.45
2009-10-12 02:58 | 60.015 | 3674.6694 | 350 | 165.1017 | 0 | 228 | 10 | 0 | -103 | 7951.44
2009-10-12 02:58 | 60.019 | 3674.5461 | 350 | 165.1017 | 0 | 228.5 | 10 | 0 | -103 | 7952.43
2009-10-12 02:58 | 60.02 | 3671.9819 | 350 | 165.4764 | 0 | 229 | 10 | 0 | -103 | 7953.42
2009-10-12 02:58 | 60.026 | 3671.0596 | 350 | 165.4764 | 0 | 229.5 | 10 | 0 | -103 | 7954.41
2009-10-12 02:58 | 60.022 | 3674.0095 | 350 | 165.4764 | 0 | 230 | 10 | 0 | -103 | 7955.4
2009-10-12 02:58 | 60.024 | 3676.0513 | 350 | 165.4764 | 0 | 230.5 | 10 | 0 | -103 | 7956.39
2009-10-12 02:58 | 60.028 | 3671.3428 | 350 | 165.4764 | 0 | 231 | 10 | 0 | -103 | 7957.38
2009-10-12 02:58 | 60.035 | 3668.7671 | 350 | 206.4591 | 0 | 231.5 | 10 | 0 | -103 | 7958.37
2009-10-12 02:58 | 60.021 | 3657.1641 | 350 | 206.4591 | 0 | 232 | 10 | 0 | -103 | 7959.36
2009-10-12 02:58 | 60.025 | 3669.3088 | 335 | 206.4591 | 0 | 232.5 | 10 | 0 | -103 | 7960.35
2009-10-12 02:59 | 60.023 | 3671.332 | 335 | 206.4591 | 0 | 233 | 10 | 0 | -103 | 7961.34
2009-10-12 02:59 | 60.02 | 3673.8325 | 335 | 206.4591 | 0 | 233.5 | 10 | 0 | -103 | 7962.33
2009-10-12 02:59 | 60.017 | 3675.9707 | 335 | 211.256 | 0 | 234 | 10 | 0 | -103 | 7963.32
2009-10-12 02:59 | 60.01 | 3679.3928 | 335 | 211.256 | 1 | 234.5 | 10 | 0 | -103 | 7964.31
2009-10-12 02:59 | 60.01 | 3679.5967 | 335 | 211.256 | 1 | 235 | 10 | 0 | -103 | 7965.3
2009-10-12 02:59 | 60.012 | 3679.0615 | 335 | 211.256 | 1 | 235.5 | 10 | 0 | -103 | 7966.29
2009-10-12 02:59 | 60.013 | 3679.6367 | 335 | 211.256 | 1 | 236 | 10 | 0 | -103 | 7967.28
2009-10-12 02:59 | 60.01 | 3679.3831 | 335 | 214.3467 | 1 | 236.5 | 10 | 0 | -103 | 7968.27
2009-10-12 02:59 | 60.011 | 3679.1382 | 335 | 214.3467 | 1 | 237 | 10 | 0 | -103 | 7969.26
2009-10-12 03:00 | 60.018 | 3678.4556 | 335 | 214.3467 | 1 | 237.5 | 10 | 0 | -103 | 7970.25
2009-10-12 03:00 | 60.019 | 3677.4314 | 335 | 214.3467 | 2 | 238 | 10 | 0 | -103 | 7971.24
2009-10-12 03:00 | 60.018 | 3678.1511 | 335 | 214.3467 | 3 | 238.5 | 10 | 0 | -103 | 7972.23
2009-10-12 03:00 | 60.016 | 3680.7708 | 335 | 212.1727 | 4 | 239 | 10 | 0 | -103 | 7973.22
2009-10-12 03:00 | 60.022 | 3679.1665 | 335 | 212.1727 | 5 | 239.5 | 10 | 0 | -103 | 7974.21
2009-10-12 03:00 | 60.016 | 3682.7297 | 335 | 212.1727 | 6 | 240 | 10 | 0 | -103 | 7975.2
2009-10-12 03:00 | 60.01 | 3682.0103 | 335 | 212.1727 | 7 | 240.5 | 10 | 0 | -103 | 7976.19
2009-10-12 03:00 | 59.995 | 3685.3064 | 335 | 212.1727 | 8 | 241 | 10 | 0 | -103 | 7977.18
2009-10-12 03:00 | 59.974 | 3687.5271 | 335 | 215.5982 | 9 | 241.5 | 10 | 0 | -103 | 7978.17
2009-10-12 03:00 | 59.968 | 3692.9663 | 335 | 215.5982 | 10 | 242 | 10 | 0 | -103 | 7979.16
2009-10-12 03:00 | 59.972 | 3694.9736 | 335 | 215.5982 | 11 | 242.5 | 10 | 0 | -103 | 7980.15
2009-10-12 03:01 | 59.964 | 3698.6169 | 335 | 215.5982 | 12 | 243 | 10 | 0 | -103 | 7981.14
2009-10-12 03:01 | 59.963 | 3702.6448 | 335 | 215.5982 | 13 | 243.5 | 10 | 0 | -103 | 7982.13
2009-10-12 03:01 | 59.968 | 3704.0234 | 335 | 218.3273 | 14 | 244 | 10 | 0 | -103 | 7983.12
2009-10-12 03:01 | 59.97 | 3703.8137 | 335 | 218.3273 | 15 | 244.5 | 10 | 0 | -103 | 7984.11
2009-10-12 03:01 | 59.976 | 3704.2935 | 335 | 218.3273 | 16 | 245 | 10 | 0 | -103 | 7985.1
2009-10-12 03:01 | 59.977 | 3703.1421 | 335 | 218.3273 | 16 | 245.5 | 10 | 0 | -103 | 7986.09
2009-10-12 03:01 | 59.974 | 3705.6624 | 335 | 218.3273 | 16 | 246 | 10 | 0 | -103 | 7987.08
2009-10-12 03:01 | 59.974 | 3707.5139 | 335 | 217.3794 | 16 | 246.5 | 10 | 0 | -103 | 7988.07
2009-10-12 03:01 | 59.979 | 3706.335 | 335 | 217.3794 | 16 | 247 | 10 | 0 | -103 | 7989.06
2009-10-12 03:02 | 59.985 | 3704.1272 | 335 | 217.3794 | 16 | 247.5 | 10 | 0 | -103 | 7990.05
2009-10-12 03:02 | 59.979 | 3705.9675 | 335 | 217.3794 | 16 | 248 | 10 | 0 | -103 | 7991.04
2009-10-12 03:02 | 59.986 | 3703.9133 | 335 | 217.3794 | 16 | 248.5 | 10 | 0 | -103 | 7992.03
2009-10-12 03:02 | 59.982 | 3705.0498 | 335 | 214.8304 | 16 | 249 | 10 | 0 | -103 | 7993.02
2009-10-12 03:02 | 59.987 | 3701.8311 | 335 | 214.8304 | 16 | 249.5 | 10 | 0 | -103 | 7994.01
2009-10-12 03:02 | 59.996 | 3701.3081 | 335 | 214.8304 | 16 | 250 | 10 | 0 | -103 | 7995
2009-10-12 03:02 | 59.997 | 3700.541 | 335 | 214.8304 | 16 | 250.5 | 10 | 0 | -103 | 7995.99
2009-10-12 03:02 | 59.996 | 3700.5486 | 335 | 214.8304 | 16 | 251 | 10 | 0 | -103 | 7996.98
2009-10-12 03:02 | 59.998 | 3699.5 | 335 | 227.6559 | 16 | 251.5 | 10 | 0 | -103 | 7997.97
2009-10-12 03:02 | 60.01 | 3699.4087 | 335 | 227.6559 | 16 | 252 | 10 | 0 | -103 | 7998.96
2009-10-12 03:02 | 60.004 | 3701.1099 | 335 | 227.6559 | 16 | 252.5 | 10 | 0 | -103 | 7999.95
2009-10-12 03:03 | 60.001 | 3700.2202 | 335 | 227.6559 | 16 | 253 | 10 | 0 | -103 | 8000.94
2009-10-12 03:03 | 60.007 | 3702.2759 | 335 | 227.6559 | 16 | 253.5 | 10 | 0 | -103 | 8001.93
2009-10-12 03:03 | 60.008 | 3702.9431 | 335 | 225.0181 | 16 | 254 | 10 | 0 | -103 | 8002.92
2009-10-12 03:03 | 60.006 | 3703.8193 | 335 | 225.0181 | 16 | 254.5 | 10 | 0 | -103 | 8003.91
2009-10-12 03:03 | 59.999 | 3705.3291 | 335 | 225.0181 | 16 | 255 | 10 | 0 | -103 | 8004.9
2009-10-12 03:03 | 60.004 | 3703.6753 | 335 | 225.0181 | 16 | 255.5 | 10 | 0 | -103 | 8005.89
2009-10-12 03:03 | 60.015 | 3703.0166 | 335 | 225.0181 | 16 | 256 | 10 | 0 | -103 | 8006.88
2009-10-12 03:03 | 60.009 | 3705.1887 | 335 | 228.3652 | 16 | 256.5 | 10 | 0 | -103 | 8007.87
2009-10-12 03:03 | 60.011 | 3704.0513 | 335 | 228.3652 | 16 | 257 | 10 | 0 | -103 | 8008.86
2009-10-12 03:04 | 60.016 | 3703.7075 | 335 | 228.3652 | 16 | 257.5 | 10 | 0 | -103 | 8009.85
2009-10-12 03:04 | 60.019 | 3704.1392 | 335 | 228.3652 | 16 | 258 | 10 | 0 | -103 | 8010.84
2009-10-12 03:04 | 60.011 | 3705.9419 | 335 | 228.3652 | 16 | 258.5 | 10 | 0 | -103 | 8011.83
2009-10-12 03:04 | 60.008 | 3705.7485 | 335 | 234.0753 | 16 | 259 | 10 | 0 | -103 | 8012.82
2009-10-12 03:04 | 60.015 | 3706.6299 | 335 | 234.0753 | 16 | 259.5 | 10 | 0 | -103 | 8013.81
2009-10-12 03:04 | 60.018 | 3704.2239 | 335 | 234.0753 | 16 | 260 | 10 | 0 | -103 | 8014.8
2009-10-12 03:04 | 60.019 | 3704.7954 | 335 | 234.0753 | 16 | 260.5 | 10 | 0 | -103 | 8015.79
2009-10-12 03:04 | 60.025 | 3702.0083 | 335 | 234.0753 | 16 | 261 | 10 | 0 | -103 | 8016.78
2009-10-12 03:04 | 60.027 | 3700.3401 | 335 | 228.7982 | 16 | 261.5 | 10 | 0 | -103 | 8017.77
2009-10-12 03:04 | 60.023 | 3702.9587 | 335 | 228.7982 | 16 | 262 | 10 | 0 | -103 | 8018.76
2009-10-12 03:05 | 60.024 | 3703.374 | 335 | 228.7982 | 16 | 262.5 | 10 | 0 | -103 | 8019.75
2009-10-12 03:05 | 60.022 | 3704.9473 | 335 | 228.7982 | 16 | 263 | 10 | 0 | -103 | 8020.74
2009-10-12 03:05 | 60.023 | 3703.1602 | 335 | 228.7982 | 16 | 263.5 | 10 | 0 | -103 | 8021.73
2009-10-12 03:05 | 60.018 | 3705.4412 | 335 | 229.467 | 16 | 264 | 10 | 0 | -103 | 8022.72
2009-10-12 03:05 | 60.012 | 3707.9707 | 335 | 229.467 | 16 | 264.5 | 10 | 0 | -103 | 8023.71
2009-10-12 03:05 | 60.019 | 3708.8311 | 335 | 229.467 | 16 | 265 | 10 | 0 | -103 | 8024.7
2009-10-12 03:05 | 60.015 | 3709.8169 | 335 | 229.467 | 16 | 265.5 | 10 | 0 | -103 | 8025.69
2009-10-12 03:05 | 60.016 | 3709.6416 | 335 | 229.467 | 16 | 266 | 10 | 0 | -103 | 8026.68
2009-10-12 03:05 | 60.016 | 3710.6768 | 335 | 228.9802 | 16 | 266.5 | 10 | 0 | -103 | 8027.67
2009-10-12 03:05 | 60.018 | 3707.696 | 335 | 228.9802 | 16 | 267 | 10 | 0 | -103 | 8028.66
2009-10-12 03:06 | 60.024 | 3706.99 | 335 | 228.9802 | 16 | 267.5 | 10 | 0 | -103 | 8029.65
2009-10-12 03:06 | 60.024 | 3704.4058 | 335 | 228.9802 | 16 | 268 | 10 | 0 | -103 | 8030.64
2009-10-12 03:06 | 60.019 | 3705.5159 | 335 | 228.9802 | 16 | 268.5 | 10 | 0 | -103 | 8031.63
2009-10-12 03:06 | 60.028 | 3704.7734 | 335 | 219.9756 | 16 | 269 | 10 | 0 | -103 | 8032.62
2009-10-12 03:06 | 60.029 | 3702.093 | 335 | 219.9756 | 16 | 269.5 | 10 | 0 | -103 | 8033.61
2009-10-12 03:06 | 60.029 | 3701.5195 | 335 | 219.9756 | 16 | 270 | 10 | 0 | -103 | 8034.6
2009-10-12 03:06 | 60.03 | 3698.0088 | 335 | 219.9756 | 16 | 270.5 | 10 | 0 | -103 | 8035.59
2009-10-12 03:06 | 60.019 | 3703.8147 | 335 | 219.9756 | 16 | 271 | 10 | 0 | -103 | 8036.58
2009-10-12 03:06 | 60.021 | 3700.8157 | 335 | 229.0892 | 16 | 271.5 | 10 | 0 | -103 | 8037.57
2009-10-12 03:06 | 60.012 | 3708.5273 | 335 | 229.0892 | 16 | 272 | 10 | 0 | -103 | 8038.56
2009-10-12 03:06 | 60.013 | 3706.9912 | 335 | 229.0892 | 16 | 272.5 | 10 | 0 | -103 | 8039.55
2009-10-12 03:07 | 60.016 | 3705.3979 | 335 | 229.0892 | 16 | 273 | 10 | 0 | -103 | 8040.54
2009-10-12 03:07 | 60.007 | 3708.9895 | 335 | 229.0892 | 16 | 273.5 | 10 | 0 | -103 | 8041.53
2009-10-12 03:07 | 59.993 | 3707.3037 | 335 | 229.6633 | 16 | 274 | 10 | 0 | -103 | 8042.52
2009-10-12 03:07 | 59.994 | 3706.9211 | 335 | 229.6633 | 16 | 274.5 | 10 | 0 | -103 | 8043.51
2009-10-12 03:07 | 59.993 | 3704.9336 | 335 | 229.6633 | 16 | 275 | 10 | 0 | -103 | 8044.5
2009-10-12 03:07 | 59.985 | 3707.0713 | 335 | 229.6633 | 16 | 275.5 | 10 | 0 | -103 | 8045.49
2009-10-12 03:07 | 59.98 | 3708.2458 | 335 | 229.6633 | 16 | 276 | 10 | 0 | -103 | 8046.48
2009-10-12 03:07 | 59.982 | 3710.1338 | 335 | 229.2339 | 16 | 276.5 | 10 | 0 | -103 | 8047.47
2009-10-12 03:07 | 59.98 | 3709.1919 | 335 | 229.2339 | 16 | 277 | 10 | 0 | -103 | 8048.46
2009-10-12 03:08 | 59.983 | 3707.9114 | 335 | 229.2339 | 16 | 277.5 | 10 | 0 | -103 | 8049.45
2009-10-12 03:08 | 59.981 | 3709.689 | 335 | 229.2339 | 16 | 278 | 10 | 0 | -103 | 8050.44
2009-10-12 03:08 | 59.981 | 3711.2563 | 350 | 229.2339 | 16 | 278.5 | 10 | 0 | -103 | 8051.43
2009-10-12 03:08 | 59.978 | 3712.0122 | 350 | 231.4099 | 16 | 279 | 10 | 0 | -103 | 8052.42
2009-10-12 03:08 | 59.978 | 3713.9917 | 350 | 231.4099 | 16 | 279.5 | 10 | 0 | -103 | 8053.41
2009-10-12 03:08 | 59.975 | 3715.3228 | 350 | 231.4099 | 16 | 280 | 10 | 0 | -103 | 8054.4
2009-10-12 03:08 | 59.979 | 3715.1614 | 350 | 231.4099 | 16 | 280.5 | 10 | 0 | -103 | 8055.39
2009-10-12 03:08 | 59.976 | 3714.0627 | 350 | 231.4099 | 16 | 281 | 10 | 0 | -103 | 8056.38
2009-10-12 03:08 | 59.975 | 3715.6885 | 350 | 218.6223 | 16 | 281.5 | 10 | 0 | -103 | 8057.37
2009-10-12 03:08 | 59.98 | 3714.8481 | 350 | 218.6223 | 16 | 282 | 10 | 0 | -103 | 8058.36
2009-10-12 03:08 | 59.979 | 3712.2747 | 350 | 218.6223 | 16 | 282.5 | 10 | 0 | -103 | 8059.35
2009-10-12 03:09 | 59.987 | 3710.0503 | 350 | 218.6223 | 16 | 283 | 10 | 0 | -103 | 8060.34
2009-10-12 03:09 | 59.98 | 3710.6235 | 350 | 218.6223 | 16 | 283.5 | 10 | 0 | -103 | 8061.33
2009-10-12 03:09 | 59.979 | 3710.4746 | 350 | 213.5359 | 16 | 284 | 10 | 0 | -103 | 8062.32
2009-10-12 03:09 | 59.979 | 3709.2859 | 350 | 213.5359 | 16 | 284.5 | 10 | 0 | -103 | 8063.31
2009-10-12 03:09 | 59.983 | 3708.3711 | 350 | 213.5359 | 16 | 285 | 10 | 0 | -103 | 8064.3
2009-10-12 03:09 | 59.987 | 3707.4905 | 350 | 213.5359 | 16 | 285.5 | 10 | 0 | -103 | 8065.29
2009-10-12 03:09 | 59.979 | 3712.3035 | 350 | 213.5359 | 16 | 286 | 10 | 0 | -103 | 8066.28
2009-10-12 03:09 | 59.979 | 3712.0762 | 350 | 225.6519 | 16 | 286.5 | 10 | 0 | -103 | 8067.27
2009-10-12 03:09 | 59.975 | 3713.5103 | 350 | 225.6519 | 16 | 287 | 10 | 0 | -103 | 8068.26
2009-10-12 03:10 | 59.999 | 3712.0918 | 350 | 225.6519 | 16 | 287.5 | 10 | 0 | -103 | 8069.25
2009-10-12 03:10 | 59.986 | 3714.9531 | 350 | 225.6519 | 16 | 288 | 10 | 0 | -103 | 8070.24
2009-10-12 03:10 | 59.982 | 3715.4385 | 350 | 225.6519 | 16 | 288.5 | 10 | 0 | -103 | 8071.23
2009-10-12 03:10 | 59.995 | 3715.0676 | 350 | 212.5736 | 16 | 289 | 10 | 0 | -103 | 8072.22
2009-10-12 03:10 | 59.989 | 3716.2847 | 350 | 212.5736 | 16 | 289.5 | 10 | 0 | -103 | 8073.21
2009-10-12 03:10 | 60 | 3711.7085 | 350 | 212.5736 | 16 | 290 | 10 | 0 | -103 | 8074.2
2009-10-12 03:10 | 60.004 | 3713.3616 | 350 | 212.5736 | 16 | 290.5 | 10 | 0 | -103 | 8075.19
2009-10-12 03:10 | 59.998 | 3719.0791 | 350 | 212.5736 | 16 | 291 | 10 | 0 | -103 | 8076.18
2009-10-12 03:10 | 60.001 | 3717.8887 | 350 | 219.8973 | 16 | 291.5 | 10 | 0 | -103 | 8077.17
2009-10-12 03:10 | 60.003 | 3719.0212 | 350 | 219.8973 | 16 | 292 | 10 | 0 | -103 | 8078.16
2009-10-12 03:10 | 60.004 | 3719.2993 | 350 | 219.8973 | 16 | 292.5 | 10 | 0 | -103 | 8079.15
2009-10-12 03:11 | 60.003 | 3719.731 | 350 | 219.8973 | 16 | 293 | 10 | 0 | -103 | 8080.14
2009-10-12 03:11 | 60.009 | 3718.9761 | 350 | 219.8973 | 16 | 293.5 | 10 | 0 | -103 | 8081.13
2009-10-12 03:11 | 60.009 | 3720.6089 | 350 | 231.1754 | 16 | 294 | 10 | 0 | -103 | 8082.12
2009-10-12 03:11 | 60.014 | 3720.3804 | 350 | 231.1754 | 16 | 294.5 | 10 | 0 | -103 | 8083.11
2009-10-12 03:11 | 60.008 | 3721.2722 | 350 | 231.1754 | 16 | 295 | 10 | 0 | -103 | 8084.1
2009-10-12 03:11 | 60.009 | 3721.5938 | 350 | 231.1754 | 16 | 295.5 | 10 | 0 | -103 | 8085.09
2009-10-12 03:11 | 60.014 | 3721.646 | 350 | 231.1754 | 16 | 296 | 10 | 0 | -103 | 8086.08
2009-10-12 03:11 | 60.01 | 3721.6453 | 350 | 226.6341 | 16 | 296.5 | 10 | 0 | -103 | 8087.07
2009-10-12 03:11 | 60.003 | 3724.656 | 350 | 226.6341 | 16 | 297 | 10 | 0 | -103 | 8088.06
2009-10-12 03:11 | 59.998 | 3723.696 | 350 | 226.6341 | 16 | 297.5 | 10 | 0 | -103 | 8089.05
2009-10-12 03:12 | 60.002 | 3721.8789 | 350 | 226.6341 | 16 | 298 | 10 | 0 | -103 | 8090.04
2009-10-12 03:12 | 59.999 | 3724.1421 | 350 | 226.6341 | 16 | 298.5 | 10 | 0 | -103 | 8091.03
2009-10-12 03:12 | 59.995 | 3723.6389 | 350 | 227.2551 | 16 | 299 | 10 | 0 | -103 | 8092.02
2009-10-12 03:12 | 59.988 | 3725.3608 | 350 | 227.2551 | 16 | 299.5 | 10 | 0 | -103 | 8093.01
2009-10-12 03:12 | 59.992 | 3723.6926 | 350 | 227.2551 | 16 | 300 | 10 | 0 | -103 | 8094

## Entry Data
Balancing Authority Name: | My BA
Balancing Authority Frequency Response Obligation (FRO from FRS Form 1) | -80
Note: See "Instruction" tab for more detailed instructions.
Step 1. | Copy and Paste Event Data into the appropriate cells of the "Data" worksheet.
Maintain date and time format of mm/dd/yy hh:mm:ss.
Step 2. | Determine Time of T(0) and edit formula in cell "C8" to reference the correct row of the "Data" worksheet. | 40098.1024
T(0) is the first change in frequency of about 0.010 Hz (10 mHz) which should be the first scan of frequency data of the event.
Step 3. | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1063
Step 4. | Enter MW output of generator or load that caused event (+ for gen loss, - for load loss) | 633 | MW
(Value from NERC Event List. If multiple units, enter total MW loss.)
If MW loss value is not known, enter a default 1000 MW.
Step 5. | Hit the big blue button to copy your data for pasting into FRS Form 1 "BA Event Data" worksheet.
Step 6. | Paste data into "FRS Form 1" in the appropriate row on the "BA Event Data" worksheet.
Step 7. | Save this workbook using the following file name format:MyBA_yymmdd_hhmm_FRS_Form2.xlsm
| 2009-10-12 02:27 | Date yymmdd
| 40098.1024 | Time hh:ss of T(0)
Where "MyBA" = your BA mnemonic
Copy Form 2 Data for Pasting into Form 1
Note on C8: Cell "C8": Observe the first change in frequency that identifies the beginning of the event. Look in column "B" of the "Data" worksheet. Select and edit the formula in this cell ("=Data!Axxx") to reference that row number in the "Data" sheet of this first change in frequency where xxx is that row number.
Note on C11: Cell "C11": Similar to identifying the end of a DCS event but only looking at frequency, observe frequency following the beginning of the event. When actual frequency recovers to 60.00 Hz or to the pre-event frequency, edit the formula in this cell to reference that row number in the "Data" worksheet that this occurs. ("=Data!Axxx")

## IPFR (hidden)
IPFR = Interconnection Primary Frequency Response

## Evaluation
scan rate | 2 | seconds |  |  | Date: | 2009-10-12 02:27 |  |  | Balancing Authority | My BA | [10 empty] | A Point | 40098.1023 |  |  |  |  | A Point | 40098.1023 | [13 empty] | Non-Conforming Load sign convention | + | (Data is positive for Load then enter "+" else "-" | [11 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27
[5 empty] | Time of T(0) | 40098.1024 |  |  | Grid Nominal Frequency | 60 | Hz | [9 empty] | FPointA | 60.041 | 40098.1023 |  |  |  | FPointA | 60.041 | 40098.1023 | [26 empty] | Time of T(0) | 40098.1024 | [12 empty] | Time of T(0) | 40098.1024 | [12 empty] | Time of T(0) | 40098.1024 | [12 empty] | Time of T(0) | 40098.1024 | [12 empty] | Time of T(0) | 40098.1024
[5 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1063 |  |  | Capacity @ Droop for Minimum Performance | 2400 | MW | [9 empty] | A Value | 60.042 |  |  |  |  | A Value | 60.042 | [27 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1063 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1063 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1063 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1063 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1063
[5 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.042 | Hz |  | Droop Setting | 5% | 3 | Hz | [8 empty] | C Value | 59.869 | 40098.1025 |  |  |  | C Value | 59.869 | #N/A | [26 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.042 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.042 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.042 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.042 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.042 | Hz
[5 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+52)] | 59.888 | Hz |  | Deadband Setting | 0 | Hz | [9 empty] | Delta FCA | -0.173 |  |  |  |  | Delta FC | [28 empty] | Value B Post-Perturbation Average Frequency [T(+12 to T(+24)] | 59.8797 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+18 to T(+30)] | 59.8834 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+40)] | 59.8873 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+18 to T(+52)] | 59.8876 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+52)] | 59.888 | Hz
[5 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.154 | Hz |  | Hz Span | 3 | Hz | [9 empty] | FR C | -365.8952 | MW/0.1 Hz | [32 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.16229 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15857 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15473 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15444 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.154 | Hz
[5 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3645.0407 | MW |  | Frequency Response Obligation (FRO) | -80 | MW/0.1 Hz | [9 empty] | Slope A-C dF/dT | -0.012286 | Hz/second |  |  |  |  | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | [18 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3645.0407 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3645.0407 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3645.0407 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3645.0407 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3645.0407 | MW
[5 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+52)] | 3788.7895 | MW | [13 empty] | C Value Maximum Resource Loss | 633 | [5 empty] | 12 to 24 sec | 12 to 24 sec | 18 to 30 sec | 18 to 30 sec | 20 to 40 sec | 20 to 40 sec | 18 to 52 sec | 18 to 52 sec | 20 to 52 sec | 20 to 52 sec | [18 empty] | Value B Post-Perturbation Average Interchange MW [T(+12 to T(+24)] | 3768.2286 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+18 to T(+30)] | 3780.4202 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+40)] | 3785.2644 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+18 to T(+52)] | 3787.5342 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+52)] | 3788.7895 | MW
[5 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 143.7488 | MW | [13 empty] | Secondary C Value | 59.857 | 40098.1032 | Time |  |  | B Frequency Value | 59.8797 |  | 59.8834 |  | 59.888 |  | 59.8876 |  | 59.888 | [19 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 123.1878 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 135.3795 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 140.2236 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 142.4934 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 143.7488 | MW
[5 empty] | Initial Performance Ramp Magnitude Adjustment | -17.5652 | MW | [19 empty] | Delta FB | -0.16229 | -390.3519 | -0.15857 | -399.2319 | -0.154 | -409.3538 | -0.15444 | -410.1357 | -0.154 | -411.2764 | [18 empty] | Net Total Adjustments | -52.6738 | MW | [11 empty] | Net Total Adjustments | -52.5451 | MW | [11 empty] | Net Total Adjustments | -54.5711 | MW | [11 empty] | Net Total Adjustments | -54.9489 | MW | [11 empty] | Net Total Adjustments | -55.0726 | MW
[5 empty] | EPFR Pre-Perturbation Average | -33.5999 | MW | [19 empty] | Slope B dF/dT | -0.0081143 |  | -0.0079286 |  | -0.0077 |  | -0.0077222 |  | -0.0077 | [19 empty] | EPFR for FRO Pre-Perturbation Average | -33.5999 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -33.5999 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -33.5999 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -33.5999 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -33.5999 | MW
[5 empty] | EPFR Post-Perturbation Average | 89.6005 | MW | [19 empty] | RatioB-C | 93.8064 |  | 91.66 |  | 89.0174 |  | 89.2743 |  | 89.0174 | [19 empty] | EPFR for FRO Post-Perturbation Average | 96.2285 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 93.2578 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 90.1822 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 89.956 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 89.6005 | MW
[5 empty] | EPFR Delta | 123.2004 | MW |  | TC (frequency response filter constant) | 0.35 | Time Constant for delayed delivery of PFR during Sustained Measure | [15 empty] | Sustainability Index | -0.012014 |  | -0.015728 |  | -0.020299 |  | -0.019855 |  | -0.020299 | [19 empty] | EPFR for FRO Delta | 129.8283 | MW | [11 empty] | EPFR for FRO Delta | 126.8576 | MW | [11 empty] | EPFR for FRO Delta | 123.7821 | MW | [11 empty] | EPFR for FRO Delta | 123.5558 | MW | [11 empty] | EPFR for FRO Delta | 123.2004 | MW
[21 empty] | Tzero | 40098.1023 | [33 empty] | EPFR for FRO Adjusted | 77.1545 | MW | [11 empty] | EPFR for FRO Adjusted | 74.3125 | MW | [11 empty] | EPFR for FRO Adjusted | 69.211 | MW | [11 empty] | EPFR for FRO Adjusted | 68.607 | MW | [11 empty] | EPFR for FRO Adjusted | 68.1278 | MW
[21 empty] | FT+4 | 59.978 | [33 empty] | Pre JOU Dynamic Schedules MW | 350 |  |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 350 |  |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 350 | MW |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 350 | MW |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 350 | MW |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz
[9 empty] | Low Hz | Delta Hz Event | [10 empty] | FT+10 | 59.869 | [33 empty] | Pre Non-Conforming Load MW | -165.4764 |  |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | -165.4764 |  |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | -165.4764 | MW |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | -165.4764 | MW |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | -165.4764 | MW |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz
[9 empty] | 3764.6602 | Actual Interchange MW Average during frequency recovery period | [10 empty] | FT+20 | 59.883 | [33 empty] | Pre Pumped Hydro MW | 0 |  |  |  | EPFR for Bias Setting Pre-Perturbation Average | -43.2598 | MW | [6 empty] | Pre Pumped Hydro MW | 0 |  |  |  | EPFR for Bias Setting Pre-Perturbation Average | -43.2598 | MW | [6 empty] | Pre Pumped Hydro MW | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | -43.2598 | MW | [6 empty] | Pre Pumped Hydro MW | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | -43.2598 | MW | [6 empty] | Pre Pumped Hydro MW | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | -43.2598 | MW
[9 empty] | 3778.5219 | Target Interchange MW Average during frequency recovery period | [10 empty] | FT+60 | 59.888 | [33 empty] | Pre Ramping Units MW | 76.0625 |  |  |  | EPFR for Bias Setting Post-Perturbation Average | 123.8941 | MW | [6 empty] | Pre Ramping Units MW | 76.0625 |  |  |  | EPFR for Bias Setting Post-Perturbation Average | 120.0694 | MW | [6 empty] | Pre Ramping Units MW | 76.0625 | MW |  |  | EPFR for Bias Setting Post-Perturbation Average | 116.1096 | MW | [6 empty] | Pre Ramping Units MW | 76.0625 | MW |  |  | EPFR for Bias Setting Post-Perturbation Average | 115.8183 | MW | [6 empty] | Pre Ramping Units MW | 76.0625 | MW |  |  | EPFR for Bias Setting Post-Perturbation Average | 115.3607 | MW
|  |  | EPFR = Expected Primary Frequency Response |  | EPFR(Final) | 105.6352 | MW |  | 3726.235 | Interchange Average Ramp MW during frequency recovery period | [8 empty] | Interconnection Evaluation | [36 empty] | Pre Transferred Frequency Response MW | -4.2 |  |  |  | EPFR for Bias Setting Delta | 167.154 | MW | [6 empty] | Pre Transferred Frequency Response MW | -4.2 |  |  |  | EPFR for Bias Setting Delta | 163.3292 | MW | [6 empty] | Pre Transferred Frequency Response MW | -4.2 | MW |  |  | EPFR for Bias Setting Delta | 159.3694 | MW | [6 empty] | Pre Transferred Frequency Response MW | -4.2 | MW |  |  | EPFR for Bias Setting Delta | 159.0781 | MW | [6 empty] | Pre Transferred Frequency Response MW | -4.2 | MW |  |  | EPFR for Bias Setting Delta | 158.6205 | MW
[5 empty] | MW Response in right direction for frequency delta | Yes |  |  | 3640.6821 | Actual MW @ T(-4) | [45 empty] | Pre Contingent BA Lost Generation MW | 15 |  |  |  | Primary Frequency Response Delivery of Bias | 73.7% | [7 empty] | Pre Contingent BA Lost Generation MW | 15 |  |  |  | Primary Frequency Response Delivery of Bias | 82.89% | [7 empty] | Pre Contingent BA Lost Generation MW | 15 | MW |  |  | Primary Frequency Response Delivery of Bias | 87.99% | [7 empty] | Pre Contingent BA Lost Generation MW | 15 | MW |  |  | Primary Frequency Response Delivery of Bias | 89.57% | [7 empty] | Pre Contingent BA Lost Generation MW | 15 | MW |  |  | Primary Frequency Response Delivery of Bias | 90.62%
[9 empty] | 105.2713 | Starting and Ending Difference in Interchange MW during frequency recovery period (indicates ramp direction during recovery period) | [45 empty] | Sum of Pre Perturbation Adjustments | 271.3861 | [12 empty] | Sum of Pre Perturbation Adjustments | 271.3861 | [12 empty] | Sum of Pre Perturbation Adjustments | 271.3861 | MW | [11 empty] | Sum of Pre Perturbation Adjustments | 271.3861 | MW | [11 empty] | Sum of Pre Perturbation Adjustments | 271.3861 | MW
[9 empty] | 0:06 | Event Duration (h:mm:ss)
[9 empty] | No | Target MW Average minus MW @ T(-4) less than zero | [10 empty] | B Value Average Resource Loss | 633 | [33 empty] | Post JOU Dynamic Schedules MW | 335 |  |  |  | Pre-Perturbation BA Load | 7650.6038 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 335 |  |  |  | Pre-Perturbation BA Load | 7650.6038 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 335 | MW |  |  | Pre-Perturbation BA Load | 7650.6038 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 335 | MW |  |  | Pre-Perturbation BA Load | 7650.6038 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 335 | MW |  |  | Pre-Perturbation BA Load | 7650.6038 | MW
[9 empty] | 137.8398 | Interchange Target Relative Average Change - MW (Low Frequency Event) | [10 empty] | B Value Average LaaR Loss | 0 | [33 empty] | Post Non-Conforming Load MW | -206.4591 |  |  |  | Post-Perturbation BA Load | 7631.7143 | MW | [6 empty] | Post Non-Conforming Load MW | -206.4591 |  |  |  | Post-Perturbation BA Load | 7630.5714 | MW | [6 empty] | Post Non-Conforming Load MW | -208.6395 | MW |  |  | Post-Perturbation BA Load | 7630.6364 | MW | [6 empty] | Post Non-Conforming Load MW | -209.3906 | MW |  |  | Post-Perturbation BA Load | 7631.5 | MW | [6 empty] | Post Non-Conforming Load MW | -209.563 | MW |  |  | Post-Perturbation BA Load | 7631.5294 | MW
[9 empty] | 123.9781 | Interchange Actual Relative Average Change - MW (Low Frequency Event) | [10 empty] | B Value Average Net Loss | 633 | [33 empty] | Post Pumped Hydro MW | 0 |  |  |  | Pre to Post Perturbation BA Load Change | -18.8895 | MW | [6 empty] | Post Pumped Hydro MW | 0 |  |  |  | Pre to Post Perturbation BA Load Change | -20.0323 | MW | [6 empty] | Post Pumped Hydro MW | 0 | MW |  |  | Pre to Post Perturbation BA Load Change | -19.9674 | MW | [6 empty] | Post Pumped Hydro MW | 0 | MW |  |  | Pre to Post Perturbation BA Load Change | -19.1038 | MW | [6 empty] | Post Pumped Hydro MW | 0 | MW |  |  | Pre to Post Perturbation BA Load Change | -19.0743 | MW
[9 empty] | No | Interchange Actual Average minus MW @ T(-4) less than zero | [45 empty] | Post Ramping Units MW | 78.1429 |  |  |  | Load Dampening Frequency Response | -11.6397 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 78.6429 |  |  |  | Load Dampening Frequency Response | -12.6329 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 79.1818 | MW |  |  | Load Dampening Frequency Response | -12.9049 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 79.5833 | MW |  |  | Load Dampening Frequency Response | -12.3693 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 79.6765 | MW |  |  | Load Dampening Frequency Response | -12.3859 | MW/0.1 Hz
[9 empty] | Yes | Interchange Average MW minus MW @ T(-4) greater than zero | [13 empty] | Interconnection Bias Total | [31 empty] | Post Transferred Frequency Response MW | 12.0286 |  |  |  | Load Dampening % of Total BA Frequency Response | 15.33% | [7 empty] | Post Transferred Frequency Response MW | 11.6572 |  |  |  | Load Dampening % of Total BA Frequency Response | 14.8% | [7 empty] | Post Transferred Frequency Response MW | 11.2728 | MW |  |  | Load Dampening % of Total BA Frequency Response | 14.24% | [7 empty] | Post Transferred Frequency Response MW | 11.2445 | MW |  |  | Load Dampening % of Total BA Frequency Response | 13.41% | [7 empty] | Post Transferred Frequency Response MW | 11.2001 | MW |  |  | Load Dampening % of Total BA Frequency Response | 13.27%
[9 empty] | Yes | Interchange Target MW Average minus MW @ T(-4) greater than zero | [13 empty] | EI | ERCOT | WECC | [29 empty] | Post Contingent BA Lost Generation MW | 0 | [12 empty] | Post Contingent BA Lost Generation MW | 0 | [12 empty] | Post Contingent BA Lost Generation MW | 0 | MW | [11 empty] | Post Contingent BA Lost Generation MW | 0 | MW | [11 empty] | Post Contingent BA Lost Generation MW | 0 | MW
[9 empty] | 32.5685 | Interchange Target Relative Average Change - MW (High Frequency Event) | [10 empty] | Interconnection Bias Setting | -660 |  | -6349 | -660 | -2024 | [29 empty] | Sum of Post Perturbation Adjustments | 218.7123 | [12 empty] | Sum of Post Perturbation Adjustments | 218.841 | [12 empty] | Sum of Post Perturbation Adjustments | 216.8151 | MW | [11 empty] | Sum of Post Perturbation Adjustments | 216.4373 | MW | [11 empty] | Sum of Post Perturbation Adjustments | 216.3135 | MW
[9 empty] | 18.7067 | Interchange Actual Relative Average Change - MW (High Frequency Event) | [10 empty] | IPFR as a % of Bias Setting | 0% | [33 empty] | Net Total Adjustments MW | -52.6738 | [12 empty] | Net Total Adjustments MW | -52.5451 | [12 empty] | Net Total Adjustments MW | -54.5711 | MW | [11 empty] | Net Total Adjustments MW | -54.9489 | MW | [11 empty] | Net Total Adjustments MW | -55.0726 | MW
[9 empty] | Up | Ramp Direction during frequency recovery period | [10 empty] | Interconnection Total Energy | 37446 | 60.07%
[21 empty] | Interconnection Peak Energy | 62339 |  |  |  |  | Frequency and Interconnection Frequency Response @ different Average periods of B | [11 empty] | Frequency, Actual Interchange, Adjustment Data, Bias and Load used in the evaluation | [12 empty] | 12 to 24 second Average Period Evaluation | [13 empty] | 18 to 30 second Average Period Evaluation | [13 empty] | 20 to 40 second Average Period Evaluation | [13 empty] | 18 to 52 second Average Period Evaluation | [13 empty] | 20 to 52 second Average Period Evaluation
[5 empty] | Initial Response P.U. Performance | 1.3608 | P.U. |  | 0.89944 | P.U. Sustianed Response P.U. Performance | [45 empty] | Initial P.U. Performance for FRO | 0.94885 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.0672 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.1328 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.1533 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.1668 | P.U.
[56 empty] | Initial P.U. Performance Adjusted for FRO | 1.3546 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 1.4814 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 1.5737 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 1.598 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 1.6138 | P.U.
[9 empty] | Initial | [6 empty] | Generator | Generator | Generator | Generator | Generator | Generator | Generator | LaaR | Total | Interconnection | FR B | [15 empty] | JOU | Non- |  |  | Transferred | Contingent | [7 empty] | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected
[7 empty] | FRO |  | Measure |  |  | Average | Average |  | Average | Trip | Trip | Trip | Trip | Trip | Trip | Trip | Trip | Generation | Primary | 20 to 52 sec |  | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Expected |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net
[7 empty] | (EPFR) | (TC) | Final |  |  | Output | Target |  | Ramp | MW | MW | MW | MW | MW | MW | MW | MW | Trip | Frequency | Average |  | 12 to 24 sec | 12 to 24 sec | 18 to 30 sec | 18 to 30 sec | 20 to 40 sec | 20 to 40 sec | 18 to 52 sec | 18 to 52 sec | 20 to 52 sec | 20 to 52 sec |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Primary |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual
|  |  |  | Value B |  |  | Expected | Delayed | Expected |  | Recovery | During | During | Recovery | During | [8 empty] | MW | Response | MW |  | Average | Average | Average | Average | Average | Average | Average | Average | Average | Average |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | Freq Response |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange
|  |  |  | 20 to 52 sec |  |  | Primary | Delivery | Primary | Average | Period | Recovery | Recovery | Period | Recovery | [12 empty] | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW
|  | Frequency | Interchange | Average | Average |  | Frequency | Frequency | Frequency | Ramp | Target | Period | Period | Ramp | Period
| T | Hz | MW | Frequency | MW |  | Response | Response | Response | MW/scan | MW | MW | MW | MW | MW | 633 | [8 empty] | MW/0.1 Hz
0
T-72 sec | 40098.1015 | 60.027 | 3668.6106 |  |  |  | -21.6003 | -7.5601 | [15 empty] | 0 |  |  | T-72 sec | [10 empty] | T-72 sec | 40098.1015 | 60.027 | 3668.6106 | 350 | -165.4764 | 0 | 71 | 10 | 15 | -103 | 7640.58 | -21.6003 | T-72 sec | 40098.1015 | [12 empty] | T-72 sec | 40098.1015 | [12 empty] | T-72 sec | 40098.1015 | [12 empty] | T-72 sec | 40098.1015 | [12 empty] | T-72 sec | 40098.1015
T-70 sec | 40098.1016 | 60.027 | 3668.6106 |  |  |  | -21.6003 | -12.4742 | [15 empty] | 0 |  |  | T-70 sec | [10 empty] | T-70 sec | 40098.1016 | 60.027 | 3668.6106 | 350 | -165.4764 | 0 | 71 | 10 | 15 | -103 | 7640.58 | -21.6003 | T-70 sec | 40098.1016 | [12 empty] | T-70 sec | 40098.1016 | [12 empty] | T-70 sec | 40098.1016 | [12 empty] | T-70 sec | 40098.1016 | [12 empty] | T-70 sec | 40098.1016
T-68 sec | 40098.1016 | 60.027 | 3668.6106 |  |  |  | -21.6003 | -15.6683 | [15 empty] | 0 |  |  | T-68 sec | [10 empty] | T-68 sec | 40098.1016 | 60.027 | 3668.6106 | 350 | -165.4764 | 0 | 71 | 10 | 15 | -103 | 7640.58 | -21.6003 | T-68 sec | 40098.1016 | [12 empty] | T-68 sec | 40098.1016 | [12 empty] | T-68 sec | 40098.1016 | [12 empty] | T-68 sec | 40098.1016 | [12 empty] | T-68 sec | 40098.1016
T-66 sec | 40098.1016 | 60.022 | 3666.0618 |  |  |  | -17.5995 | -16.3442 | [15 empty] | 0 |  |  | T-66 sec | [10 empty] | T-66 sec | 40098.1016 | 60.022 | 3666.0618 | 350 | -165.4764 | 0 | 71.5 | 10 | 15 | -103 | 7641.57 | -17.5995 | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016
T-64 sec | 40098.1016 | 60.022 | 3666.0618 |  |  |  | -17.5995 | -16.7836 | [15 empty] | 0 |  |  | T-64 sec | [10 empty] | T-64 sec | 40098.1016 | 60.022 | 3666.0618 | 350 | -165.4764 | 0 | 71.5 | 10 | 15 | -103 | 7641.57 | -17.5995 | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016
T-62 sec | 40098.1016 | 60.022 | 3666.0618 |  |  |  | -17.5995 | -17.0691 | [15 empty] | 0 |  |  | T-62 sec | [10 empty] | T-62 sec | 40098.1016 | 60.022 | 3666.0618 | 350 | -165.4764 | 0 | 71.5 | 10 | 15 | -103 | 7641.57 | -17.5995 | T-62 sec | 40098.1016 | [12 empty] | T-62 sec | 40098.1016 | [12 empty] | T-62 sec | 40098.1016 | [12 empty] | T-62 sec | 40098.1016 | [12 empty] | T-62 sec | 40098.1016
T-60 sec | 40098.1017 | 60.019 | 3670.4536 |  |  |  | -15.2008 | -16.4152 |  | -0.44216 | 3670.4536 | [12 empty] | 0 |  |  | T-60 sec | [10 empty] | T-60 sec | 40098.1017 | 60.019 | 3670.4536 | 350 | -165.4764 | 0 | 72 | 10 | 15 | -103 | 7642.56 | -15.2008 | T-60 sec | 40098.1017 | [12 empty] | T-60 sec | 40098.1017 | [12 empty] | T-60 sec | 40098.1017 | [12 empty] | T-60 sec | 40098.1017 | [12 empty] | T-60 sec | 40098.1017
T-58 sec | 40098.1017 | 60.019 | 3670.4536 |  |  |  | -15.2008 | -15.9902 |  | -0.44216 | 3670.4365 | [12 empty] | 0 |  |  | T-58 sec | [10 empty] | T-58 sec | 40098.1017 | 60.019 | 3670.4536 | 350 | -165.4764 | 0 | 72 | 10 | 15 | -103 | 7642.56 | -15.2008 | T-58 sec | 40098.1017 | [12 empty] | T-58 sec | 40098.1017 | [12 empty] | T-58 sec | 40098.1017 | [12 empty] | T-58 sec | 40098.1017 | [12 empty] | T-58 sec | 40098.1017
T-56 sec | 40098.1017 | 60.019 | 3670.4536 |  |  |  | -15.2008 | -15.7139 |  | -0.44216 | 3670.2706 | [12 empty] | 0 |  |  | T-56 sec | [10 empty] | T-56 sec | 40098.1017 | 60.019 | 3670.4536 | 350 | -165.4764 | 0 | 72 | 10 | 15 | -103 | 7642.56 | -15.2008 | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017
T-54 sec | 40098.1017 | 60.021 | 3672.4932 |  |  |  | -16.7999 | -16.094 |  | -0.44216 | 3669.4483 | [12 empty] | 0 |  |  | T-54 sec | [10 empty] | T-54 sec | 40098.1017 | 60.021 | 3672.4932 | 350 | -165.4764 | 0 | 72.5 | 10 | 15 | -103 | 7643.55 | -16.7999 | T-54 sec | 40098.1017 | [12 empty] | T-54 sec | 40098.1017 | [12 empty] | T-54 sec | 40098.1017 | [12 empty] | T-54 sec | 40098.1017 | [12 empty] | T-54 sec | 40098.1017
T-52 sec | 40098.1018 | 60.021 | 3672.4932 |  |  |  | -16.7999 | -16.3411 |  | -0.44216 | 3668.7591 | [12 empty] | 0 |  |  | T-52 sec | [10 empty] | T-52 sec | 40098.1018 | 60.021 | 3672.4932 | 350 | -165.4764 | 0 | 72.5 | 10 | 15 | -103 | 7643.55 | -16.7999 | T-52 sec | 40098.1018 | [12 empty] | T-52 sec | 40098.1018 | [12 empty] | T-52 sec | 40098.1018 | [12 empty] | T-52 sec | 40098.1018 | [12 empty] | T-52 sec | 40098.1018
T-50 sec | 40098.1018 | 60.021 | 3672.4932 |  |  |  | -16.7999 | -16.5017 |  | -0.44216 | 3668.1563 | [12 empty] | 0 |  |  | T-50 sec | [10 empty] | T-50 sec | 40098.1018 | 60.021 | 3672.4932 | 350 | -165.4764 | 0 | 72.5 | 10 | 15 | -103 | 7643.55 | -16.7999 | T-50 sec | 40098.1018 | [12 empty] | T-50 sec | 40098.1018 | [12 empty] | T-50 sec | 40098.1018 | [12 empty] | T-50 sec | 40098.1018 | [12 empty] | T-50 sec | 40098.1018
T-48 sec | 40098.1018 | 60.019 | 3672.1641 |  |  |  | -15.2008 | -16.0464 |  | -0.44216 | 3668.1695 | [12 empty] | 0 |  |  | T-48 sec | [10 empty] | T-48 sec | 40098.1018 | 60.019 | 3672.1641 | 350 | -165.4764 | 0 | 73 | 10 | 15 | -103 | 7644.54 | -15.2008 | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018
T-46 sec | 40098.1018 | 60.019 | 3672.1641 |  |  |  | -15.2008 | -15.7504 |  | -0.44216 | 3668.0233 | [12 empty] | 0 |  |  | T-46 sec | [10 empty] | T-46 sec | 40098.1018 | 60.019 | 3672.1641 | 350 | -165.4764 | 0 | 73 | 10 | 15 | -103 | 7644.54 | -15.2008 | T-46 sec | 40098.1018 | [12 empty] | T-46 sec | 40098.1018 | [12 empty] | T-46 sec | 40098.1018 | [12 empty] | T-46 sec | 40098.1018 | [12 empty] | T-46 sec | 40098.1018
T-44 sec | 40098.1019 | 60.019 | 3672.1641 |  |  |  | -15.2008 | -15.5581 |  | -0.44216 | 3667.7735 | [12 empty] | 0 |  |  | T-44 sec | [10 empty] | T-44 sec | 40098.1019 | 60.019 | 3672.1641 | 350 | -165.4764 | 0 | 73 | 10 | 15 | -103 | 7644.54 | -15.2008 | T-44 sec | 40098.1019 | [12 empty] | T-44 sec | 40098.1019 | [12 empty] | T-44 sec | 40098.1019 | [12 empty] | T-44 sec | 40098.1019 | [12 empty] | T-44 sec | 40098.1019
T-42 sec | 40098.1019 | 60.031 | 3666.4673 |  |  |  | -24.7986 | -18.7922 |  | -0.44216 | 3664.0971 | [12 empty] | 0 |  |  | T-42 sec | [10 empty] | T-42 sec | 40098.1019 | 60.031 | 3666.4673 | 350 | -165.4764 | 0 | 73.5 | 10 | 15 | -103 | 7645.53 | -24.7986 | T-42 sec | 40098.1019 | [12 empty] | T-42 sec | 40098.1019 | [12 empty] | T-42 sec | 40098.1019 | [12 empty] | T-42 sec | 40098.1019 | [12 empty] | T-42 sec | 40098.1019
T-40 sec | 40098.1019 | 60.031 | 3666.4673 |  |  |  | -24.7986 | -20.8945 |  | -0.44216 | 3661.5527 | [12 empty] | 0 |  |  | T-40 sec | [10 empty] | T-40 sec | 40098.1019 | 60.031 | 3666.4673 | 350 | -165.4764 | 0 | 73.5 | 10 | 15 | -103 | 7645.53 | -24.7986 | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019
T-38 sec | 40098.1019 | 60.031 | 3666.4673 |  |  |  | -24.7986 | -22.2609 |  | -0.44216 | 3659.7441 | [12 empty] | 0 |  |  | T-38 sec | [10 empty] | T-38 sec | 40098.1019 | 60.031 | 3666.4673 | 350 | -165.4764 | 0 | 73.5 | 10 | 15 | -103 | 7645.53 | -24.7986 | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019
T-36 sec | 40098.1019 | 60.036 | 3660.6724 |  |  |  | -28.7994 | -24.5494 |  | -0.44216 | 3657.0135 | [12 empty] | 0 |  |  | T-36 sec | [10 empty] | T-36 sec | 40098.1019 | 60.036 | 3660.6724 | 350 | -165.4764 | 0 | 74 | 10 | 15 | -103 | 7646.52 | -28.7994 | T-36 sec | 40098.1019 | [12 empty] | T-36 sec | 40098.1019 | [12 empty] | T-36 sec | 40098.1019 | [12 empty] | T-36 sec | 40098.1019 | [12 empty] | T-36 sec | 40098.1019
T-34 sec | 40098.102 | 60.036 | 3660.6724 |  |  |  | -28.7994 | -26.0369 |  | -0.44216 | 3655.0838 | [12 empty] | 0 |  |  | T-34 sec | [10 empty] | T-34 sec | 40098.102 | 60.036 | 3660.6724 | 350 | -165.4764 | 0 | 74 | 10 | 15 | -103 | 7646.52 | -28.7994 | T-34 sec | 40098.102 | [12 empty] | T-34 sec | 40098.102 | [12 empty] | T-34 sec | 40098.102 | [12 empty] | T-34 sec | 40098.102 | [12 empty] | T-34 sec | 40098.102
T-32 sec | 40098.102 | 60.036 | 3660.6724 |  |  |  | -28.7994 | -27.0038 |  | -0.44216 | 3653.6748 | [12 empty] | 0 |  |  | T-32 sec | [10 empty] | T-32 sec | 40098.102 | 60.036 | 3660.6724 | 350 | -165.4764 | 0 | 74 | 10 | 15 | -103 | 7646.52 | -28.7994 | T-32 sec | 40098.102 | [12 empty] | T-32 sec | 40098.102 | [12 empty] | T-32 sec | 40098.102 | [12 empty] | T-32 sec | 40098.102 | [12 empty] | T-32 sec | 40098.102
T-30 sec | 40098.102 | 60.048 | 3650.0251 |  |  |  | -38.4003 | -30.9926 |  | -0.44216 | 3649.2438 | [12 empty] | 0 |  |  | T-30 sec | [10 empty] | T-30 sec | 40098.102 | 60.048 | 3650.0251 | 350 | -165.4764 | 0 | 74.5 | 10 | 15 | -103 | 7647.51 | -38.4003 | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102
T-28 sec | 40098.102 | 60.048 | 3650.0251 |  |  |  | -38.4003 | -33.5853 |  | -0.44216 | 3646.209 | [12 empty] | 0 |  |  | T-28 sec | [10 empty] | T-28 sec | 40098.102 | 60.048 | 3650.0251 | 350 | -165.4764 | 0 | 74.5 | 10 | 15 | -103 | 7647.51 | -38.4003 | T-28 sec | 40098.102 | [12 empty] | T-28 sec | 40098.102 | [12 empty] | T-28 sec | 40098.102 | [12 empty] | T-28 sec | 40098.102 | [12 empty] | T-28 sec | 40098.102
T-26 sec | 40098.1021 | 60.048 | 3650.0251 |  |  |  | -38.4003 | -35.2705 |  | -0.44216 | 3644.0815 | [12 empty] | 0 |  |  | T-26 sec | [10 empty] | T-26 sec | 40098.1021 | 60.048 | 3650.0251 | 350 | -165.4764 | 0 | 74.5 | 10 | 15 | -103 | 7647.51 | -38.4003 | T-26 sec | 40098.1021 | [12 empty] | T-26 sec | 40098.1021 | [12 empty] | T-26 sec | 40098.1021 | [12 empty] | T-26 sec | 40098.1021 | [12 empty] | T-26 sec | 40098.1021
T-24 sec | 40098.1021 | 60.041 | 3654.2944 |  |  |  | -32.8003 | -34.4059 |  | -0.44216 | 3644.504 | [12 empty] | 0 |  |  | T-24 sec | [10 empty] | T-24 sec | 40098.1021 | 60.041 | 3654.2944 | 350 | -165.4764 | 0 | 75 | 10 | 15 | -103 | 7648.5 | -32.8003 | T-24 sec | 40098.1021 | [12 empty] | T-24 sec | 40098.1021 | [12 empty] | T-24 sec | 40098.1021 | [12 empty] | T-24 sec | 40098.1021 | [12 empty] | T-24 sec | 40098.1021
T-22 sec | 40098.1021 | 60.041 | 3654.2944 |  |  |  | -32.8003 | -33.844 |  | -0.44216 | 3644.6238 | [12 empty] | 0 |  |  | T-22 sec | [10 empty] | T-22 sec | 40098.1021 | 60.041 | 3654.2944 | 350 | -165.4764 | 0 | 75 | 10 | 15 | -103 | 7648.5 | -32.8003 | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021
T-20 sec | 40098.1021 | 60.041 | 3654.2944 |  |  |  | -32.8003 | -33.4787 |  | -0.44216 | 3644.5469 | [12 empty] | 0 |  |  | T-20 sec | [10 empty] | T-20 sec | 40098.1021 | 60.041 | 3654.2944 | 350 | -165.4764 | 0 | 75 | 10 | 15 | -103 | 7648.5 | -32.8003 | T-20 sec | 40098.1021 | [12 empty] | T-20 sec | 40098.1021 | [12 empty] | T-20 sec | 40098.1021 | [12 empty] | T-20 sec | 40098.1021 | [12 empty] | T-20 sec | 40098.1021
T-18 sec | 40098.1022 | 60.039 | 3651.0593 |  |  |  | -31.2012 | -32.6816 |  | -0.44216 | 3644.9019 | [12 empty] | 0 |  |  | T-18 sec | [10 empty] | T-18 sec | 40098.1022 | 60.039 | 3651.0593 | 350 | -165.4764 | 0 | 75.5 | 10 | 15 | -103 | 7649.49 | -31.2012 | T-18 sec | 40098.1022 | [12 empty] | T-18 sec | 40098.1022 | [12 empty] | T-18 sec | 40098.1022 | [12 empty] | T-18 sec | 40098.1022 | [12 empty] | T-18 sec | 40098.1022
T-16 sec | 40098.1022 | 60.039 | 3651.0593 | 60.042 | 3645.0407 |  | -31.2012 | -32.1634 |  | -0.44216 | 3644.9778 | [12 empty] | 0 |  |  | T-16 sec | 60.042 | [9 empty] | T-16 sec | 40098.1022 | 60.039 | 3651.0593 | 350 | -165.4764 | 0 | 75.5 | 10 | 15 | -103 | 7649.49 | -31.2012 | T-16 sec | 40098.1022 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-16 sec | 40098.1022 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-16 sec | 40098.1022 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-16 sec | 40098.1022 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-16 sec | 40098.1022 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999
T-14 sec | 40098.1022 | 60.039 | 3651.0593 | 60.042 | 3645.0407 |  | -31.2012 | -31.8266 |  | -0.44216 | 3644.8724 | [12 empty] | 0 |  |  | T-14 sec | 60.042 | [9 empty] | T-14 sec | 40098.1022 | 60.039 | 3651.0593 | 350 | -165.4764 | 0 | 75.5 | 10 | 15 | -103 | 7649.49 | -31.2012 | T-14 sec | 40098.1022 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-14 sec | 40098.1022 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-14 sec | 40098.1022 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-14 sec | 40098.1022 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-14 sec | 40098.1022 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999
T-12 sec | 40098.1022 | 60.045 | 3645.387 | 60.042 | 3645.0407 |  | -35.9985 | -33.2868 |  | -0.44216 | 3642.9701 | [12 empty] | 0 |  |  | T-12 sec | 60.042 | [9 empty] | T-12 sec | 40098.1022 | 60.045 | 3645.387 | 350 | -165.4764 | 0 | 76 | 10 | 15 | -103 | 7650.48 | -35.9985 | T-12 sec | 40098.1022 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-12 sec | 40098.1022 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-12 sec | 40098.1022 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-12 sec | 40098.1022 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-12 sec | 40098.1022 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999
T-10 sec | 40098.1022 | 60.045 | 3645.387 | 60.042 | 3645.0407 |  | -35.9985 | -34.2359 |  | -0.44216 | 3641.5788 | [12 empty] | 0 |  |  | T-10 sec | 60.042 | [9 empty] | T-10 sec | 40098.1022 | 60.045 | 3645.387 | 350 | -165.4764 | 0 | 76 | 10 | 15 | -103 | 7650.48 | -35.9985 | T-10 sec | 40098.1022 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-10 sec | 40098.1022 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-10 sec | 40098.1022 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-10 sec | 40098.1022 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-10 sec | 40098.1022 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999
T-08 sec | 40098.1023 | 60.045 | 3645.387 | 60.042 | 3645.0407 |  | -35.9985 | -34.8528 |  | -0.44216 | 3640.5198 | [12 empty] | 0 |  |  | T-08 sec | 60.042 | [9 empty] | T-08 sec | 40098.1023 | 60.045 | 3645.387 | 350 | -165.4764 | 0 | 76 | 10 | 15 | -103 | 7650.48 | -35.9985 | T-08 sec | 40098.1023 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-08 sec | 40098.1023 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-08 sec | 40098.1023 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-08 sec | 40098.1023 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-08 sec | 40098.1023 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999
T-06 sec | 40098.1023 | 60.041 | 3640.6821 | 60.042 | 3645.0407 |  | -32.8003 | -34.1344 |  | -0.44216 | 3640.796 | [12 empty] | 0 |  |  | T-06 sec | 60.042 | [9 empty] | T-06 sec | 40098.1023 | 60.041 | 3640.6821 | 350 | -165.4764 | 0 | 76.5 | 10 | 15 | -103 | 7651.47 | -32.8003 | T-06 sec | 40098.1023 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-06 sec | 40098.1023 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-06 sec | 40098.1023 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-06 sec | 40098.1023 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-06 sec | 40098.1023 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999
T-04 sec | 40098.1023 | 60.041 | 3640.6821 | 60.042 | 3645.0407 |  | -32.8003 | -33.6675 |  | -0.44216 | 3640.8208 | [12 empty] | 0 |  |  | T-04 sec | 60.042 | [9 empty] | T-04 sec | 40098.1023 | 60.041 | 3640.6821 | 350 | -165.4764 | 0 | 76.5 | 10 | 15 | -103 | 7651.47 | -32.8003 | T-04 sec | 40098.1023 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-04 sec | 40098.1023 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-04 sec | 40098.1023 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-04 sec | 40098.1023 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-04 sec | 40098.1023 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999
T-02 sec | 40098.1023 | 60.041 | 3640.6821 | 60.042 | 3645.0407 |  | -32.8003 | -33.364 |  | -0.44216 | 3640.6821 | [12 empty] | 0 |  |  | T-02 sec | 60.042 | [9 empty] | T-02 sec | 40098.1023 | 60.041 | 3640.6821 | 350 | -165.4764 | 0 | 76.5 | 10 | 15 | -103 | 7651.47 | -32.8003 | T-02 sec | 40098.1023 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-02 sec | 40098.1023 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-02 sec | 40098.1023 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-02 sec | 40098.1023 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999 |  | T-02 sec | 40098.1023 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | 10 | 15 | -103 | 7650.6038 | -33.5999
T+0 sec | 40098.1024 | 59.978 | 3696.3623 |  |  |  | 17.5995 | -15.5268 |  | 0 | 3658.5193 |  |  |  |  | 633 | [7 empty] | 633 | -989.0752 |  | T+0 sec | [10 empty] | T+0 sec | 40098.1024 | 59.978 | 3696.3623 | 350 | -206.4591 | 0 | 77 | 10 | 15 | -103 | 7645 | 17.5995 | T+0 sec | 40098.1024 | [12 empty] | T+0 sec | 40098.1024 | [12 empty] | T+0 sec | 40098.1024 | [12 empty] | T+0 sec | 40098.1024 | [12 empty] | T+0 sec | 40098.1024
T+02 sec | 40098.1024 | 59.978 | 3696.3623 |  |  |  | 17.5995 | -3.9326 |  | 0.61562 | 3670.7291 | 3696.3623 | 3664.6242 | 3673.9075 | 3673.9075 | 633 | [7 empty] | 633 | -989.0752 |  | T+02 sec | [10 empty] | T+02 sec | 40098.1024 | 59.978 | 3696.3623 | 350 | -206.4591 | 0 | 77 | 10 | 15 | -103 | 7645 | 17.5995 | T+02 sec | 40098.1024 | [12 empty] | T+02 sec | 40098.1024 | [12 empty] | T+02 sec | 40098.1024 | [12 empty] | T+02 sec | 40098.1024 | [12 empty] | T+02 sec | 40098.1024
T+04 sec | 40098.1024 | 59.978 | 3696.3623 |  |  |  | 17.5995 | 3.6036 |  | 0.61562 | 3678.881 | 3696.3623 | 3669.3765 | 3674.5231 | 3674.2153 | 633 | [7 empty] | 633 | -989.0752 |  | T+04 sec | [10 empty] | T+04 sec | 40098.1024 | 59.978 | 3696.3623 | 350 | -206.4591 | 0 | 77 | 10 | 15 | -103 | 7645 | 17.5995 | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024
T+06 sec | 40098.1024 | 59.978 | 3696.3623 |  |  |  | 17.5995 | 8.5022 |  | 0.61562 | 3684.3951 | 3696.3623 | 3673.1312 | 3675.1387 | 3674.5231 | 633 | [6 empty] | 0 | 633 | -989.0752 |  | T+06 sec | [10 empty] | T+06 sec | 40098.1024 | 59.978 | 3696.3623 | 350 | -206.4591 | 0 | 77 | 10 | 15 | -103 | 7645 | 17.5995 | T+06 sec | 40098.1024 | [12 empty] | T+06 sec | 40098.1024 | [12 empty] | T+06 sec | 40098.1024 | [12 empty] | T+06 sec | 40098.1024 | [12 empty] | T+06 sec | 40098.1024
T+08 sec | 40098.1025 | 59.869 | 3737.1567 |  |  |  | 104.8004 | 42.2066 |  | 0.61562 | 3718.7151 | 3704.5212 | 3682.2479 | 3675.7543 | 3674.8309 | 633 | [6 empty] | 0 | 633 | -365.8952 |  | T+08 sec | [10 empty] | T+08 sec | 40098.1025 | 59.869 | 3737.1567 | 335 | -206.4591 | 0 | 77.5 | 10 | 0 | -103 | 7639 | 104.8004 | T+08 sec | 40098.1025 | [12 empty] | T+08 sec | 40098.1025 | [12 empty] | T+08 sec | 40098.1025 | [12 empty] | T+08 sec | 40098.1025 | [12 empty] | T+08 sec | 40098.1025
T+10 sec | 40098.1025 | 59.869 | 3737.1567 |  |  |  | 104.8004 | 64.1144 |  | 0.61562 | 3741.2386 | 3709.9604 | 3692.0797 | 3676.3699 | 3675.1387 | 633 | [6 empty] | 0 | 633 | -365.8952 |  | T+10 sec | [10 empty] | T+10 sec | 40098.1025 | 59.869 | 3737.1567 | 335 | -206.4591 | 0 | 77.5 | 10 | 0 | -103 | 7639 | 104.8004 | T+10 sec | 40098.1025 | [12 empty] | T+10 sec | 40098.1025 | [12 empty] | T+10 sec | 40098.1025 | [12 empty] | T+10 sec | 40098.1025 | [12 empty] | T+10 sec | 40098.1025
T+12 sec | 40098.1025 | 59.869 | 3737.1567 |  |  |  | 104.8004 | 78.3545 |  | 0.61562 | 3756.0943 | 3713.8456 | 3701.2247 | 3676.9855 | 3675.4465 | 633 | [6 empty] | 0 | 633 | -365.8952 |  | T+12 sec | 59.8797 | -390.3519 | [8 empty] | T+12 sec | 40098.1025 | 59.869 | 3737.1567 | 335 | -206.4591 | 0 | 77.5 | 10 | 0 | -103 | 7639 | 104.8004 | T+12 sec | 40098.1025 | 59.8797 | 3768.2286 | 335 | -206.4591 | 0 | 78.1429 | 10 | 0 | -103 | 7631.7143 | 96.2285 | 3722.1952 | T+12 sec | 40098.1025 | [12 empty] | T+12 sec | 40098.1025 | [12 empty] | T+12 sec | 40098.1025 | [12 empty] | T+12 sec | 40098.1025
T+14 sec | 40098.1025 | 59.88 | 3766.1938 |  |  |  | 95.9991 | 84.5301 |  | 0.61562 | 3762.8856 | 3720.3892 | 3708.9323 | 3677.6012 | 3675.7543 | 633 | [6 empty] | 0 | 633 | -390.7438 |  | T+14 sec | 59.8797 | -390.3519 | [8 empty] | T+14 sec | 40098.1025 | 59.88 | 3766.1938 | 335 | -206.4591 | 0 | 78 | 10 | 0 | -103 | 7631 | 95.9991 | T+14 sec | 40098.1025 | 59.8797 | 3768.2286 | 335 | -206.4591 | 0 | 78.1429 | 10 | 0 | -103 | 7631.7143 | 96.2285 | 3722.1952 | T+14 sec | 40098.1025 | [12 empty] | T+14 sec | 40098.1025 | [12 empty] | T+14 sec | 40098.1025 | [12 empty] | T+14 sec | 40098.1025
T+16 sec | 40098.1025 | 59.88 | 3766.1938 |  |  |  | 95.9991 | 88.5443 |  | 0.61562 | 3767.5153 | 3725.4786 | 3715.4415 | 3678.2168 | 3676.0621 | 633 | [6 empty] | 0 | 633 | -390.7438 |  | T+16 sec | 59.8797 | -390.3519 | [8 empty] | T+16 sec | 40098.1025 | 59.88 | 3766.1938 | 335 | -206.4591 | 0 | 78 | 10 | 0 | -103 | 7631 | 95.9991 | T+16 sec | 40098.1025 | 59.8797 | 3768.2286 | 335 | -206.4591 | 0 | 78.1429 | 10 | 0 | -103 | 7631.7143 | 96.2285 | 3722.1952 | T+16 sec | 40098.1025 | [12 empty] | T+16 sec | 40098.1025 | [12 empty] | T+16 sec | 40098.1025 | [12 empty] | T+16 sec | 40098.1025
T+18 sec | 40098.1026 | 59.88 | 3766.1938 |  |  |  | 95.9991 | 91.1535 |  | 0.61562 | 3770.7401 | 3729.5501 | 3720.9714 | 3678.8324 | 3676.3699 | 633 | [6 empty] | 0 | 633 | -390.7438 |  | T+18 sec | 59.8797 | -390.3519 | 59.8834 | -399.2319 |  |  | 59.8876 | -410.1357 |  |  | T+18 sec | 40098.1026 | 59.88 | 3766.1938 | 335 | -206.4591 | 0 | 78 | 10 | 0 | -103 | 7631 | 95.9991 | T+18 sec | 40098.1026 | 59.8797 | 3768.2286 | 335 | -206.4591 | 0 | 78.1429 | 10 | 0 | -103 | 7631.7143 | 96.2285 | 3722.1952 | T+18 sec | 40098.1026 | 59.8834 | 3780.4202 | 335 | -206.4591 | 0 | 78.6429 | 10 | 0 | -103 | 7630.5714 | 93.2578 | 3719.3532 | T+18 sec | 40098.1026 | [12 empty] | T+18 sec | 40098.1026 | 59.8876 | 3787.5342 | 335 | -209.3906 | 0 | 79.5833 | 10 | 0 | -103 | 7631.5 | 89.956 | 3713.6477 | T+18 sec | 40098.1026
T+20 sec | 40098.1026 | 59.883 | 3780.6206 | 59.888 | 3788.7895 |  | 93.6005 | 92.0099 | 3750.6759 | 0.61562 | 3772.2122 | 3734.1929 | 3725.6296 | 3679.448 | 3676.6777 | 633 | [6 empty] | 0 | 633 | -398.1122 | -411.2764 | T+20 sec | 59.8797 | -390.3519 | 59.8834 | -399.2319 | 59.888 | -409.3538 | 59.8876 | -410.1357 | 59.888 | -411.2764 | T+20 sec | 40098.1026 | 59.883 | 3780.6206 | 335 | -206.4591 | 0 | 78.5 | 10 | 0 | -103 | 7630 | 93.6005 | T+20 sec | 40098.1026 | 59.8797 | 3768.2286 | 335 | -206.4591 | 0 | 78.1429 | 10 | 0 | -103 | 7631.7143 | 96.2285 | 3722.1952 | T+20 sec | 40098.1026 | 59.8834 | 3780.4202 | 335 | -206.4591 | 0 | 78.6429 | 10 | 0 | -103 | 7630.5714 | 93.2578 | 3719.3532 | T+20 sec | 40098.1026 | 59.8873 | 3785.2644 | 335 | -208.6395 | 0 | 79.1818 | 10 | 0 | -103 | 7630.6364 | 90.1822 | 3714.2518 | T+20 sec | 40098.1026 | 59.8876 | 3787.5342 | 335 | -209.3906 | 0 | 79.5833 | 10 | 0 | -103 | 7631.5 | 89.956 | 3713.6477 | T+20 sec | 40098.1026 | 59.888 | 3788.7895 | 335 | -209.563 | 0 | 79.6765 | 10 | 0 | -103 | 7631.5294 | 89.6005 | 3713.1685
T+22 sec | 40098.1026 | 59.883 | 3780.6206 | 59.888 | 3788.7895 |  | 93.6005 | 92.5666 | 3750.6759 | 0.61562 | 3773.3845 | 3738.0618 | 3729.6092 | 3680.0636 | 3676.9855 | 633 | [6 empty] | 0 | 633 | -398.1122 | -411.2764 | T+22 sec | 59.8797 | -390.3519 | 59.8834 | -399.2319 | 59.888 | -409.3538 | 59.8876 | -410.1357 | 59.888 | -411.2764 | T+22 sec | 40098.1026 | 59.883 | 3780.6206 | 335 | -206.4591 | 0 | 78.5 | 10 | 0 | -103 | 7630 | 93.6005 | T+22 sec | 40098.1026 | 59.8797 | 3768.2286 | 335 | -206.4591 | 0 | 78.1429 | 10 | 0 | -103 | 7631.7143 | 96.2285 | 3722.1952 | T+22 sec | 40098.1026 | 59.8834 | 3780.4202 | 335 | -206.4591 | 0 | 78.6429 | 10 | 0 | -103 | 7630.5714 | 93.2578 | 3719.3532 | T+22 sec | 40098.1026 | 59.8873 | 3785.2644 | 335 | -208.6395 | 0 | 79.1818 | 10 | 0 | -103 | 7630.6364 | 90.1822 | 3714.2518 | T+22 sec | 40098.1026 | 59.8876 | 3787.5342 | 335 | -209.3906 | 0 | 79.5833 | 10 | 0 | -103 | 7631.5 | 89.956 | 3713.6477 | T+22 sec | 40098.1026 | 59.888 | 3788.7895 | 335 | -209.563 | 0 | 79.6765 | 10 | 0 | -103 | 7631.5294 | 89.6005 | 3713.1685
T+24 sec | 40098.1026 | 59.883 | 3780.6206 | 59.888 | 3788.7895 |  | 93.6005 | 92.9285 | 3750.6759 | 0.61562 | 3774.362 | 3741.3356 | 3733.0517 | 3680.6793 | 3677.2934 | 633 | [6 empty] | 0 | 633 | -398.1122 | -411.2764 | T+24 sec | 59.8797 | -390.3519 | 59.8834 | -399.2319 | 59.888 | -409.3538 | 59.8876 | -410.1357 | 59.888 | -411.2764 | T+24 sec | 40098.1026 | 59.883 | 3780.6206 | 335 | -206.4591 | 0 | 78.5 | 10 | 0 | -103 | 7630 | 93.6005 | T+24 sec | 40098.1026 | 59.8797 | 3768.2286 | 335 | -206.4591 | 0 | 78.1429 | 10 | 0 | -103 | 7631.7143 | 96.2285 | 3722.1952 | T+24 sec | 40098.1026 | 59.8834 | 3780.4202 | 335 | -206.4591 | 0 | 78.6429 | 10 | 0 | -103 | 7630.5714 | 93.2578 | 3719.3532 | T+24 sec | 40098.1026 | 59.8873 | 3785.2644 | 335 | -208.6395 | 0 | 79.1818 | 10 | 0 | -103 | 7630.6364 | 90.1822 | 3714.2518 | T+24 sec | 40098.1026 | 59.8876 | 3787.5342 | 335 | -209.3906 | 0 | 79.5833 | 10 | 0 | -103 | 7631.5 | 89.956 | 3713.6477 | T+24 sec | 40098.1026 | 59.888 | 3788.7895 | 335 | -209.563 | 0 | 79.6765 | 10 | 0 | -103 | 7631.5294 | 89.6005 | 3713.1685
T+26 sec | 40098.1027 | 59.885 | 3784.9619 | 59.888 | 3788.7895 |  | 92.0013 | 92.604 | 3750.6759 | 0.61562 | 3774.6531 | 3744.4518 | 3736.0233 | 3681.2949 | 3677.6012 | 633 | [6 empty] | 0 | 633 | -403.1809 | -411.2764 | T+26 sec |  |  | 59.8834 | -399.2319 | 59.888 | -409.3538 | 59.8876 | -410.1357 | 59.888 | -411.2764 | T+26 sec | 40098.1027 | 59.885 | 3784.9619 | 335 | -206.4591 | 0 | 79 | 10 | 0 | -103 | 7631 | 92.0013 | T+26 sec | 40098.1027 | [12 empty] | T+26 sec | 40098.1027 | 59.8834 | 3780.4202 | 335 | -206.4591 | 0 | 78.6429 | 10 | 0 | -103 | 7630.5714 | 93.2578 | 3719.3532 | T+26 sec | 40098.1027 | 59.8873 | 3785.2644 | 335 | -208.6395 | 0 | 79.1818 | 10 | 0 | -103 | 7630.6364 | 90.1822 | 3714.2518 | T+26 sec | 40098.1027 | 59.8876 | 3787.5342 | 335 | -209.3906 | 0 | 79.5833 | 10 | 0 | -103 | 7631.5 | 89.956 | 3713.6477 | T+26 sec | 40098.1027 | 59.888 | 3788.7895 | 335 | -209.563 | 0 | 79.6765 | 10 | 0 | -103 | 7631.5294 | 89.6005 | 3713.1685
T+28 sec | 40098.1027 | 59.885 | 3784.9619 | 59.888 | 3788.7895 |  | 92.0013 | 92.3931 | 3750.6759 | 0.61562 | 3775.0578 | 3747.1524 | 3738.6256 | 3681.9105 | 3677.909 | 633 | [6 empty] | 0 | 633 | -403.1809 | -411.2764 | T+28 sec |  |  | 59.8834 | -399.2319 | 59.888 | -409.3538 | 59.8876 | -410.1357 | 59.888 | -411.2764 | T+28 sec | 40098.1027 | 59.885 | 3784.9619 | 335 | -206.4591 | 0 | 79 | 10 | 0 | -103 | 7631 | 92.0013 | T+28 sec | 40098.1027 | [12 empty] | T+28 sec | 40098.1027 | 59.8834 | 3780.4202 | 335 | -206.4591 | 0 | 78.6429 | 10 | 0 | -103 | 7630.5714 | 93.2578 | 3719.3532 | T+28 sec | 40098.1027 | 59.8873 | 3785.2644 | 335 | -208.6395 | 0 | 79.1818 | 10 | 0 | -103 | 7630.6364 | 90.1822 | 3714.2518 | T+28 sec | 40098.1027 | 59.8876 | 3787.5342 | 335 | -209.3906 | 0 | 79.5833 | 10 | 0 | -103 | 7631.5 | 89.956 | 3713.6477 | T+28 sec | 40098.1027 | 59.888 | 3788.7895 | 335 | -209.563 | 0 | 79.6765 | 10 | 0 | -103 | 7631.5294 | 89.6005 | 3713.1685
T+30 sec | 40098.1027 | 59.885 | 3784.9619 | 59.888 | 3788.7895 |  | 92.0013 | 92.256 | 3750.6759 | 0.61562 | 3775.5363 | 3749.5155 | 3740.9325 | 3682.5261 | 3678.2168 | 633 | [6 empty] | 0 | 633 | -403.1809 | -411.2764 | T+30 sec |  |  | 59.8834 | -399.2319 | 59.888 | -409.3538 | 59.8876 | -410.1357 | 59.888 | -411.2764 | T+30 sec | 40098.1027 | 59.885 | 3784.9619 | 335 | -206.4591 | 0 | 79 | 10 | 0 | -103 | 7631 | 92.0013 | T+30 sec | 40098.1027 | [12 empty] | T+30 sec | 40098.1027 | 59.8834 | 3780.4202 | 335 | -206.4591 | 0 | 78.6429 | 10 | 0 | -103 | 7630.5714 | 93.2578 | 3719.3532 | T+30 sec | 40098.1027 | 59.8873 | 3785.2644 | 335 | -208.6395 | 0 | 79.1818 | 10 | 0 | -103 | 7630.6364 | 90.1822 | 3714.2518 | T+30 sec | 40098.1027 | 59.8876 | 3787.5342 | 335 | -209.3906 | 0 | 79.5833 | 10 | 0 | -103 | 7631.5 | 89.956 | 3713.6477 | T+30 sec | 40098.1027 | 59.888 | 3788.7895 | 335 | -209.563 | 0 | 79.6765 | 10 | 0 | -103 | 7631.5294 | 89.6005 | 3713.1685
T+32 sec | 40098.1027 | 59.89 | 3788.0723 | 59.888 | 3788.7895 |  | 88.0005 | 90.7665 | 3750.6759 | 0.61562 | 3774.6625 | 3751.7836 | 3742.9166 | 3683.1417 | 3678.5246 | 633 | [6 empty] | 0 | 633 | -416.4462 | -411.2764 | T+32 sec |  |  |  |  | 59.888 | -409.3538 | 59.8876 | -410.1357 | 59.888 | -411.2764 | T+32 sec | 40098.1027 | 59.89 | 3788.0723 | 335 | -211.256 | 0 | 79.5 | 10 | 0 | -103 | 7630 | 88.0005 | T+32 sec | 40098.1027 | [12 empty] | T+32 sec | 40098.1027 | [12 empty] | T+32 sec | 40098.1027 | 59.8873 | 3785.2644 | 335 | -208.6395 | 0 | 79.1818 | 10 | 0 | -103 | 7630.6364 | 90.1822 | 3714.2518 | T+32 sec | 40098.1027 | 59.8876 | 3787.5342 | 335 | -209.3906 | 0 | 79.5833 | 10 | 0 | -103 | 7631.5 | 89.956 | 3713.6477 | T+32 sec | 40098.1027 | 59.888 | 3788.7895 | 335 | -209.563 | 0 | 79.6765 | 10 | 0 | -103 | 7631.5294 | 89.6005 | 3713.1685
T+34 sec | 40098.1028 | 59.89 | 3788.0723 | 59.888 | 3788.7895 |  | 88.0005 | 89.7984 | 3750.6759 | 0.61562 | 3774.31 | 3753.7996 | 3744.6607 | 3683.7573 | 3678.8324 | 633 | [6 empty] | 0 | 633 | -416.4462 | -411.2764 | T+34 sec |  |  |  |  | 59.888 | -409.3538 | 59.8876 | -410.1357 | 59.888 | -411.2764 | T+34 sec | 40098.1028 | 59.89 | 3788.0723 | 335 | -211.256 | 0 | 79.5 | 10 | 0 | -103 | 7630 | 88.0005 | T+34 sec | 40098.1028 | [12 empty] | T+34 sec | 40098.1028 | [12 empty] | T+34 sec | 40098.1028 | 59.8873 | 3785.2644 | 335 | -208.6395 | 0 | 79.1818 | 10 | 0 | -103 | 7630.6364 | 90.1822 | 3714.2518 | T+34 sec | 40098.1028 | 59.8876 | 3787.5342 | 335 | -209.3906 | 0 | 79.5833 | 10 | 0 | -103 | 7631.5 | 89.956 | 3713.6477 | T+34 sec | 40098.1028 | 59.888 | 3788.7895 | 335 | -209.563 | 0 | 79.6765 | 10 | 0 | -103 | 7631.5294 | 89.6005 | 3713.1685
T+36 sec | 40098.1028 | 59.89 | 3788.0723 | 59.888 | 3788.7895 |  | 88.0005 | 89.1691 | 3750.6759 | 0.61562 | 3774.2964 | 3755.6034 | 3746.2205 | 3684.373 | 3679.1402 | 633 | [6 empty] | 0 | 633 | -416.4462 | -411.2764 | T+36 sec |  |  |  |  | 59.888 | -409.3538 | 59.8876 | -410.1357 | 59.888 | -411.2764 | T+36 sec | 40098.1028 | 59.89 | 3788.0723 | 335 | -211.256 | 0 | 79.5 | 10 | 0 | -103 | 7630 | 88.0005 | T+36 sec | 40098.1028 | [12 empty] | T+36 sec | 40098.1028 | [12 empty] | T+36 sec | 40098.1028 | 59.8873 | 3785.2644 | 335 | -208.6395 | 0 | 79.1818 | 10 | 0 | -103 | 7630.6364 | 90.1822 | 3714.2518 | T+36 sec | 40098.1028 | 59.8876 | 3787.5342 | 335 | -209.3906 | 0 | 79.5833 | 10 | 0 | -103 | 7631.5 | 89.956 | 3713.6477 | T+36 sec | 40098.1028 | 59.888 | 3788.7895 | 335 | -209.563 | 0 | 79.6765 | 10 | 0 | -103 | 7631.5294 | 89.6005 | 3713.1685
T+38 sec | 40098.1028 | 59.893 | 3788.4719 | 59.888 | 3788.7895 |  | 85.5988 | 87.9195 | 3750.6759 | 0.61562 | 3773.6623 | 3757.2469 | 3747.5925 | 3684.9886 | 3679.448 | 633 | [6 empty] | 0 | 633 | -424.8372 | -411.2764 | T+38 sec |  |  |  |  | 59.888 | -409.3538 | 59.8876 | -410.1357 | 59.888 | -411.2764 | T+38 sec | 40098.1028 | 59.893 | 3788.4719 | 335 | -211.256 | 0 | 80 | 10 | 0 | -103 | 7632 | 85.5988 | T+38 sec | 40098.1028 | [12 empty] | T+38 sec | 40098.1028 | [12 empty] | T+38 sec | 40098.1028 | 59.8873 | 3785.2644 | 335 | -208.6395 | 0 | 79.1818 | 10 | 0 | -103 | 7630.6364 | 90.1822 | 3714.2518 | T+38 sec | 40098.1028 | 59.8876 | 3787.5342 | 335 | -209.3906 | 0 | 79.5833 | 10 | 0 | -103 | 7631.5 | 89.956 | 3713.6477 | T+38 sec | 40098.1028 | 59.888 | 3788.7895 | 335 | -209.563 | 0 | 79.6765 | 10 | 0 | -103 | 7631.5294 | 89.6005 | 3713.1685
T+40 sec | 40098.1028 | 59.893 | 3788.4719 | 59.888 | 3788.7895 |  | 85.5988 | 87.1072 | 3750.6759 | 0.61562 | 3773.4657 | 3758.7338 | 3748.8246 | 3685.6042 | 3679.7558 | 633 | [6 empty] | 0 | 633 | -424.8372 | -411.2764 | T+40 sec |  |  |  |  | 59.888 | -409.3538 | 59.8876 | -410.1357 | 59.888 | -411.2764 | T+40 sec | 40098.1028 | 59.893 | 3788.4719 | 335 | -211.256 | 0 | 80 | 10 | 0 | -103 | 7632 | 85.5988 | T+40 sec | 40098.1028 | [12 empty] | T+40 sec | 40098.1028 | [12 empty] | T+40 sec | 40098.1028 | 59.8873 | 3785.2644 | 335 | -208.6395 | 0 | 79.1818 | 10 | 0 | -103 | 7630.6364 | 90.1822 | 3714.2518 | T+40 sec | 40098.1028 | 59.8876 | 3787.5342 | 335 | -209.3906 | 0 | 79.5833 | 10 | 0 | -103 | 7631.5 | 89.956 | 3713.6477 | T+40 sec | 40098.1028 | 59.888 | 3788.7895 | 335 | -209.563 | 0 | 79.6765 | 10 | 0 | -103 | 7631.5294 | 89.6005 | 3713.1685
T+42 sec | 40098.1028 | 59.893 | 3788.4719 | 59.888 | 3788.7895 |  | 85.5988 | 86.5793 | 3750.6759 | 0.61562 | 3773.5533 | 3760.0855 | 3749.9486 | 3686.2198 | 3680.0636 | 633 | [6 empty] | 0 | 633 | -424.8372 | -411.2764 | T+42 sec | [6 empty] | 59.8876 | -410.1357 | 59.888 | -411.2764 | T+42 sec | 40098.1028 | 59.893 | 3788.4719 | 335 | -211.256 | 0 | 80 | 10 | 0 | -103 | 7632 | 85.5988 | T+42 sec | 40098.1028 | [12 empty] | T+42 sec | 40098.1028 | [12 empty] | T+42 sec | 40098.1028 | [12 empty] | T+42 sec | 40098.1028 | 59.8876 | 3787.5342 | 335 | -209.3906 | 0 | 79.5833 | 10 | 0 | -103 | 7631.5 | 89.956 | 3713.6477 | T+42 sec | 40098.1028 | 59.888 | 3788.7895 | 335 | -209.563 | 0 | 79.6765 | 10 | 0 | -103 | 7631.5294 | 89.6005 | 3713.1685
T+44 sec | 40098.1029 | 59.891 | 3794.3743 | 59.888 | 3788.7895 |  | 87.2009 | 86.7969 | 3750.6759 | 0.61562 | 3774.3865 | 3761.5763 | 3751.0112 | 3686.8354 | 3680.3714 | 633 | [6 empty] | 0 | 633 | -419.2026 | -411.2764 | T+44 sec | [6 empty] | 59.8876 | -410.1357 | 59.888 | -411.2764 | T+44 sec | 40098.1029 | 59.891 | 3794.3743 | 335 | -211.256 | 0 | 80.5 | 10 | 0 | -103 | 7633 | 87.2009 | T+44 sec | 40098.1029 | [12 empty] | T+44 sec | 40098.1029 | [12 empty] | T+44 sec | 40098.1029 | [12 empty] | T+44 sec | 40098.1029 | 59.8876 | 3787.5342 | 335 | -209.3906 | 0 | 79.5833 | 10 | 0 | -103 | 7631.5 | 89.956 | 3713.6477 | T+44 sec | 40098.1029 | 59.888 | 3788.7895 | 335 | -209.563 | 0 | 79.6765 | 10 | 0 | -103 | 7631.5294 | 89.6005 | 3713.1685
T+46 sec | 40098.1029 | 59.891 | 3794.3743 | 59.888 | 3788.7895 |  | 87.2009 | 86.9383 | 3750.6759 | 0.61562 | 3775.1436 | 3762.9429 | 3752.0167 | 3687.451 | 3680.6793 | 633 | [6 empty] | 0 | 633 | -419.2026 | -411.2764 | T+46 sec | [6 empty] | 59.8876 | -410.1357 | 59.888 | -411.2764 | T+46 sec | 40098.1029 | 59.891 | 3794.3743 | 335 | -211.256 | 0 | 80.5 | 10 | 0 | -103 | 7633 | 87.2009 | T+46 sec | 40098.1029 | [12 empty] | T+46 sec | 40098.1029 | [12 empty] | T+46 sec | 40098.1029 | [12 empty] | T+46 sec | 40098.1029 | 59.8876 | 3787.5342 | 335 | -209.3906 | 0 | 79.5833 | 10 | 0 | -103 | 7631.5 | 89.956 | 3713.6477 | T+46 sec | 40098.1029 | 59.888 | 3788.7895 | 335 | -209.563 | 0 | 79.6765 | 10 | 0 | -103 | 7631.5294 | 89.6005 | 3713.1685
T+48 sec | 40098.1029 | 59.891 | 3794.3743 | 59.888 | 3788.7895 |  | 87.2009 | 87.0302 | 3750.6759 | 0.61562 | 3775.8511 | 3764.2002 | 3752.97 | 3688.0667 | 3680.9871 | 633 | [6 empty] | 0 | 633 | -419.2026 | -411.2764 | T+48 sec | [6 empty] | 59.8876 | -410.1357 | 59.888 | -411.2764 | T+48 sec | 40098.1029 | 59.891 | 3794.3743 | 335 | -211.256 | 0 | 80.5 | 10 | 0 | -103 | 7633 | 87.2009 | T+48 sec | 40098.1029 | [12 empty] | T+48 sec | 40098.1029 | [12 empty] | T+48 sec | 40098.1029 | [12 empty] | T+48 sec | 40098.1029 | 59.8876 | 3787.5342 | 335 | -209.3906 | 0 | 79.5833 | 10 | 0 | -103 | 7631.5 | 89.956 | 3713.6477 | T+48 sec | 40098.1029 | 59.888 | 3788.7895 | 335 | -209.563 | 0 | 79.6765 | 10 | 0 | -103 | 7631.5294 | 89.6005 | 3713.1685
T+50 sec | 40098.1029 | 59.885 | 3799.9592 | 59.888 | 3788.7895 |  | 92.0013 | 88.7701 | 3750.6759 | 0.61562 | 3778.2067 | 3765.5755 | 3753.9407 | 3688.6823 | 3681.2949 | 633 | [6 empty] | 0 | 633 | -403.1809 | -411.2764 | T+50 sec | [6 empty] | 59.8876 | -410.1357 | 59.888 | -411.2764 | T+50 sec | 40098.1029 | 59.885 | 3799.9592 | 335 | -211.256 | 0 | 81 | 10 | 0 | -103 | 7634 | 92.0013 | T+50 sec | 40098.1029 | [12 empty] | T+50 sec | 40098.1029 | [12 empty] | T+50 sec | 40098.1029 | [12 empty] | T+50 sec | 40098.1029 | 59.8876 | 3787.5342 | 335 | -209.3906 | 0 | 79.5833 | 10 | 0 | -103 | 7631.5 | 89.956 | 3713.6477 | T+50 sec | 40098.1029 | 59.888 | 3788.7895 | 335 | -209.563 | 0 | 79.6765 | 10 | 0 | -103 | 7631.5294 | 89.6005 | 3713.1685
T+52 sec | 40098.103 | 59.885 | 3799.9592 | 59.888 | 3788.7895 |  | 92.0013 | 89.901 | 3750.6759 | 0.61562 | 3779.9532 | 3766.849 | 3754.9041 | 3689.2979 | 3681.6027 | 633 | [6 empty] | 0 | 633 | -403.1809 | -411.2764 | T+52 sec | [6 empty] | 59.8876 | -410.1357 | 59.888 | -411.2764 | T+52 sec | 40098.103 | 59.885 | 3799.9592 | 335 | -211.256 | 0 | 81 | 10 | 0 | -103 | 7634 | 92.0013 | T+52 sec | 40098.103 | [12 empty] | T+52 sec | 40098.103 | [12 empty] | T+52 sec | 40098.103 | [12 empty] | T+52 sec | 40098.103 | 59.8876 | 3787.5342 | 335 | -209.3906 | 0 | 79.5833 | 10 | 0 | -103 | 7631.5 | 89.956 | 3713.6477 | T+52 sec | 40098.103 | 59.888 | 3788.7895 | 335 | -209.563 | 0 | 79.6765 | 10 | 0 | -103 | 7631.5294 | 89.6005 | 3713.1685
T+54 sec | 40098.103 | 59.885 | 3799.9592 |  |  |  | 92.0013 | 90.6361 |  | 0.61562 | 3781.3039 | 3768.0315 | 3755.847 | 3689.9135 | 3681.9105 | 633 | [6 empty] | 0 | 633 | -403.1809 |  | T+54 sec | [10 empty] | T+54 sec | 40098.103 | 59.885 | 3799.9592 | 335 | -211.256 | 0 | 81 | 10 | 0 | -103 | 7634 | 92.0013 | T+54 sec | 40098.103 | [12 empty] | T+54 sec | 40098.103 | [12 empty] | T+54 sec | 40098.103 | [12 empty] | T+54 sec | 40098.103 | [12 empty] | T+54 sec | 40098.103
T+56 sec | 40098.103 | 59.888 | 3802.9509 |  |  |  | 89.5996 | 90.2734 |  | 0.61562 | 3781.5568 | 3769.2356 | 3756.7335 | 3690.5291 | 3682.2183 | 633 | [6 empty] | 0 | 633 | -411.0408 |  | T+56 sec | [10 empty] | T+56 sec | 40098.103 | 59.888 | 3802.9509 | 335 | -211.256 | 0 | 81.5 | 10 | 0 | -103 | 7635 | 89.5996 | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103
T+58 sec | 40098.103 | 59.888 | 3802.9509 |  |  |  | 89.5996 | 90.0375 |  | 0.61562 | 3781.9366 | 3770.3594 | 3757.5736 | 3691.1448 | 3682.5261 | 633 | [6 empty] | 0 | 633 | -411.0408 |  | T+58 sec | [10 empty] | T+58 sec | 40098.103 | 59.888 | 3802.9509 | 335 | -211.256 | 0 | 81.5 | 10 | 0 | -103 | 7635 | 89.5996 | T+58 sec | 40098.103 | [12 empty] | T+58 sec | 40098.103 | [12 empty] | T+58 sec | 40098.103 | [12 empty] | T+58 sec | 40098.103 | [12 empty] | T+58 sec | 40098.103
T+60 sec | 40098.1031 | 59.888 | 3802.9509 |  |  |  | 89.5996 | 89.8843 |  | 0.61562 | 3782.3989 | 3771.4108 | 3758.3744 | 3691.7604 | 3682.8339 | 633 | [6 empty] | 0 | 633 | -411.0408 |  | T+60 sec | [10 empty] | T+60 sec | 40098.1031 | 59.888 | 3802.9509 | 335 | -211.256 | 0 | 81.5 | 10 | 0 | -103 | 7635 | 89.5996 | T+60 sec | 40098.1031 | [12 empty] | T+60 sec | 40098.1031 | [12 empty] | T+60 sec | 40098.1031 | [12 empty] | T+60 sec | 40098.1031 | [12 empty] | T+60 sec | 40098.1031
T+62 sec | 40098.1031 | 59.889 | 3805.6167 |  |  |  | 88.8 | 89.5048 |  | 0.61562 | 3782.635 | 3772.4797 | 3759.1326 | 3692.376 | 3683.1417 | 633 | [6 empty] | 0 | 633 | -413.7258 |  | T+62 sec | [10 empty] | T+62 sec | 40098.1031 | 59.889 | 3805.6167 | 335 | -214.3467 | 0 | 82 | 10 | 0 | -103 | 7636 | 88.8 | T+62 sec | 40098.1031 | [12 empty] | T+62 sec | 40098.1031 | [12 empty] | T+62 sec | 40098.1031 | [12 empty] | T+62 sec | 40098.1031 | [12 empty] | T+62 sec | 40098.1031
T+64 sec | 40098.1031 | 59.889 | 3805.6167 |  |  |  | 88.8 | 89.2581 |  | 0.61562 | 3783.004 | 3773.4839 | 3759.8559 | 3692.9916 | 3683.4495 | 633 | [6 empty] | 0 | 633 | -413.7258 |  | T+64 sec | [10 empty] | T+64 sec | 40098.1031 | 59.889 | 3805.6167 | 335 | -214.3467 | 0 | 82 | 10 | 0 | -103 | 7636 | 88.8 | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031
T+66 sec | 40098.1031 | 59.889 | 3805.6167 |  |  |  | 88.8 | 89.0978 |  | 0.61562 | 3783.4593 | 3774.429 | 3760.5502 | 3693.6072 | 3683.7573 | 633 | [6 empty] | 0 | 633 | -413.7258 |  | T+66 sec | [10 empty] | T+66 sec | 40098.1031 | 59.889 | 3805.6167 | 335 | -214.3467 | 0 | 82 | 10 | 0 | -103 | 7636 | 88.8 | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031
T+68 sec | 40098.1031 | 59.857 | 3814.8623 |  |  |  | 114.4012 | 97.954 |  | 0.61562 | 3792.9311 | 3775.5842 | 3761.4753 | 3694.2228 | 3684.0651 | 633 | [6 empty] | 0 | 633 | -342.1596 |  | T+68 sec | [10 empty] | T+68 sec | 40098.1031 | 59.857 | 3814.8623 | 335 | -214.3467 | 0 | 82.5 | 10 | 0 | -103 | 7637 | 114.4012 | T+68 sec | 40098.1031 | [12 empty] | T+68 sec | 40098.1031 | [12 empty] | T+68 sec | 40098.1031 | [12 empty] | T+68 sec | 40098.1031 | [12 empty] | T+68 sec | 40098.1031
T+70 sec | 40098.1032 | 59.857 | 3814.8623 |  |  |  | 114.4012 | 103.7105 |  | 0.61562 | 3799.3033 | 3776.6753 | 3762.5261 | 3694.8385 | 3684.373 | 633 | [6 empty] | 0 | 633 | -342.1596 |  | T+70 sec | [10 empty] | T+70 sec | 40098.1032 | 59.857 | 3814.8623 | 335 | -214.3467 | 0 | 82.5 | 10 | 0 | -103 | 7637 | 114.4012 | T+70 sec | 40098.1032 | [12 empty] | T+70 sec | 40098.1032 | [12 empty] | T+70 sec | 40098.1032 | [12 empty] | T+70 sec | 40098.1032 | [12 empty] | T+70 sec | 40098.1032
T+72 sec | 40098.1032 | 59.857 | 3814.8623 |  |  |  | 114.4012 | 107.4523 |  | 0.61562 | 3803.6606 | 3777.7073 | 3763.6379 | 3695.4541 | 3684.6808 | 633 | [6 empty] | 0 | 633 | -342.1596 |  | T+72 sec | [10 empty] | T+72 sec | 40098.1032 | 59.857 | 3814.8623 | 335 | -214.3467 | 0 | 82.5 | 10 | 0 | -103 | 7637 | 114.4012 | T+72 sec | 40098.1032 | [12 empty] | T+72 sec | 40098.1032 | [12 empty] | T+72 sec | 40098.1032 | [12 empty] | T+72 sec | 40098.1032 | [12 empty] | T+72 sec | 40098.1032
T+74 sec | 40098.1032 | 59.858 | 3826.0532 |  |  |  | 113.5986 | 109.6035 |  | 0.61562 | 3806.4275 | 3778.9796 | 3764.7639 | 3696.0697 | 3684.9886 | 633 | [6 empty] | 0 | 633 | -344.0253 |  | T+74 sec | [10 empty] | T+74 sec | 40098.1032 | 59.858 | 3826.0532 | 335 | -214.3467 | 0 | 83 | 10 | 0 | -103 | 7638 | 113.5986 | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032
T+76 sec | 40098.1032 | 59.858 | 3826.0532 |  |  |  | 113.5986 | 111.0018 |  | 0.61562 | 3808.4414 | 3780.1866 | 3765.8838 | 3696.6853 | 3685.2964 | 633 | [6 empty] | 0 | 633 | -344.0253 |  | T+76 sec | [10 empty] | T+76 sec | 40098.1032 | 59.858 | 3826.0532 | 335 | -214.3467 | 0 | 83 | 10 | 0 | -103 | 7638 | 113.5986 | T+76 sec | 40098.1032 | [12 empty] | T+76 sec | 40098.1032 | [12 empty] | T+76 sec | 40098.1032 | [12 empty] | T+76 sec | 40098.1032 | [12 empty] | T+76 sec | 40098.1032
T+78 sec | 40098.1033 | 59.858 | 3826.0532 |  |  |  | 113.5986 | 111.9107 |  | 0.61562 | 3809.9659 | 3781.3333 | 3766.9859 | 3697.3009 | 3685.6042 | 633 | [6 empty] | 0 | 633 | -344.0253 |  | T+78 sec | [10 empty] | T+78 sec | 40098.1033 | 59.858 | 3826.0532 | 335 | -214.3467 | 0 | 83 | 10 | 0 | -103 | 7638 | 113.5986 | T+78 sec | 40098.1033 | [12 empty] | T+78 sec | 40098.1033 | [12 empty] | T+78 sec | 40098.1033 | [12 empty] | T+78 sec | 40098.1033 | [12 empty] | T+78 sec | 40098.1033
T+80 sec | 40098.1033 | 59.865 | 3826.7532 |  |  |  | 107.9987 | 110.5415 |  | 0.61562 | 3809.2123 | 3782.4411 | 3768.0158 | 3697.9166 | 3685.912 | 633 | [6 empty] | 0 | 633 | -357.6309 |  | T+80 sec | [10 empty] | T+80 sec | 40098.1033 | 59.865 | 3826.7532 | 335 | -214.3467 | 0 | 83.5 | 10 | 0 | -103 | 7641 | 107.9987 | T+80 sec | 40098.1033 | [12 empty] | T+80 sec | 40098.1033 | [12 empty] | T+80 sec | 40098.1033 | [12 empty] | T+80 sec | 40098.1033 | [12 empty] | T+80 sec | 40098.1033
| 40098.1033 | 59.865 | 3826.7532 |  |  |  | 107.9987 | 109.6515 |  | 0.61562 | 3808.9379 | 3783.4961 | 3768.9901 | 3698.5322 | 3686.2198 | 633 | [6 empty] | 0 | 633 | -357.6309 | [13 empty] | 40098.1033 | 59.865 | 3826.7532 | 335 | -214.3467 | 0 | 83.5 | 10 | 0 | -103 | 7641 | 107.9987
| 40098.1033 | 59.865 | 3826.7532 |  |  |  | 107.9987 | 109.073 |  | 0.61562 | 3808.9751 | 3784.5021 | 3769.92 | 3699.1478 | 3686.5276 | 633 | [6 empty] | 0 | 633 | -357.6309 | [13 empty] | 40098.1033 | 59.865 | 3826.7532 | 335 | -214.3467 | 0 | 83.5 | 10 | 0 | -103 | 7641 | 107.9987
| 40098.1034 | 59.871 | 3825.7134 |  |  |  | 103.2013 | 107.0179 |  | 0.61562 | 3807.5356 | 3785.4387 | 3770.7749 | 3699.7634 | 3686.8354 | 633 | [6 empty] | 0 | 633 | -370.1723 | [13 empty] | 40098.1034 | 59.871 | 3825.7134 | 335 | -214.3467 | 0 | 84 | 10 | 0 | -103 | 7642 | 103.2013
| 40098.1034 | 59.871 | 3825.7134 |  |  |  | 103.2013 | 105.6821 |  | 0.61562 | 3806.8154 | 3786.3337 | 3771.5758 | 3700.379 | 3687.1432 | 633 | [6 empty] | 0 | 633 | -370.1723 | [13 empty] | 40098.1034 | 59.871 | 3825.7134 | 335 | -214.3467 | 0 | 84 | 10 | 0 | -103 | 7642 | 103.2013
| 40098.1034 | 59.871 | 3825.7134 |  |  |  | 103.2013 | 104.8138 |  | 0.61562 | 3806.5627 | 3787.1898 | 3772.3364 | 3700.9946 | 3687.451 | 633 | [6 empty] | 0 | 633 | -370.1723 | [13 empty] | 40098.1034 | 59.871 | 3825.7134 | 335 | -214.3467 | 0 | 84 | 10 | 0 | -103 | 7642 | 103.2013
| 40098.1034 | 59.88 | 3819.0811 |  |  |  | 95.9991 | 101.7287 |  | 0.61562 | 3804.0932 | 3787.8683 | 3773.0121 | 3701.6103 | 3687.7589 | 633 | [6 empty] | 0 | 633 | -390.7438 | [13 empty] | 40098.1034 | 59.88 | 3819.0811 | 335 | -212.1727 | 0 | 84.5 | 10 | 0 | -103 | 7629 | 95.9991
| 40098.1034 | 59.88 | 3819.0811 |  |  |  | 95.9991 | 99.7233 |  | 0.61562 | 3802.7035 | 3788.5186 | 3773.6306 | 3702.2259 | 3688.0667 | 633 | [6 empty] | 0 | 633 | -390.7438 | [13 empty] | 40098.1034 | 59.88 | 3819.0811 | 335 | -212.1727 | 0 | 84.5 | 10 | 0 | -103 | 7629 | 95.9991
| 40098.1035 | 59.88 | 3819.0811 |  |  |  | 95.9991 | 98.4199 |  | 0.61562 | 3802.0156 | 3789.1423 | 3774.2099 | 3702.8415 | 3688.3745 | 633 | [6 empty] | 0 | 633 | -390.7438 | [13 empty] | 40098.1035 | 59.88 | 3819.0811 | 335 | -212.1727 | 0 | 84.5 | 10 | 0 | -103 | 7629 | 95.9991
| 40098.1035 | 59.89 | 3815.0098 |  |  |  | 88.0005 | 94.7731 |  | 0.61562 | 3798.9845 | 3789.6597 | 3774.7054 | 3703.4571 | 3688.6823 | 633 | [6 empty] | 0 | 633 | -416.4462 | [13 empty] | 40098.1035 | 59.89 | 3815.0098 | 335 | -212.1727 | 0 | 85 | 10 | 0 | -103 | 7630 | 88.0005
| 40098.1035 | 59.89 | 3815.0098 |  |  |  | 88.0005 | 92.4027 |  | 0.61562 | 3797.2297 | 3790.1567 | 3775.1471 | 3704.0727 | 3688.9901 | 633 | [6 empty] | 0 | 633 | -416.4462 | [13 empty] | 40098.1035 | 59.89 | 3815.0098 | 335 | -212.1727 | 0 | 85 | 10 | 0 | -103 | 7630 | 88.0005
| 40098.1035 | 59.89 | 3815.0098 |  |  |  | 88.0005 | 90.8619 |  | 0.61562 | 3796.3045 | 3790.6347 | 3775.5539 | 3704.6883 | 3689.2979 | 633 | [6 empty] | 0 | 633 | -416.4462 | [13 empty] | 40098.1035 | 59.89 | 3815.0098 | 335 | -212.1727 | 0 | 85 | 10 | 0 | -103 | 7630 | 88.0005
| 40098.1036 | 59.893 | 3809.6519 |  |  |  | 85.5988 | 89.0198 |  | 0.61562 | 3795.078 | 3790.9935 | 3775.9223 | 3705.304 | 3689.6057 | 633 | [6 empty] | 0 | 633 | -424.8372 | [13 empty] | 40098.1036 | 59.893 | 3809.6519 | 335 | -212.1727 | 0 | 85.5 | 10 | 0 | -103 | 7630 | 85.5988
| 40098.1036 | 59.893 | 3809.6519 |  |  |  | 85.5988 | 87.8224 |  | 0.61562 | 3794.4963 | 3791.339 | 3776.2663 | 3705.9196 | 3689.9135 | 633 | [6 empty] | 0 | 633 | -424.8372 | [13 empty] | 40098.1036 | 59.893 | 3809.6519 | 335 | -212.1727 | 0 | 85.5 | 10 | 0 | -103 | 7630 | 85.5988
| 40098.1036 | 59.893 | 3809.6519 |  |  |  | 85.5988 | 87.0441 |  | 0.61562 | 3794.3336 | 3791.672 | 3776.5948 | 3706.5352 | 3690.2213 | 633 | [6 empty] | 0 | 633 | -424.8372 | [13 empty] | 40098.1036 | 59.893 | 3809.6519 | 335 | -212.1727 | 0 | 85.5 | 10 | 0 | -103 | 7630 | 85.5988
| 40098.1036 | 59.902 | 3804.1885 |  |  |  | 78.3997 | 84.0186 |  | 0.61562 | 3791.9237 | 3791.8955 | 3776.8685 | 3707.1508 | 3690.5291 | 633 | [6 empty] | 0 | 633 | -452.1448 | [13 empty] | 40098.1036 | 59.902 | 3804.1885 | 335 | -329.9882 | 0 | 86 | 10 | 0 | -103 | 7631 | 78.3997
| 40098.1037 | 59.902 | 3804.1885 |  |  |  | 78.3997 | 82.052 |  | 0.61562 | 3790.5727 | 3792.1112 | 3777.1089 | 3707.7664 | 3690.8369 | 633 | [6 empty] | 0 | 633 | -452.1448 | [13 empty] | 40098.1037 | 59.902 | 3804.1885 | 335 | -329.9882 | 0 | 86 | 10 | 0 | -103 | 7631 | 78.3997
| 40098.1037 | 59.902 | 3804.1885 |  |  |  | 78.3997 | 80.7737 |  | 0.61562 | 3789.91 | 3792.3194 | 3777.3296 | 3708.3821 | 3691.1448 | 633 | [6 empty] | 0 | 633 | -452.1448 | [13 empty] | 40098.1037 | 59.902 | 3804.1885 | 335 | -329.9882 | 0 | 86 | 10 | 0 | -103 | 7631 | 78.3997
| 40098.1037 | 59.907 | 3792.1694 |  |  |  | 74.3988 | 78.5425 |  | 0.61562 | 3788.2944 | 3792.3168 | 3777.5155 | 3708.9977 | 3691.4526 | 633 | [6 empty] | 0 | 633 | -468.8947 | [13 empty] | 40098.1037 | 59.907 | 3792.1694 | 335 | -255.4442 | 0 | 86.5 | 10 | 0 | -103 | 7633 | 74.3988
| 40098.1037 | 59.907 | 3792.1694 |  |  |  | 74.3988 | 77.0922 |  | 0.61562 | 3787.4597 | 3792.3144 | 3777.6812 | 3709.6133 | 3691.7604 | 633 | [6 empty] | 0 | 633 | -468.8947 | [13 empty] | 40098.1037 | 59.907 | 3792.1694 | 335 | -255.4442 | 0 | 86.5 | 10 | 0 | -103 | 7633 | 74.3988
| 40098.1037 | 59.907 | 3792.1694 |  |  |  | 74.3988 | 76.1495 |  | 0.61562 | 3787.1327 | 3792.312 | 3777.8362 | 3710.2289 | 3692.0682 | 633 | [6 empty] | 0 | 633 | -468.8947 | [13 empty] | 40098.1037 | 59.907 | 3792.1694 | 335 | -255.4442 | 0 | 86.5 | 10 | 0 | -103 | 7633 | 74.3988
| 40098.1038 | 59.916 | 3788.1321 |  |  |  | 67.1997 | 73.0171 |  | 0.61562 | 3784.6159 | 3792.2446 | 3777.9455 | 3710.8445 | 3692.376 | 633 | [6 empty] | 0 | 633 | -502.3831 | [13 empty] | 40098.1038 | 59.916 | 3788.1321 | 335 | -255.4442 | 0 | 87 | 10 | 0 | -103 | 7636 | 67.1997
| 40098.1038 | 59.916 | 3788.1321 |  |  |  | 67.1997 | 70.981 |  | 0.61562 | 3783.1954 | 3792.1793 | 3778.0288 | 3711.4601 | 3692.6838 | 633 | [6 empty] | 0 | 633 | -502.3831 | [13 empty] | 40098.1038 | 59.916 | 3788.1321 | 335 | -255.4442 | 0 | 87 | 10 | 0 | -103 | 7636 | 67.1997
| 40098.1038 | 59.916 | 3788.1321 |  |  |  | 67.1997 | 69.6575 |  | 0.61562 | 3782.4876 | 3792.1161 | 3778.0985 | 3712.0758 | 3692.9916 | 633 | [6 empty] | 0 | 633 | -502.3831 | [13 empty] | 40098.1038 | 59.916 | 3788.1321 | 335 | -255.4442 | 0 | 87 | 10 | 0 | -103 | 7636 | 67.1997
| 40098.1038 | 59.92 | 3781.7012 |  |  |  | 64.0015 | 67.6779 |  | 0.61562 | 3781.1236 | 3791.9558 | 3778.1451 | 3712.6914 | 3693.2994 | 633 | [6 empty] | 0 | 633 | -518.8455 | [13 empty] | 40098.1038 | 59.92 | 3781.7012 | 335 | -255.4442 | 0 | 87.5 | 10 | 0 | -103 | 7640 | 64.0015
| 40098.1039 | 59.92 | 3781.7012 |  |  |  | 64.0015 | 66.3912 |  | 0.61562 | 3780.4524 | 3791.8005 | 3778.18 | 3713.307 | 3693.6072 | 633 | [6 empty] | 0 | 633 | -518.8455 | [13 empty] | 40098.1039 | 59.92 | 3781.7012 | 335 | -255.4442 | 0 | 87.5 | 10 | 0 | -103 | 7640 | 64.0015
| 40098.1039 | 59.92 | 3781.7012 |  |  |  | 64.0015 | 65.5548 |  | 0.61562 | 3780.2316 | 3791.6497 | 3778.2106 | 3713.9226 | 3693.915 | 633 | [6 empty] | 0 | 633 | -518.8455 | [13 empty] | 40098.1039 | 59.92 | 3781.7012 | 335 | -255.4442 | 0 | 87.5 | 10 | 0 | -103 | 7640 | 64.0015
| 40098.1039 | 59.917 | 3774.6042 |  |  |  | 66.4001 | 65.8506 |  | 0.61562 | 3781.1431 | 3791.3991 | 3778.2538 | 3714.5382 | 3694.2228 | 633 | [6 empty] | 0 | 633 | -506.4 | [13 empty] | 40098.1039 | 59.917 | 3774.6042 | 335 | -255.4442 | 0 | 88 | 10 | 0 | -103 | 7644 | 66.4001
| 40098.1039 | 59.917 | 3774.6042 |  |  |  | 66.4001 | 66.043 |  | 0.61562 | 3781.9511 | 3791.1557 | 3778.3073 | 3715.1539 | 3694.5307 | 633 | [6 empty] | 0 | 633 | -506.4 | [13 empty] | 40098.1039 | 59.917 | 3774.6042 | 335 | -255.4442 | 0 | 88 | 10 | 0 | -103 | 7644 | 66.4001
| 40098.104 | 59.917 | 3774.6042 |  |  |  | 66.4001 | 66.168 |  | 0.61562 | 3782.6917 | 3790.9192 | 3778.37 | 3715.7695 | 3694.8385 | 633 | [6 empty] | 0 | 633 | -506.4 | [13 empty] | 40098.104 | 59.917 | 3774.6042 | 335 | -255.4442 | 0 | 88 | 10 | 0 | -103 | 7644 | 66.4001
| 40098.104 | 59.923 | 3772.7224 |  |  |  | 61.5997 | 64.5691 |  | 0.61562 | 3781.7084 | 3790.6629 | 3778.417 | 3716.3851 | 3695.1463 | 633 | [6 empty] | 0 | 633 | -531.9351 | [13 empty] | 40098.104 | 59.923 | 3772.7224 | 335 | -255.4442 | 0 | 88.5 | 10 | 0 | -103 | 7648 | 61.5997
| 40098.104 | 59.923 | 3772.7224 |  |  |  | 61.5997 | 63.5298 |  | 0.61562 | 3781.2848 | 3790.4137 | 3778.4568 | 3717.0007 | 3695.4541 | 633 | [6 empty] | 0 | 633 | -531.9351 | [13 empty] | 40098.104 | 59.923 | 3772.7224 | 335 | -255.4442 | 0 | 88.5 | 10 | 0 | -103 | 7648 | 61.5997
| 40098.104 | 59.923 | 3772.7224 |  |  |  | 61.5997 | 62.8543 |  | 0.61562 | 3781.2249 | 3790.1714 | 3778.4948 | 3717.6163 | 3695.7619 | 633 | [6 empty] | 0 | 633 | -531.9351 | [13 empty] | 40098.104 | 59.923 | 3772.7224 | 335 | -255.4442 | 0 | 88.5 | 10 | 0 | -103 | 7648 | 61.5997
| 40098.1041 | 59.928 | 3768.707 |  |  |  | 57.5989 | 61.0149 |  | 0.61562 | 3780.0011 | 3789.8813 | 3778.5151 | 3718.2319 | 3696.0697 | 633 | [6 empty] | 0 | 633 | -555.2709 | [13 empty] | 40098.1041 | 59.928 | 3768.707 | 335 | -254.8383 | 0 | 89 | 10 | 0 | -103 | 7652 | 57.5989
| 40098.1041 | 59.928 | 3768.707 |  |  |  | 57.5989 | 59.8193 |  | 0.61562 | 3779.4211 | 3789.599 | 3778.5272 | 3718.8476 | 3696.3775 | 633 | [6 empty] | 0 | 633 | -555.2709 | [13 empty] | 40098.1041 | 59.928 | 3768.707 | 335 | -254.8383 | 0 | 89 | 10 | 0 | -103 | 7652 | 57.5989
| 40098.1041 | 59.928 | 3768.707 |  |  |  | 57.5989 | 59.0421 |  | 0.61562 | 3779.2596 | 3789.3241 | 3778.5368 | 3719.4632 | 3696.6853 | 633 | [6 empty] | 0 | 633 | -555.2709 | [13 empty] | 40098.1041 | 59.928 | 3768.707 | 335 | -254.8383 | 0 | 89 | 10 | 0 | -103 | 7652 | 57.5989
| 40098.1041 | 59.927 | 3767.408 |  |  |  | 58.4015 | 58.8179 |  | 0.61562 | 3779.651 | 3789.0395 | 3778.5513 | 3720.0788 | 3696.9931 | 633 | [6 empty] | 0 | 633 | -550.4267 | [13 empty] | 40098.1041 | 59.927 | 3767.408 | 335 | -254.8383 | 0 | 89.5 | 10 | 0 | -103 | 7656 | 58.4015
| 40098.1041 | 59.927 | 3767.408 |  |  |  | 58.4015 | 58.6722 |  | 0.61562 | 3780.1208 | 3788.7622 | 3778.5714 | 3720.6944 | 3697.3009 | 633 | [6 empty] | 0 | 633 | -550.4267 | [13 empty] | 40098.1041 | 59.927 | 3767.408 | 335 | -254.8383 | 0 | 89.5 | 10 | 0 | -103 | 7656 | 58.4015
| 40098.1042 | 59.927 | 3767.408 |  |  |  | 58.4015 | 58.5774 |  | 0.61562 | 3780.6417 | 3788.4919 | 3778.5976 | 3721.31 | 3697.6087 | 633 | [6 empty] | 0 | 633 | -550.4267 | [13 empty] | 40098.1042 | 59.927 | 3767.408 | 335 | -254.8383 | 0 | 89.5 | 10 | 0 | -103 | 7656 | 58.4015
| 40098.1042 | 59.929 | 3765.6716 |  |  |  | 56.7993 | 57.9551 |  | 0.61562 | 3780.635 | 3788.2066 | 3778.6231 | 3721.9257 | 3697.9166 | 633 | [6 empty] | 0 | 633 | -560.1821 | [13 empty] | 40098.1042 | 59.929 | 3765.6716 | 350 | -254.8383 | 0 | 90 | 10 | 0 | -103 | 7662 | 56.7993
| 40098.1042 | 59.929 | 3765.6716 |  |  |  | 56.7993 | 57.5506 |  | 0.61562 | 3780.8461 | 3787.9284 | 3778.6505 | 3722.5413 | 3698.2244 | 633 | [6 empty] | 0 | 633 | -560.1821 | [13 empty] | 40098.1042 | 59.929 | 3765.6716 | 350 | -254.8383 | 0 | 90 | 10 | 0 | -103 | 7662 | 56.7993
| 40098.1042 | 59.929 | 3765.6716 |  |  |  | 56.7993 | 57.2876 |  | 0.61562 | 3781.1988 | 3787.657 | 3778.6816 | 3723.1569 | 3698.5322 | 633 | [6 empty] | 0 | 633 | -560.1821 | [13 empty] | 40098.1042 | 59.929 | 3765.6716 | 350 | -254.8383 | 0 | 90 | 10 | 0 | -103 | 7662 | 56.7993
| 40098.1043 | 59.937 | 3765.105 |  |  |  | 50.3998 | 54.8769 |  | 0.61562 | 3779.4037 | 3787.3853 | 3778.6903 | 3723.7725 | 3698.84 | 633 | [6 empty] | 0 | 633 | -602.8598 | [13 empty] | 40098.1043 | 59.937 | 3765.105 | 350 | -254.8383 | 0 | 90.5 | 10 | 0 | -103 | 7665 | 50.3998
| 40098.1043 | 59.937 | 3765.105 |  |  |  | 50.3998 | 53.3099 |  | 0.61562 | 3778.4523 | 3787.12 | 3778.6875 | 3724.3881 | 3699.1478 | 633 | [6 empty] | 0 | 633 | -602.8598 | [13 empty] | 40098.1043 | 59.937 | 3765.105 | 350 | -254.8383 | 0 | 90.5 | 10 | 0 | -103 | 7665 | 50.3998
| 40098.1043 | 59.937 | 3765.105 |  |  |  | 50.3998 | 52.2914 |  | 0.61562 | 3778.0494 | 3786.861 | 3778.68 | 3725.0037 | 3699.4556 | 633 | [6 empty] | 0 | 633 | -602.8598 | [13 empty] | 40098.1043 | 59.937 | 3765.105 | 350 | -254.8383 | 0 | 90.5 | 10 | 0 | -103 | 7665 | 50.3998
| 40098.1043 | 59.949 | 3753.9224 |  |  |  | 40.799 | 48.269 |  | 0.61562 | 3774.6426 | 3786.478 | 3778.633 | 3725.6194 | 3699.7634 | 633 | [6 empty] | 0 | 633 | -680.6561 | [13 empty] | 40098.1043 | 59.949 | 3753.9224 | 350 | -254.8383 | 0 | 91 | 10 | 0 | -103 | 7670 | 40.799
| 40098.1044 | 59.949 | 3753.9224 |  |  |  | 40.799 | 45.6545 |  | 0.61562 | 3772.6437 | 3786.1038 | 3778.5642 | 3726.235 | 3700.0712 | 633 | [6 empty] | 0 | 633 | -680.6561 | [13 empty] | 40098.1044 | 59.949 | 3753.9224 | 350 | -254.8383 | 0 | 91 | 10 | 0 | -103 | 7670 | 40.799
| 40098.1044 | 59.949 | 3753.9224 |  |  |  | 40.799 | 43.9551 |  | 0.61562 | 3771.5599 | 3785.7381 | 3778.4846 | 3726.8506 | 3700.379 | 633 | [6 empty] | 0 | 633 | -680.6561 | [13 empty] | 40098.1044 | 59.949 | 3753.9224 | 350 | -254.8383 | 0 | 91 | 10 | 0 | -103 | 7670 | 40.799
| 40098.1044 | 59.941 | 3747.8755 |  |  |  | 47.1985 | 45.0903 |  | 0.61562 | 3773.3107 | 3785.3127 | 3778.4265 | 3727.4662 | 3700.6868 | 633 | [6 empty] | 0 | 633 | -626.7456 | [13 empty] | 40098.1044 | 59.941 | 3747.8755 | 350 | -257.147 | 0 | 91.5 | 10 | 0 | -103 | 7674 | 47.1985
| 40098.1044 | 59.941 | 3747.8755 |  |  |  | 47.1985 | 45.8281 |  | 0.61562 | 3774.6642 | 3784.8967 | 3778.3847 | 3728.0818 | 3700.9946 | 633 | [6 empty] | 0 | 633 | -626.7456 | [13 empty] | 40098.1044 | 59.941 | 3747.8755 | 350 | -257.147 | 0 | 91.5 | 10 | 0 | -103 | 7674 | 47.1985
| 40098.1044 | 59.941 | 3747.8755 |  |  |  | 47.1985 | 46.3078 |  | 0.61562 | 3775.7595 | 3784.4899 | 3778.3558 | 3728.6974 | 3701.3025 | 633 | [6 empty] | 0 | 633 | -626.7456 | [13 empty] | 40098.1044 | 59.941 | 3747.8755 | 350 | -257.147 | 0 | 91.5 | 10 | 0 | -103 | 7674 | 47.1985
| 40098.1045 | 59.948 | 3746.7061 |  |  |  | 41.5985 | 44.6595 |  | 0.61562 | 3774.7269 | 3784.0792 | 3778.3164 | 3729.3131 | 3701.6103 | 633 | [6 empty] | 0 | 633 | -673.4189 | [13 empty] | 40098.1045 | 59.948 | 3746.7061 | 350 | -257.147 | 0 | 92 | 10 | 0 | -103 | 7679 | 41.5985
| 40098.1045 | 59.948 | 3746.7061 |  |  |  | 41.5985 | 43.5882 |  | 0.61562 | 3774.2711 | 3783.6773 | 3778.2729 | 3729.9287 | 3701.9181 | 633 | [6 empty] | 0 | 633 | -673.4189 | [13 empty] | 40098.1045 | 59.948 | 3746.7061 | 350 | -257.147 | 0 | 92 | 10 | 0 | -103 | 7679 | 41.5985
| 40098.1045 | 59.948 | 3746.7061 |  |  |  | 41.5985 | 42.8918 |  | 0.61562 | 3774.1904 | 3783.284 | 3778.2294 | 3730.5443 | 3702.2259 | 633 | [6 empty] | 0 | 633 | -673.4189 | [13 empty] | 40098.1045 | 59.948 | 3746.7061 | 350 | -257.147 | 0 | 92 | 10 | 0 | -103 | 7679 | 41.5985
| 40098.1045 | 59.951 | 3740.259 |  |  |  | 39.1998 | 41.5996 |  | 0.61562 | 3773.5138 | 3782.8311 | 3778.1798 | 3731.1599 | 3702.5337 | 633 | [6 empty] | 0 | 633 | -695.6074 | [13 empty] | 40098.1045 | 59.951 | 3740.259 | 350 | -257.147 | 0 | 92.5 | 10 | 0 | -103 | 7682 | 39.1998
| 40098.1046 | 59.951 | 3740.259 |  |  |  | 39.1998 | 40.7597 |  | 0.61562 | 3773.2895 | 3782.3877 | 3778.1289 | 3731.7755 | 3702.8415 | 633 | [6 empty] | 0 | 633 | -695.6074 | [13 empty] | 40098.1046 | 59.951 | 3740.259 | 350 | -257.147 | 0 | 92.5 | 10 | 0 | -103 | 7682 | 39.1998
| 40098.1046 | 59.951 | 3740.259 |  |  |  | 39.1998 | 40.2137 |  | 0.61562 | 3773.3592 | 3781.9534 | 3778.0797 | 3732.3912 | 3703.1493 | 633 | [6 empty] | 0 | 633 | -695.6074 | [13 empty] | 40098.1046 | 59.951 | 3740.259 | 350 | -257.147 | 0 | 92.5 | 10 | 0 | -103 | 7682 | 39.1998
| 40098.1046 | 59.951 | 3727.8384 |  |  |  | 39.1998 | 39.8589 |  | 0.61562 | 3773.6199 | 3781.4012 | 3778.0342 | 3733.0068 | 3703.4571 | 633 | [6 empty] | 0 | 633 | -695.6074 | [13 empty] | 40098.1046 | 59.951 | 3727.8384 | 350 | -257.147 | 0 | 93 | 10 | 0 | -103 | 7684 | 39.1998
| 40098.1046 | 59.951 | 3727.8384 |  |  |  | 39.1998 | 39.6282 |  | 0.61562 | 3774.0049 | 3780.8601 | 3777.9935 | 3733.6224 | 3703.7649 | 633 | [6 empty] | 0 | 633 | -695.6074 | [13 empty] | 40098.1046 | 59.951 | 3727.8384 | 350 | -257.147 | 0 | 93 | 10 | 0 | -103 | 7684 | 39.1998
| 40098.1047 | 59.951 | 3727.8384 |  |  |  | 39.1998 | 39.4783 |  | 0.61562 | 3774.4705 | 3780.3299 | 3777.9582 | 3734.238 | 3704.0727 | 633 | [6 empty] | 0 | 633 | -695.6074 | [13 empty] | 40098.1047 | 59.951 | 3727.8384 | 350 | -257.147 | 0 | 93 | 10 | 0 | -103 | 7684 | 39.1998
| 40098.1047 | 59.952 | 3720.5781 |  |  |  | 38.4003 | 39.101 |  | 0.61562 | 3774.7089 | 3779.7383 | 3777.9261 | 3734.8536 | 3704.3805 | 633 | [6 empty] | 0 | 633 | -703.3321 | [13 empty] | 40098.1047 | 59.952 | 3720.5781 | 350 | -257.147 | 0 | 93.5 | 10 | 0 | -103 | 7686 | 38.4003
| 40098.1047 | 59.952 | 3720.5781 |  |  |  | 38.4003 | 38.8557 |  | 0.61562 | 3775.0792 | 3779.1583 | 3777.8982 | 3735.4692 | 3704.6883 | 633 | [6 empty] | 0 | 633 | -703.3321 | [13 empty] | 40098.1047 | 59.952 | 3720.5781 | 350 | -257.147 | 0 | 93.5 | 10 | 0 | -103 | 7686 | 38.4003
| 40098.1047 | 59.952 | 3720.5781 |  |  |  | 38.4003 | 38.6963 |  | 0.61562 | 3775.5354 | 3778.5896 | 3777.8752 | 3736.0849 | 3704.9962 | 633 | [6 empty] | 0 | 633 | -703.3321 | [13 empty] | 40098.1047 | 59.952 | 3720.5781 | 350 | -257.147 | 0 | 93.5 | 10 | 0 | -103 | 7686 | 38.4003
| 40098.1047 | 59.954 | 3715.7527 |  |  |  | 36.8011 | 38.033 |  | 0.61562 | 3775.4878 | 3777.9854 | 3777.8523 | 3736.7005 | 3705.304 | 633 | [6 empty] | 0 | 633 | -719.308 | [13 empty] | 40098.1047 | 59.954 | 3715.7527 | 350 | -262.2894 | 0 | 94 | 10 | 0 | -103 | 7688 | 36.8011
| 40098.1048 | 59.954 | 3715.7527 |  |  |  | 36.8011 | 37.6019 |  | 0.61562 | 3775.6722 | 3777.3927 | 3777.8315 | 3737.3161 | 3705.6118 | 633 | [6 empty] | 0 | 633 | -719.308 | [13 empty] | 40098.1048 | 59.954 | 3715.7527 | 350 | -262.2894 | 0 | 94 | 10 | 0 | -103 | 7688 | 36.8011
| 40098.1048 | 59.954 | 3715.7527 |  |  |  | 36.8011 | 37.3216 |  | 0.61562 | 3776.0076 | 3776.8112 | 3777.8143 | 3737.9317 | 3705.9196 | 633 | [6 empty] | 0 | 633 | -719.308 | [13 empty] | 40098.1048 | 59.954 | 3715.7527 | 350 | -262.2894 | 0 | 94 | 10 | 0 | -103 | 7688 | 36.8011
| 40098.1048 | 59.953 | 3710.8481 |  |  |  | 37.6007 | 37.4193 |  | 0.61562 | 3776.7209 | 3776.1947 | 3777.8041 | 3738.5473 | 3706.2274 | 633 | [6 empty] | 0 | 633 | -711.2303 | [13 empty] | 40098.1048 | 59.953 | 3710.8481 | 350 | -262.2894 | 0 | 94.5 | 10 | 0 | -103 | 7689 | 37.6007
| 40098.1048 | 59.953 | 3710.8481 |  |  |  | 37.6007 | 37.4828 |  | 0.61562 | 3777.4 | 3775.5896 | 3777.8003 | 3739.163 | 3706.5352 | 633 | [6 empty] | 0 | 633 | -711.2303 | [13 empty] | 40098.1048 | 59.953 | 3710.8481 | 350 | -262.2894 | 0 | 94.5 | 10 | 0 | -103 | 7689 | 37.6007
| 40098.1049 | 59.953 | 3710.8481 |  |  |  | 37.6007 | 37.5241 |  | 0.61562 | 3778.0569 | 3774.9957 | 3777.8027 | 3739.7786 | 3706.843 | 633 | [6 empty] | 0 | 633 | -711.2303 | [13 empty] | 40098.1049 | 59.953 | 3710.8481 | 350 | -262.2894 | 0 | 94.5 | 10 | 0 | -103 | 7689 | 37.6007
| 40098.1049 | 59.954 | 3714.6226 |  |  |  | 36.8011 | 37.271 |  | 0.61562 | 3778.4195 | 3774.4468 | 3777.8083 | 3740.3942 | 3707.1508 | 633 | [6 empty] | 0 | 633 | -719.308 | [13 empty] | 40098.1049 | 59.954 | 3714.6226 | 350 | -262.2894 | 0 | 95 | 10 | 0 | -103 | 7689 | 36.8011
| 40098.1049 | 59.954 | 3714.6226 |  |  |  | 36.8011 | 37.1066 |  | 0.61562 | 3778.8706 | 3773.9079 | 3777.8179 | 3741.0098 | 3707.4586 | 633 | [6 empty] | 0 | 633 | -719.308 | [13 empty] | 40098.1049 | 59.954 | 3714.6226 | 350 | -262.2894 | 0 | 95 | 10 | 0 | -103 | 7689 | 36.8011
| 40098.1049 | 59.954 | 3714.6226 |  |  |  | 36.8011 | 36.9997 |  | 0.61562 | 3779.3794 | 3773.3785 | 3777.8318 | 3741.6254 | 3707.7664 | 633 | [6 empty] | 0 | 633 | -719.308 | [13 empty] | 40098.1049 | 59.954 | 3714.6226 | 350 | -262.2894 | 0 | 95 | 10 | 0 | -103 | 7689 | 36.8011
| 40098.105 | 59.956 | 3716.4614 |  |  |  | 35.199 | 36.3694 |  | 0.61562 | 3779.3647 | 3772.8748 | 3777.8454 | 3742.241 | 3708.0742 | 633 | [6 empty] | 0 | 633 | -736.059 | [13 empty] | 40098.105 | 59.956 | 3716.4614 | 350 | -262.2894 | 0 | 95.5 | 10 | 0 | -103 | 7690 | 35.199
| 40098.105 | 59.956 | 3716.4614 |  |  |  | 35.199 | 35.9598 |  | 0.61562 | 3779.5707 | 3772.38 | 3777.8605 | 3742.8567 | 3708.3821 | 633 | [6 empty] | 0 | 633 | -736.059 | [13 empty] | 40098.105 | 59.956 | 3716.4614 | 350 | -262.2894 | 0 | 95.5 | 10 | 0 | -103 | 7690 | 35.199
| 40098.105 | 59.956 | 3716.4614 |  |  |  | 35.199 | 35.6935 |  | 0.61562 | 3779.92 | 3771.8937 | 3777.8784 | 3743.4723 | 3708.6899 | 633 | [6 empty] | 0 | 633 | -736.059 | [13 empty] | 40098.105 | 59.956 | 3716.4614 | 350 | -262.2894 | 0 | 95.5 | 10 | 0 | -103 | 7690 | 35.199
| 40098.105 | 59.955 | 3722.3613 |  |  |  | 35.9985 | 35.8003 |  | 0.61562 | 3780.6424 | 3771.4667 | 3777.9022 | 3744.0879 | 3708.9977 | 633 | [6 empty] | 0 | 633 | -727.6031 | [13 empty] | 40098.105 | 59.955 | 3722.3613 | 350 | -262.2894 | 0 | 96 | 10 | 0 | -103 | 7690.08 | 35.9985
| 40098.105 | 59.955 | 3722.3613 |  |  |  | 35.9985 | 35.8697 |  | 0.61562 | 3781.3274 | 3771.047 | 3777.9315 | 3744.7035 | 3709.3055 | 633 | [6 empty] | 0 | 633 | -727.6031 | [13 empty] | 40098.105 | 59.955 | 3722.3613 | 350 | -262.2894 | 0 | 96 | 10 | 0 | -103 | 7690.08 | 35.9985
| 40098.1051 | 59.955 | 3722.3613 |  |  |  | 35.9985 | 35.9148 |  | 0.61562 | 3781.9882 | 3770.6344 | 3777.9659 | 3745.3191 | 3709.6133 | 633 | [6 empty] | 0 | 633 | -727.6031 | [13 empty] | 40098.1051 | 59.955 | 3722.3613 | 350 | -262.2894 | 0 | 96 | 10 | 0 | -103 | 7690.08 | 35.9985
| 40098.1051 | 59.962 | 3722.2666 |  |  |  | 30.3986 | 33.9841 |  | 0.61562 | 3780.6731 | 3770.228 | 3777.9886 | 3745.9347 | 3709.9211 | 633 | [6 empty] | 0 | 633 | -791.2696 | [13 empty] | 40098.1051 | 59.962 | 3722.2666 | 350 | -256.6479 | 0 | 96.5 | 10 | 0 | -103 | 7690 | 30.3986
| 40098.1051 | 59.962 | 3722.2666 |  |  |  | 30.3986 | 32.7292 |  | 0.61562 | 3780.0338 | 3769.8283 | 3778.0057 | 3746.5504 | 3710.2289 | 633 | [6 empty] | 0 | 633 | -791.2696 | [13 empty] | 40098.1051 | 59.962 | 3722.2666 | 350 | -256.6479 | 0 | 96.5 | 10 | 0 | -103 | 7690 | 30.3986
| 40098.1051 | 59.962 | 3722.2666 |  |  |  | 30.3986 | 31.9134 |  | 0.61562 | 3779.8337 | 3769.4352 | 3778.0208 | 3747.166 | 3710.5367 | 633 | [6 empty] | 0 | 633 | -791.2696 | [13 empty] | 40098.1051 | 59.962 | 3722.2666 | 350 | -256.6479 | 0 | 96.5 | 10 | 0 | -103 | 7690 | 30.3986
| 40098.1052 | 59.966 | 3723.0908 |  |  |  | 27.2003 | 30.2639 |  | 0.61562 | 3778.7997 | 3769.0554 | 3778.0272 | 3747.7816 | 3710.8445 | 633 | [6 empty] | 0 | 633 | -832.8924 | [13 empty] | 40098.1052 | 59.966 | 3723.0908 | 350 | -256.6479 | 0 | 97 | 10 | 0 | -103 | 7692.06 | 27.2003
| 40098.1052 | 59.966 | 3723.0908 |  |  |  | 27.2003 | 29.1916 |  | 0.61562 | 3778.3431 | 3768.6817 | 3778.0298 | 3748.3972 | 3711.1523 | 633 | [6 empty] | 0 | 633 | -832.8924 | [13 empty] | 40098.1052 | 59.966 | 3723.0908 | 350 | -256.6479 | 0 | 97 | 10 | 0 | -103 | 7692.06 | 27.2003
| 40098.1052 | 59.966 | 3723.0908 |  |  |  | 27.2003 | 28.4947 |  | 0.61562 | 3778.2618 | 3768.314 | 3778.0316 | 3749.0128 | 3711.4601 | 633 | [6 empty] | 0 | 633 | -832.8924 | [13 empty] | 40098.1052 | 59.966 | 3723.0908 | 350 | -256.6479 | 0 | 97 | 10 | 0 | -103 | 7692.06 | 27.2003
| 40098.1052 | 59.97 | 3723.8931 |  |  |  | 23.999 | 26.9212 |  | 0.61562 | 3777.3039 | 3767.9586 | 3778.0258 | 3749.6285 | 3711.768 | 633 | [6 empty] | 0 | 633 | -879.1838 | [13 empty] | 40098.1052 | 59.97 | 3723.8931 | 350 | -256.6479 | 0 | 97.5 | 10 | 0 | -103 | 7693.05 | 23.999
| 40098.1053 | 59.97 | 3723.8931 |  |  |  | 23.999 | 25.8984 |  | 0.61562 | 3776.8968 | 3767.6089 | 3778.0168 | 3750.2441 | 3712.0758 | 633 | [6 empty] | 0 | 633 | -879.1838 | [13 empty] | 40098.1053 | 59.97 | 3723.8931 | 350 | -256.6479 | 0 | 97.5 | 10 | 0 | -103 | 7693.05 | 23.999
| 40098.1053 | 59.97 | 3723.8931 |  |  |  | 23.999 | 25.2336 |  | 0.61562 | 3776.8476 | 3767.2647 | 3778.0076 | 3750.8597 | 3712.3836 | 633 | [6 empty] | 0 | 633 | -879.1838 | [13 empty] | 40098.1053 | 59.97 | 3723.8931 | 350 | -256.6479 | 0 | 97.5 | 10 | 0 | -103 | 7693.05 | 23.999
| 40098.1053 | 59.969 | 3728.053 |  |  |  | 24.7986 | 25.0814 |  | 0.61562 | 3777.3109 | 3766.9583 | 3778.0022 | 3751.4753 | 3712.6914 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.1053 | 59.969 | 3728.053 | 350 | -256.6479 | 0 | 98 | 10 | 0 | -103 | 7694.04 | 24.7986
| 40098.1053 | 59.969 | 3728.053 |  |  |  | 24.7986 | 24.9824 |  | 0.61562 | 3777.8276 | 3766.6568 | 3778.0008 | 3752.0909 | 3712.9992 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.1053 | 59.969 | 3728.053 | 350 | -256.6479 | 0 | 98 | 10 | 0 | -103 | 7694.04 | 24.7986
| 40098.1053 | 59.969 | 3728.053 |  |  |  | 24.7986 | 24.9181 |  | 0.61562 | 3778.3789 | 3766.3598 | 3778.0037 | 3752.7065 | 3713.307 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.1053 | 59.969 | 3728.053 | 350 | -256.6479 | 0 | 98 | 10 | 0 | -103 | 7694.04 | 24.7986
| 40098.1054 | 59.971 | 3733.3271 |  |  |  | 23.1995 | 24.3166 |  | 0.61562 | 3778.393 | 3766.1076 | 3778.0067 | 3753.3222 | 3713.6148 | 633 | [6 empty] | 0 | 633 | -891.56 | [13 empty] | 40098.1054 | 59.971 | 3733.3271 | 350 | -256.6479 | 0 | 98.5 | 10 | 0 | -103 | 7695.03 | 23.1995
| 40098.1054 | 59.971 | 3733.3271 |  |  |  | 23.1995 | 23.9256 |  | 0.61562 | 3778.6176 | 3765.8593 | 3778.0113 | 3753.9378 | 3713.9226 | 633 | [6 empty] | 0 | 633 | -891.56 | [13 empty] | 40098.1054 | 59.971 | 3733.3271 | 350 | -256.6479 | 0 | 98.5 | 10 | 0 | -103 | 7695.03 | 23.1995
| 40098.1054 | 59.971 | 3733.3271 |  |  |  | 23.1995 | 23.6714 |  | 0.61562 | 3778.9791 | 3765.6147 | 3778.0186 | 3754.5534 | 3714.2304 | 633 | [6 empty] | 0 | 633 | -891.56 | [13 empty] | 40098.1054 | 59.971 | 3733.3271 | 350 | -256.6479 | 0 | 98.5 | 10 | 0 | -103 | 7695.03 | 23.1995
| 40098.1054 | 59.976 | 3736.8218 |  |  |  | 19.1986 | 22.1059 |  | 0.61562 | 3778.0292 | 3765.3998 | 3778.0187 | 3755.169 | 3714.5382 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1054 | 59.976 | 3736.8218 | 350 | -256.3073 | 0 | 99 | 10 | 0 | -103 | 7696.02 | 19.1986
| 40098.1055 | 59.976 | 3736.8218 |  |  |  | 19.1986 | 21.0884 |  | 0.61562 | 3777.6273 | 3765.1881 | 3778.0158 | 3755.7846 | 3714.846 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1055 | 59.976 | 3736.8218 | 350 | -256.3073 | 0 | 99 | 10 | 0 | -103 | 7696.02 | 19.1986
| 40098.1055 | 59.976 | 3736.8218 |  |  |  | 19.1986 | 20.427 |  | 0.61562 | 3777.5815 | 3764.9796 | 3778.0126 | 3756.4003 | 3715.1539 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1055 | 59.976 | 3736.8218 | 350 | -256.3073 | 0 | 99 | 10 | 0 | -103 | 7696.02 | 19.1986
| 40098.1055 | 59.976 | 3740.877 |  |  |  | 19.1986 | 19.997 |  | 0.61562 | 3777.7672 | 3764.8036 | 3778.0108 | 3757.0159 | 3715.4617 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1055 | 59.976 | 3740.877 | 350 | -256.3073 | 0 | 99.5 | 10 | 0 | -103 | 7697.01 | 19.1986
| 40098.1055 | 59.976 | 3740.877 |  |  |  | 19.1986 | 19.7176 |  | 0.61562 | 3778.1033 | 3764.6303 | 3778.0115 | 3757.6315 | 3715.7695 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1055 | 59.976 | 3740.877 | 350 | -256.3073 | 0 | 99.5 | 10 | 0 | -103 | 7697.01 | 19.1986
| 40098.1056 | 59.976 | 3740.877 |  |  |  | 19.1986 | 19.5359 |  | 0.61562 | 3778.5373 | 3764.4594 | 3778.0153 | 3758.2471 | 3716.0773 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1056 | 59.976 | 3740.877 | 350 | -256.3073 | 0 | 99.5 | 10 | 0 | -103 | 7697.01 | 19.1986
| 40098.1056 | 59.978 | 3746.6079 |  |  |  | 17.5995 | 18.8582 |  | 0.61562 | 3778.4752 | 3764.3319 | 3778.0186 | 3758.8627 | 3716.3851 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1056 | 59.978 | 3746.6079 | 350 | -256.3073 | 0 | 100 | 10 | 0 | -103 | 7698 | 17.5995
| 40098.1056 | 59.978 | 3746.6079 |  |  |  | 17.5995 | 18.4176 |  | 0.61562 | 3778.6502 | 3764.2062 | 3778.023 | 3759.4783 | 3716.6929 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1056 | 59.978 | 3746.6079 | 350 | -256.3073 | 0 | 100 | 10 | 0 | -103 | 7698 | 17.5995
| 40098.1056 | 59.978 | 3746.6079 |  |  |  | 17.5995 | 18.1313 |  | 0.61562 | 3778.9795 | 3764.0822 | 3778.0298 | 3760.094 | 3717.0007 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1056 | 59.978 | 3746.6079 | 350 | -256.3073 | 0 | 100 | 10 | 0 | -103 | 7698 | 17.5995
| 40098.1056 | 59.982 | 3751.5576 |  |  |  | 14.4012 | 16.8258 |  | 0.61562 | 3778.2896 | 3763.9946 | 3778.0316 | 3760.7096 | 3717.3085 | 633 | [6 empty] | 0 | 633 | -1054.9759 | [13 empty] | 40098.1056 | 59.982 | 3751.5576 | 350 | -256.3073 | 0 | 100.5 | 10 | 0 | -103 | 7699 | 14.4012
| 40098.1057 | 59.982 | 3751.5576 |  |  |  | 14.4012 | 15.9772 |  | 0.61562 | 3778.0566 | 3763.9083 | 3778.0318 | 3761.3252 | 3717.6163 | 633 | [6 empty] | 0 | 633 | -1054.9759 | [13 empty] | 40098.1057 | 59.982 | 3751.5576 | 350 | -256.3073 | 0 | 100.5 | 10 | 0 | -103 | 7699 | 14.4012
| 40098.1057 | 59.982 | 3751.5576 |  |  |  | 14.4012 | 15.4256 |  | 0.61562 | 3778.1207 | 3763.8231 | 3778.0324 | 3761.9408 | 3717.9241 | 633 | [6 empty] | 0 | 633 | -1054.9759 | [13 empty] | 40098.1057 | 59.982 | 3751.5576 | 350 | -256.3073 | 0 | 100.5 | 10 | 0 | -103 | 7699 | 14.4012
| 40098.1057 | 59.979 | 3756.4072 |  |  |  | 16.7999 | 15.9066 |  | 0.61562 | 3779.2173 | 3763.7723 | 3778.0405 | 3762.5564 | 3718.2319 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.1057 | 59.979 | 3756.4072 | 350 | -256.3073 | 0 | 101 | 10 | 0 | -103 | 7699.98 | 16.7999
| 40098.1057 | 59.979 | 3756.4072 |  |  |  | 16.7999 | 16.2193 |  | 0.61562 | 3780.1456 | 3763.7222 | 3778.0548 | 3763.1721 | 3718.5398 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.1057 | 59.979 | 3756.4072 | 350 | -256.3073 | 0 | 101 | 10 | 0 | -103 | 7699.98 | 16.7999
| 40098.1058 | 59.979 | 3756.4072 |  |  |  | 16.7999 | 16.4225 |  | 0.61562 | 3780.9644 | 3763.6728 | 3778.0745 | 3763.7877 | 3718.8476 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.1058 | 59.979 | 3756.4072 | 350 | -256.3073 | 0 | 101 | 10 | 0 | -103 | 7699.98 | 16.7999
| 40098.1058 | 59.983 | 3760.9822 |  |  |  | 13.5986 | 15.4341 |  | 0.61562 | 3780.5917 | 3763.6547 | 3778.0914 | 3764.4033 | 3719.1554 | 633 | [6 empty] | 0 | 633 | -1072.9158 | [13 empty] | 40098.1058 | 59.983 | 3760.9822 | 350 | -249.0864 | 0 | 101.5 | 10 | 0 | -103 | 7700.97 | 13.5986
| 40098.1058 | 59.983 | 3760.9822 |  |  |  | 13.5986 | 14.7917 |  | 0.61562 | 3780.5649 | 3763.6369 | 3778.1079 | 3765.0189 | 3719.4632 | 633 | [6 empty] | 0 | 633 | -1072.9158 | [13 empty] | 40098.1058 | 59.983 | 3760.9822 | 350 | -249.0864 | 0 | 101.5 | 10 | 0 | -103 | 7700.97 | 13.5986
| 40098.1058 | 59.983 | 3760.9822 |  |  |  | 13.5986 | 14.3741 |  | 0.61562 | 3780.7629 | 3763.6193 | 3778.1254 | 3765.6345 | 3719.771 | 633 | [6 empty] | 0 | 633 | -1072.9158 | [13 empty] | 40098.1058 | 59.983 | 3760.9822 | 350 | -249.0864 | 0 | 101.5 | 10 | 0 | -103 | 7700.97 | 13.5986
| 40098.1059 | 59.988 | 3763.2122 |  |  |  | 9.6008 | 12.7035 |  | 0.61562 | 3779.7079 | 3763.6166 | 3778.1358 | 3766.2501 | 3720.0788 | 633 | [6 empty] | 0 | 633 | -1172.2037 | [13 empty] | 40098.1059 | 59.988 | 3763.2122 | 350 | -249.0864 | 0 | 102 | 10 | 0 | -103 | 7701.96 | 9.6008
| 40098.1059 | 59.988 | 3763.2122 |  |  |  | 9.6008 | 11.6176 |  | 0.61562 | 3779.2376 | 3763.614 | 3778.143 | 3766.8658 | 3720.3866 | 633 | [6 empty] | 0 | 633 | -1172.2037 | [13 empty] | 40098.1059 | 59.988 | 3763.2122 | 350 | -249.0864 | 0 | 102 | 10 | 0 | -103 | 7701.96 | 9.6008
| 40098.1059 | 59.988 | 3763.2122 |  |  |  | 9.6008 | 10.9117 |  | 0.61562 | 3779.1473 | 3763.6114 | 3778.1496 | 3767.4814 | 3720.6944 | 633 | [6 empty] | 0 | 633 | -1172.2037 | [13 empty] | 40098.1059 | 59.988 | 3763.2122 | 350 | -249.0864 | 0 | 102 | 10 | 0 | -103 | 7701.96 | 9.6008
| 40098.1059 | 59.987 | 3766.4331 |  |  |  | 10.4004 | 10.7327 |  | 0.61562 | 3779.584 | 3763.6296 | 3778.1588 | 3768.097 | 3721.0022 | 633 | [6 empty] | 0 | 633 | -1150.9027 | [13 empty] | 40098.1059 | 59.987 | 3766.4331 | 350 | -249.0864 | 0 | 102.5 | 10 | 0 | -103 | 7702.95 | 10.4004
| 40098.1059 | 59.987 | 3766.4331 |  |  |  | 10.4004 | 10.6164 |  | 0.61562 | 3780.0833 | 3763.6476 | 3778.1712 | 3768.7126 | 3721.31 | 633 | [6 empty] | 0 | 633 | -1150.9027 | [13 empty] | 40098.1059 | 59.987 | 3766.4331 | 350 | -249.0864 | 0 | 102.5 | 10 | 0 | -103 | 7702.95 | 10.4004
| 40098.106 | 59.987 | 3766.4331 |  |  |  | 10.4004 | 10.5408 |  | 0.61562 | 3780.6233 | 3763.6653 | 3778.1868 | 3769.3282 | 3721.6178 | 633 | [6 empty] | 0 | 633 | -1150.9027 | [13 empty] | 40098.106 | 59.987 | 3766.4331 | 350 | -249.0864 | 0 | 102.5 | 10 | 0 | -103 | 7702.95 | 10.4004
| 40098.106 | 59.992 | 3768.6335 |  |  |  | 6.3995 | 9.0914 |  | 0.61562 | 3779.7895 | 3763.6967 | 3778.1969 | 3769.9438 | 3721.9257 | 633 | [6 empty] | 0 | 633 | -1266.0193 | [13 empty] | 40098.106 | 59.992 | 3768.6335 | 350 | -249.0864 | 0 | 103 | 10 | 0 | -103 | 7703.94 | 6.3995
| 40098.106 | 59.992 | 3768.6335 |  |  |  | 6.3995 | 8.1492 |  | 0.61562 | 3779.463 | 3763.7278 | 3778.2049 | 3770.5595 | 3722.2335 | 633 | [6 empty] | 0 | 633 | -1266.0193 | [13 empty] | 40098.106 | 59.992 | 3768.6335 | 350 | -249.0864 | 0 | 103 | 10 | 0 | -103 | 7703.94 | 6.3995
| 40098.106 | 59.992 | 3768.6335 |  |  |  | 6.3995 | 7.5368 |  | 0.61562 | 3779.4662 | 3763.7585 | 3778.2128 | 3771.1751 | 3722.5413 | 633 | [6 empty] | 0 | 633 | -1266.0193 | [13 empty] | 40098.106 | 59.992 | 3768.6335 | 350 | -249.0864 | 0 | 103 | 10 | 0 | -103 | 7703.94 | 6.3995
| 40098.1061 | 59.986 | 3773.6948 |  |  |  | 11.2 | 8.8189 |  | 0.61562 | 3781.3639 | 3763.8202 | 3778.2323 | 3771.7907 | 3722.8491 | 633 | [6 empty] | 0 | 633 | -1130.3621 | [13 empty] | 40098.1061 | 59.986 | 3773.6948 | 350 | -249.0864 | 0 | 103.5 | 10 | 0 | -103 | 7704.93 | 11.2
| 40098.1061 | 59.986 | 3773.6948 |  |  |  | 11.2 | 9.6523 |  | 0.61562 | 3782.8129 | 3763.8811 | 3778.2606 | 3772.4063 | 3723.1569 | 633 | [6 empty] | 0 | 633 | -1130.3621 | [13 empty] | 40098.1061 | 59.986 | 3773.6948 | 350 | -249.0864 | 0 | 103.5 | 10 | 0 | -103 | 7704.93 | 11.2
| 40098.1061 | 59.986 | 3773.6948 |  |  |  | 11.2 | 10.194 |  | 0.61562 | 3783.9702 | 3763.9413 | 3778.2956 | 3773.0219 | 3723.4647 | 633 | [6 empty] | 0 | 633 | -1130.3621 | [13 empty] | 40098.1061 | 59.986 | 3773.6948 | 350 | -249.0864 | 0 | 103.5 | 10 | 0 | -103 | 7704.93 | 11.2
| 40098.1061 | 59.988 | 3775.3633 |  |  |  | 9.6008 | 9.9864 |  | 0.61562 | 3784.3782 | 3764.011 | 3778.3327 | 3773.6376 | 3723.7725 | 633 | [6 empty] | 0 | 633 | -1172.2037 | [13 empty] | 40098.1061 | 59.988 | 3775.3633 | 350 | -253.7425 | 0 | 104 | 10 | 0 | -103 | 7705.92 | 9.6008
| 40098.1062 | 59.988 | 3775.3633 |  |  |  | 9.6008 | 9.8514 |  | 0.61562 | 3784.8589 | 3764.0798 | 3778.3723 | 3774.2532 | 3724.0803 | 633 | [6 empty] | 0 | 633 | -1172.2037 | [13 empty] | 40098.1062 | 59.988 | 3775.3633 | 350 | -253.7425 | 0 | 104 | 10 | 0 | -103 | 7705.92 | 9.6008
| 40098.1062 | 59.988 | 3775.3633 |  |  |  | 9.6008 | 9.7637 |  | 0.61562 | 3785.3868 | 3764.1478 | 3778.4145 | 3774.8688 | 3724.3881 | 633 | [6 empty] | 0 | 633 | -1172.2037 | [13 empty] | 40098.1062 | 59.988 | 3775.3633 | 350 | -253.7425 | 0 | 104 | 10 | 0 | -103 | 7705.92 | 9.6008
| 40098.1062 | 59.998 | 3776.4202 |  |  |  | 1.5991 | 6.9061 |  | 0.61562 | 3783.1448 | 3764.2212 | 3778.4429 | 3775.4844 | 3724.6959 | 633 | [6 empty] | 0 | 633 | -1438.6783 | [13 empty] | 40098.1062 | 59.998 | 3776.4202 | 350 | -253.7425 | 0 | 104.5 | 10 | 0 | -103 | 7706.91 | 1.5991
| 40098.1062 | 59.998 | 3776.4202 |  |  |  | 1.5991 | 5.0487 |  | 0.61562 | 3781.903 | 3764.2939 | 3778.4635 | 3776.1 | 3725.0037 | 633 | [6 empty] | 0 | 633 | -1438.6783 | [13 empty] | 40098.1062 | 59.998 | 3776.4202 | 350 | -253.7425 | 0 | 104.5 | 10 | 0 | -103 | 7706.91 | 1.5991
| 40098.1062 | 59.998 | 3776.4202 |  |  |  | 1.5991 | 3.8413 |  | 0.61562 | 3781.3112 | 3764.3656 | 3778.4803 | 3776.7156 | 3725.3115 | 633 | [6 empty] | 0 | 633 | -1438.6783 | [13 empty] | 40098.1062 | 59.998 | 3776.4202 | 350 | -253.7425 | 0 | 104.5 | 10 | 0 | -103 | 7706.91 | 1.5991
| 40098.1063 | 59.999 | 3781.2559 |  |  |  | 0.79956 | 2.7767 |  | 0.61562 | 3780.8622 | 3764.465 | 3778.4943 | 3777.3313 | 3725.6194 | 633 | [6 empty] | 0 | 633 | -1472.1181 | [13 empty] | 40098.1063 | 59.999 | 3781.2559 | 350 | -253.7425 | 0 | 105 | 10 | 0 | -103 | 7707.9 | 0.79956
| 40098.1063 | 59.999 | 3781.2559 |  |  |  | 0.79956 | 2.0847 |  | 0.61562 | 3780.7859 | 3764.5632 | 3778.5077 | 3777.9469 | 3725.9272 | 633 | [6 empty] | 0 | 633 | -1472.1181 | [13 empty] | 40098.1063 | 59.999 | 3781.2559 | 350 | -253.7425 | 0 | 105 | 10 | 0 | -103 | 7707.9 | 0.79956
| 40098.1063 | 59.999 | 3781.2559 |  |  |  | 0.79956 | 1.6349 |  | 0.61562 | 3780.9517 | 3764.6602 | 3778.5219 | 3778.5625 | 3726.235 | 633 | [6 empty] | 0 | 633 | -1472.1181 | [13 empty] | 40098.1063 | 59.999 | 3781.2559 | 350 | -253.7425 | 0 | 105 | 10 | 0 | -103 | 7707.9 | 0.79956
| 40098.1063 | 60.002 | 3783.8955 |  |  |  | -1.5991 | 0.503 |  | 0 | 3779.8198 | 3764.7714 | 3778.5294 | 3778.5625 | 3726.5392 | 633 | [6 empty] | 0 | 633 | -1582.4638 | [13 empty] | 40098.1063 | 60.002 | 3783.8955 | 350 | -253.7425 | 0 | 105.5 | 10 | 0 | -103 | 7708.89 | -1.5991
| 40098.1064 | 60.002 | 3783.8955 |  |  |  | -1.5991 | -0.23275 |  | 0 | 3779.084 | 3764.8813 | 3778.5326 | 3778.5625 | 3726.8399 | 633 | [6 empty] | 0 | 633 | -1582.4638 | [13 empty] | 40098.1064 | 60.002 | 3783.8955 | 350 | -253.7425 | 0 | 105.5 | 10 | 0 | -103 | 7708.89 | -1.5991
| 40098.1064 | 60.002 | 3783.8955 |  |  |  | -1.5991 | -0.71098 |  | 0 | 3778.6058 | 3764.99 | 3778.533 | 3778.5625 | 3727.1372 | 633 | [6 empty] | 0 | 633 | -1582.4638 | [13 empty] | 40098.1064 | 60.002 | 3783.8955 | 350 | -253.7425 | 0 | 105.5 | 10 | 0 | -103 | 7708.89 | -1.5991
| 40098.1064 | 60.008 | 3785.4626 |  |  |  | -6.3995 | -2.702 |  | 0 | 3776.6148 | 3765.1063 | 3778.5221 | 3778.5625 | 3727.431 | 633 | [6 empty] | 0 | 633 | -1861.743 | [13 empty] | 40098.1064 | 60.008 | 3785.4626 | 350 | -253.7425 | 0 | 106 | 10 | 0 | -103 | 7709.88 | -6.3995
| 40098.1064 | 60.008 | 3785.4626 |  |  |  | -6.3995 | -3.9961 |  | 0 | 3775.3206 | 3765.2213 | 3778.5041 | 3778.5625 | 3727.7216 | 633 | [6 empty] | 0 | 633 | -1861.743 | [13 empty] | 40098.1064 | 60.008 | 3785.4626 | 350 | -253.7425 | 0 | 106 | 10 | 0 | -103 | 7709.88 | -6.3995
| 40098.1065 | 60.008 | 3785.4626 |  |  |  | -6.3995 | -4.8373 |  | 0 | 3774.4794 | 3765.335 | 3778.4814 | 3778.5625 | 3728.0088 | 633 | [6 empty] | 0 | 633 | -1861.743 | [13 empty] | 40098.1065 | 60.008 | 3785.4626 | 350 | -253.7425 | 0 | 106 | 10 | 0 | -103 | 7709.88 | -6.3995
| 40098.1065 | 60.017 | 3787.2593 |  |  |  | -13.5986 | -7.9038 |  | 0 | 3771.413 | 3765.4575 | 3778.442 | 3778.5625 | 3728.2928 | 633 | [6 empty] | 0 | 633 | -2531.8455 | [13 empty] | 40098.1065 | 60.017 | 3787.2593 | 350 | -257.4212 | 0 | 106.5 | 10 | 0 | -103 | 7710.87 | -13.5986
| 40098.1065 | 60.017 | 3787.2593 |  |  |  | -13.5986 | -9.897 |  | 0 | 3769.4198 | 3765.5786 | 3778.3918 | 3778.5625 | 3728.5736 | 633 | [6 empty] | 0 | 633 | -2531.8455 | [13 empty] | 40098.1065 | 60.017 | 3787.2593 | 350 | -257.4212 | 0 | 106.5 | 10 | 0 | -103 | 7710.87 | -13.5986
| 40098.1065 | 60.017 | 3787.2593 |  |  |  | -13.5986 | -11.1926 |  | 0 | 3768.1242 | 3765.6984 | 3778.3351 | 3778.5625 | 3728.8514 | 633 | [6 empty] | 0 | 633 | -2531.8455 | [13 empty] | 40098.1065 | 60.017 | 3787.2593 | 350 | -257.4212 | 0 | 106.5 | 10 | 0 | -103 | 7710.87 | -13.5986
| 40098.1066 | 60.017 | 3788.0303 |  |  |  | -13.5986 | -12.0347 |  | 0 | 3767.2821 | 3765.8211 | 3778.2744 | 3778.5625 | 3729.126 | 633 | [6 empty] | 0 | 633 | -2531.8455 | [13 empty] | 40098.1066 | 60.017 | 3788.0303 | 350 | -257.4212 | 0 | 107 | 10 | 0 | -103 | 7711.86 | -13.5986
| 40098.1066 | 60.017 | 3788.0303 |  |  |  | -13.5986 | -12.5821 |  | 0 | 3766.7347 | 3765.9424 | 3778.2113 | 3778.5625 | 3729.3976 | 633 | [6 empty] | 0 | 633 | -2531.8455 | [13 empty] | 40098.1066 | 60.017 | 3788.0303 | 350 | -257.4212 | 0 | 107 | 10 | 0 | -103 | 7711.86 | -13.5986
| 40098.1066 | 60.017 | 3788.0303 |  |  |  | -13.5986 | -12.9379 |  | 0 | 3766.3789 | 3766.0625 | 3778.147 | 3778.5625 | 3729.6663 | 633 | [6 empty] | 0 | 633 | -2531.8455 | [13 empty] | 40098.1066 | 60.017 | 3788.0303 | 350 | -257.4212 | 0 | 107 | 10 | 0 | -103 | 7711.86 | -13.5986
| 40098.1066 | 60.023 | 3787.5366 |  |  |  | -18.399 | -14.8493 |  | 0 | 3764.4675 | 3766.1786 | 3778.0731 | 3778.5625 | 3729.932 | 633 | [6 empty] | 0 | 633 | -3331.4024 | [13 empty] | 40098.1066 | 60.023 | 3787.5366 | 350 | -257.4212 | 0 | 107.5 | 10 | 0 | -103 | 7712.85 | -18.399
| 40098.1066 | 60.023 | 3787.5366 |  |  |  | -18.399 | -16.0917 |  | 0 | 3763.2251 | 3766.2934 | 3777.9932 | 3778.5625 | 3730.1949 | 633 | [6 empty] | 0 | 633 | -3331.4024 | [13 empty] | 40098.1066 | 60.023 | 3787.5366 | 350 | -257.4212 | 0 | 107.5 | 10 | 0 | -103 | 7712.85 | -18.399
| 40098.1067 | 60.023 | 3787.5366 |  |  |  | -18.399 | -16.8993 |  | 0 | 3762.4175 | 3766.407 | 3777.9099 | 3778.5625 | 3730.4549 | 633 | [6 empty] | 0 | 633 | -3331.4024 | [13 empty] | 40098.1067 | 60.023 | 3787.5366 | 350 | -257.4212 | 0 | 107.5 | 10 | 0 | -103 | 7712.85 | -18.399
| 40098.1067 | 60.021 | 3787.9304 |  |  |  | -16.7999 | -16.8645 |  | 0 | 3762.4523 | 3766.5215 | 3777.8277 | 3778.5625 | 3730.7122 | 633 | [6 empty] | 0 | 633 | -3014.2989 | [13 empty] | 40098.1067 | 60.021 | 3787.9304 | 350 | -257.4212 | 0 | 108 | 10 | 0 | -103 | 7713.84 | -16.7999
| 40098.1067 | 60.021 | 3787.9304 |  |  |  | -16.7999 | -16.8419 |  | 0 | 3762.4749 | 3766.6348 | 3777.7465 | 3778.5625 | 3730.9667 | 633 | [6 empty] | 0 | 633 | -3014.2989 | [13 empty] | 40098.1067 | 60.021 | 3787.9304 | 350 | -257.4212 | 0 | 108 | 10 | 0 | -103 | 7713.84 | -16.7999
| 40098.1067 | 60.021 | 3787.9304 |  |  |  | -16.7999 | -16.8272 |  | 0 | 3762.4896 | 3766.7468 | 3777.6662 | 3778.5625 | 3731.2186 | 633 | [6 empty] | 0 | 633 | -3014.2989 | [13 empty] | 40098.1067 | 60.021 | 3787.9304 | 350 | -257.4212 | 0 | 108 | 10 | 0 | -103 | 7713.84 | -16.7999
| 40098.1068 | 60.024 | 3786.5498 |  |  |  | -19.1986 | -17.6572 |  | 0 | 3761.6596 | 3766.8505 | 3777.5824 | 3778.5625 | 3731.4677 | 633 | [6 empty] | 0 | 633 | -3516.3626 | [13 empty] | 40098.1068 | 60.024 | 3786.5498 | 350 | -257.4212 | 0 | 108.5 | 10 | 0 | -103 | 7714.83 | -19.1986
| 40098.1068 | 60.024 | 3786.5498 |  |  |  | -19.1986 | -18.1967 |  | 0 | 3761.1201 | 3766.9531 | 3777.4966 | 3778.5625 | 3731.7143 | 633 | [6 empty] | 0 | 633 | -3516.3626 | [13 empty] | 40098.1068 | 60.024 | 3786.5498 | 350 | -257.4212 | 0 | 108.5 | 10 | 0 | -103 | 7714.83 | -19.1986
| 40098.1068 | 60.024 | 3786.5498 |  |  |  | -19.1986 | -18.5474 |  | 0 | 3760.7694 | 3767.0547 | 3777.41 | 3778.5625 | 3731.9583 | 633 | [6 empty] | 0 | 633 | -3516.3626 | [13 empty] | 40098.1068 | 60.024 | 3786.5498 | 350 | -257.4212 | 0 | 108.5 | 10 | 0 | -103 | 7714.83 | -19.1986
| 40098.1068 | 60.025 | 3785.614 |  |  |  | -20.0012 | -19.0562 |  | 0 | 3760.2605 | 3767.1503 | 3777.3216 | 3778.5625 | 3732.1998 | 633 | [6 empty] | 0 | 633 | -3723.9038 | [13 empty] | 40098.1068 | 60.025 | 3785.614 | 350 | -261.7382 | 0 | 109 | 10 | 0 | -103 | 7715.82 | -20.0012
| 40098.1069 | 60.025 | 3785.614 |  |  |  | -20.0012 | -19.387 |  | 0 | 3759.9298 | 3767.245 | 3777.2324 | 3778.5625 | 3732.4388 | 633 | [6 empty] | 0 | 633 | -3723.9038 | [13 empty] | 40098.1069 | 60.025 | 3785.614 | 350 | -261.7382 | 0 | 109 | 10 | 0 | -103 | 7715.82 | -20.0012
| 40098.1069 | 60.025 | 3785.614 |  |  |  | -20.0012 | -19.602 |  | 0 | 3759.7148 | 3767.3387 | 3777.143 | 3778.5625 | 3732.6753 | 633 | [6 empty] | 0 | 633 | -3723.9038 | [13 empty] | 40098.1069 | 60.025 | 3785.614 | 350 | -261.7382 | 0 | 109 | 10 | 0 | -103 | 7715.82 | -20.0012
| 40098.1069 | 60.02 | 3786.8643 |  |  |  | -16.0004 | -18.3414 |  | 0 | 3760.9754 | 3767.4378 | 3777.0609 | 3778.5625 | 3732.9094 | 633 | [6 empty] | 0 | 633 | -2877.3565 | [13 empty] | 40098.1069 | 60.02 | 3786.8643 | 350 | -261.7382 | 0 | 109.5 | 10 | 0 | -103 | 7716.81 | -16.0004
| 40098.1069 | 60.02 | 3786.8643 |  |  |  | -16.0004 | -17.522 |  | 0 | 3761.7947 | 3767.536 | 3776.9838 | 3778.5625 | 3733.1411 | 633 | [6 empty] | 0 | 633 | -2877.3565 | [13 empty] | 40098.1069 | 60.02 | 3786.8643 | 350 | -261.7382 | 0 | 109.5 | 10 | 0 | -103 | 7716.81 | -16.0004
| 40098.1069 | 60.02 | 3786.8643 |  |  |  | -16.0004 | -16.9895 |  | 0 | 3762.3273 | 3767.6331 | 3776.9102 | 3778.5625 | 3733.3705 | 633 | [6 empty] | 0 | 633 | -2877.3565 | [13 empty] | 40098.1069 | 60.02 | 3786.8643 | 350 | -261.7382 | 0 | 109.5 | 10 | 0 | -103 | 7716.81 | -16.0004
| 40098.107 | 60.022 | 3785.7261 |  |  |  | -17.5995 | -17.203 |  | 0 | 3762.1138 | 3767.7235 | 3776.8362 | 3778.5625 | 3733.5976 | 633 | [6 empty] | 0 | 633 | -3164.9276 | [13 empty] | 40098.107 | 60.022 | 3785.7261 | 350 | -261.7382 | 0 | 110 | 10 | 0 | -103 | 7717.8 | -17.5995
| 40098.107 | 60.022 | 3785.7261 |  |  |  | -17.5995 | -17.3417 |  | 0 | 3761.975 | 3767.8131 | 3776.7623 | 3778.5625 | 3733.8225 | 633 | [6 empty] | 0 | 633 | -3164.9276 | [13 empty] | 40098.107 | 60.022 | 3785.7261 | 350 | -261.7382 | 0 | 110 | 10 | 0 | -103 | 7717.8 | -17.5995
| 40098.107 | 60.022 | 3785.7261 |  |  |  | -17.5995 | -17.432 |  | 0 | 3761.8848 | 3767.9018 | 3776.6886 | 3778.5625 | 3734.0451 | 633 | [6 empty] | 0 | 633 | -3164.9276 | [13 empty] | 40098.107 | 60.022 | 3785.7261 | 350 | -261.7382 | 0 | 110 | 10 | 0 | -103 | 7717.8 | -17.5995
| 40098.107 | 60.023 | 3785.7983 |  |  |  | -18.399 | -17.7704 |  | 0 | 3761.5463 | 3767.99 | 3776.614 | 3778.5625 | 3734.2654 | 633 | [6 empty] | 0 | 633 | -3331.4024 | [13 empty] | 40098.107 | 60.023 | 3785.7983 | 350 | -261.7382 | 0 | 110.5 | 10 | 0 | -103 | 7718.79 | -18.399
| 40098.1071 | 60.023 | 3785.7983 |  |  |  | -18.399 | -17.9905 |  | 0 | 3761.3263 | 3768.0772 | 3776.5391 | 3778.5625 | 3734.4836 | 633 | [6 empty] | 0 | 633 | -3331.4024 | [13 empty] | 40098.1071 | 60.023 | 3785.7983 | 350 | -261.7382 | 0 | 110.5 | 10 | 0 | -103 | 7718.79 | -18.399
| 40098.1071 | 60.023 | 3785.7983 |  |  |  | -18.399 | -18.1335 |  | 0 | 3761.1833 | 3768.1637 | 3776.4642 | 3778.5625 | 3734.6997 | 633 | [6 empty] | 0 | 633 | -3331.4024 | [13 empty] | 40098.1071 | 60.023 | 3785.7983 | 350 | -261.7382 | 0 | 110.5 | 10 | 0 | -103 | 7718.79 | -18.399
| 40098.1071 | 60.019 | 3787.6274 |  |  |  | -15.2008 | -17.107 |  | 0 | 3762.2097 | 3768.2582 | 3776.395 | 3778.5625 | 3734.9137 | 633 | [6 empty] | 0 | 633 | -2752.3163 | [13 empty] | 40098.1071 | 60.019 | 3787.6274 | 350 | -261.7382 | 0 | 111 | 10 | 0 | -103 | 7719.78 | -15.2008
| 40098.1071 | 60.019 | 3787.6274 |  |  |  | -15.2008 | -16.4399 |  | 0 | 3762.8769 | 3768.3517 | 3776.3297 | 3778.5625 | 3735.1256 | 633 | [6 empty] | 0 | 633 | -2752.3163 | [13 empty] | 40098.1071 | 60.019 | 3787.6274 | 350 | -261.7382 | 0 | 111 | 10 | 0 | -103 | 7719.78 | -15.2008
| 40098.1072 | 60.019 | 3787.6274 |  |  |  | -15.2008 | -16.0062 |  | 0 | 3763.3106 | 3768.4444 | 3776.2671 | 3778.5625 | 3735.3354 | 633 | [6 empty] | 0 | 633 | -2752.3163 | [13 empty] | 40098.1072 | 60.019 | 3787.6274 | 350 | -261.7382 | 0 | 111 | 10 | 0 | -103 | 7719.78 | -15.2008
| 40098.1072 | 60.018 | 3789.4043 |  |  |  | -14.4012 | -15.4445 |  | 0 | 3763.8723 | 3768.5447 | 3776.2078 | 3778.5625 | 3735.5432 | 633 | [6 empty] | 0 | 633 | -2637.6912 | [13 empty] | 40098.1072 | 60.018 | 3789.4043 | 350 | -271.876 | 0 | 111.5 | 10 | 0 | -103 | 7720.77 | -14.4012
| 40098.1072 | 60.018 | 3789.4043 |  |  |  | -14.4012 | -15.0793 |  | 0 | 3764.2374 | 3768.644 | 3776.1508 | 3778.5625 | 3735.7491 | 633 | [6 empty] | 0 | 633 | -2637.6912 | [13 empty] | 40098.1072 | 60.018 | 3789.4043 | 350 | -271.876 | 0 | 111.5 | 10 | 0 | -103 | 7720.77 | -14.4012
| 40098.1072 | 60.018 | 3789.4043 |  |  |  | -14.4012 | -14.842 |  | 0 | 3764.4748 | 3768.7424 | 3776.0954 | 3778.5625 | 3735.9529 | 633 | [6 empty] | 0 | 633 | -2637.6912 | [13 empty] | 40098.1072 | 60.018 | 3789.4043 | 350 | -271.876 | 0 | 111.5 | 10 | 0 | -103 | 7720.77 | -14.4012
| 40098.1072 | 60.019 | 3789.3689 |  |  |  | -15.2008 | -14.9676 |  | 0 | 3764.3492 | 3768.8397 | 3776.04 | 3778.5625 | 3736.1549 | 633 | [6 empty] | 0 | 633 | -2752.3163 | [13 empty] | 40098.1072 | 60.019 | 3789.3689 | 350 | -271.876 | 0 | 112 | 10 | 0 | -103 | 7721.76 | -15.2008
| 40098.1073 | 60.019 | 3789.3689 |  |  |  | -15.2008 | -15.0492 |  | 0 | 3764.2676 | 3768.9361 | 3775.9848 | 3778.5625 | 3736.3549 | 633 | [6 empty] | 0 | 633 | -2752.3163 | [13 empty] | 40098.1073 | 60.019 | 3789.3689 | 350 | -271.876 | 0 | 112 | 10 | 0 | -103 | 7721.76 | -15.2008
| 40098.1073 | 60.019 | 3789.3689 |  |  |  | -15.2008 | -15.1023 |  | 0 | 3764.2145 | 3769.0316 | 3775.9298 | 3778.5625 | 3736.5531 | 633 | [6 empty] | 0 | 633 | -2752.3163 | [13 empty] | 40098.1073 | 60.019 | 3789.3689 | 350 | -271.876 | 0 | 112 | 10 | 0 | -103 | 7721.76 | -15.2008
| 40098.1073 | 60.016 | 3788.9329 |  |  |  | -12.7991 | -14.2962 |  | 0 | 3765.0206 | 3769.1241 | 3775.879 | 3778.5625 | 3736.7494 | 633 | [6 empty] | 0 | 633 | -2434.5239 | [13 empty] | 40098.1073 | 60.016 | 3788.9329 | 350 | -271.876 | 0 | 112.5 | 10 | 0 | -103 | 7722.75 | -12.7991
| 40098.1073 | 60.016 | 3788.9329 |  |  |  | -12.7991 | -13.7722 |  | 0 | 3765.5446 | 3769.2159 | 3775.8312 | 3778.5625 | 3736.9439 | 633 | [6 empty] | 0 | 633 | -2434.5239 | [13 empty] | 40098.1073 | 60.016 | 3788.9329 | 350 | -271.876 | 0 | 112.5 | 10 | 0 | -103 | 7722.75 | -12.7991
| 40098.1074 | 60.016 | 3788.9329 |  |  |  | -12.7991 | -13.4316 |  | 0 | 3765.8852 | 3769.3067 | 3775.7853 | 3778.5625 | 3737.1365 | 633 | [6 empty] | 0 | 633 | -2434.5239 | [13 empty] | 40098.1074 | 60.016 | 3788.9329 | 350 | -271.876 | 0 | 112.5 | 10 | 0 | -103 | 7722.75 | -12.7991
| 40098.1074 | 60.012 | 3790.4111 |  |  |  | -9.6008 | -12.0908 |  | 0 | 3767.2259 | 3769.4035 | 3775.7461 | 3778.5625 | 3737.3274 | 633 | [6 empty] | 0 | 633 | -2110.0859 | [13 empty] | 40098.1074 | 60.012 | 3790.4111 | 350 | -271.876 | 0 | 113 | 10 | 0 | -103 | 7723.74 | -9.6008
| 40098.1074 | 60.012 | 3790.4111 |  |  |  | -9.6008 | -11.2193 |  | 0 | 3768.0974 | 3769.4995 | 3775.7112 | 3778.5625 | 3737.5166 | 633 | [6 empty] | 0 | 633 | -2110.0859 | [13 empty] | 40098.1074 | 60.012 | 3790.4111 | 350 | -271.876 | 0 | 113 | 10 | 0 | -103 | 7723.74 | -9.6008
| 40098.1074 | 60.012 | 3790.4111 |  |  |  | -9.6008 | -10.6529 |  | 0 | 3768.6639 | 3769.5945 | 3775.6791 | 3778.5625 | 3737.704 | 633 | [6 empty] | 0 | 633 | -2110.0859 | [13 empty] | 40098.1074 | 60.012 | 3790.4111 | 350 | -271.876 | 0 | 113 | 10 | 0 | -103 | 7723.74 | -9.6008
| 40098.1075 | 60.007 | 3792.9453 |  |  |  | -5.6 | -8.8843 |  | 0 | 3770.4324 | 3769.7002 | 3775.6554 | 3778.5625 | 3737.8897 | 633 | [6 empty] | 0 | 633 | -1808.5793 | [13 empty] | 40098.1075 | 60.007 | 3792.9453 | 350 | -271.876 | 0 | 113.5 | 10 | 0 | -103 | 7724.73 | -5.6
| 40098.1075 | 60.007 | 3792.9453 |  |  |  | -5.6 | -7.7348 |  | 0 | 3771.5819 | 3769.8049 | 3775.637 | 3778.5625 | 3738.0738 | 633 | [6 empty] | 0 | 633 | -1808.5793 | [13 empty] | 40098.1075 | 60.007 | 3792.9453 | 350 | -271.876 | 0 | 113.5 | 10 | 0 | -103 | 7724.73 | -5.6
| 40098.1075 | 60.007 | 3792.9453 |  |  |  | -5.6 | -6.9876 |  | 0 | 3772.3291 | 3769.9086 | 3775.6222 | 3778.5625 | 3738.2562 | 633 | [6 empty] | 0 | 633 | -1808.5793 | [13 empty] | 40098.1075 | 60.007 | 3792.9453 | 350 | -271.876 | 0 | 113.5 | 10 | 0 | -103 | 7724.73 | -5.6
| 40098.1075 | 60.009 | 3791.426 |  |  |  | -7.1991 | -7.0616 |  | 0 | 3772.2551 | 3770.0047 | 3775.6072 | 3778.5625 | 3738.4369 | 633 | [6 empty] | 0 | 633 | -1918.1268 | [13 empty] | 40098.1075 | 60.009 | 3791.426 | 350 | -262.0735 | 0 | 114 | 10 | 0 | -103 | 7725.72 | -7.1991
| 40098.1075 | 60.009 | 3791.426 |  |  |  | -7.1991 | -7.1097 |  | 0 | 3772.207 | 3770.0999 | 3775.5921 | 3778.5625 | 3738.616 | 633 | [6 empty] | 0 | 633 | -1918.1268 | [13 empty] | 40098.1075 | 60.009 | 3791.426 | 350 | -262.0735 | 0 | 114 | 10 | 0 | -103 | 7725.72 | -7.1991
| 40098.1076 | 60.009 | 3791.426 |  |  |  | -7.1991 | -7.141 |  | 0 | 3772.1757 | 3770.1943 | 3775.5769 | 3778.5625 | 3738.7936 | 633 | [6 empty] | 0 | 633 | -1918.1268 | [13 empty] | 40098.1076 | 60.009 | 3791.426 | 350 | -262.0735 | 0 | 114 | 10 | 0 | -103 | 7725.72 | -7.1991
| 40098.1076 | 59.999 | 3790.2163 |  |  |  | 0.79956 | -4.3618 |  | 0 | 3774.9549 | 3770.2825 | 3775.5742 | 3778.5625 | 3738.9696 | 633 | [6 empty] | 0 | 633 | -1472.1181 | [13 empty] | 40098.1076 | 59.999 | 3790.2163 | 350 | -262.0735 | 0 | 114.5 | 10 | 0 | -103 | 7726.71 | 0.79956
| 40098.1076 | 59.999 | 3790.2163 |  |  |  | 0.79956 | -2.5553 |  | 0 | 3776.7614 | 3770.3699 | 3775.5794 | 3778.5625 | 3739.144 | 633 | [6 empty] | 0 | 633 | -1472.1181 | [13 empty] | 40098.1076 | 59.999 | 3790.2163 | 350 | -262.0735 | 0 | 114.5 | 10 | 0 | -103 | 7726.71 | 0.79956
| 40098.1076 | 59.999 | 3790.2163 |  |  |  | 0.79956 | -1.3811 |  | 0 | 3777.9356 | 3770.4566 | 3775.5897 | 3778.5625 | 3739.3169 | 633 | [6 empty] | 0 | 633 | -1472.1181 | [13 empty] | 40098.1076 | 59.999 | 3790.2163 | 350 | -262.0735 | 0 | 114.5 | 10 | 0 | -103 | 7726.71 | 0.79956
| 40098.1077 | 59.991 | 3788.105 |  |  |  | 7.1991 | 1.622 |  | 0 | 3780.9387 | 3770.5333 | 3775.613 | 3778.5625 | 3739.4882 | 633 | [6 empty] | 0 | 633 | -1241.2084 | [13 empty] | 40098.1077 | 59.991 | 3788.105 | 350 | -262.0735 | 0 | 115 | 10 | 0 | -103 | 7727.7 | 7.1991
| 40098.1077 | 59.991 | 3788.105 |  |  |  | 7.1991 | 3.574 |  | 0 | 3782.8907 | 3770.6094 | 3775.6445 | 3778.5625 | 3739.6581 | 633 | [6 empty] | 0 | 633 | -1241.2084 | [13 empty] | 40098.1077 | 59.991 | 3788.105 | 350 | -262.0735 | 0 | 115 | 10 | 0 | -103 | 7727.7 | 7.1991
| 40098.1077 | 59.991 | 3788.105 |  |  |  | 7.1991 | 4.8428 |  | 0 | 3784.1595 | 3770.6848 | 3775.6812 | 3778.5625 | 3739.8265 | 633 | [6 empty] | 0 | 633 | -1241.2084 | [13 empty] | 40098.1077 | 59.991 | 3788.105 | 350 | -262.0735 | 0 | 115 | 10 | 0 | -103 | 7727.7 | 7.1991
| 40098.1077 | 59.988 | 3788.4973 |  |  |  | 9.6008 | 6.5081 |  | 0 | 3785.8248 | 3770.7612 | 3775.7247 | 3778.5625 | 3739.9935 | 633 | [6 empty] | 0 | 633 | -1172.2037 | [13 empty] | 40098.1077 | 59.988 | 3788.4973 | 350 | -262.0735 | 0 | 115.5 | 10 | 0 | -103 | 7728.69 | 9.6008
| 40098.1078 | 59.988 | 3788.4973 |  |  |  | 9.6008 | 7.5905 |  | 0 | 3786.9073 | 3770.837 | 3775.7725 | 3778.5625 | 3740.159 | 633 | [6 empty] | 0 | 633 | -1172.2037 | [13 empty] | 40098.1078 | 59.988 | 3788.4973 | 350 | -262.0735 | 0 | 115.5 | 10 | 0 | -103 | 7728.69 | 9.6008
| 40098.1078 | 59.988 | 3788.4973 |  |  |  | 9.6008 | 8.2941 |  | 0 | 3787.6109 | 3770.9122 | 3775.8229 | 3778.5625 | 3740.3232 | 633 | [6 empty] | 0 | 633 | -1172.2037 | [13 empty] | 40098.1078 | 59.988 | 3788.4973 | 350 | -262.0735 | 0 | 115.5 | 10 | 0 | -103 | 7728.69 | 9.6008
| 40098.1078 | 59.984 | 3788.1011 |  |  |  | 12.7991 | 9.8709 |  | 0 | 3789.1876 | 3770.985 | 3775.8795 | 3778.5625 | 3740.4859 | 633 | [6 empty] | 0 | 633 | -1091.4046 | [13 empty] | 40098.1078 | 59.984 | 3788.1011 | 350 | -262.0735 | 0 | 116 | 10 | 0 | -103 | 7729.68 | 12.7991
| 40098.1078 | 59.984 | 3788.1011 |  |  |  | 12.7991 | 10.8957 |  | 0 | 3790.2125 | 3771.0572 | 3775.94 | 3778.5625 | 3740.6472 | 633 | [6 empty] | 0 | 633 | -1091.4046 | [13 empty] | 40098.1078 | 59.984 | 3788.1011 | 350 | -262.0735 | 0 | 116 | 10 | 0 | -103 | 7729.68 | 12.7991
| 40098.1078 | 59.984 | 3788.1011 |  |  |  | 12.7991 | 11.5619 |  | 0 | 3790.8787 | 3771.1288 | 3776.0027 | 3778.5625 | 3740.8072 | 633 | [6 empty] | 0 | 633 | -1091.4046 | [13 empty] | 40098.1078 | 59.984 | 3788.1011 | 350 | -262.0735 | 0 | 116 | 10 | 0 | -103 | 7729.68 | 12.7991
| 40098.1079 | 59.982 | 3787.7324 |  |  |  | 14.4012 | 12.5557 |  | 0 | 3791.8724 | 3771.1983 | 3776.0691 | 3778.5625 | 3740.9658 | 633 | [6 empty] | 0 | 633 | -1054.9759 | [13 empty] | 40098.1079 | 59.982 | 3787.7324 | 350 | -260.3644 | 0 | 116.5 | 10 | 0 | -103 | 7730.67 | 14.4012
| 40098.1079 | 59.982 | 3787.7324 |  |  |  | 14.4012 | 13.2016 |  | 0 | 3792.5184 | 3771.2672 | 3776.1377 | 3778.5625 | 3741.1231 | 633 | [6 empty] | 0 | 633 | -1054.9759 | [13 empty] | 40098.1079 | 59.982 | 3787.7324 | 350 | -260.3644 | 0 | 116.5 | 10 | 0 | -103 | 7730.67 | 14.4012
| 40098.1079 | 59.982 | 3787.7324 |  |  |  | 14.4012 | 13.6215 |  | 0 | 3792.9383 | 3771.3355 | 3776.2074 | 3778.5625 | 3741.2791 | 633 | [6 empty] | 0 | 633 | -1054.9759 | [13 empty] | 40098.1079 | 59.982 | 3787.7324 | 350 | -260.3644 | 0 | 116.5 | 10 | 0 | -103 | 7730.67 | 14.4012
| 40098.1079 | 59.979 | 3788.2563 |  |  |  | 16.7999 | 14.7339 |  | 0 | 3794.0507 | 3771.4054 | 3776.2811 | 3778.5625 | 3741.4338 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.1079 | 59.979 | 3788.2563 | 350 | -260.3644 | 0 | 117 | 10 | 0 | -103 | 7731.66 | 16.7999
| 40098.108 | 59.979 | 3788.2563 |  |  |  | 16.7999 | 15.457 |  | 0 | 3794.7738 | 3771.4748 | 3776.3572 | 3778.5625 | 3741.5873 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.108 | 59.979 | 3788.2563 | 350 | -260.3644 | 0 | 117 | 10 | 0 | -103 | 7731.66 | 16.7999
| 40098.108 | 59.979 | 3788.2563 |  |  |  | 16.7999 | 15.927 |  | 0 | 3795.2438 | 3771.5436 | 3776.4346 | 3778.5625 | 3741.7394 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.108 | 59.979 | 3788.2563 | 350 | -260.3644 | 0 | 117 | 10 | 0 | -103 | 7731.66 | 16.7999
| 40098.108 | 59.976 | 3790.6646 |  |  |  | 19.1986 | 17.0721 |  | 0 | 3796.3889 | 3771.6216 | 3776.5161 | 3778.5625 | 3741.8903 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.108 | 59.976 | 3790.6646 | 350 | -260.3644 | 0 | 117.5 | 10 | 0 | -103 | 7732.65 | 19.1986
| 40098.108 | 59.976 | 3790.6646 |  |  |  | 19.1986 | 17.8164 |  | 0 | 3797.1331 | 3771.699 | 3776.5999 | 3778.5625 | 3742.04 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.108 | 59.976 | 3790.6646 | 350 | -260.3644 | 0 | 117.5 | 10 | 0 | -103 | 7732.65 | 19.1986
| 40098.1081 | 59.976 | 3790.6646 |  |  |  | 19.1986 | 18.3002 |  | 0 | 3797.6169 | 3771.7758 | 3776.685 | 3778.5625 | 3742.1885 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1081 | 59.976 | 3790.6646 | 350 | -260.3644 | 0 | 117.5 | 10 | 0 | -103 | 7732.65 | 19.1986
| 40098.1081 | 59.978 | 3789.2671 |  |  |  | 17.5995 | 18.0549 |  | 0 | 3797.3717 | 3771.8463 | 3776.7684 | 3778.5625 | 3742.3358 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1081 | 59.978 | 3789.2671 | 350 | -260.3644 | 0 | 118 | 10 | 0 | -103 | 7733.64 | 17.5995
| 40098.1081 | 59.978 | 3789.2671 |  |  |  | 17.5995 | 17.8955 |  | 0 | 3797.2123 | 3771.9163 | 3776.8505 | 3778.5625 | 3742.4818 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1081 | 59.978 | 3789.2671 | 350 | -260.3644 | 0 | 118 | 10 | 0 | -103 | 7733.64 | 17.5995
| 40098.1081 | 59.978 | 3789.2671 |  |  |  | 17.5995 | 17.7919 |  | 0 | 3797.1087 | 3771.9857 | 3776.9315 | 3778.5625 | 3742.6267 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1081 | 59.978 | 3789.2671 | 350 | -260.3644 | 0 | 118 | 10 | 0 | -103 | 7733.64 | 17.5995
| 40098.1081 | 59.976 | 3789.9143 |  |  |  | 19.1986 | 18.2843 |  | 0 | 3797.601 | 3772.0571 | 3777.0139 | 3778.5625 | 3742.7705 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1081 | 59.976 | 3789.9143 | 350 | -260.3644 | 0 | 118.5 | 10 | 0 | -103 | 7734.63 | 19.1986
| 40098.1082 | 59.976 | 3789.9143 |  |  |  | 19.1986 | 18.6043 |  | 0 | 3797.921 | 3772.128 | 3777.0968 | 3778.5625 | 3742.9131 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1082 | 59.976 | 3789.9143 | 350 | -260.3644 | 0 | 118.5 | 10 | 0 | -103 | 7734.63 | 19.1986
| 40098.1082 | 59.976 | 3789.9143 |  |  |  | 19.1986 | 18.8123 |  | 0 | 3798.1291 | 3772.1983 | 3777.18 | 3778.5625 | 3743.0545 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1082 | 59.976 | 3789.9143 | 350 | -260.3644 | 0 | 118.5 | 10 | 0 | -103 | 7734.63 | 19.1986
| 40098.1082 | 59.975 | 3788.9629 |  |  |  | 20.0012 | 19.2284 |  | 0 | 3798.5452 | 3772.2643 | 3777.2641 | 3778.5625 | 3743.1949 | 633 | [6 empty] | 0 | 633 | -944.7572 | [13 empty] | 40098.1082 | 59.975 | 3788.9629 | 350 | -352.6444 | 0 | 119 | 10 | 0 | -103 | 7735.62 | 20.0012
| 40098.1082 | 59.975 | 3788.9629 |  |  |  | 20.0012 | 19.4989 |  | 0 | 3798.8157 | 3772.3298 | 3777.3486 | 3778.5625 | 3743.3341 | 633 | [6 empty] | 0 | 633 | -944.7572 | [13 empty] | 40098.1082 | 59.975 | 3788.9629 | 350 | -352.6444 | 0 | 119 | 10 | 0 | -103 | 7735.62 | 20.0012
| 40098.1083 | 59.975 | 3788.9629 |  |  |  | 20.0012 | 19.6747 |  | 0 | 3798.9915 | 3772.3948 | 3777.4331 | 3778.5625 | 3743.4723 | 633 | [6 empty] | 0 | 633 | -944.7572 | [13 empty] | 40098.1083 | 59.975 | 3788.9629 | 350 | -352.6444 | 0 | 119 | 10 | 0 | -103 | 7735.62 | 20.0012
| 40098.1083 | 59.97 | 3792.9106 |  |  |  | 23.999 | 21.1882 |  | 0 | 3800.505 | 3772.4746 | 3777.5229 | 3778.5625 | 3743.6093 | 633 | [6 empty] | 0 | 633 | -879.1838 | [13 empty] | 40098.1083 | 59.97 | 3792.9106 | 350 | -352.6444 | 0 | 119.5 | 10 | 0 | -103 | 7736.61 | 23.999
| 40098.1083 | 59.97 | 3792.9106 |  |  |  | 23.999 | 22.172 |  | 0 | 3801.4888 | 3772.5538 | 3777.6158 | 3778.5625 | 3743.7454 | 633 | [6 empty] | 0 | 633 | -879.1838 | [13 empty] | 40098.1083 | 59.97 | 3792.9106 | 350 | -352.6444 | 0 | 119.5 | 10 | 0 | -103 | 7736.61 | 23.999
| 40098.1083 | 59.97 | 3792.9106 |  |  |  | 23.999 | 22.8115 |  | 0 | 3802.1282 | 3772.6324 | 3777.7105 | 3778.5625 | 3743.8803 | 633 | [6 empty] | 0 | 633 | -879.1838 | [13 empty] | 40098.1083 | 59.97 | 3792.9106 | 350 | -352.6444 | 0 | 119.5 | 10 | 0 | -103 | 7736.61 | 23.999
| 40098.1084 | 59.978 | 3788.0796 |  |  |  | 17.5995 | 20.9873 |  | 0 | 3800.304 | 3772.6918 | 3777.7973 | 3778.5625 | 3744.0142 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1084 | 59.978 | 3788.0796 | 350 | -352.6444 | 0 | 120 | 10 | 0 | -103 | 7737.6 | 17.5995
| 40098.1084 | 59.978 | 3788.0796 |  |  |  | 17.5995 | 19.8015 |  | 0 | 3799.1183 | 3772.7508 | 3777.879 | 3778.5625 | 3744.1471 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1084 | 59.978 | 3788.0796 | 350 | -352.6444 | 0 | 120 | 10 | 0 | -103 | 7737.6 | 17.5995
| 40098.1084 | 59.978 | 3788.0796 |  |  |  | 17.5995 | 19.0308 |  | 0 | 3798.3476 | 3772.8093 | 3777.9572 | 3778.5625 | 3744.2789 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1084 | 59.978 | 3788.0796 | 350 | -352.6444 | 0 | 120 | 10 | 0 | -103 | 7737.6 | 17.5995
| 40098.1084 | 59.975 | 3787.1643 |  |  |  | 20.0012 | 19.3705 |  | 0 | 3798.6872 | 3772.8638 | 3778.036 | 3778.5625 | 3744.4098 | 633 | [6 empty] | 0 | 633 | -944.7572 | [13 empty] | 40098.1084 | 59.975 | 3787.1643 | 350 | -352.6444 | 0 | 120.5 | 10 | 0 | -103 | 7738.59 | 20.0012
| 40098.1084 | 59.975 | 3787.1643 |  |  |  | 20.0012 | 19.5912 |  | 0 | 3798.908 | 3772.918 | 3778.115 | 3778.5625 | 3744.5397 | 633 | [6 empty] | 0 | 633 | -944.7572 | [13 empty] | 40098.1084 | 59.975 | 3787.1643 | 350 | -352.6444 | 0 | 120.5 | 10 | 0 | -103 | 7738.59 | 20.0012
| 40098.1085 | 59.975 | 3787.1643 |  |  |  | 20.0012 | 19.7347 |  | 0 | 3799.0515 | 3772.9718 | 3778.194 | 3778.5625 | 3744.6685 | 633 | [6 empty] | 0 | 633 | -944.7572 | [13 empty] | 40098.1085 | 59.975 | 3787.1643 | 350 | -352.6444 | 0 | 120.5 | 10 | 0 | -103 | 7738.59 | 20.0012
| 40098.1085 | 59.975 | 3786.4868 |  |  |  | 20.0012 | 19.828 |  | 0 | 3799.1448 | 3773.0226 | 3778.2728 | 3778.5625 | 3744.7964 | 633 | [6 empty] | 0 | 633 | -944.7572 | [13 empty] | 40098.1085 | 59.975 | 3786.4868 | 350 | -352.6444 | 0 | 121 | 10 | 0 | -103 | 7739.58 | 20.0012
| 40098.1085 | 59.975 | 3786.4868 |  |  |  | 20.0012 | 19.8886 |  | 0 | 3799.2054 | 3773.073 | 3778.3512 | 3778.5625 | 3744.9234 | 633 | [6 empty] | 0 | 633 | -944.7572 | [13 empty] | 40098.1085 | 59.975 | 3786.4868 | 350 | -352.6444 | 0 | 121 | 10 | 0 | -103 | 7739.58 | 20.0012
| 40098.1085 | 59.975 | 3786.4868 |  |  |  | 20.0012 | 19.928 |  | 0 | 3799.2448 | 3773.1231 | 3778.4292 | 3778.5625 | 3745.0494 | 633 | [6 empty] | 0 | 633 | -944.7572 | [13 empty] | 40098.1085 | 59.975 | 3786.4868 | 350 | -352.6444 | 0 | 121 | 10 | 0 | -103 | 7739.58 | 20.0012
| 40098.1086 | 59.966 | 3790.5117 |  |  |  | 27.2003 | 22.4733 |  | 0 | 3801.7901 | 3773.1877 | 3778.516 | 3778.5625 | 3745.1744 | 633 | [6 empty] | 0 | 633 | -832.8924 | [13 empty] | 40098.1086 | 59.966 | 3790.5117 | 350 | -354.8957 | 0 | 121.5 | 10 | 0 | -103 | 7740.57 | 27.2003
| 40098.1086 | 59.966 | 3790.5117 |  |  |  | 27.2003 | 24.1278 |  | 0 | 3803.4445 | 3773.2519 | 3778.6083 | 3778.5625 | 3745.2985 | 633 | [6 empty] | 0 | 633 | -832.8924 | [13 empty] | 40098.1086 | 59.966 | 3790.5117 | 350 | -354.8957 | 0 | 121.5 | 10 | 0 | -103 | 7740.57 | 27.2003
| 40098.1086 | 59.966 | 3790.5117 |  |  |  | 27.2003 | 25.2032 |  | 0 | 3804.5199 | 3773.3156 | 3778.704 | 3778.5625 | 3745.4217 | 633 | [6 empty] | 0 | 633 | -832.8924 | [13 empty] | 40098.1086 | 59.966 | 3790.5117 | 350 | -354.8957 | 0 | 121.5 | 10 | 0 | -103 | 7740.57 | 27.2003
| 40098.1086 | 59.969 | 3790.9595 |  |  |  | 24.7986 | 25.0616 |  | 0 | 3804.3783 | 3773.3804 | 3778.7983 | 3778.5625 | 3745.544 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.1086 | 59.969 | 3790.9595 | 350 | -354.8957 | 0 | 122 | 10 | 0 | -103 | 7741.56 | 24.7986
| 40098.1087 | 59.969 | 3790.9595 |  |  |  | 24.7986 | 24.9695 |  | 0 | 3804.2863 | 3773.4448 | 3778.8917 | 3778.5625 | 3745.6654 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.1087 | 59.969 | 3790.9595 | 350 | -354.8957 | 0 | 122 | 10 | 0 | -103 | 7741.56 | 24.7986
| 40098.1087 | 59.969 | 3790.9595 |  |  |  | 24.7986 | 24.9097 |  | 0 | 3804.2265 | 3773.5087 | 3778.9842 | 3778.5625 | 3745.7859 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.1087 | 59.969 | 3790.9595 | 350 | -354.8957 | 0 | 122 | 10 | 0 | -103 | 7741.56 | 24.7986
| 40098.1087 | 59.965 | 3789.1675 |  |  |  | 27.9999 | 25.9913 |  | 0 | 3805.308 | 3773.5657 | 3779.0799 | 3778.5625 | 3745.9055 | 633 | [6 empty] | 0 | 633 | -822.0815 | [13 empty] | 40098.1087 | 59.965 | 3789.1675 | 350 | -354.8957 | 0 | 122.5 | 10 | 0 | -103 | 7742.55 | 27.9999
| 40098.1087 | 59.965 | 3789.1675 |  |  |  | 27.9999 | 26.6943 |  | 0 | 3806.011 | 3773.6222 | 3779.1775 | 3778.5625 | 3746.0243 | 633 | [6 empty] | 0 | 633 | -822.0815 | [13 empty] | 40098.1087 | 59.965 | 3789.1675 | 350 | -354.8957 | 0 | 122.5 | 10 | 0 | -103 | 7742.55 | 27.9999
| 40098.1087 | 59.965 | 3789.1675 |  |  |  | 27.9999 | 27.1512 |  | 0 | 3806.468 | 3773.6783 | 3779.276 | 3778.5625 | 3746.1422 | 633 | [6 empty] | 0 | 633 | -822.0815 | [13 empty] | 40098.1087 | 59.965 | 3789.1675 | 350 | -354.8957 | 0 | 122.5 | 10 | 0 | -103 | 7742.55 | 27.9999
| 40098.1088 | 59.972 | 3784.8306 |  |  |  | 22.3999 | 25.4883 |  | 0 | 3804.805 | 3773.7184 | 3779.3678 | 3778.5625 | 3746.2592 | 633 | [6 empty] | 0 | 633 | -904.2897 | [13 empty] | 40098.1088 | 59.972 | 3784.8306 | 350 | -354.8957 | 0 | 123 | 10 | 0 | -103 | 7743.54 | 22.3999
| 40098.1088 | 59.972 | 3784.8306 |  |  |  | 22.3999 | 24.4073 |  | 0 | 3803.7241 | 3773.7583 | 3779.4551 | 3778.5625 | 3746.3754 | 633 | [6 empty] | 0 | 633 | -904.2897 | [13 empty] | 40098.1088 | 59.972 | 3784.8306 | 350 | -354.8957 | 0 | 123 | 10 | 0 | -103 | 7743.54 | 22.3999
| 40098.1088 | 59.972 | 3784.8306 |  |  |  | 22.3999 | 23.7047 |  | 0 | 3803.0215 | 3773.7978 | 3779.5393 | 3778.5625 | 3746.4908 | 633 | [6 empty] | 0 | 633 | -904.2897 | [13 empty] | 40098.1088 | 59.972 | 3784.8306 | 350 | -354.8957 | 0 | 123 | 10 | 0 | -103 | 7743.54 | 22.3999
| 40098.1088 | 59.969 | 3782.8086 |  |  |  | 24.7986 | 24.0876 |  | 0 | 3803.4043 | 3773.8299 | 3779.6242 | 3778.5625 | 3746.6053 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.1088 | 59.969 | 3782.8086 | 350 | -354.8957 | 0 | 123.5 | 10 | 0 | -103 | 7744.53 | 24.7986
| 40098.1089 | 59.969 | 3782.8086 |  |  |  | 24.7986 | 24.3364 |  | 0 | 3803.6532 | 3773.8617 | 3779.7094 | 3778.5625 | 3746.7191 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.1089 | 59.969 | 3782.8086 | 350 | -354.8957 | 0 | 123.5 | 10 | 0 | -103 | 7744.53 | 24.7986
| 40098.1089 | 59.969 | 3782.8086 |  |  |  | 24.7986 | 24.4982 |  | 0 | 3803.8149 | 3773.8933 | 3779.7946 | 3778.5625 | 3746.832 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.1089 | 59.969 | 3782.8086 | 350 | -354.8957 | 0 | 123.5 | 10 | 0 | -103 | 7744.53 | 24.7986
| 40098.1089 | 59.967 | 3779.0562 |  |  |  | 26.4008 | 25.1641 |  | 0 | 3804.4808 | 3773.9115 | 3779.8815 | 3778.5625 | 3746.9441 | 633 | [6 empty] | 0 | 633 | -843.9914 | [13 empty] | 40098.1089 | 59.967 | 3779.0562 | 350 | -340.4694 | 0 | 124 | 10 | 0 | -103 | 7745.52 | 26.4008
| 40098.1089 | 59.967 | 3779.0562 |  |  |  | 26.4008 | 25.5969 |  | 0 | 3804.9137 | 3773.9296 | 3779.9694 | 3778.5625 | 3747.0554 | 633 | [6 empty] | 0 | 633 | -843.9914 | [13 empty] | 40098.1089 | 59.967 | 3779.0562 | 350 | -340.4694 | 0 | 124 | 10 | 0 | -103 | 7745.52 | 26.4008
| 40098.109 | 59.967 | 3779.0562 |  |  |  | 26.4008 | 25.8783 |  | 0 | 3805.195 | 3773.9475 | 3780.0576 | 3778.5625 | 3747.166 | 633 | [6 empty] | 0 | 633 | -843.9914 | [13 empty] | 40098.109 | 59.967 | 3779.0562 | 350 | -340.4694 | 0 | 124 | 10 | 0 | -103 | 7745.52 | 26.4008
| 40098.109 | 59.965 | 3779.3347 |  |  |  | 27.9999 | 26.6208 |  | 0 | 3805.9376 | 3773.9663 | 3780.1477 | 3778.5625 | 3747.2758 | 633 | [6 empty] | 0 | 633 | -822.0815 | [13 empty] | 40098.109 | 59.965 | 3779.3347 | 350 | -340.4694 | 0 | 124.5 | 10 | 0 | -103 | 7746.51 | 27.9999
| 40098.109 | 59.965 | 3779.3347 |  |  |  | 27.9999 | 27.1035 |  | 0 | 3806.4203 | 3773.9849 | 3780.239 | 3778.5625 | 3747.3848 | 633 | [6 empty] | 0 | 633 | -822.0815 | [13 empty] | 40098.109 | 59.965 | 3779.3347 | 350 | -340.4694 | 0 | 124.5 | 10 | 0 | -103 | 7746.51 | 27.9999
| 40098.109 | 59.965 | 3779.3347 |  |  |  | 27.9999 | 27.4172 |  | 0 | 3806.734 | 3774.0034 | 3780.3306 | 3778.5625 | 3747.493 | 633 | [6 empty] | 0 | 633 | -822.0815 | [13 empty] | 40098.109 | 59.965 | 3779.3347 | 350 | -340.4694 | 0 | 124.5 | 10 | 0 | -103 | 7746.51 | 27.9999
| 40098.1091 | 59.965 | 3776.5967 |  |  |  | 27.9999 | 27.6212 |  | 0 | 3806.9379 | 3774.0124 | 3780.4224 | 3778.5625 | 3747.6005 | 633 | [6 empty] | 0 | 633 | -822.0815 | [13 empty] | 40098.1091 | 59.965 | 3776.5967 | 350 | -340.4694 | 0 | 125 | 10 | 0 | -103 | 7747.5 | 27.9999
| 40098.1091 | 59.965 | 3776.5967 |  |  |  | 27.9999 | 27.7537 |  | 0 | 3807.0705 | 3774.0212 | 3780.514 | 3778.5625 | 3747.7073 | 633 | [6 empty] | 0 | 633 | -822.0815 | [13 empty] | 40098.1091 | 59.965 | 3776.5967 | 350 | -340.4694 | 0 | 125 | 10 | 0 | -103 | 7747.5 | 27.9999
| 40098.1091 | 59.965 | 3776.5967 |  |  |  | 27.9999 | 27.8399 |  | 0 | 3807.1566 | 3774.0301 | 3780.6052 | 3778.5625 | 3747.8133 | 633 | [6 empty] | 0 | 633 | -822.0815 | [13 empty] | 40098.1091 | 59.965 | 3776.5967 | 350 | -340.4694 | 0 | 125 | 10 | 0 | -103 | 7747.5 | 27.9999
| 40098.1091 | 59.97 | 3773.1699 |  |  |  | 23.999 | 26.4956 |  | 0 | 3805.8123 | 3774.0271 | 3780.6912 | 3778.5625 | 3747.9186 | 633 | [6 empty] | 0 | 633 | -879.1838 | [13 empty] | 40098.1091 | 59.97 | 3773.1699 | 350 | -340.4694 | 0 | 125.5 | 10 | 0 | -103 | 7748.49 | 23.999
| 40098.1091 | 59.97 | 3773.1699 |  |  |  | 23.999 | 25.6218 |  | 0 | 3804.9385 | 3774.0242 | 3780.7737 | 3778.5625 | 3748.0232 | 633 | [6 empty] | 0 | 633 | -879.1838 | [13 empty] | 40098.1091 | 59.97 | 3773.1699 | 350 | -340.4694 | 0 | 125.5 | 10 | 0 | -103 | 7748.49 | 23.999
| 40098.1092 | 59.97 | 3773.1699 |  |  |  | 23.999 | 25.0538 |  | 0 | 3804.3706 | 3774.0213 | 3780.8537 | 3778.5625 | 3748.1271 | 633 | [6 empty] | 0 | 633 | -879.1838 | [13 empty] | 40098.1092 | 59.97 | 3773.1699 | 350 | -340.4694 | 0 | 125.5 | 10 | 0 | -103 | 7748.49 | 23.999
| 40098.1092 | 59.968 | 3768.5029 |  |  |  | 25.6012 | 25.2454 |  | 0 | 3804.5622 | 3774.0027 | 3780.9338 | 3778.5625 | 3748.2303 | 633 | [6 empty] | 0 | 633 | -855.3902 | [13 empty] | 40098.1092 | 59.968 | 3768.5029 | 350 | -340.4694 | 0 | 126 | 10 | 0 | -103 | 7749.48 | 25.6012
| 40098.1092 | 59.968 | 3768.5029 |  |  |  | 25.6012 | 25.3699 |  | 0 | 3804.6867 | 3773.9842 | 3781.0138 | 3778.5625 | 3748.3327 | 633 | [6 empty] | 0 | 633 | -855.3902 | [13 empty] | 40098.1092 | 59.968 | 3768.5029 | 350 | -340.4694 | 0 | 126 | 10 | 0 | -103 | 7749.48 | 25.6012
| 40098.1092 | 59.968 | 3768.5029 |  |  |  | 25.6012 | 25.4509 |  | 0 | 3804.7676 | 3773.9658 | 3781.0935 | 3778.5625 | 3748.4345 | 633 | [6 empty] | 0 | 633 | -855.3902 | [13 empty] | 40098.1092 | 59.968 | 3768.5029 | 350 | -340.4694 | 0 | 126 | 10 | 0 | -103 | 7749.48 | 25.6012
| 40098.1093 | 59.97 | 3764.7861 |  |  |  | 23.999 | 24.9427 |  | 0 | 3804.2595 | 3773.9351 | 3781.171 | 3778.5625 | 3748.5356 | 633 | [6 empty] | 0 | 633 | -879.1838 | [13 empty] | 40098.1093 | 59.97 | 3764.7861 | 350 | -337.6429 | 0 | 126.5 | 10 | 0 | -103 | 7750.47 | 23.999
| 40098.1093 | 59.97 | 3764.7861 |  |  |  | 23.999 | 24.6124 |  | 0 | 3803.9292 | 3773.9046 | 3781.2468 | 3778.5625 | 3748.6361 | 633 | [6 empty] | 0 | 633 | -879.1838 | [13 empty] | 40098.1093 | 59.97 | 3764.7861 | 350 | -337.6429 | 0 | 126.5 | 10 | 0 | -103 | 7750.47 | 23.999
| 40098.1093 | 59.97 | 3764.7861 |  |  |  | 23.999 | 24.3977 |  | 0 | 3803.7145 | 3773.8743 | 3781.3215 | 3778.5625 | 3748.7358 | 633 | [6 empty] | 0 | 633 | -879.1838 | [13 empty] | 40098.1093 | 59.97 | 3764.7861 | 350 | -337.6429 | 0 | 126.5 | 10 | 0 | -103 | 7750.47 | 23.999
| 40098.1093 | 59.965 | 3761.8938 |  |  |  | 27.9999 | 25.6585 |  | 0 | 3804.9752 | 3773.8346 | 3781.3998 | 3778.5625 | 3748.8349 | 633 | [6 empty] | 0 | 633 | -822.0815 | [13 empty] | 40098.1093 | 59.965 | 3761.8938 | 350 | -337.6429 | 0 | 127 | 10 | 0 | -103 | 7751.46 | 27.9999
| 40098.1094 | 59.965 | 3761.8938 |  |  |  | 27.9999 | 26.478 |  | 0 | 3805.7947 | 3773.7952 | 3781.4803 | 3778.5625 | 3748.9333 | 633 | [6 empty] | 0 | 633 | -822.0815 | [13 empty] | 40098.1094 | 59.965 | 3761.8938 | 350 | -337.6429 | 0 | 127 | 10 | 0 | -103 | 7751.46 | 27.9999
| 40098.1094 | 59.965 | 3761.8938 |  |  |  | 27.9999 | 27.0106 |  | 0 | 3806.3274 | 3773.756 | 3781.562 | 3778.5625 | 3749.0311 | 633 | [6 empty] | 0 | 633 | -822.0815 | [13 empty] | 40098.1094 | 59.965 | 3761.8938 | 350 | -337.6429 | 0 | 127 | 10 | 0 | -103 | 7751.46 | 27.9999
| 40098.1094 | 59.967 | 3760.1575 |  |  |  | 26.4008 | 26.7972 |  | 0 | 3806.1139 | 3773.7115 | 3781.6425 | 3778.5625 | 3749.1283 | 633 | [6 empty] | 0 | 633 | -843.9914 | [13 empty] | 40098.1094 | 59.967 | 3760.1575 | 350 | -337.6429 | 0 | 127.5 | 10 | 0 | -103 | 7752.45 | 26.4008
| 40098.1094 | 59.967 | 3760.1575 |  |  |  | 26.4008 | 26.6584 |  | 0 | 3805.9752 | 3773.6672 | 3781.7221 | 3778.5625 | 3749.2248 | 633 | [6 empty] | 0 | 633 | -843.9914 | [13 empty] | 40098.1094 | 59.967 | 3760.1575 | 350 | -337.6429 | 0 | 127.5 | 10 | 0 | -103 | 7752.45 | 26.4008
| 40098.1094 | 59.967 | 3760.1575 |  |  |  | 26.4008 | 26.5682 |  | 0 | 3805.885 | 3773.6232 | 3781.8008 | 3778.5625 | 3749.3206 | 633 | [6 empty] | 0 | 633 | -843.9914 | [13 empty] | 40098.1094 | 59.967 | 3760.1575 | 350 | -337.6429 | 0 | 127.5 | 10 | 0 | -103 | 7752.45 | 26.4008
| 40098.1095 | 59.979 | 3757.7729 |  |  |  | 16.7999 | 23.1493 |  | 0 | 3802.4661 | 3773.5717 | 3781.8679 | 3778.5625 | 3749.4159 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.1095 | 59.979 | 3757.7729 | 350 | -337.6429 | 0 | 128 | 10 | 0 | -103 | 7753.44 | 16.7999
| 40098.1095 | 59.979 | 3757.7729 |  |  |  | 16.7999 | 20.927 |  | 0 | 3800.2438 | 3773.5206 | 3781.9273 | 3778.5625 | 3749.5105 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.1095 | 59.979 | 3757.7729 | 350 | -337.6429 | 0 | 128 | 10 | 0 | -103 | 7753.44 | 16.7999
| 40098.1095 | 59.979 | 3757.7729 |  |  |  | 16.7999 | 19.4826 |  | 0 | 3798.7993 | 3773.4698 | 3781.9817 | 3778.5625 | 3749.6045 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.1095 | 59.979 | 3757.7729 | 350 | -337.6429 | 0 | 128 | 10 | 0 | -103 | 7753.44 | 16.7999
| 40098.1095 | 59.974 | 3751.6367 |  |  |  | 20.8008 | 19.9439 |  | 0 | 3799.2607 | 3773.3996 | 3782.0373 | 3778.5625 | 3749.698 | 633 | [6 empty] | 0 | 633 | -930.8715 | [13 empty] | 40098.1095 | 59.974 | 3751.6367 | 350 | -337.6429 | 0 | 128.5 | 10 | 0 | -103 | 7754.43 | 20.8008
| 40098.1096 | 59.974 | 3751.6367 |  |  |  | 20.8008 | 20.2438 |  | 0 | 3799.5606 | 3773.3298 | 3782.0935 | 3778.5625 | 3749.7908 | 633 | [6 empty] | 0 | 633 | -930.8715 | [13 empty] | 40098.1096 | 59.974 | 3751.6367 | 350 | -337.6429 | 0 | 128.5 | 10 | 0 | -103 | 7754.43 | 20.8008
| 40098.1096 | 59.974 | 3751.6367 |  |  |  | 20.8008 | 20.4388 |  | 0 | 3799.7555 | 3773.2605 | 3782.1499 | 3778.5625 | 3749.883 | 633 | [6 empty] | 0 | 633 | -930.8715 | [13 empty] | 40098.1096 | 59.974 | 3751.6367 | 350 | -337.6429 | 0 | 128.5 | 10 | 0 | -103 | 7754.43 | 20.8008
| 40098.1096 | 59.962 | 3759.2498 |  |  |  | 30.3986 | 23.9247 |  | 0 | 3803.2415 | 3773.2159 | 3782.2171 | 3778.5625 | 3749.9746 | 633 | [6 empty] | 0 | 633 | -791.2696 | [13 empty] | 40098.1096 | 59.962 | 3759.2498 | 350 | -284.3608 | 0 | 129 | 10 | 0 | -103 | 7755.42 | 30.3986
| 40098.1096 | 59.962 | 3759.2498 |  |  |  | 30.3986 | 26.1905 |  | 0 | 3805.5073 | 3773.1715 | 3782.291 | 3778.5625 | 3750.0657 | 633 | [6 empty] | 0 | 633 | -791.2696 | [13 empty] | 40098.1096 | 59.962 | 3759.2498 | 350 | -284.3608 | 0 | 129 | 10 | 0 | -103 | 7755.42 | 30.3986
| 40098.1097 | 59.962 | 3759.2498 |  |  |  | 30.3986 | 27.6634 |  | 0 | 3806.9801 | 3773.1275 | 3782.3691 | 3778.5625 | 3750.1561 | 633 | [6 empty] | 0 | 633 | -791.2696 | [13 empty] | 40098.1097 | 59.962 | 3759.2498 | 350 | -284.3608 | 0 | 129 | 10 | 0 | -103 | 7755.42 | 30.3986
| 40098.1097 | 59.961 | 3762.0222 |  |  |  | 31.2012 | 28.9016 |  | 0 | 3808.2184 | 3773.0925 | 3782.4507 | 3778.5625 | 3750.246 | 633 | [6 empty] | 0 | 633 | -781.4691 | [13 empty] | 40098.1097 | 59.961 | 3762.0222 | 350 | -284.3608 | 0 | 129.5 | 10 | 0 | -103 | 7756.41 | 31.2012
| 40098.1097 | 59.961 | 3762.0222 |  |  |  | 31.2012 | 29.7064 |  | 0 | 3809.0232 | 3773.0576 | 3782.5342 | 3778.5625 | 3750.3353 | 633 | [6 empty] | 0 | 633 | -781.4691 | [13 empty] | 40098.1097 | 59.961 | 3762.0222 | 350 | -284.3608 | 0 | 129.5 | 10 | 0 | -103 | 7756.41 | 31.2012
| 40098.1097 | 59.961 | 3762.0222 |  |  |  | 31.2012 | 30.2296 |  | 0 | 3809.5464 | 3773.023 | 3782.6189 | 3778.5625 | 3750.4241 | 633 | [6 empty] | 0 | 633 | -781.4691 | [13 empty] | 40098.1097 | 59.961 | 3762.0222 | 350 | -284.3608 | 0 | 129.5 | 10 | 0 | -103 | 7756.41 | 31.2012
| 40098.1097 | 59.959 | 3763.8582 |  |  |  | 32.8003 | 31.1293 |  | 0 | 3810.4461 | 3772.9944 | 3782.7059 | 3778.5625 | 3750.5123 | 633 | [6 empty] | 0 | 633 | -762.6489 | [13 empty] | 40098.1097 | 59.959 | 3763.8582 | 350 | -284.3608 | 0 | 130 | 10 | 0 | -103 | 7757.4 | 32.8003
| 40098.1098 | 59.959 | 3763.8582 |  |  |  | 32.8003 | 31.7142 |  | 0 | 3811.0309 | 3772.9659 | 3782.7941 | 3778.5625 | 3750.6 | 633 | [6 empty] | 0 | 633 | -762.6489 | [13 empty] | 40098.1098 | 59.959 | 3763.8582 | 350 | -284.3608 | 0 | 130 | 10 | 0 | -103 | 7757.4 | 32.8003
| 40098.1098 | 59.959 | 3763.8582 |  |  |  | 32.8003 | 32.0943 |  | 0 | 3811.4111 | 3772.9377 | 3782.883 | 3778.5625 | 3750.6871 | 633 | [6 empty] | 0 | 633 | -762.6489 | [13 empty] | 40098.1098 | 59.959 | 3763.8582 | 350 | -284.3608 | 0 | 130 | 10 | 0 | -103 | 7757.4 | 32.8003
| 40098.1098 | 59.953 | 3768.3389 |  |  |  | 37.6007 | 34.0216 |  | 0 | 3813.3383 | 3772.9234 | 3782.9773 | 3778.5625 | 3750.7737 | 633 | [6 empty] | 0 | 633 | -711.2303 | [13 empty] | 40098.1098 | 59.953 | 3768.3389 | 350 | -284.3608 | 0 | 130.5 | 10 | 0 | -103 | 7758.39 | 37.6007
| 40098.1098 | 59.953 | 3768.3389 |  |  |  | 37.6007 | 35.2743 |  | 0 | 3814.591 | 3772.9093 | 3783.0749 | 3778.5625 | 3750.8597 | 633 | [6 empty] | 0 | 633 | -711.2303 | [13 empty] | 40098.1098 | 59.953 | 3768.3389 | 350 | -284.3608 | 0 | 130.5 | 10 | 0 | -103 | 7758.39 | 37.6007
| 40098.1099 | 59.953 | 3768.3389 |  |  |  | 37.6007 | 36.0885 |  | 0 | 3815.4053 | 3772.8952 | 3783.1743 | 3778.5625 | 3750.9452 | 633 | [6 empty] | 0 | 633 | -711.2303 | [13 empty] | 40098.1099 | 59.953 | 3768.3389 | 350 | -284.3608 | 0 | 130.5 | 10 | 0 | -103 | 7758.39 | 37.6007
| 40098.1099 | 59.956 | 3765.6064 |  |  |  | 35.199 | 35.7772 |  | 0 | 3815.0939 | 3772.8729 | 3783.2722 | 3778.5625 | 3751.0302 | 633 | [6 empty] | 0 | 633 | -736.059 | [13 empty] | 40098.1099 | 59.956 | 3765.6064 | 350 | -284.3608 | 0 | 131 | 10 | 0 | -103 | 7759.38 | 35.199
| 40098.1099 | 59.956 | 3765.6064 |  |  |  | 35.199 | 35.5748 |  | 0 | 3814.8916 | 3772.8506 | 3783.3689 | 3778.5625 | 3751.1146 | 633 | [6 empty] | 0 | 633 | -736.059 | [13 empty] | 40098.1099 | 59.956 | 3765.6064 | 350 | -284.3608 | 0 | 131 | 10 | 0 | -103 | 7759.38 | 35.199
| 40098.1099 | 59.956 | 3765.6064 |  |  |  | 35.199 | 35.4433 |  | 0 | 3814.76 | 3772.8285 | 3783.4646 | 3778.5625 | 3751.1986 | 633 | [6 empty] | 0 | 633 | -736.059 | [13 empty] | 40098.1099 | 59.956 | 3765.6064 | 350 | -284.3608 | 0 | 131 | 10 | 0 | -103 | 7759.38 | 35.199
| 40098.11 | 59.961 | 3761.9199 |  |  |  | 31.2012 | 33.9585 |  | 0 | 3813.2753 | 3772.7954 | 3783.5553 | 3778.5625 | 3751.282 | 633 | [6 empty] | 0 | 633 | -781.4691 | [13 empty] | 40098.11 | 59.961 | 3761.9199 | 350 | -260.468 | 0 | 131.5 | 10 | 0 | -103 | 7760.37 | 31.2012
| 40098.11 | 59.961 | 3761.9199 |  |  |  | 31.2012 | 32.9935 |  | 0 | 3812.3102 | 3772.7624 | 3783.6424 | 3778.5625 | 3751.3649 | 633 | [6 empty] | 0 | 633 | -781.4691 | [13 empty] | 40098.11 | 59.961 | 3761.9199 | 350 | -260.468 | 0 | 131.5 | 10 | 0 | -103 | 7760.37 | 31.2012
| 40098.11 | 59.961 | 3761.9199 |  |  |  | 31.2012 | 32.3662 |  | 0 | 3811.6829 | 3772.7297 | 3783.7271 | 3778.5625 | 3751.4473 | 633 | [6 empty] | 0 | 633 | -781.4691 | [13 empty] | 40098.11 | 59.961 | 3761.9199 | 350 | -260.468 | 0 | 131.5 | 10 | 0 | -103 | 7760.37 | 31.2012
| 40098.11 | 59.963 | 3752.4287 |  |  |  | 29.599 | 31.3977 |  | 0 | 3810.7144 | 3772.6685 | 3783.8084 | 3778.5625 | 3751.5292 | 633 | [6 empty] | 0 | 633 | -801.2804 | [13 empty] | 40098.11 | 59.963 | 3752.4287 | 350 | -260.468 | 0 | 132 | 10 | 0 | -103 | 7761.36 | 29.599
| 40098.11 | 59.963 | 3752.4287 |  |  |  | 29.599 | 30.7681 |  | 0 | 3810.0849 | 3772.6077 | 3783.8873 | 3778.5625 | 3751.6107 | 633 | [6 empty] | 0 | 633 | -801.2804 | [13 empty] | 40098.11 | 59.963 | 3752.4287 | 350 | -260.468 | 0 | 132 | 10 | 0 | -103 | 7761.36 | 29.599
| 40098.1101 | 59.963 | 3752.4287 |  |  |  | 29.599 | 30.3589 |  | 0 | 3809.6757 | 3772.5473 | 3783.9645 | 3778.5625 | 3751.6916 | 633 | [6 empty] | 0 | 633 | -801.2804 | [13 empty] | 40098.1101 | 59.963 | 3752.4287 | 350 | -260.468 | 0 | 132 | 10 | 0 | -103 | 7761.36 | 29.599
| 40098.1101 | 59.968 | 3753.5103 |  |  |  | 25.6012 | 28.6937 |  | 0 | 3808.0105 | 3772.4905 | 3784.0363 | 3778.5625 | 3751.7721 | 633 | [6 empty] | 0 | 633 | -855.3902 | [13 empty] | 40098.1101 | 59.968 | 3753.5103 | 350 | -260.468 | 0 | 132.5 | 10 | 0 | -103 | 7762.35 | 25.6012
| 40098.1101 | 59.968 | 3753.5103 |  |  |  | 25.6012 | 27.6113 |  | 0 | 3806.9281 | 3772.434 | 3784.1044 | 3778.5625 | 3751.852 | 633 | [6 empty] | 0 | 633 | -855.3902 | [13 empty] | 40098.1101 | 59.968 | 3753.5103 | 350 | -260.468 | 0 | 132.5 | 10 | 0 | -103 | 7762.35 | 25.6012
| 40098.1101 | 59.968 | 3753.5103 |  |  |  | 25.6012 | 26.9078 |  | 0 | 3806.2246 | 3772.3779 | 3784.1701 | 3778.5625 | 3751.9315 | 633 | [6 empty] | 0 | 633 | -855.3902 | [13 empty] | 40098.1101 | 59.968 | 3753.5103 | 350 | -260.468 | 0 | 132.5 | 10 | 0 | -103 | 7762.35 | 25.6012
| 40098.1102 | 59.973 | 3753.1782 |  |  |  | 21.6003 | 25.0502 |  | 0 | 3804.3669 | 3772.3211 | 3784.2298 | 3778.5625 | 3752.0106 | 633 | [6 empty] | 0 | 633 | -917.3881 | [13 empty] | 40098.1102 | 59.973 | 3753.1782 | 350 | -260.468 | 0 | 133 | 10 | 0 | -103 | 7763.34 | 21.6003
| 40098.1102 | 59.973 | 3753.1782 |  |  |  | 21.6003 | 23.8427 |  | 0 | 3803.1595 | 3772.2646 | 3784.2857 | 3778.5625 | 3752.0891 | 633 | [6 empty] | 0 | 633 | -917.3881 | [13 empty] | 40098.1102 | 59.973 | 3753.1782 | 350 | -260.468 | 0 | 133 | 10 | 0 | -103 | 7763.34 | 21.6003
| 40098.1102 | 59.973 | 3753.1782 |  |  |  | 21.6003 | 23.0579 |  | 0 | 3802.3747 | 3772.2085 | 3784.3389 | 3778.5625 | 3752.1672 | 633 | [6 empty] | 0 | 633 | -917.3881 | [13 empty] | 40098.1102 | 59.973 | 3753.1782 | 350 | -260.468 | 0 | 133 | 10 | 0 | -103 | 7763.34 | 21.6003
| 40098.1102 | 59.967 | 3752.8716 |  |  |  | 26.4008 | 24.2279 |  | 0 | 3803.5447 | 3772.1517 | 3784.3952 | 3778.5625 | 3752.2448 | 633 | [6 empty] | 0 | 633 | -843.9914 | [13 empty] | 40098.1102 | 59.967 | 3752.8716 | 350 | -260.468 | 0 | 133.5 | 10 | 0 | -103 | 7764.33 | 26.4008
| 40098.1103 | 59.967 | 3752.8716 |  |  |  | 26.4008 | 24.9884 |  | 0 | 3804.3052 | 3772.0954 | 3784.4534 | 3778.5625 | 3752.322 | 633 | [6 empty] | 0 | 633 | -843.9914 | [13 empty] | 40098.1103 | 59.967 | 3752.8716 | 350 | -260.468 | 0 | 133.5 | 10 | 0 | -103 | 7764.33 | 26.4008
| 40098.1103 | 59.967 | 3752.8716 |  |  |  | 26.4008 | 25.4827 |  | 0 | 3804.7995 | 3772.0393 | 3784.5127 | 3778.5625 | 3752.3987 | 633 | [6 empty] | 0 | 633 | -843.9914 | [13 empty] | 40098.1103 | 59.967 | 3752.8716 | 350 | -260.468 | 0 | 133.5 | 10 | 0 | -103 | 7764.33 | 26.4008
| 40098.1103 | 59.976 | 3747.4758 |  |  |  | 19.1986 | 23.2833 |  | 0 | 3802.6 | 3771.9679 | 3784.5653 | 3778.5625 | 3752.475 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1103 | 59.976 | 3747.4758 | 350 | -253.1415 | 0 | 134 | 10 | 0 | -103 | 7765.32 | 19.1986
| 40098.1103 | 59.976 | 3747.4758 |  |  |  | 19.1986 | 21.8536 |  | 0 | 3801.1704 | 3771.8969 | 3784.6134 | 3778.5625 | 3752.5509 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1103 | 59.976 | 3747.4758 | 350 | -253.1415 | 0 | 134 | 10 | 0 | -103 | 7765.32 | 19.1986
| 40098.1103 | 59.976 | 3747.4758 |  |  |  | 19.1986 | 20.9244 |  | 0 | 3800.2411 | 3771.8263 | 3784.6586 | 3778.5625 | 3752.6262 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1103 | 59.976 | 3747.4758 | 350 | -253.1415 | 0 | 134 | 10 | 0 | -103 | 7765.32 | 19.1986
| 40098.1104 | 59.973 | 3746.6509 |  |  |  | 21.6003 | 21.161 |  | 0 | 3800.4777 | 3771.7538 | 3784.7042 | 3778.5625 | 3752.7012 | 633 | [6 empty] | 0 | 633 | -917.3881 | [13 empty] | 40098.1104 | 59.973 | 3746.6509 | 350 | -253.1415 | 0 | 134.5 | 10 | 0 | -103 | 7766.31 | 21.6003
| 40098.1104 | 59.973 | 3746.6509 |  |  |  | 21.6003 | 21.3147 |  | 0 | 3800.6315 | 3771.6817 | 3784.7499 | 3778.5625 | 3752.7757 | 633 | [6 empty] | 0 | 633 | -917.3881 | [13 empty] | 40098.1104 | 59.973 | 3746.6509 | 350 | -253.1415 | 0 | 134.5 | 10 | 0 | -103 | 7766.31 | 21.6003
| 40098.1104 | 59.973 | 3746.6509 |  |  |  | 21.6003 | 21.4147 |  | 0 | 3800.7315 | 3771.6099 | 3784.7957 | 3778.5625 | 3752.8498 | 633 | [6 empty] | 0 | 633 | -917.3881 | [13 empty] | 40098.1104 | 59.973 | 3746.6509 | 350 | -253.1415 | 0 | 134.5 | 10 | 0 | -103 | 7766.31 | 21.6003
| 40098.1104 | 59.981 | 3741.6182 |  |  |  | 15.2008 | 19.2398 |  | 0 | 3798.5566 | 3771.5243 | 3784.8351 | 3778.5625 | 3752.9235 | 633 | [6 empty] | 0 | 633 | -1037.6909 | [13 empty] | 40098.1104 | 59.981 | 3741.6182 | 350 | -253.1415 | 0 | 135 | 10 | 0 | -103 | 7767.3 | 15.2008
| 40098.1105 | 59.981 | 3741.6182 |  |  |  | 15.2008 | 17.8262 |  | 0 | 3797.1429 | 3771.439 | 3784.8701 | 3778.5625 | 3752.9968 | 633 | [6 empty] | 0 | 633 | -1037.6909 | [13 empty] | 40098.1105 | 59.981 | 3741.6182 | 350 | -253.1415 | 0 | 135 | 10 | 0 | -103 | 7767.3 | 15.2008
| 40098.1105 | 59.981 | 3741.6182 |  |  |  | 15.2008 | 16.9073 |  | 0 | 3796.2241 | 3771.3543 | 3784.9024 | 3778.5625 | 3753.0696 | 633 | [6 empty] | 0 | 633 | -1037.6909 | [13 empty] | 40098.1105 | 59.981 | 3741.6182 | 350 | -253.1415 | 0 | 135 | 10 | 0 | -103 | 7767.3 | 15.2008
| 40098.1105 | 59.982 | 3738.9014 |  |  |  | 14.4012 | 16.0302 |  | 0 | 3795.3469 | 3771.2624 | 3784.932 | 3778.5625 | 3753.142 | 633 | [6 empty] | 0 | 633 | -1054.9759 | [13 empty] | 40098.1105 | 59.982 | 3738.9014 | 350 | -253.1415 | 0 | 135.5 | 10 | 0 | -103 | 7768.29 | 14.4012
| 40098.1105 | 59.982 | 3738.9014 |  |  |  | 14.4012 | 15.4601 |  | 0 | 3794.7768 | 3771.171 | 3784.9598 | 3778.5625 | 3753.214 | 633 | [6 empty] | 0 | 633 | -1054.9759 | [13 empty] | 40098.1105 | 59.982 | 3738.9014 | 350 | -253.1415 | 0 | 135.5 | 10 | 0 | -103 | 7768.29 | 14.4012
| 40098.1106 | 59.982 | 3738.9014 |  |  |  | 14.4012 | 15.0895 |  | 0 | 3794.4062 | 3771.0801 | 3784.9864 | 3778.5625 | 3753.2856 | 633 | [6 empty] | 0 | 633 | -1054.9759 | [13 empty] | 40098.1106 | 59.982 | 3738.9014 | 350 | -253.1415 | 0 | 135.5 | 10 | 0 | -103 | 7768.29 | 14.4012
| 40098.1106 | 59.982 | 3736.3083 |  |  |  | 14.4012 | 14.8486 |  | 0 | 3794.1654 | 3770.9824 | 3785.0122 | 3778.5625 | 3753.3568 | 633 | [6 empty] | 0 | 633 | -1054.9759 | [13 empty] | 40098.1106 | 59.982 | 3736.3083 | 350 | -253.1415 | 0 | 136 | 10 | 0 | -103 | 7769.28 | 14.4012
| 40098.1106 | 59.982 | 3736.3083 |  |  |  | 14.4012 | 14.692 |  | 0 | 3794.0088 | 3770.8853 | 3785.0374 | 3778.5625 | 3753.4276 | 633 | [6 empty] | 0 | 633 | -1054.9759 | [13 empty] | 40098.1106 | 59.982 | 3736.3083 | 350 | -253.1415 | 0 | 136 | 10 | 0 | -103 | 7769.28 | 14.4012
| 40098.1106 | 59.982 | 3736.3083 |  |  |  | 14.4012 | 14.5902 |  | 0 | 3793.907 | 3770.7887 | 3785.0621 | 3778.5625 | 3753.4981 | 633 | [6 empty] | 0 | 633 | -1054.9759 | [13 empty] | 40098.1106 | 59.982 | 3736.3083 | 350 | -253.1415 | 0 | 136 | 10 | 0 | -103 | 7769.28 | 14.4012
| 40098.1106 | 59.98 | 3735.6497 |  |  |  | 16.0004 | 15.0838 |  | 0 | 3794.4006 | 3770.6908 | 3785.0882 | 3778.5625 | 3753.5681 | 633 | [6 empty] | 0 | 633 | -1020.9632 | [13 empty] | 40098.1106 | 59.98 | 3735.6497 | 350 | -251.9299 | 0 | 136.5 | 10 | 0 | -103 | 7770.27 | 16.0004
| 40098.1107 | 59.98 | 3735.6497 |  |  |  | 16.0004 | 15.4046 |  | 0 | 3794.7214 | 3770.5935 | 3785.1149 | 3778.5625 | 3753.6377 | 633 | [6 empty] | 0 | 633 | -1020.9632 | [13 empty] | 40098.1107 | 59.98 | 3735.6497 | 350 | -251.9299 | 0 | 136.5 | 10 | 0 | -103 | 7770.27 | 16.0004
| 40098.1107 | 59.98 | 3735.6497 |  |  |  | 16.0004 | 15.6131 |  | 0 | 3794.9299 | 3770.4967 | 3785.1421 | 3778.5625 | 3753.7069 | 633 | [6 empty] | 0 | 633 | -1020.9632 | [13 empty] | 40098.1107 | 59.98 | 3735.6497 | 350 | -251.9299 | 0 | 136.5 | 10 | 0 | -103 | 7770.27 | 16.0004
| 40098.1107 | 59.98 | 3736.7476 |  |  |  | 16.0004 | 15.7487 |  | 0 | 3795.0654 | 3770.4035 | 3785.1695 | 3778.5625 | 3753.7758 | 633 | [6 empty] | 0 | 633 | -1020.9632 | [13 empty] | 40098.1107 | 59.98 | 3736.7476 | 350 | -251.9299 | 0 | 137 | 10 | 0 | -103 | 7771.26 | 16.0004
| 40098.1107 | 59.98 | 3736.7476 |  |  |  | 16.0004 | 15.8368 |  | 0 | 3795.1535 | 3770.3107 | 3785.197 | 3778.5625 | 3753.8442 | 633 | [6 empty] | 0 | 633 | -1020.9632 | [13 empty] | 40098.1107 | 59.98 | 3736.7476 | 350 | -251.9299 | 0 | 137 | 10 | 0 | -103 | 7771.26 | 16.0004
| 40098.1108 | 59.98 | 3736.7476 |  |  |  | 16.0004 | 15.894 |  | 0 | 3795.2108 | 3770.2185 | 3785.2245 | 3778.5625 | 3753.9123 | 633 | [6 empty] | 0 | 633 | -1020.9632 | [13 empty] | 40098.1108 | 59.98 | 3736.7476 | 350 | -251.9299 | 0 | 137 | 10 | 0 | -103 | 7771.26 | 16.0004
| 40098.1108 | 59.978 | 3736.0942 |  |  |  | 17.5995 | 16.4909 |  | 0 | 3795.8077 | 3770.125 | 3785.2535 | 3778.5625 | 3753.9801 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1108 | 59.978 | 3736.0942 | 350 | -251.9299 | 0 | 137.5 | 10 | 0 | -103 | 7772.25 | 17.5995
| 40098.1108 | 59.978 | 3736.0942 |  |  |  | 17.5995 | 16.8789 |  | 0 | 3796.1957 | 3770.0321 | 3785.2834 | 3778.5625 | 3754.0474 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1108 | 59.978 | 3736.0942 | 350 | -251.9299 | 0 | 137.5 | 10 | 0 | -103 | 7772.25 | 17.5995
| 40098.1108 | 59.978 | 3736.0942 |  |  |  | 17.5995 | 17.1311 |  | 0 | 3796.4479 | 3769.9396 | 3785.3138 | 3778.5625 | 3754.1144 | 633 | [6 empty] | 0 | 633 | -989.0752 | [13 empty] | 40098.1108 | 59.978 | 3736.0942 | 350 | -251.9299 | 0 | 137.5 | 10 | 0 | -103 | 7772.25 | 17.5995
| 40098.1109 | 59.971 | 3738.8748 |  |  |  | 23.1995 | 19.255 |  | 0 | 3798.5718 | 3769.8552 | 3785.3499 | 3778.5625 | 3754.181 | 633 | [6 empty] | 0 | 633 | -891.56 | [13 empty] | 40098.1109 | 59.971 | 3738.8748 | 350 | -251.9299 | 0 | 138 | 10 | 0 | -103 | 7773.24 | 23.1995
| 40098.1109 | 59.971 | 3738.8748 |  |  |  | 23.1995 | 20.6356 |  | 0 | 3799.9524 | 3769.7712 | 3785.3894 | 3778.5625 | 3754.2473 | 633 | [6 empty] | 0 | 633 | -891.56 | [13 empty] | 40098.1109 | 59.971 | 3738.8748 | 350 | -251.9299 | 0 | 138 | 10 | 0 | -103 | 7773.24 | 23.1995
| 40098.1109 | 59.971 | 3738.8748 |  |  |  | 23.1995 | 21.5329 |  | 0 | 3800.8497 | 3769.6877 | 3785.4312 | 3778.5625 | 3754.3132 | 633 | [6 empty] | 0 | 633 | -891.56 | [13 empty] | 40098.1109 | 59.971 | 3738.8748 | 350 | -251.9299 | 0 | 138 | 10 | 0 | -103 | 7773.24 | 23.1995
| 40098.1109 | 59.975 | 3737.6841 |  |  |  | 20.0012 | 20.9968 |  | 0 | 3800.3136 | 3769.6014 | 3785.4713 | 3778.5625 | 3754.3787 | 633 | [6 empty] | 0 | 633 | -944.7572 | [13 empty] | 40098.1109 | 59.975 | 3737.6841 | 350 | -251.9299 | 0 | 138.5 | 10 | 0 | -103 | 7774.23 | 20.0012
| 40098.1109 | 59.975 | 3737.6841 |  |  |  | 20.0012 | 20.6484 |  | 0 | 3799.9651 | 3769.5156 | 3785.5103 | 3778.5625 | 3754.4439 | 633 | [6 empty] | 0 | 633 | -944.7572 | [13 empty] | 40098.1109 | 59.975 | 3737.6841 | 350 | -251.9299 | 0 | 138.5 | 10 | 0 | -103 | 7774.23 | 20.0012
| 40098.111 | 59.975 | 3737.6841 |  |  |  | 20.0012 | 20.4219 |  | 0 | 3799.7386 | 3769.4303 | 3785.5485 | 3778.5625 | 3754.5087 | 633 | [6 empty] | 0 | 633 | -944.7572 | [13 empty] | 40098.111 | 59.975 | 3737.6841 | 350 | -251.9299 | 0 | 138.5 | 10 | 0 | -103 | 7774.23 | 20.0012
| 40098.111 | 59.969 | 3740.0168 |  |  |  | 24.7986 | 21.9537 |  | 0 | 3801.2705 | 3769.3517 | 3785.5905 | 3778.5625 | 3754.5732 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.111 | 59.969 | 3740.0168 | 350 | -250.6742 | 0 | 139 | 10 | 0 | -103 | 7775.22 | 24.7986
| 40098.111 | 59.969 | 3740.0168 |  |  |  | 24.7986 | 22.9494 |  | 0 | 3802.2662 | 3769.2734 | 3785.635 | 3778.5625 | 3754.6373 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.111 | 59.969 | 3740.0168 | 350 | -250.6742 | 0 | 139 | 10 | 0 | -103 | 7775.22 | 24.7986
| 40098.111 | 59.969 | 3740.0168 |  |  |  | 24.7986 | 23.5966 |  | 0 | 3802.9134 | 3769.1956 | 3785.6809 | 3778.5625 | 3754.7011 | 633 | [6 empty] | 0 | 633 | -867.1465 | [13 empty] | 40098.111 | 59.969 | 3740.0168 | 350 | -250.6742 | 0 | 139 | 10 | 0 | -103 | 7775.22 | 24.7986
| 40098.1111 | 59.972 | 3742.4238 |  |  |  | 22.3999 | 23.1778 |  | 0 | 3802.4945 | 3769.1246 | 3785.7255 | 3778.5625 | 3754.7646 | 633 | [6 empty] | 0 | 633 | -904.2897 | [13 empty] | 40098.1111 | 59.972 | 3742.4238 | 350 | -250.6742 | 0 | 139.5 | 10 | 0 | -103 | 7776.21 | 22.3999
| 40098.1111 | 59.972 | 3742.4238 |  |  |  | 22.3999 | 22.9055 |  | 0 | 3802.2223 | 3769.054 | 3785.7692 | 3778.5625 | 3754.8277 | 633 | [6 empty] | 0 | 633 | -904.2897 | [13 empty] | 40098.1111 | 59.972 | 3742.4238 | 350 | -250.6742 | 0 | 139.5 | 10 | 0 | -103 | 7776.21 | 22.3999
| 40098.1111 | 59.972 | 3742.4238 |  |  |  | 22.3999 | 22.7286 |  | 0 | 3802.0453 | 3768.9837 | 3785.8121 | 3778.5625 | 3754.8905 | 633 | [6 empty] | 0 | 633 | -904.2897 | [13 empty] | 40098.1111 | 59.972 | 3742.4238 | 350 | -250.6742 | 0 | 139.5 | 10 | 0 | -103 | 7776.21 | 22.3999
| 40098.1111 | 59.977 | 3741.7231 |  |  |  | 18.399 | 21.2132 |  | 0 | 3800.53 | 3768.912 | 3785.8508 | 3778.5625 | 3754.953 | 633 | [6 empty] | 0 | 633 | -973.8667 | [13 empty] | 40098.1111 | 59.977 | 3741.7231 | 350 | -250.6742 | 0 | 140 | 10 | 0 | -103 | 7777.2 | 18.399
| 40098.1112 | 59.977 | 3741.7231 |  |  |  | 18.399 | 20.2283 |  | 0 | 3799.545 | 3768.8406 | 3785.8868 | 3778.5625 | 3755.0151 | 633 | [6 empty] | 0 | 633 | -973.8667 | [13 empty] | 40098.1112 | 59.977 | 3741.7231 | 350 | -250.6742 | 0 | 140 | 10 | 0 | -103 | 7777.2 | 18.399
| 40098.1112 | 59.977 | 3741.7231 |  |  |  | 18.399 | 19.588 |  | 0 | 3798.9048 | 3768.7696 | 3785.9208 | 3778.5625 | 3755.0769 | 633 | [6 empty] | 0 | 633 | -973.8667 | [13 empty] | 40098.1112 | 59.977 | 3741.7231 | 350 | -250.6742 | 0 | 140 | 10 | 0 | -103 | 7777.2 | 18.399
| 40098.1112 | 59.976 | 3739.9644 |  |  |  | 19.1986 | 19.4517 |  | 0 | 3798.7685 | 3768.6944 | 3785.9544 | 3778.5625 | 3755.1384 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1112 | 59.976 | 3739.9644 | 350 | -250.6742 | 0 | 140.5 | 10 | 0 | -103 | 7778.19 | 19.1986
| 40098.1112 | 59.976 | 3739.9644 |  |  |  | 19.1986 | 19.3631 |  | 0 | 3798.6799 | 3768.6196 | 3785.9875 | 3778.5625 | 3755.1996 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1112 | 59.976 | 3739.9644 | 350 | -250.6742 | 0 | 140.5 | 10 | 0 | -103 | 7778.19 | 19.1986
| 40098.1112 | 59.976 | 3739.9644 |  |  |  | 19.1986 | 19.3056 |  | 0 | 3798.6223 | 3768.5452 | 3786.0204 | 3778.5625 | 3755.2604 | 633 | [6 empty] | 0 | 633 | -959.1188 | [13 empty] | 40098.1112 | 59.976 | 3739.9644 | 350 | -250.6742 | 0 | 140.5 | 10 | 0 | -103 | 7778.19 | 19.1986
| 40098.1113 | 59.977 | 3741.2678 |  |  |  | 18.399 | 18.9883 |  | 0 | 3798.305 | 3768.4745 | 3786.0522 | 3778.5625 | 3755.3209 | 633 | [6 empty] | 0 | 633 | -973.8667 | [13 empty] | 40098.1113 | 59.977 | 3741.2678 | 350 | -250.6742 | 0 | 141 | 10 | 0 | -103 | 7779.18 | 18.399
| 40098.1113 | 59.977 | 3741.2678 |  |  |  | 18.399 | 18.782 |  | 0 | 3798.0988 | 3768.4042 | 3786.0833 | 3778.5625 | 3755.3811 | 633 | [6 empty] | 0 | 633 | -973.8667 | [13 empty] | 40098.1113 | 59.977 | 3741.2678 | 350 | -250.6742 | 0 | 141 | 10 | 0 | -103 | 7779.18 | 18.399
| 40098.1113 | 59.977 | 3741.2678 |  |  |  | 18.399 | 18.648 |  | 0 | 3797.9648 | 3768.3343 | 3786.1139 | 3778.5625 | 3755.441 | 633 | [6 empty] | 0 | 633 | -973.8667 | [13 empty] | 40098.1113 | 59.977 | 3741.2678 | 350 | -250.6742 | 0 | 141 | 10 | 0 | -103 | 7779.18 | 18.399
| 40098.1113 | 59.979 | 3738.7061 |  |  |  | 16.7999 | 18.0012 |  | 0 | 3797.3179 | 3768.2581 | 3786.1427 | 3778.5625 | 3755.5006 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.1113 | 59.979 | 3738.7061 | 350 | -253.6319 | 0 | 141.5 | 10 | 0 | -103 | 7780.17 | 16.7999
| 40098.1114 | 59.979 | 3738.7061 |  |  |  | 16.7999 | 17.5807 |  | 0 | 3796.8975 | 3768.1823 | 3786.1703 | 3778.5625 | 3755.5599 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.1114 | 59.979 | 3738.7061 | 350 | -253.6319 | 0 | 141.5 | 10 | 0 | -103 | 7780.17 | 16.7999
| 40098.1114 | 59.979 | 3738.7061 |  |  |  | 16.7999 | 17.3075 |  | 0 | 3796.6242 | 3768.1069 | 3786.197 | 3778.5625 | 3755.6189 | 633 | [6 empty] | 0 | 633 | -1004.7663 | [13 empty] | 40098.1114 | 59.979 | 3738.7061 | 350 | -253.6319 | 0 | 141.5 | 10 | 0 | -103 | 7780.17 | 16.7999
| 40098.1114 | 59.974 | 3738.1016 |  |  |  | 20.8008 | 18.5301 |  | 0 | 3797.8469 | 3768.0304 | 3786.2268 | 3778.5625 | 3755.6776 | 633 | [6 empty] | 0 | 633 | -930.8715 | [13 empty] | 40098.1114 | 59.974 | 3738.1016 | 350 | -253.6319 | 0 | 142 | 10 | 0 | -103 | 7781.16 | 20.8008
| 40098.1114 | 59.974 | 3738.1016 |  |  |  | 20.8008 | 19.3249 |  | 0 | 3798.6416 | 3767.9542 | 3786.2584 | 3778.5625 | 3755.736 | 633 | [6 empty] | 0 | 633 | -930.8715 | [13 empty] | 40098.1114 | 59.974 | 3738.1016 | 350 | -253.6319 | 0 | 142 | 10 | 0 | -103 | 7781.16 | 20.8008
| 40098.1115 | 59.974 | 3738.1016 |  |  |  | 20.8008 | 19.8414 |  | 0 | 3799.1582 | 3767.8785 | 3786.2911 | 3778.5625 | 3755.794 | 633 | [6 empty] | 0 | 633 | -930.8715 | [13 empty] | 40098.1115 | 59.974 | 3738.1016 | 350 | -253.6319 | 0 | 142 | 10 | 0 | -103 | 7781.16 | 20.8008
| 40098.1115 | 59.971 | 3743.4187 |  |  |  | 23.1995 | 21.0167 |  | 0 | 3800.3335 | 3767.8165 | 3786.3266 | 3778.5625 | 3755.8518 | 633 | [6 empty] | 0 | 633 | -891.56 | [13 empty] | 40098.1115 | 59.971 | 3743.4187 | 350 | -253.6319 | 0 | 142.5 | 10 | 0 | -103 | 7782.15 | 23.1995
| 40098.1115 | 59.971 | 3743.4187 |  |  |  | 23.1995 | 21.7807 |  | 0 | 3801.0975 | 3767.7549 | 3786.3639 | 3778.5625 | 3755.9093 | 633 | [6 empty] | 0 | 633 | -891.56 | [13 empty] | 40098.1115 | 59.971 | 3743.4187 | 350 | -253.6319 | 0 | 142.5 | 10 | 0 | -103 | 7782.15 | 23.1995
| 40098.1115 | 59.971 | 3743.4187 |  |  |  | 23.1995 | 22.2773 |  | 0 | 3801.594 | 3767.6936 | 3786.4023 | 3778.5625 | 3755.9665 | 633 | [6 empty] | 0 | 633 | -891.56 | [13 empty] | 40098.1115 | 59.971 | 3743.4187 | 350 | -253.6319 | 0 | 142.5 | 10 | 0 | -103 | 7782.15 | 23.1995
| 40098.1116 | 59.966 | 3747.3396 |  |  |  | 27.2003 | 24.0003 |  | 0 | 3803.3171 | 3767.6425 | 3786.4448 | 3778.5625 | 3756.0234 | 633 | [6 empty] | 0 | 633 | -832.8924 | [13 empty] | 40098.1116 | 59.966 | 3747.3396 | 350 | -253.6319 | 0 | 143 | 10 | 0 | -103 | 7783.14 | 27.2003
| 40098.1116 | 59.966 | 3747.3396 |  |  |  | 27.2003 | 25.1203 |  | 0 | 3804.4371 | 3767.5916 | 3786.4899 | 3778.5625 | 3756.0801 | 633 | [6 empty] | 0 | 633 | -832.8924 | [13 empty] | 40098.1116 | 59.966 | 3747.3396 | 350 | -253.6319 | 0 | 143 | 10 | 0 | -103 | 7783.14 | 27.2003
| 40098.1116 | 59.966 | 3747.3396 |  |  |  | 27.2003 | 25.8483 |  | 0 | 3805.1651 | 3767.541 | 3786.5366 | 3778.5625 | 3756.1364 | 633 | [6 empty] | 0 | 633 | -832.8924 | [13 empty] | 40098.1116 | 59.966 | 3747.3396 | 350 | -253.6319 | 0 | 143 | 10 | 0 | -103 | 7783.14 | 27.2003
| 40098.1116 | 59.973 | 3746.2166 |  |  |  | 21.6003 | 24.3615 |  | 0 | 3803.6783 | 3767.4878 | 3786.5793 | 3778.5625 | 3756.1925 | 633 | [6 empty] | 0 | 633 | -917.3881 | [13 empty] | 40098.1116 | 59.973 | 3746.2166 | 350 | -253.6319 | 0 | 143.5 | 10 | 0 | -103 | 7784.13 | 21.6003
| 40098.1116 | 59.973 | 3746.2166 |  |  |  | 21.6003 | 23.3951 |  | 0 | 3802.7119 | 3767.4349 | 3786.6195 | 3778.5625 | 3756.2483 | 633 | [6 empty] | 0 | 633 | -917.3881 | [13 empty] | 40098.1116 | 59.973 | 3746.2166 | 350 | -253.6319 | 0 | 143.5 | 10 | 0 | -103 | 7784.13 | 21.6003
| 40098.1117 | 59.973 | 3746.2166 |  |  |  | 21.6003 | 22.7669 |  | 0 | 3802.0837 | 3767.3822 | 3786.6578 | 3778.5625 | 3756.3038 | 633 | [6 empty] | 0 | 633 | -917.3881 | [13 empty] | 40098.1117 | 59.973 | 3746.2166 | 350 | -253.6319 | 0 | 143.5 | 10 | 0 | -103 | 7784.13 | 21.6003
| 40098.1117 | 59.972 | 3743.1489 |  |  |  | 22.3999 | 22.6385 |  | 0 | 3801.9552 | 3767.3222 | 3786.6957 | 3778.5625 | 3756.359 | 633 | [6 empty] | 0 | 633 | -904.2897 | [13 empty] | 40098.1117 | 59.972 | 3743.1489 | 350 | -246.9573 | 0 | 144 | 10 | 0 | -103 | 7785.12 | 22.3999
| 40098.1117 | 59.972 | 3743.1489 |  |  |  | 22.3999 | 22.555 |  | 0 | 3801.8717 | 3767.2626 | 3786.7332 | 3778.5625 | 3756.414 | 633 | [6 empty] | 0 | 633 | -904.2897 | [13 empty] | 40098.1117 | 59.972 | 3743.1489 | 350 | -246.9573 | 0 | 144 | 10 | 0 | -103 | 7785.12 | 22.3999
| 40098.1117 | 59.972 | 3743.1489 |  |  |  | 22.3999 | 22.5007 |  | 0 | 3801.8175 | 3767.2032 | 3786.7703 | 3778.5625 | 3756.4687 | 633 | [6 empty] | 0 | 633 | -904.2897 | [13 empty] | 40098.1117 | 59.972 | 3743.1489 | 350 | -246.9573 | 0 | 144 | 10 | 0 | -103 | 7785.12 | 22.3999
| 40098.1118 | 59.97 | 3733.376 |  |  |  | 23.999 | 23.0251 |  | 0 | 3802.3419 | 3767.1201 | 3786.8086 | 3778.5625 | 3756.5231 | 633 | [6 empty] | 0 | 633 | -879.1838 | [13 empty] | 40098.1118 | 59.97 | 3733.376 | 350 | -246.9573 | 0 | 144.5 | 10 | 0 | -103 | 7786.11 | 23.999
| 40098.1118 | 59.97 | 3733.376 |  |  |  | 23.999 | 23.366 |  | 0 | 3802.6827 | 3767.0373 | 3786.8475 | 3778.5625 | 3756.5772 | 633 | [6 empty] | 0 | 633 | -879.1838 | [13 empty] | 40098.1118 | 59.97 | 3733.376 | 350 | -246.9573 | 0 | 144.5 | 10 | 0 | -103 | 7786.11 | 23.999
| 40098.1118 | 59.97 | 3733.376 |  |  |  | 23.999 | 23.5875 |  | 0 | 3802.9043 | 3766.955 | 3786.8868 | 3778.5625 | 3756.6311 | 633 | [6 empty] | 0 | 633 | -879.1838 | [13 empty] | 40098.1118 | 59.97 | 3733.376 | 350 | -246.9573 | 0 | 144.5 | 10 | 0 | -103 | 7786.11 | 23.999
| 40098.1118 | 59.982 | 3736.2295 |  |  |  | 14.4012 | 20.3723 |  | 0 | 3799.6891 | 3766.8801 | 3786.918 | 3778.5625 | 3756.6847 | 633 | [6 empty] | 0 | 633 | -1054.9759 | [13 empty] | 40098.1118 | 59.982 | 3736.2295 | 350 | -246.9573 | 0 | 145 | 10 | 0 | -103 | 7787.1 | 14.4012
| 40098.1119 | 59.982 | 3736.2295 |  |  |  | 14.4012 | 18.2825 |  | 0 | 3797.5992 | 3766.8055 | 3786.944 | 3778.5625 | 3756.7381 | 633 | [6 empty] | 0 | 633 | -1054.9759 | [13 empty] | 40098.1119 | 59.982 | 3736.2295 | 350 | -246.9573 | 0 | 145 | 10 | 0 | -103 | 7787.1 | 14.4012
| 40098.1119 | 59.982 | 3736.2295 |  |  |  | 14.4012 | 16.924 |  | 0 | 3796.2408 | 3766.7313 | 3786.9665 | 3778.5625 | 3756.7912 | 633 | [6 empty] | 0 | 633 | -1054.9759 | [13 empty] | 40098.1119 | 59.982 | 3736.2295 | 350 | -246.9573 | 0 | 145 | 10 | 0 | -103 | 7787.1 | 14.4012
| 40098.1119 | 59.985 | 3733.1152 |  |  |  | 11.9995 | 15.2005 |  | 0 | 3794.5172 | 3766.6499 | 3786.9848 | 3778.5625 | 3756.844 | 633 | [6 empty] | 0 | 633 | -1110.5418 | [13 empty] | 40098.1119 | 59.985 | 3733.1152 | 350 | -246.9573 | 0 | 145.5 | 10 | 0 | -103 | 7788.09 | 11.9995
| 40098.1119 | 59.985 | 3733.1152 |  |  |  | 11.9995 | 14.0801 |  | 0 | 3793.3969 | 3766.5689 | 3787.0003 | 3778.5625 | 3756.8966 | 633 | [6 empty] | 0 | 633 | -1110.5418 | [13 empty] | 40098.1119 | 59.985 | 3733.1152 | 350 | -246.9573 | 0 | 145.5 | 10 | 0 | -103 | 7788.09 | 11.9995
| 40098.1119 | 59.985 | 3733.1152 |  |  |  | 11.9995 | 13.3519 |  | 0 | 3792.6687 | 3766.4883 | 3787.014 | 3778.5625 | 3756.949 | 633 | [6 empty] | 0 | 633 | -1110.5418 | [13 empty] | 40098.1119 | 59.985 | 3733.1152 | 350 | -246.9573 | 0 | 145.5 | 10 | 0 | -103 | 7788.09 | 11.9995
| 40098.112 | 59.989 | 3725.4587 |  |  |  | 8.8013 | 11.7592 |  | 0 | 3791.0759 | 3766.3897 | 3787.0237 | 3778.5625 | 3757.001 | 633 | [6 empty] | 0 | 633 | -1194.308 | [13 empty] | 40098.112 | 59.989 | 3725.4587 | 350 | -246.9573 | 0 | 146 | 10 | 0 | -103 | 7789.08 | 8.8013
| 40098.112 | 59.989 | 3725.4587 |  |  |  | 8.8013 | 10.7239 |  | 0 | 3790.0407 | 3766.2915 | 3787.031 | 3778.5625 | 3757.0529 | 633 | [6 empty] | 0 | 633 | -1194.308 | [13 empty] | 40098.112 | 59.989 | 3725.4587 | 350 | -246.9573 | 0 | 146 | 10 | 0 | -103 | 7789.08 | 8.8013
| 40098.112 | 59.989 | 3725.4587 |  |  |  | 8.8013 | 10.051 |  | 0 | 3789.3678 | 3766.1938 | 3787.0365 | 3778.5625 | 3757.1045 | 633 | [6 empty] | 0 | 633 | -1194.308 | [13 empty] | 40098.112 | 59.989 | 3725.4587 | 350 | -246.9573 | 0 | 146 | 10 | 0 | -103 | 7789.08 | 8.8013
| 40098.112 | 59.99 | 3720.9382 |  |  |  | 7.9987 | 9.3327 |  | 0 | 3788.6494 | 3766.0858 | 3787.0404 | 3778.5625 | 3757.1558 | 633 | [6 empty] | 0 | 633 | -1217.3513 | [13 empty] | 40098.112 | 59.99 | 3720.9382 | 350 | -254.5418 | 0 | 146.5 | 10 | 0 | -103 | 7790.07 | 7.9987
| 40098.1121 | 59.99 | 3720.9382 |  |  |  | 7.9987 | 8.8658 |  | 0 | 3788.1825 | 3765.9783 | 3787.0431 | 3778.5625 | 3757.2069 | 633 | [6 empty] | 0 | 633 | -1217.3513 | [13 empty] | 40098.1121 | 59.99 | 3720.9382 | 350 | -254.5418 | 0 | 146.5 | 10 | 0 | -103 | 7790.07 | 7.9987
| 40098.1121 | 59.99 | 3720.9382 |  |  |  | 7.9987 | 8.5623 |  | 0 | 3787.879 | 3765.8714 | 3787.0451 | 3778.5625 | 3757.2577 | 633 | [6 empty] | 0 | 633 | -1217.3513 | [13 empty] | 40098.1121 | 59.99 | 3720.9382 | 350 | -254.5418 | 0 | 146.5 | 10 | 0 | -103 | 7790.07 | 7.9987
| 40098.1121 | 60.001 | 3727.7542 |  |  |  | -0.79956 | 5.2856 |  | 0 | 3784.6024 | 3765.781 | 3787.0393 | 3778.5625 | 3757.3083 | 633 | [6 empty] | 0 | 633 | -1543.8886 | [13 empty] | 40098.1121 | 60.001 | 3727.7542 | 350 | -254.5418 | 0 | 147 | 10 | 0 | -103 | 7791.06 | -0.79956
| 40098.1121 | 60.001 | 3727.7542 |  |  |  | -0.79956 | 3.1558 |  | 0 | 3782.4726 | 3765.6911 | 3787.0285 | 3778.5625 | 3757.3587 | 633 | [6 empty] | 0 | 633 | -1543.8886 | [13 empty] | 40098.1121 | 60.001 | 3727.7542 | 350 | -254.5418 | 0 | 147 | 10 | 0 | -103 | 7791.06 | -0.79956
| 40098.1122 | 60.001 | 3727.7542 |  |  |  | -0.79956 | 1.7714 |  | 0 | 3781.0882 | 3765.6017 | 3787.0145 | 3778.5625 | 3757.4088 | 633 | [6 empty] | 0 | 633 | -1543.8886 | [13 empty] | 40098.1122 | 60.001 | 3727.7542 | 350 | -254.5418 | 0 | 147 | 10 | 0 | -103 | 7791.06 | -0.79956
| 40098.1122 | 60.006 | 3727.2314 |  |  |  | -4.8004 | -0.52871 |  | 0 | 3778.788 | 3765.5114 | 3786.9952 | 3778.5625 | 3757.4587 | 633 | [6 empty] | 0 | 633 | -1758.3676 | [13 empty] | 40098.1122 | 60.006 | 3727.2314 | 350 | -254.5418 | 0 | 147.5 | 10 | 0 | -103 | 7792.05 | -4.8004
| 40098.1122 | 60.006 | 3727.2314 |  |  |  | -4.8004 | -2.0238 |  | 0 | 3777.293 | 3765.4215 | 3786.9724 | 3778.5625 | 3757.5084 | 633 | [6 empty] | 0 | 633 | -1758.3676 | [13 empty] | 40098.1122 | 60.006 | 3727.2314 | 350 | -254.5418 | 0 | 147.5 | 10 | 0 | -103 | 7792.05 | -4.8004
| 40098.1122 | 60.006 | 3727.2314 |  |  |  | -4.8004 | -2.9956 |  | 0 | 3776.3211 | 3765.3321 | 3786.9474 | 3778.5625 | 3757.5578 | 633 | [6 empty] | 0 | 633 | -1758.3676 | [13 empty] | 40098.1122 | 60.006 | 3727.2314 | 350 | -254.5418 | 0 | 147.5 | 10 | 0 | -103 | 7792.05 | -4.8004
| 40098.1122 | 60.019 | 3726.0156 |  |  |  | -15.2008 | -7.2674 |  | 0 | 3772.0493 | 3765.2402 | 3786.9126 | 3778.5625 | 3757.607 | 633 | [6 empty] | 0 | 633 | -2752.3163 | [13 empty] | 40098.1122 | 60.019 | 3726.0156 | 350 | -254.5418 | 0 | 148 | 10 | 0 | -103 | 7793.04 | -15.2008
| 40098.1123 | 60.019 | 3726.0156 |  |  |  | -15.2008 | -10.0441 |  | 0 | 3769.2726 | 3765.1488 | 3786.8715 | 3778.5625 | 3757.6559 | 633 | [6 empty] | 0 | 633 | -2752.3163 | [13 empty] | 40098.1123 | 60.019 | 3726.0156 | 350 | -254.5418 | 0 | 148 | 10 | 0 | -103 | 7793.04 | -15.2008
| 40098.1123 | 60.019 | 3726.0156 |  |  |  | -15.2008 | -11.849 |  | 0 | 3767.4678 | 3765.0578 | 3786.8264 | 3778.5625 | 3757.7047 | 633 | [6 empty] | 0 | 633 | -2752.3163 | [13 empty] | 40098.1123 | 60.019 | 3726.0156 | 350 | -254.5418 | 0 | 148 | 10 | 0 | -103 | 7793.04 | -15.2008
| 40098.1123 | 60.026 | 3717.3325 |  |  |  | -20.8008 | -14.9821 |  | 0 | 3764.3347 | 3764.947 | 3786.7742 | 3778.5625 | 3757.7532 | 633 | [6 empty] | 0 | 633 | -3956.5368 | [13 empty] | 40098.1123 | 60.026 | 3717.3325 | 350 | -254.5418 | 0 | 148.5 | 10 | 0 | -103 | 7794.03 | -20.8008
| 40098.1123 | 60.026 | 3717.3325 |  |  |  | -20.8008 | -17.0186 |  | 0 | 3762.2981 | 3764.8368 | 3786.7175 | 3778.5625 | 3757.8015 | 633 | [6 empty] | 0 | 633 | -3956.5368 | [13 empty] | 40098.1123 | 60.026 | 3717.3325 | 350 | -254.5418 | 0 | 148.5 | 10 | 0 | -103 | 7794.03 | -20.8008
| 40098.1124 | 60.026 | 3717.3325 |  |  |  | -20.8008 | -18.3424 |  | 0 | 3760.9744 | 3764.7271 | 3786.6581 | 3778.5625 | 3757.8495 | 633 | [6 empty] | 0 | 633 | -3956.5368 | [13 empty] | 40098.1124 | 60.026 | 3717.3325 | 350 | -254.5418 | 0 | 148.5 | 10 | 0 | -103 | 7794.03 | -20.8008
| 40098.1124 | 60.029 | 3715.166 |  |  |  | -23.1995 | -20.0424 |  | 0 | 3759.2744 | 3764.6129 | 3786.595 | 3778.5625 | 3757.8974 | 633 | [6 empty] | 0 | 633 | -4869.0479 | [13 empty] | 40098.1124 | 60.029 | 3715.166 | 350 | -256.5716 | 0 | 149 | 10 | 0 | -103 | 7795.02 | -23.1995
| 40098.1124 | 60.029 | 3715.166 |  |  |  | -23.1995 | -21.1473 |  | 0 | 3758.1694 | 3764.4992 | 3786.5296 | 3778.5625 | 3757.945 | 633 | [6 empty] | 0 | 633 | -4869.0479 | [13 empty] | 40098.1124 | 60.029 | 3715.166 | 350 | -256.5716 | 0 | 149 | 10 | 0 | -103 | 7795.02 | -23.1995
| 40098.1124 | 60.029 | 3715.166 |  |  |  | -23.1995 | -21.8656 |  | 0 | 3757.4512 | 3764.3861 | 3786.4629 | 3778.5625 | 3757.9924 | 633 | [6 empty] | 0 | 633 | -4869.0479 | [13 empty] | 40098.1124 | 60.029 | 3715.166 | 350 | -256.5716 | 0 | 149 | 10 | 0 | -103 | 7795.02 | -23.1995
| 40098.1125 | 60.037 | 3710.1577 |  |  |  | -29.599 | -24.5723 |  | 0 | 3754.7445 | 3764.262 | 3786.3904 | 3778.5625 | 3758.0395 | 633 | [6 empty] | 0 | 633 | -12657.2961 | [13 empty] | 40098.1125 | 60.037 | 3710.1577 | 350 | -256.5716 | 0 | 149.5 | 10 | 0 | -103 | 7796.01 | -29.599
| 40098.1125 | 60.037 | 3710.1577 |  |  |  | -29.599 | -26.3316 |  | 0 | 3752.9851 | 3764.1385 | 3786.3141 | 3778.5625 | 3758.0865 | 633 | [6 empty] | 0 | 633 | -12657.2961 | [13 empty] | 40098.1125 | 60.037 | 3710.1577 | 350 | -256.5716 | 0 | 149.5 | 10 | 0 | -103 | 7796.01 | -29.599
| 40098.1125 | 60.037 | 3710.1577 |  |  |  | -29.599 | -27.4752 |  | 0 | 3751.8416 | 3764.0155 | 3786.2356 | 3778.5625 | 3758.1333 | 633 | [6 empty] | 0 | 633 | -12657.2961 | [13 empty] | 40098.1125 | 60.037 | 3710.1577 | 350 | -256.5716 | 0 | 149.5 | 10 | 0 | -103 | 7796.01 | -29.599
| 40098.1125 | 60.041 | 3704.5913 |  |  |  | -32.8003 | -29.339 |  | 0 | 3749.9778 | 3763.8805 | 3786.1532 | 3778.5625 | 3758.1798 | 633 | [6 empty] | 0 | 633 | -63334.7908 | [13 empty] | 40098.1125 | 60.041 | 3704.5913 | 350 | -256.5716 | 0 | 150 | 10 | 0 | -103 | 7797 | -32.8003
| 40098.1125 | 60.041 | 3704.5913 |  |  |  | -32.8003 | -30.5504 |  | 0 | 3748.7663 | 3763.746 | 3786.0684 | 3778.5625 | 3758.2261 | 633 | [6 empty] | 0 | 633 | -63334.7908 | [13 empty] | 40098.1125 | 60.041 | 3704.5913 | 350 | -256.5716 | 0 | 150 | 10 | 0 | -103 | 7797 | -32.8003
| 40098.1126 | 60.041 | 3704.5913 |  |  |  | -32.8003 | -31.3379 |  | 0 | 3747.9789 | 3763.6122 | 3785.9822 | 3778.5625 | 3758.2722 | 633 | [6 empty] | 0 | 633 | -63334.7908 | [13 empty] | 40098.1126 | 60.041 | 3704.5913 | 350 | -256.5716 | 0 | 150 | 10 | 0 | -103 | 7797 | -32.8003
| 40098.1126 | 60.043 | 3701.3164 |  |  |  | -34.3994 | -32.4094 |  | 0 | 3746.9073 | 3763.4716 | 3785.894 | 3778.5625 | 3758.3181 | 633 | [6 empty] | 0 | 633 | 63334.7908 | [13 empty] | 40098.1126 | 60.043 | 3701.3164 | 350 | -256.5716 | 0 | 150.5 | 10 | 0 | -103 | 7797.99 | -34.3994
| 40098.1126 | 60.043 | 3701.3164 |  |  |  | -34.3994 | -33.1059 |  | 0 | 3746.2108 | 3763.3316 | 3785.8046 | 3778.5625 | 3758.3638 | 633 | [6 empty] | 0 | 633 | 63334.7908 | [13 empty] | 40098.1126 | 60.043 | 3701.3164 | 350 | -256.5716 | 0 | 150.5 | 10 | 0 | -103 | 7797.99 | -34.3994
| 40098.1126 | 60.043 | 3701.3164 |  |  |  | -34.3994 | -33.5586 |  | 0 | 3745.7581 | 3763.1922 | 3785.7146 | 3778.5625 | 3758.4093 | 633 | [6 empty] | 0 | 633 | 63334.7908 | [13 empty] | 40098.1126 | 60.043 | 3701.3164 | 350 | -256.5716 | 0 | 150.5 | 10 | 0 | -103 | 7797.99 | -34.3994
| 40098.1127 | 60.046 | 3699.7261 |  |  |  | -36.8011 | -34.6935 |  | 0 | 3744.6232 | 3763.0499 | 3785.6225 | 3778.5625 | 3758.4546 | 633 | [6 empty] | 0 | 633 | 15818.6036 | [13 empty] | 40098.1127 | 60.046 | 3699.7261 | 350 | -256.5716 | 0 | 151 | 10 | 0 | -103 | 7798.98 | -36.8011
| 40098.1127 | 60.046 | 3699.7261 |  |  |  | -36.8011 | -35.4312 |  | 0 | 3743.8856 | 3762.9082 | 3785.5291 | 3778.5625 | 3758.4997 | 633 | [6 empty] | 0 | 633 | 15818.6036 | [13 empty] | 40098.1127 | 60.046 | 3699.7261 | 350 | -256.5716 | 0 | 151 | 10 | 0 | -103 | 7798.98 | -36.8011
| 40098.1127 | 60.046 | 3699.7261 |  |  |  | -36.8011 | -35.9107 |  | 0 | 3743.4061 | 3762.7672 | 3785.4351 | 3778.5625 | 3758.5446 | 633 | [6 empty] | 0 | 633 | 15818.6036 | [13 empty] | 40098.1127 | 60.046 | 3699.7261 | 350 | -256.5716 | 0 | 151 | 10 | 0 | -103 | 7798.98 | -36.8011
| 40098.1127 | 60.043 | 3696.8645 |  |  |  | -34.3994 | -35.3817 |  | 0 | 3743.935 | 3762.6204 | 3785.3427 | 3778.5625 | 3758.5893 | 633 | [6 empty] | 0 | 633 | 63334.7908 | [13 empty] | 40098.1127 | 60.043 | 3696.8645 | 350 | -258.3726 | 0 | 151.5 | 10 | 0 | -103 | 7799.97 | -34.3994
| 40098.1128 | 60.043 | 3696.8645 |  |  |  | -34.3994 | -35.0379 |  | 0 | 3744.2788 | 3762.4743 | 3785.2514 | 3778.5625 | 3758.6338 | 633 | [6 empty] | 0 | 633 | 63334.7908 | [13 empty] | 40098.1128 | 60.043 | 3696.8645 | 350 | -258.3726 | 0 | 151.5 | 10 | 0 | -103 | 7799.97 | -34.3994
| 40098.1128 | 60.043 | 3696.8645 |  |  |  | -34.3994 | -34.8144 |  | 0 | 3744.5023 | 3762.3288 | 3785.1611 | 3778.5625 | 3758.678 | 633 | [6 empty] | 0 | 633 | 63334.7908 | [13 empty] | 40098.1128 | 60.043 | 3696.8645 | 350 | -258.3726 | 0 | 151.5 | 10 | 0 | -103 | 7799.97 | -34.3994
Note on L13: TC allowable range 0.050 to 1.000 with 1.0 turning filter off. Beginning Target slope should align with Actual slope.

## Graph 20 to 52s
60.0420

## Form 1 Summary Data
[6 empty] | Interconnection Performance | [9 empty] | Value A Data |  | BA Performance | [8 empty] | Value B |  | 12 to 24 second Average Period Evaluation | [11 empty] | Value B | 18 to 30 second Average Period Evaluation | [12 empty] | Value B | 20 to 40 second Average Period Evaluation | [12 empty] | Value B | 18 to 52 second Average Period Evaluation | [12 empty] | Value B | 20 to 52 second Average Period Evaluation
[18 empty] | JOU | Non- |  |  | Transferred | Contingent | [5 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent
Date | A Point | FPointA | A Value | t(0) Time | C Value | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias
| Time | Hz | Hz |  | Hz | 12 to 24 sec | 12 to 24 sec | 18 to 30 sec | 18 to 30 sec | 20 to 40 sec | 20 to 40 sec | 18 to 52 sec | 18 to 52 sec | 20 to 52 sec | 20 to 52 sec |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting
[6 empty] | Average | Average | Average | Average | Average | Average | Average | Average | Average | Average | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR
[6 empty] | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Hz | MW | MW | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW | Hz | MW | MW | MW | MW | MW | MW | MW | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | P.U. | P.U. | P.U. | MW | MW | MW | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | P.U. | P.U. | P.U. | MW | MW | MW | Hz | MW | MW | MW | MW | MW | MW | MW | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW | Hz | MW | MW | MW | MW | MW | MW | MW | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW
2009-10-12 02:27 | 40098.1023 | 60.041 | 60.042 | 40098.1024 | 59.869 | 59.8797 | -390.3519 | 59.8834 | -399.2319 | 59.888 | -409.3538 | 59.8876 | -410.1357 | 59.888 | -411.2764 | 60.042 | 3645.0407 | 350 | -165.4764 | 0 | 76.0625 | -4.2 | 15 | -103 | 7650.6038 | -43.2598 | 59.8797 | 3768.2286 | 335 | -206.4591 | 0 | 78.1429 | 12.0286 | 0 | 1.3546 | 0.94885 | 0.89944 | -103 | 7631.7143 | 123.8941 | 59.8834 | 3780.4202 | 335 | -206.4591 | 0 | 78.6429 | 11.6572 | 0 | 1.4814 | 1.0672 | 0.89944 | -103 | 7630.5714 | 120.0694 | 59.8873 | 3785.2644 | 335 | -208.6395 | 0 | 79.1818 | 11.2728 | 0 | 1.5737 | 1.1328 | 0.89944 | -103 | 7630.6364 | 116.1096 | 59.8876 | 3787.5342 | 335 | -209.3906 | 0 | 79.5833 | 11.2445 | 0 | 1.598 | 1.1533 | 0.89944 | -103 | 7631.5 | 115.8183 | 59.888 | 3788.7895 | 335 | -209.563 | 0 | 79.6765 | 11.2001 | 0 | 1.6138 | 1.1668 | 0.89944 | -103 | 7631.5294 | 115.3607