## SOL
| DBH Notes: | 1st Pass. Looking in http://www.nerc.com/pa/Stand/Reliability%20Standards%20Complete%20Set/RSCompleteSet.pdf for "system operating" |  |  |  | http://www.nerc.com/pa/Stand/Reliability%20Standards%20Complete%20Set/RSCompleteSet.pdf
Pending future enforcement - Orange Rows
Does the proposed SOL definition work in the context of this standard? | Standard | Requirement ID | Page(s) | Requirement Details | Corresponding Measure | VSL | Needs to be Modified? | Modification Description | Notes
yes | CIP-002-5.1a | Guidelines & Tech. Basis | 21 | Bullet item under Managing Contstraints: Identify and monitor SOL’s & IROL’s (TOP, RC) | n/a | n/a | no | n/a
yes | CIP-002-5.1a | Guidelines & Tech. Basis | 25 | Criterion 2.6 includes BES Cyber Systems for those Generation Facilities that have been identified as critical to the derivation of IROLs and their associated contingencies, as specified by FAC-014-2, Establish and Communicate System Operating Limits, R5.1.1 and R5.1.3. | n/a | n/a | yes - clean up (not critical) | need to change the reference to the revised FAC standard and associated requirements | Addressed by proposed modifications in CIP-002-6
yes | CIP-002-5.1a | Guidelines & Tech. Basis | 28 | Criterion 2.6 includes BES Cyber Systems for those Generation Facilities that have been identified as critical to the derivation of IROLs and their associated contingencies, as specified by FAC-014-2, Establish and Communicate System Operating Limits, R5.1.1 and R5.1.3. | n/a | n/a | yes - clean up (not critical) | need to change the reference to the revised FAC standard and associated requirements | Addressed by proposed modifications in CIP-002-6
yes | CIP-002-5.1a | Attachment 1 | 12 | The Reliability Coordinator shall review Transmission outages and work with the Transmission Operator(s) to see if it’s possible to return to service any Transmission Elements that may relieve the loading on System Operating Limits (SOLs) or Interconnection Reliability Operating Limits (IROLs). | n/a | n/a | no | n/a
yes | EOP-004-3 | Attachment 1 | 10 of 22 | Event Type: IROL Violation (all Interconnections) or SOL Violation for Major WECC Transfer Paths (WECC only) Threshold for Reporting: Operate outside the IROL for time greater than IROL Tv (all Interconnections) or Operate outside the SOL for more than 30 minutes for Major WECC Transfer Paths (WECC only). | n/a | n/a | yes - clean up (not critical) | Remove reference to Major WECC Path SOL violations. TOP-007-WECC-1 was retired on April 1. Not related to FAC SDT project.
yes | EOP-004-3 | Attachment 2 | 12 | There is a checkbox for IROL Violation (all Interconnections) or SOL Violation for Major WECC Transfer Paths (WECC only) | n/a | n/a | yes - clean up (not critical) | Remove reference to Major WECC Path SOL violations. TOP-007-WECC-1 was retired on April 1. Not related to FAC SDT project.
yes | EOP-011-1 | Attachment 1 | 12-13 | See EOP-011-1 tab | n/a | n/a | no | n/a
yes | FAC-008-3 | Purpose | 1 | A Facility Rating is essential for the determination of System Operating Limits. | n/a | n/a | no | n/a | IF a Facility Rating is an SOL, then by default, it is essential for determining SOLs. This statement is not necessary in the purpose of FAC-008, but it does no harm.
yes | FAC-013-2 | R1.2 | 1 | A statement that the assessment shall respect known System Operating Limits (SOLs). | n/a | n/a | yes | Needs to remove the reference to SOLs since this requirement is applicable to PCs. Revision could reference TPL performance table. | Addressed by proposed modifications in FAC-013-3
yes | FAC-501-WECC-1 | R.1. | 1 | Transmission Owners shall have a TMIP detailing their inspection and maintenance requirements that apply to all transmission facilities necessary for System Operating Limits associated with each of the transmission paths identified in table titled “Major WECC Transfer Paths in the Bulk Electric System.” | n/a | n/a | yes - clean up (not critical) | Remove reference to Major WECC Path SOL violations. TOP-007-WECC-1 was retired o April 1. Not related to FAC SDT project.
yes | FAC-501-WECC-1 | Attachment 1 | 4 | 1) A list of Facilities and associated Elements necessary to maintain the SOL for the transfer paths identified in the most current Table titled “Major WECC Transfer Paths in the Bulk Electric System;” |  |  | yes - clean up (not critical) | Remove reference to Major WECC Path SOL violations. TOP-007-WECC-1 was retired o April 1. Not related to FAC SDT project.
yes | IRO-002-4 | R3. | 1,2, 4 | Each Reliability Coordinator shall monitor Facilities, the status of Special Protection Systems, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | Each Reliability Coordinator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it has monitored Facilities, the status of Special Protection Systems, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | The Reliability Coordinator did not monitor Facilities, the status of Special Protection Systems, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | IRO-002-4 | Guidelines & Tech. Basis | 8 (multiple) | See IRO-002-4 tab |  |  | no | n/a
yes | IRO-002-5 | R5. | 2 | Each Reliability Coordinator shall monitor Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | Each Reliability Coordinator shall have, and provide upon request, evidence that could include, but is not limited to, Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it has monitored Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | The Reliability Coordinator did not monitor Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | IRO-006-5 | Purpose | 1 | To ensure coordinated action between Interconnections when implementing Interconnection-wide transmission loading relief procedures to prevent or manage potential or actual SOL and IROL exceedances to maintain reliability of the bulk electric system. | n/a | n/a | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | IRO-006-EAST-2 | Purpose | 1 | To coordinate action between Reliability Coordinators within the Eastern Interconnection when implementing transmission loading relief procedures (TLR) for the Eastern Interconnection to prevent or manage potential or actual System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) exceedances to maintain reliability of the Bulk Electric System (BES). | n/a | n/a | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | IRO-006-EAST-2 | R1. | 1 | Each Reliability Coordinator that initiates the Eastern Interconnection TLR procedure to prevent or mitigate an SOL or IROL exceedance shall identify the TLR level and the congestion management actions to be implemented, and shall update this information at least every clock hour (except TLR-1) after initiation up to and including the hour when the TLR level has been identified as TLR Level 0.1 | n/a | n/a | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | IRO-006-TRE-1 | Purpose | 1 | To provide and execute transmission loading relief procedures that can be used to mitigate SOL or IROL exceedances for the purpose of maintaining reliable operation of the bulk electric system in the ERCOT Region. | n/a | n/a | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | IRO-006-TRE-1 | R1. | 1 | The RC shall have procedures to identify and mitigate exceedances of identified Interconnection Reliability Operating Limits (IROL) and System Operating Limits (SOL) that will not be resolved by the automatic actions of the ERCOT Nodal market operations system. | The RC shall provide evidence including documentation of procedures to identify and mitigate exceedances of identified IROLs and SOLs to demonstrate compliance with Requirement R1. | The RC did not have procedures to identify and mitigate exceedances of identified IROLs and SOLs. | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | IRO-006-TRE-1 | R2. | 1 | The RC shall act to identify and mitigate exceedances of identified Interconnection Reliability Operating Limits and System Operating Limits that will not be resolved by the automatic actions of the ERCOT Nodal market operations system, in accordance with the procedures required by R1. | To demonstrate compliance with Requirement R2, the RC shall provide evidence, such as system logs, voice recordings, or operating messages that shows that it acted to identify and to mitigate exceedances of IROLs and SOLs in accordance with the procedures required by R1. | The RC failed to follow its procedures in identifying and mitigating an exceedance of an SOL. | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | IRO-008-2 | R1. | 1, 5 | Each Reliability Coordinator shall perform an Operational Planning Analysis that will allow it to assess whether the planned operations for the next-day will exceed System Operating Limits (SOLs) and Interconnection Operating Reliability Limits (IROLs) within its Wide Area. | n/a | The Reliability Coordinator did not perform an Operational Planning Analysis allowing it to assess whether its planned operations for the next-day within its Wide Area will exceed any of its System Operating Limits (SOLs) and Interconnection Operating Reliability Limits (IROLs). | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | IRO-008-2 | R2. | 1, 5 | Each Reliability Coordinator shall have a coordinated Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) exceedances identified as a result of its Operational Planning Analysis as performed in Requirement R1 while considering the Operating Plans for the next-day provided by its Transmission Operators and Balancing Authorities. | Each Reliability Coordinator shall have evidence that it has a coordinated Operating Plan for next-day operations to address potential System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1 while considering the Operating Plans for the next-day provided by its Transmission Operators and Balancing Authorities. Such evidence could include but is not limited to plans for precluding operating in excess of each SOL and IROL that were identified as a result of the Operational Planning Analysis. | The Reliability Coordinator did not have a coordinated Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) exceedances identified as a result of its Operational Planning Analysis as performed in Requirement R1 while considering the Operating Plans for the nextday provided by its Transmission Operators and Balancing Authorities. | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | IRO-008-2 | R5. | 2, 7-8 | Each Reliability Coordinator shall notify impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the results of a Realtime Assessment indicate an actual or expected condition that results in, or could result in, a System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area. | Each Reliability Coordinator shall make available upon request, evidence that it informed impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, of its actual or expected operations that result in, or could result in, a System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area. | Multiple levels | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | IRO-008-2 | R6. | 2-3, 9-11 | Each Reliability Coordinator shall notify impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 has been prevented or mitigated. | Each Reliability Coordinator shall make available upon request, evidence that it informed impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 has been prevented or mitigated. | Multiple levels | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | IRO-008-2 | F. Associated Documents | 12 | various (Same exact language is found in the Associated Documents section of IR0-008-2, IRO-014-3, TOP-001-3, TOP-002-4) See Associated Docs tab. |  |  | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | MOD-001-2 | R1.1 | 2-3 | Each methodology shall describe the method used to account for the following limitations in both the pre‐ and post‐contingency state: 1.1.1 Facility ratings; 1.1.2 System voltage limits; 1.1.3 Transient stability limits; 1.1.4 Voltage stability limits; and 1.1.5 Other System Operating Limits (SOLs). | A description of the method used to account for the limits specified in part 1.1. Methods of accounting for these limits may include, but are not limited to, one or more of the following: o TFC or TTC being determined by one or more limits. o Simulation being used to find the maximum TFC or TTC that remains within the limit. o The application of a distribution factor in determining if a limit affects the TFC or TTC value. o Monitoring a subset of limits and a statement that those limits are expected to produce the most severe results. o A statement that the monitoring of a select limit(s) results in the TFC or TTC not exceeding another set of limits. o A statement that one or more of those limits are not applicable to the TFC or TTC determination. | Multiple levels | no | n/a | While the proposed definition of SOL dos not allow for "Other SOLs" as listed in R1.1.5, this requirement does not cause a problem. It will just never be used.
yes | MOD-028-2 | R6.1. | 4 | Determine the incremental Transfer Capability for each ATC Path by increasing generation and/or decreasing load within the source Balancing Authority area and decreasing generation and/or increasing load within the sink Balancing Authority area until either: - A System Operating Limit is reached on the Transmission Service Provider’s system, or - A SOL is reached on any other adjacent system in the Transmission model that is not on the study path and the distribution factor is 5% or greater1. | n/a | n/a | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | MOD-029-2a | R3. | 3,6 | Each Transmission Operator shall establish the TTC at the lesser of the value calculated in R2 or any System Operating Limit (SOL) for that ATC Path. | Each Transmission Operator shall provide evidence that it used the lesser of the calculated TTC or the SOL as the TTC, by producing: 1) all values calculated pursuant to R2 for each ATC Path, 2) Any corresponding SOLs for those ATC Paths, and 3) the TTC set by the Transmission Operator and given to the Transmission Service Provider for use in R7and R8 for each ATC Path. | n/a | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | MOD-030-3 | R.2.4. | 3 | Establish the TFC of each of the defined Flowgates as equal to: - For thermal limits, the System Operating Limit (SOL) of the Flowgate. - For voltage or stability limits, the flow that will respect the SOL of the Flowgate. | n/a | n/a | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | PER-004-2 | R2. | 1 | Reliability Coordinator operating personnel shall place particular attention on SOLs and IROLs and inter-tie facility limits. The Reliability Coordinator shall ensure protocols are in place to allow Reliability Coordinator operating personnel to have the best available information at all times. | NONE | [MULTIPLE LEVELS] Reliability Coordinator operating personnel did not place particular attention on X% or less of the SOLs or IROLs or inter-tie facility limits. | no | n/a
yes | PER-005-2 | Guidelines & Tech. Basis | 12 | Rationales for R5. | n/a | n/a | no | n/a
yes | PRC-002-2 | R5., R5.1 & R5.1.2 | 3 | [R5.] Each Responsible Entity shall: [R5.1] Identify BES Elements for which dynamic Disturbance recording (DDR) data is required, including the following: [R5.1.2] Any one BES Element that is part of a stability (angular or voltage) related System Operating Limit (SOL). | n/a | n/a | no | n/a
yes | PRC-002-2 | Guidelines for R5 | 33 | Permanent System Operating Limits (SOLs) are used to operate the System within reliable and secure limits. In particular, SOLs related to angular or voltage stability have a significant impact on BES reliability and performance. Therefore, at least one BES Element of an SOL should be monitored. | n/a | n/a | no | n/a
yes | PRC-004-WECC-2 | R2.3.2.2. | 2-3 | Transmission Operators shall adjust the SOL and operate the facilities within established limits. | The Generator Owners and Transmission Operators shall have documentation describing all actions taken that adjusted generation or SOLs and operated facilities within established limits. | The Transmission Operator and Generator Owner did not adjust generation to a reliable operating level, adjust the SOL and operate the facilities within established limits or implement other compliance measures for the Protection System or RAS that misoperated as required within X hours but did perform the requirements within Y hours. | no | n/a
yes | PRC-010-2 | Guidelines & Tech. Basis | 29 | Rationale for R8 - Requirement R8 supports the integrated and coordinated approach to UVLS programs directed by Paragraph 1509 of Order No. 693 by requiring that UVLS Program data be shared with neighboring Planning Coordinators and Transmission Planners within a reasonable time period. Requests for the database should also be fulfilled for those functional entities that have a reliability need for the data (such as the Transmission Operators that develop System Operating Limits and Reliability Coordinators that develop Interconnection Reliability Operating Limits). | n/a | n/a | no | n/a
yes | PRC-026-1 | R1. | 3 | Each Planning Coordinator shall, at least once each calendar year, provide notification of each generator, transformer, and transmission line BES Element in its area that meets one or more of the following criteria, if any, to the respective Generator Owner and Transmission Owner: Criteria: 1. Generator(s) where an angular stability constraint exists that is addressed by a System Operating Limit (SOL) or a Remedial Action Scheme (RAS) and those Elements terminating at the Transmission station associated with the generator(s). 2. An Element that is monitored as part of an SOL identified by the Planning Coordinator’s methodology1 based on an angular stability constraint. 1 NERC Reliability Standard FAC-014-2 – Establish and Communicate System Operating Limits, Requirement R3. | Each Planning Coordinator shall have dated evidence that demonstrates notification of the generator, transformer, and transmission line BES Element(s) that meet one or more of the criteria in Requirement R1, if any, to the respective Generator Owner and Transmission Owner. Evidence may include, but is not limited to, the following documentation: emails, facsimiles, records, reports, transmittals, lists, or spreadsheets. | n/a | yes | Address reference to SOLs identified by the PC's SOL Methodology. Also address reference to revised FAC-014 standard. | Addressed by proposed modifications in PRC-026-2
yes | PRC-026-1 | Guidelines & Tech. Basis | 16-17 | R1 Criterion - The first criterion involves generator(s) where an angular stability constraint exists that is addressed by a System Operating Limit (SOL) or a Remedial Action Scheme (RAS) and those Elements terminating at the Transmission station associated with the generator(s). For example, a scheme to remove generation for specific conditions is implemented for a four-unit generating plant (1,100 MW). Two of the units are 500 MW each; one is connected to the 345 kV system and one is connected to the 230 kV system. The Transmission Owner has two 230 kV transmission lines and one 345 kV transmission line all terminating at the generating facility as well as a 345/230 kV autotransformer. The remaining 100 MW consists of two 50 MW combustion turbine (CT) units connected to four 66 kV transmission lines. The 66 kV transmission lines are not electrically joined to the 345 kV and 230 kV transmission lines at the plant site and are not subject to the operating limit or RAS. A stability constraint limits the output of the portion of the plant affected by the RAS to 700 MW for an outage of the 345 kV transmission line. The RAS trips one of the 500 MW units to maintain stability for a loss of the 345 kV transmission line when the total output from both 500 MW units is above 700 MW. For this example, both 500 MW generating units and the associated generator step-up (GSU) transformers would be identified as Elements meeting this criterion. The 345/230 kV autotransformer, the 345 kV transmission line, and the two 230 kV transmission lines would also be identified as Elements meeting this criterion. The 50 MW combustion turbines and 66 kV transmission lines would not be identified pursuant to Criterion 1 because these Elements are not subject to an operating limit or RAS and do not terminate at the Transmission station associated with the generators that are subject to the SOL or RAS. |  |  | yes | Address reference to SOLs identified by the PC's SOL Methodology. Also address reference to revised FAC-014 standard. | Addressed by proposed modifications in PRC-026-2
yes | PRC-026-1 | Guidelines & Tech. Basis | 17 | R1 Criterion - The second criterion involves Elements that are monitored as a part of an established System Operating Limit (SOL) based on an angular stability limit regardless of the outage conditions that result in the enforcement of the SOL. For example, if two long parallel 500 kV transmission lines have a combined SOL of 1,200 MW, and this limit is based on angular instability resulting from a fault and subsequent loss of one of the two lines, then both lines would be identified as Elements meeting the criterion. |  |  | yes | Address reference to SOLs identified by the PC's SOL Methodology. Also address reference to revised FAC-014 standard. | Addressed by proposed modifications in PRC-026-2
yes | TOP-001-3 | R10. | 4 | Each Transmission Operator shall perform the following as necessary for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, SCADA data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized status, voltages, and flow data for Facilities and the status of Special Protection Systems as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | n/a | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | TOP-001-3 | R14. | 5 | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. | Each Transmission Operator shall have evidence that it initiated its Operating Plan for mitigating SOL exceedances identified as part of its Real-time monitoring or Real-time Assessments. This evidence could include but is not limited to dated computer logs showing times the Operating Plan was initiated, dated checklists, or other evidence. | The Transmission Operator did not initiate its Operating Plan for mitigating a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | TOP-001-3 | R15. | 5 | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. | Each Transmission Operator shall make available evidence that it informed its Reliability Coordinator of actions taken to return the System to within limits when a SOL was exceeded. Such evidence could include but is not limited to dated operator logs, voice recordings or transcripts of voice recordings, or dated computer printouts. If such a situation has not occurred, the Transmission Operator may provide an attestation. | The Transmission Operator did not inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL had been exceeded. | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | TOP-001-3 | R18. | 5-6 | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to operator logs, voice recordings, electronic communications, or equivalent evidence that will be used to determine if it operated to the most limiting parameter in instances where there is a difference in SOLs. | The Transmission Operator failed to operate to the most limiting parameter in instances where there was a difference in SOLs. | no | n/a
yes | TOP-001-3 | Guidelines & Tech. Basis | 7, 19 | See TOP-001-3 tab | n/a | n/a | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | TOP-001-4 | R10. | 4-5 | [R10.] Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | n/a | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | TOP-001-4 | R14 | 5 | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment | Each Transmission Operator shall have evidence that it initiated its Operating Plan for mitigating SOL exceedances identified as part of its Real-time monitoring or Real-time Assessments. This evidence could include but is not limited to dated computer logs showing times the Operating Plan was initiated, dated checklists, or other evidence | The Transmission Operator did not initiate its Operating Plan for mitigating a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | TOP-001-4 | R15 | 6 | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded | The Transmission Operator did not inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL had been exceeded. | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | TOP-001-4 | R18. | 6 | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to operator logs, voice recordings, electronic communications, or equivalent evidence that will be used to determine if it operated to the most limiting parameter in instances where there is a difference in SOLs. | The Transmission Operator failed to operate to the most limiting parameter in instances where there was a difference in SOLs. | no | n/a
yes | TOP-001-4 | C. Compliance | 9 | Each Transmission Operator shall retain evidence and that it initiated its Operating Plan to mitigate a SOL exceedance as specified in Requirement R14 and Measurement M14 for three calendar years. | n/a | n/a | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | TOP-001-4 | Guidelines & Tech. Basis | 24 | See TOP-001-4 tab | n/a | n/a | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | TOP-002-4 | R1. | 1,4 | Each Transmission Operator shall have an Operational Planning Analysis that will allow it to assess whether its planned operations for the next day within its Transmission Operator Area will exceed any of its System Operating Limits (SOLs). | n/a | The Transmission Operator did not have an Operational Planning Analysis allowing it to assess whether its planned operations for the next day within its Transmission Operator Area exceeded any of its System Operating Limits (SOLs). | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | TOP-002-4 | R2. | 1,4 | Each Transmission Operator shall have an Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) exceedances identified as a result of its Operational Planning Analysis as required in Requirement R1. | Each Transmission Operator shall have evidence that it has an Operating Plan to address potential System Operating Limits (SOLs) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1. Such evidence could include but it is not limited to plans for precluding operating in excess of each SOL that was identified as a result of the Operational Planning Analysis. | The Transmission Operator did not have an Operating Plan to address potential System Operating Limit (SOL) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1. | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | TOP-002-4 | Guidelines & Tech. Basis | 10 | See TOP-002-4 tab | n/a | n/a | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.
yes | VAR-001-4.1 | R1. | 2 | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. | n/a | References to SOLs is included in the VSLs for R2 and R3. | no | n/a
yes | VAR-001-4.1 | Guidelines & Tech. Basis | 13 | See VAR-001-4.1 tab | n/a | n/a | yes - clean up (not critical) | Rationale references current SOL definition. Need to fix based on new definition.
yes | Burden | Glossary of Terms | n/a | Operation of the Bulk Electric System that violates or is expected to violate a System Operating Limit or Interconnection Reliability Operating Limit in the Interconnection, or that violates any other NERC, Regional Reliability Organization, or local operating reliability standards or criteria. | n/a | n/a | no | n/a | The term "Burden" is used once in the body of Reliability Standards. BAL-005-0.2b requirement R3 states, "A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas." This standard has been replaced by BAL-005-1 which is pending regulatory approval.
yes | Constrained Facility | Glossary of Terms | n/a | A transmission facility (line, transformer, breaker, etc.) that is approaching, is at, or is beyond its System Operating Limit or Interconnection Reliability Operating Limit. | n/a | n/a | no | n/a | The term "Constrained Facility" is not used in the current body of Reliability Standards
yes | Interconnection Reliability Operating Limit | Glossary of Terms | n/a | A System Operating Limit that, if violated, could lead to instability, uncontrolled separation, or Cascading outages that adversely impact the reliability of the Bulk Electric System. | n/a | n/a | no | n/a
yes | Operations Support Personnel | Glossary of Terms | n/a | Individuals who perform current day or next day outage coordination or assessments, or who determine SOLs, IROLs, or operating nomograms,1 in direct support of Real-time operations of the Bulk Electric System. | n/a | n/a | no | n/a
yes | Total Flowgate Capability | Glossary of Terms | n/a | The maximum flow capability on a Flowgate, is not to exceed its thermal rating, or in the case of a flowgate used to represent a specific operating constraint (such as a voltage or stability limit), is not to exceed the associated System Operating Limit. | n/a | n/a | no | n/a | BES performance criteria specified in FAC-011-4 Requirement R6 correlates to SOL exceedance through FAC-014-3 Requirement R7.

## EOP-011-1
2.4 Evaluating and mitigating Transmission limitations. The Reliability Coordinator shall review Transmission outages and work with the Transmission Operator(s) to see if it’s possible to return to service any Transmission Elements that may relieve the loading on System Operating Limits (SOLs) or Interconnection Reliability Operating Limits (IROLs). 3.3 Reevaluating and revising SOLs and IROLs. The Reliability Coordinator shall evaluate the risks of revising SOLs and IROLs for the possibility of delivery of energy to the energy deficient Balancing Authority. Reevaluation of SOLs and IROLs shall be coordinated with other Reliability Coordinators and only with the agreement of the Transmission Operator whose Transmission Owner (TO) equipment would be affected. SOLs and IROLs shall only be revised as long as an EEA 3 condition exists, or as allowed by the Transmission Owner whose equipment is at risk. The following are minimum requirements that must be met before SOLs or IROLs are revised: 3.4 Returning to pre-Emergency conditions. Whenever energy is made available to an energy deficient Balancing Authority such that the Systems can be returned to its pre-Emergency SOLs or IROLs condition, the energy deficient Balancing Authority shall request the Reliability Coordinator to downgrade the alert level.

## IRO-002-4
During development of this standard, text boxes were embedded within the standard to explain the rationale for various parts of the standard. Upon BOT approval, the text from the rationale text boxes was moved to this section. Changes made to the proposed definitions were made in order to respond to issues raised in NOPR paragraphs 55, 73, and 74 dealing with analysis of SOLs in all time horizons, questions on Protection Systems and Special Protection Systems in NOPR paragraph 78, and recommendations on phase angles from the SW Outage Report (recommendation 27). The intent of such changes is to ensure that Real-time Assessments contain sufficient details to result in an appropriate level of situational awareness. Some examples include: 1) analyzing phase angles which may result in the implementation of an Operating Plan to adjust generation or curtail transactions so that a Transmission facility may be returned to service, or 2) evaluating the impact of a modified Contingency resulting from the status change of a Special Protection Scheme from enabled/in-service to disabled/out-of-service. Rationale for R2: Requirement R2 from IRO-002-3 has been deleted because approved EOP-008-1, Requirement R1, part 1.6.2 addresses redundancy and back-up concerns for outages of analysis tools. New Requirement R4 has been added to address NOPR paragraphs 96 and 97: “…As we explain above, the reliability coordinator’s obligation to monitor SOLs is important to reliability because a SOL can evolve into an IROL during deteriorating system conditions, and for potential system conditions such as this, the reliability coordinator’s monitoring of SOLs provides a necessary backup function to the transmission operator….”

## Associated Docs
Operating Plan - An Operating Plan includes general Operating Processes and specific Operating Procedures. It may be an overview document which provides a prescription for an Operating Plan for the next-day, or it may be a specific plan to address a specific SOL or IROL exceedance identified in the Operational Planning Analysis (OPA). Consistent with the NERC definition, Operating Plans can be general in nature, or they can be specific plans to address specific reliability issues. The use of the term Operating Plan in the revised TOP/IRO standards allows room for both. An Operating Plan references processes and procedures, including electronic data exchange, which are available to the System Operator on a daily basis to allow the operator to reliably address conditions which may arise throughout the day. It is valid for tomorrow, the day after, and the day after that. Operating Plans should be augmented by temporary operating guides which outline prevention/mitigation plans for specific situations which are identified day-to-day in an OPA or a Real-time Assessment (RTA). As the definition in the Glossary of Terms states, a restoration plan is an example of an Operating Plan. It contains all the overarching principles that the System Operator needs to work his/her way through the restoration process. It is not a specific document written for a specific blackout scenario but rather a collection of tools consisting of processes, procedures, and automated software systems that are available to the operator to use in restoring the system. An Operating Plan can in turn be looked upon in a similar manner. It does not contain a prescription for the specific set-up for tomorrow but contains a treatment of all the processes, procedures, and automated software systems that are at the operator’s disposal. The existence of an Operating Plan, however, does not preclude the need for creating specific action plans for specific SOL or IROL exceedances identified in the OPA. When a Reliability Coordinator performs an OPA, the analysis may reveal instances of possible SOL or IROL exceedances for pre- or post-Contingency conditions. In these instances, Reliability Coordinators are expected to ensure that there are plans in place to prevent or mitigate those SOLs or IROLs, should those operating conditions be encountered the next day. The Operating Plan may contain a description of the process by which specific prevention or mitigation plans for day-to-day SOL or IROL exceedances identified in the OPA are handled and communicated. This approach could alleviate any potential administrative burden associated with perceived requirements for continual day-to-day updating of “the Operating Plan document” for compliance purposes.

## TOP-001-3
Compliance/Data Retention Each Transmission Operator shall retain evidence for three calendar years of any occasion in which it has exceeded an identified IROL and its associated IROL Tv as specified in Requirement R12 and Measure M12 and that it initiated its Operating Plan to mitigate a SOL exceedance as specified in Requirement R14 and Measurement M14.
TOP-001-3 also contains the same write-up as seen in the Associated Docs tab
Rationale for Requirement R14: The original Requirement R8 was deleted and original Requirements R9 and R11 were revised in order to respond to NOPR paragraph 42 which raised the issue of handling all SOLs and not just a sub-set of SOLs. The SDT has developed a white paper on SOL exceedances that explains its intent on what needs to be contained in such an Operating Plan. These Operating Plans are developed and documented in advance of Real-time and may be developed from Operational Planning Assessments required per proposed TOP-002-4 or other assessments. Operating Plans could be augmented by temporary operating guides which outline prevention/mitigation plans for specific situations which are identified day-to-day in an Operational Planning Assessment or a Real-time Assessment. The intent is to have a plan and philosophy that can be followed by an operator.
Rationale for Requirement R18: Moved from approved IRO-005-3.1a, Requirement R10. Transmission Service Provider, Distribution Provider, Load-Serving Entity, Generator Operator, and Purchasing-Selling Entity are deleted as those entities will receive instructions on limits from the responsible entities cited in the requirement. Note – Derived limits replaced by SOLs for clarity and specificity. SOLs include voltage, Stability, and thermal limits and are thus the most limiting factor.

## TOP-001-4
Includes the same occurrences as TOP-001-3 plus the one below
Rationale for Requirement R10: New proposed Requirement R10 is derived from approved IRO-003-2, Requirement R1, adapted to the Transmission Operator Area. This new requirement is in response to NOPR paragraph 60 concerning monitoring capabilities for the Transmission Operator. New Requirement R11 covers the Balancing Authorities. Monitoring of external systems can be accomplished via data links. The revised requirement addresses directives for Transmission Operator (TOP) monitoring of some non-Bulk Electric System (BES) facilities as necessary for determining System Operating Limit (SOL) exceedances (FERC Order No. 817 Para 35-36). The proposed requirement corresponds with approved IRO-002-4 Requirement R4 (proposed IRO-002-5 Requirement R5), which specifies the Reliability Coordinator's (RC) monitoring responsibilities for determining SOL exceedances. The intent of the requirement is to ensure that all facilities (i.e., BES and non-BES) that can adversely impact reliability of the BES are monitored. As used in TOP and IRO Reliability Standards, monitoring involves observing operating status and operating values in Real-time for awareness of system conditions. The facilities that are necessary for determining SOL exceedances should be either designated as part of the BES, or otherwise be incorporated into monitoring when identified by planning and operating studies such as the Operational Planning Analysis (OPA) required by TOP-002-4 Requirement R1 and IRO-008-2 Requirement R1. The SDT recognizes that not all non-BES facilities that a TOP considers necessary for its monitoring needs will need to be included in the BES.
The non-BES facilities that the TOP is required to monitor are only those that are necessary for the TOP to determine SOL exceedances within its Transmission Operator Area. TOPs perform various analyses and studies as part of their functional obligations that could lead to identification of non-BES facilities that should be monitored for determining SOL exceedances. Examples include: • OPA; • Real-time Assessments (RTA); • Analysis performed by the TOP as part of BES Exception processing for including a facility in the BES; and • Analysis which may be specified in the RC's outage coordination process that leads the TOP to identify a non-BES facility that should be temporarily monitored for determining SOL exceedances. TOP-003-3 Requirement R1 specifies that the TOP shall develop a data specification which includes data and information needed by the TOP to support its OPAs, Real-time monitoring, and RTAs. This includes non-BES data and external network data as deemed necessary by the TOP. The format of the proposed requirement has been changed from the approved standard to more clearly indicate which monitoring activities are required to be performed.

## TOP-002-4
Rationale for Definitions: Changes made to the proposed definitions were made in order to respond to issues raised in NOPR paragraphs 55, 73, and 74 dealing with analysis of SOLs in all time horizons, questions on Protection Systems and Special Protection Systems in NOPR paragraph 78, and recommendations on phase angles from the SW Outage Report (recommendation 27). The intent of such changes is to ensure that Real-time Assessments contain sufficient details to result in an appropriate level of situational awareness. Some examples include: 1) analyzing phase angles which may result in the implementation of an Operating Plan to adjust generation or curtail transactions so that a Transmission facility may be returned to service, or 2) evaluating the impact of a modified Contingency resulting from the status change of a Special Protection Scheme from enabled/in-service to disabled/out-of-service.
TOP-002-4 also contains the same write-up as seen in the Associated Docs tab

## VAR-001-4.1
Rationale for R1: Paragraph 1868 of Order No. 693 requires NERC to add more "detailed and definitive requirements on “established limits” and “sufficient reactive resources”, and identify acceptable margins (i.e. voltage and/or reactive power margins)." Since Order No. 693 was issued, however, several FAC and TOP standards have become enforceable to add more requirements around voltage limits. More specifically, FAC-011 and FAC-014 require that System Operating Limits (SOLs) and reliability margins are established. The NERC Glossary definition of SOLs includes both: 1) Voltage Stability Ratings (Applicable pre- and post- Contingency Voltage Stability) and 2) System Voltage Limits (Applicable pre- and post- Contingency Voltage Limits). Therefore, for reliability reasons Requirement R1 now requires a Transmission Operator (TOP) to set voltage or Reactive Power schedules with associated tolerance bands. Further, since neighboring areas can affect each other greatly, each TOP must also provide a copy of these schedules to its Reliability Coordinator (RC) and adjacent TOP upon request.
Rationale for R2: Paragraph 1875 from Order No. 693 directed NERC to include requirements to run voltage stability analysis periodically, using online techniques where commercially available and offline tools when online tools are not available. This standard does not explicitly require the periodic voltage stability analysis because such analysis would be performed pursuant to the SOL methodology developed under the FAC standards. TOP standards also require the TOP to operate within SOLs and Interconnection Reliability Operating Limits (IROL). The VAR standard drafting team (SDT) and industry participants also concluded that the best models and tools are the ones that have been proven and the standard should not add a requirement for a responsible entity to purchase new online simulations tools. Thus, the VAR SDT simplified the requirements to ensuring sufficient reactive resources are online or scheduled. Controllable load is specifically included to answer FERC's directive in Order No. 693 at Paragraph 1879.
Rationale for R3: Similar to Requirement R2, the VAR SDT determined that for reliability purposes, the TOP must ensure sufficient voltage support is provided in Real-time in order to operate within an SOL.