## Sheet1
2016 Generating Unit Statistical Brochure -- Units Reporting Events
NOTE: This brochure contains data on units reporting events only. For a review of statistics containing all units that reported , see the brochure "2016 Generating Unit Statistical Brochure -- All Units Reporting".
(The differences between statistics with or with events will appear in equations needing derating information such as EAF, EFOR, and other equations. The equations are more accurate if events are reported.)
|  | MW Trb/Gen | # of | Unit-
| Unit Type | Nameplate | Units | Years | ART | SR | NCF | NOF | SF | AF | EAF | FOR | EFOR | EFORd | SOF | FOF | UOF | EUOF | EUOR | POF | MOF | WSF | WAF | WEAF | WFOR | WEFOR | WSOF | WFOF
| FOSSIL | All Sizes | 1141 | 1143 | 145.36 | 98.98 | 42.29 | 70.67 | 52.51 | 83.46 | 80.95 | 7.69 | 10.39 | 8 | 12.17 | 4.37 | 7.43 | 9.18 | 15.22 | 9.11 | 3.05 | 59.85 | 82.28 | 79.76 | 7.17 | 9.84 | 13.1 | 4.62
| All Fuel Types | 1-99 | 248 | 248 | 118.7 | 99.39 | 29.7 | 64.57 | 43.64 | 86.83 | 84.38 | 8.27 | 10.88 | 7.54 | 9.24 | 3.93 | 6.19 | 7.69 | 15.27 | 6.98 | 2.26 | 46 | 85.93 | 83.51 | 7.89 | 10.48 | 10.13 | 3.94
|  | 100-199 | 260 | 260 | 52.8 | 99.58 | 26.28 | 59.31 | 42.28 | 84.77 | 82.06 | 6.47 | 9.27 | 5.85 | 12.3 | 2.92 | 5.86 | 7.26 | 14.94 | 9.37 | 2.94 | 44.31 | 84.43 | 81.66 | 6.55 | 9.39 | 12.46 | 3.11
|  | 200-299 | 131 | 131 | 222.99 | 98.07 | 34.8 | 65.87 | 53.19 | 81.97 | 79.81 | 8.26 | 10.56 | 8.59 | 13.24 | 4.79 | 8.36 | 9.89 | 15.95 | 9.67 | 3.57 | 52.83 | 82.06 | 79.95 | 8.42 | 10.67 | 13.08 | 4.86
|  | 300-399 | 106 | 107 | 201.89 | 98.61 | 31.72 | 64 | 50.1 | 80.42 | 78.21 | 10.6 | 13.34 | 10.52 | 13.64 | 5.94 | 8.78 | 10.46 | 17.65 | 10.8 | 2.84 | 49.55 | 80.45 | 78.29 | 10.59 | 13.27 | 13.69 | 5.87
|  | 400-599 | 192 | 192 | 312.49 | 97.77 | 43.9 | 70.79 | 61.66 | 81.25 | 78.44 | 8.79 | 11.95 | 10.34 | 12.81 | 5.95 | 9.45 | 11.83 | 16.55 | 9.3 | 3.5 | 62.02 | 81.38 | 78.55 | 8.76 | 11.94 | 12.66 | 5.96
|  | 600-799 | 132 | 132 | 481.85 | 96.58 | 49.39 | 75.55 | 65.36 | 83.35 | 80.76 | 5.81 | 8.43 | 7.5 | 12.62 | 4.03 | 7.07 | 9.15 | 12.58 | 9.58 | 3.04 | 65.38 | 83.28 | 80.71 | 5.8 | 8.43 | 12.7 | 4.02
|  | 800-999 | 59 | 59 | 287.82 | 98.34 | 47.96 | 71.79 | 66.33 | 82.88 | 80.78 | 5.54 | 7.98 | 7 | 13.23 | 3.89 | 7.29 | 9.26 | 12.56 | 9.83 | 3.4 | 66.8 | 83.08 | 80.99 | 5.43 | 7.84 | 13.09 | 3.83
|  | 1000 Plus | 13 | 13 | 690.55 | 96.67 | 53.38 | 74.8 | 70.75 | 76.69 | 73.76 | 4.15 | 5.59 | 5.32 | 20.25 | 3.06 | 11.33 | 12.83 | 15.62 | 11.98 | 8.27 | 71.36 | 77.1 | 74.37 | 4.06 | 5.41 | 19.88 | 3.02
| Coal | All Sizes | 682 | 674.5 | 459.16 | 97.38 | 52.1 | 73.57 | 64.46 | 83.26 | 80.61 | 6.58 | 8.96 | 7.94 | 12.2 | 4.54 | 7.8 | 9.66 | 13.33 | 8.94 | 3.26 | 70.82 | 82.54 | 79.92 | 6.21 | 8.56 | 12.78 | 4.69
| Primary | 1-99 | 92 | 90.67 | 212.42 | 98.25 | 34.82 | 73.2 | 42.93 | 87.98 | 86 | 6.18 | 8.05 | 6.21 | 9.19 | 2.83 | 4.56 | 5.81 | 12.05 | 7.46 | 1.73 | 47.57 | 87.73 | 85.84 | 5.21 | 7.08 | 9.66 | 2.61
|  | 100-199 | 144 | 140.5 | 435.61 | 97.48 | 35.93 | 63.19 | 56.49 | 84.75 | 81.45 | 5.62 | 8.2 | 6.85 | 11.89 | 3.36 | 6.98 | 8.65 | 13.55 | 8.27 | 3.62 | 56.86 | 84.81 | 81.48 | 5.88 | 8.69 | 11.64 | 3.55
|  | 200-299 | 89 | 85.75 | 436.49 | 97.07 | 43.51 | 70.75 | 62.22 | 81.48 | 79.1 | 8.26 | 10.17 | 9.02 | 12.91 | 5.61 | 9.21 | 10.66 | 14.9 | 9.31 | 3.6 | 61.5 | 81.84 | 79.48 | 8.6 | 10.49 | 12.38 | 5.79
|  | 300-399 | 63 | 63.42 | 472.75 | 97.59 | 45.54 | 70.17 | 64.62 | 79.53 | 76.79 | 9.72 | 12.44 | 11.18 | 13.51 | 6.96 | 9.92 | 12.02 | 16.08 | 10.55 | 2.96 | 64.89 | 79.66 | 76.93 | 9.59 | 12.28 | 13.46 | 6.88
|  | 400-599 | 134 | 133.25 | 532.15 | 97.22 | 54.81 | 73.48 | 74.44 | 82.46 | 79.52 | 6.56 | 9.4 | 8.84 | 12.32 | 5.22 | 8.56 | 11.02 | 13.25 | 8.98 | 3.34 | 74.59 | 82.59 | 79.62 | 6.49 | 9.37 | 12.23 | 5.18
|  | 600-799 | 106 | 105.92 | 618.52 | 96.91 | 56.26 | 76.53 | 73.3 | 83.42 | 80.8 | 5.41 | 7.72 | 7.21 | 12.39 | 4.19 | 7.43 | 9.46 | 11.69 | 9.15 | 3.23 | 73.51 | 83.37 | 80.74 | 5.39 | 7.72 | 12.45 | 4.19
|  | 800-999 | 42 | 42 | 657.9 | 96.55 | 55.29 | 73.19 | 75.42 | 82.68 | 80.74 | 5.6 | 7.44 | 7.05 | 12.85 | 4.47 | 7.82 | 9.63 | 11.56 | 9.5 | 3.35 | 75.54 | 82.94 | 81.02 | 5.48 | 7.3 | 12.69 | 4.38
|  | 1000 Plus | 12 | 12 | 665.06 | 96.57 | 55.45 | 76.18 | 72.53 | 78.34 | 75.88 | 4.37 | 5.53 | 5.27 | 18.34 | 3.32 | 12.27 | 13.53 | 15.95 | 9.38 | 8.96 | 72.79 | 78.41 | 76.06 | 4.24 | 5.36 | 18.37 | 3.22
| Oil | All Sizes | 60 | 54 | 97.47 | 98.6 | 7.35 | 42.46 | 27.6 | 84.16 | 82.58 | 8.42 | 12.31 | 7.3 | 13.3 | 2.54 | 7.1 | 8.52 | 24.38 | 8.74 | 4.56 | 17.31 | 80.38 | 79.01 | 13.3 | 17.28 | 16.96 | 2.66
| Primary | 1-99 | 16 | 15.83 | 88.3 | 99.88 | 26.21 | 40.26 | 59.73 | 85.07 | 81.62 | 2.47 | 6.98 | 5.23 | 13.41 | 1.52 | 9.18 | 12.62 | 18.31 | 5.74 | 7.67 | 65.09 | 83.2 | 79.23 | 2.46 | 7.07 | 15.15 | 1.64
|  | 100-199 | 14 | 13.25 | 149.88 | 94.77 | 11.53 | 61.64 | 16.38 | 90.52 | 90.06 | 5.83 | 8.31 | 5.48 | 8.47 | 1.01 | 4.47 | 4.93 | 23.51 | 5.01 | 3.46 | 18.7 | 89.79 | 89.29 | 5.11 | 7.52 | 9.2 | 1.01
|  | 200-299 | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | ****
|  | 300-399 | 9 | 9 | 239.13 | 95.6 | 12.57 | 41.83 | 29.28 | 78.41 | 77.71 | 17.54 | 18.11 | 13.92 | 15.36 | 6.23 | 10.04 | 10.26 | 26.03 | 11.55 | 3.81 | 30.04 | 78.82 | 78.09 | 16.13 | 16.71 | 15.41 | 5.78
|  | 400-599 | 8 | 7.17 | 16.46 | 98.71 | 0.62 | 31.05 | 2.01 | 87.71 | 86.53 | 71.11 | 76.06 | 28 | 7.33 | 4.96 | 6.75 | 7.93 | 80.41 | 5.54 | 1.79 | 2 | 88.03 | 86.92 | 70.1 | 75.11 | 7.28 | 4.69
|  | 600-799 | 5 | 5 | 33.54 | 96.49 | 2.55 | 31.92 | 8.4 | 80.87 | 80.42 | 11.54 | 15.37 | 8.47 | 18.03 | 1.1 | 6.07 | 6.52 | 43.9 | 13.06 | 4.98 | 8 | 79.25 | 78.72 | 11.53 | 16.35 | 19.7 | 1.04
|  | 800-999 | 6 | 2.5 | 10.65 | 90.91 | 0.17 | 35.43 | 0.48 | 75.15 | 75.15 | 33.12 | 33.12 | 19.98 | 24.61 | 0.24 | 4.1 | 4.1 | 89.43 | 20.75 | 3.86 | 0.49 | 75.3 | 75.3 | 33.2 | 33.2 | 24.45 | 0.24
| Gas | All Sizes | 329 | 320.42 | 50.85 | 99.36 | 11.81 | 44.58 | 25.31 | 82.09 | 80.21 | 15.57 | 19.18 | 9.83 | 13.24 | 4.67 | 7.66 | 8.98 | 26.65 | 10.24 | 2.99 | 26.49 | 79.83 | 77.81 | 16.66 | 20.73 | 14.88 | 5.29
| Primary | 1-99 | 91 | 90.25 | 61.87 | 99.61 | 13.57 | 49.31 | 22.52 | 85.23 | 84.06 | 19.68 | 21.36 | 9.93 | 9.25 | 5.52 | 8.04 | 8.62 | 27.76 | 6.72 | 2.52 | 27.52 | 83.35 | 82.21 | 18.13 | 19.15 | 10.55 | 6.1
|  | 100-199 | 100 | 96.25 | 36.31 | 99.53 | 12.13 | 44.13 | 25.74 | 83.42 | 81.12 | 9.86 | 13.68 | 6.85 | 13.77 | 2.82 | 5.15 | 6.42 | 20.4 | 11.43 | 2.34 | 27.48 | 82.52 | 80.05 | 9.81 | 13.4 | 14.49 | 2.99
|  | 200-299 | 41 | 38 | 71.92 | 99.11 | 13.78 | 46.55 | 29.34 | 80.51 | 78.58 | 11.4 | 16.3 | 9.42 | 15.71 | 3.77 | 7.89 | 9.8 | 25.57 | 11.6 | 4.11 | 29.6 | 80.06 | 78.23 | 10.98 | 15.58 | 16.29 | 3.65
|  | 300-399 | 32 | 31.58 | 51.92 | 99.3 | 8.71 | 37.22 | 23.37 | 81.38 | 79.66 | 15.8 | 19.86 | 10.12 | 14.23 | 4.39 | 6.99 | 8.34 | 26.78 | 11.63 | 2.6 | 23.4 | 81.19 | 79.55 | 16.06 | 19.92 | 14.33 | 4.48
|  | 400-599 | 46 | 45.83 | 75.5 | 98.88 | 14.06 | 46.14 | 30.19 | 76.33 | 73.79 | 21.68 | 26.22 | 15.9 | 15.31 | 8.36 | 12.87 | 15.06 | 34.22 | 10.8 | 4.51 | 30.47 | 76.5 | 73.92 | 22 | 26.55 | 14.9 | 8.59
|  | 600-799 | 12 | 12 | 145.68 | 94.41 | 11 | 51.46 | 21.01 | 79.41 | 77.4 | 16.7 | 22.39 | 14.5 | 16.38 | 4.21 | 6.35 | 8.37 | 29.31 | 14.24 | 2.14 | 21.38 | 80.36 | 78.41 | 16.16 | 21.79 | 15.52 | 4.12
|  | 800-999 | 7 | 6.5 | 15.16 | 99.55 | 5.57 | 31.4 | 17.59 | 79.82 | 79.17 | 15.09 | 17.45 | 6.12 | 17.05 | 3.13 | 8.64 | 9.25 | 34.58 | 11.54 | 5.51 | 17.74 | 79.78 | 79.13 | 14.79 | 17.14 | 17.14 | 3.08
| Lignite Primary | All Sizes | 32 | 30.83 | 25.47 | 99.72 | 64.16 | 78.62 | 80.48 | 88.32 | 85.15 | 3.76 | 6.56 | 6.01 | 8.53 | 3.15 | 4.69 | 7.29 | 8.56 | 6.98 | 1.54 | 81.61 | 88.64 | 84.69 | 3.93 | 7.79 | 8.02 | 3.34
| Oil/Gas | All Sizes | 382 | 374.42 | 54.86 | 99.27 | 11.02 | 44.32 | 25.64 | 82.39 | 80.54 | 14.55 | 18.21 | 9.52 | 13.25 | 4.37 | 7.58 | 8.91 | 26.32 | 10.03 | 3.22 | 24.87 | 79.92 | 78.02 | 16.26 | 20.32 | 15.25 | 4.83
| Primary | 1-99 | 107 | 106.08 | 68.37 | 99.65 | 15.9 | 46.16 | 28.07 | 85.21 | 83.7 | 14.91 | 17.42 | 8.87 | 9.87 | 4.92 | 8.21 | 9.22 | 25.11 | 6.58 | 3.29 | 34.44 | 83.32 | 81.66 | 13.29 | 15.44 | 11.4 | 5.28
|  | 100-199 | 113 | 109.5 | 38.43 | 99.43 | 12.06 | 45.4 | 24.71 | 84.2 | 82.1 | 9.58 | 13.31 | 6.66 | 13.18 | 2.62 | 5.08 | 6.26 | 20.64 | 10.72 | 2.46 | 26.57 | 83.27 | 81.01 | 9.48 | 13 | 13.95 | 2.78
|  | 200-299 | 41 | 38.25 | 71.73 | 99.11 | 13.68 | 46.55 | 29.14 | 80.62 | 78.7 | 11.44 | 16.34 | 9.45 | 15.61 | 3.76 | 7.86 | 9.77 | 25.63 | 11.52 | 4.1 | 29.39 | 80.18 | 78.36 | 11.02 | 15.62 | 16.18 | 3.64
|  | 300-399 | 41 | 40.58 | 63.98 | 99.04 | 9.52 | 38.4 | 24.57 | 80.78 | 79.26 | 16.22 | 19.44 | 10.64 | 14.46 | 4.76 | 7.61 | 8.73 | 26.6 | 11.61 | 2.85 | 24.8 | 80.69 | 79.24 | 16.08 | 19.11 | 14.56 | 4.75
|  | 400-599 | 53 | 53 | 72.6 | 98.86 | 12.2 | 45.98 | 26.13 | 77.98 | 75.63 | 23.14 | 27.89 | 15.99 | 14.16 | 7.87 | 11.99 | 14.03 | 35.91 | 10.04 | 4.12 | 26.53 | 78.1 | 75.72 | 23.29 | 28.02 | 13.85 | 8.05
|  | 600-799 | 17 | 17 | 98.63 | 95.24 | 8.72 | 49.09 | 17.3 | 79.84 | 78.29 | 16 | 21.42 | 13.03 | 16.86 | 3.3 | 6.27 | 7.82 | 31.91 | 13.89 | 2.97 | 17.77 | 80.06 | 78.5 | 15.62 | 21.15 | 16.65 | 3.29
|  | 800-999 | 9 | 9 | 15.1 | 99.41 | 4.02 | 31.45 | 12.83 | 78.52 | 78.05 | 15.33 | 17.66 | 5.64 | 19.16 | 2.32 | 7.37 | 7.82 | 37.97 | 14.1 | 5.05 | 12.78 | 78.49 | 78.03 | 15.05 | 17.36 | 19.24 | 2.26
| NUCLEAR | All Sizes | 98 | 98 | 5139.5 | 97.53 | 91.5 | 99.05 | 92.53 | 92.53 | 90.7 | 2.23 | 2.77 | 2.77 | 5.37 | 2.11 | 2.5 | 3.26 | 3.44 | 4.97 | 0.39 | 92.38 | 92.38 | 90.58 | 2.37 | 2.89 | 5.38 | 2.24
| All Types | 400-799 | 12 | 12 | 5090.49 | 94.61 | 89.83 | 97.24 | 92.21 | 92.21 | 89.96 | 2.33 | 2.87 | 2.87 | 5.58 | 2.2 | 2.96 | 3.65 | 3.84 | 4.83 | 0.76 | 92.38 | 92.38 | 90.16 | 2.24 | 2.8 | 5.5 | 2.12
|  | 800-999 | 33 | 33 | 5563.7 | 97.37 | 93.18 | 99.42 | 93.74 | 93.74 | 92.07 | 1.34 | 2.06 | 2.06 | 4.99 | 1.27 | 1.62 | 2.65 | 2.78 | 4.63 | 0.35 | 93.72 | 93.72 | 92.07 | 1.36 | 2.06 | 4.98 | 1.29
|  | 1000 Plus | 53 | 53 | 4918.93 | 97.62 | 90.91 | 99.09 | 91.84 | 91.84 | 90.01 | 2.76 | 3.19 | 3.19 | 5.55 | 2.61 | 2.95 | 3.56 | 3.76 | 5.21 | 0.34 | 91.74 | 91.74 | 89.93 | 2.86 | 3.28 | 5.56 | 2.7
| PWR | All Sizes | 61 | 61 | 5240.74 | 96.86 | 91.72 | 99.57 | 92.01 | 92.01 | 90.71 | 2.43 | 2.75 | 2.75 | 5.7 | 2.3 | 2.58 | 3.01 | 3.19 | 5.41 | 0.28 | 92.11 | 92.11 | 90.78 | 2.37 | 2.71 | 5.65 | 2.24
|  | 400-799 | 4 | 4 | 6167.5 | 100 | 90.11 | 99.89 | 89.66 | 89.66 | 87.98 | 4.82 | 4.91 | 4.91 | 5.8 | 4.54 | 5.16 | 5.31 | 5.61 | 5.18 | 0.62 | 90.21 | 90.21 | 88.62 | 4.59 | 4.7 | 5.45 | 4.34
|  | 800-999 | 22 | 22 | 4707.58 | 97.74 | 92.83 | 100.18 | 92.72 | 92.72 | 91.8 | 1.66 | 1.89 | 1.89 | 5.72 | 1.56 | 1.99 | 2.39 | 2.53 | 5.29 | 0.43 | 92.67 | 92.67 | 91.74 | 1.7 | 1.93 | 5.73 | 1.6
|  | 1000 Plus | 35 | 35 | 5524.61 | 96.69 | 91.28 | 99.27 | 91.83 | 91.83 | 90.33 | 2.66 | 3.06 | 3.06 | 5.67 | 2.51 | 2.66 | 3.15 | 3.33 | 5.52 | 0.15 | 91.96 | 91.96 | 90.45 | 2.57 | 2.97 | 5.62 | 2.42
| BWR | All Sizes | 32 | 32 | 4610.84 | 98.34 | 91.18 | 98.26 | 93.43 | 93.43 | 90.61 | 2.15 | 3.13 | 3.13 | 4.51 | 2.05 | 2.72 | 4.15 | 4.32 | 3.84 | 0.67 | 92.8 | 92.8 | 90.1 | 2.58 | 3.45 | 4.75 | 2.45
|  | 400-799 | 4 | 4 | 3361.07 | 90.91 | 91.58 | 95.7 | 95.66 | 95.66 | 92.93 | 1.92 | 2.96 | 2.96 | 2.47 | 1.87 | 3.52 | 4.93 | 4.97 | 0.82 | 1.65 | 95.7 | 95.7 | 93.01 | 2 | 3.03 | 2.35 | 1.95
|  | 800-999 | 10 | 10 | 7616.05 | 100 | 93.4 | 97.84 | 95.37 | 95.37 | 91.87 | 0.79 | 2.64 | 2.64 | 3.86 | 0.76 | 0.97 | 3.47 | 3.6 | 3.65 | 0.21 | 95.47 | 95.47 | 92.09 | 0.77 | 2.54 | 3.79 | 0.74
|  | 1000 Plus | 18 | 18 | 4034.62 | 100 | 90.2 | 98.76 | 91.86 | 91.86 | 89.39 | 2.96 | 3.44 | 3.44 | 5.33 | 2.81 | 3.51 | 4.36 | 4.58 | 4.62 | 0.71 | 91.34 | 91.34 | 88.92 | 3.41 | 3.88 | 5.43 | 3.23
| CANDU | All Sizes | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | ****
| JET | All Sizes | 263 | 263 | 6.1 | 98.75 | 5.09 | 73.09 | 5.37 | 90.5 | 89.24 | 26.89 | 29.43 | 9.23 | 6.97 | 2.53 | 5.85 | 6.37 | 47.69 | 3.65 | 3.32 | 6.97 | 90.25 | 88.37 | 24.16 | 27.84 | 6.96 | 2.78
| ENGINE** | 1-19 | 27 | 27 | 1.6 | 96.58 | 0.18 | 78.51 | 0.24 | 88.83 | 88.83 | 82.97 | 83.05 | 18.49 | 10.02 | 1.15 | 5.25 | 5.25 | 95.79 | 5.92 | 4.1 | 0.23 | 87.74 | 87.74 | 84.63 | 84.71 | 11.01 | 1.25
|  | 20 Plus | 236 | 236 | 6.17 | 98.77 | 5.31 | 73.08 | 5.97 | 90.69 | 89.29 | 26.02 | 28.63 | 9.18 | 6.62 | 2.69 | 5.92 | 6.5 | 45.55 | 3.39 | 3.23 | 7.27 | 90.36 | 88.4 | 23.83 | 27.54 | 6.79 | 2.85
| GAS | All Sizes | 704 | 703.25 | 9.38 | 98.38 | 6.29 | 75.4 | 5.27 | 90.22 | 88.59 | 36.79 | 39.52 | 9.05 | 6.72 | 3.07 | 5.61 | 6 | 53.33 | 4.17 | 2.55 | 8.34 | 90.78 | 89.25 | 22.78 | 25.37 | 6.76 | 2.46
| TURBINE** | 1-19 | 108 | 108 | 3.28 | 96.5 | 0.88 | 73.89 | 1.15 | 89.37 | 88.86 | 76.9 | 77.18 | 14.46 | 6.78 | 3.84 | 8.05 | 8.11 | 87.56 | 2.57 | 4.21 | 1.19 | 89.33 | 88.89 | 76.68 | 76.95 | 6.75 | 3.92
|  | 20-49 | 134 | 133.25 | 5.94 | 98.97 | 4.64 | 89.66 | 3.42 | 90.88 | 88.49 | 49.66 | 51.02 | 8.64 | 5.74 | 3.38 | 5.68 | 5.86 | 63.19 | 3.44 | 2.3 | 5.17 | 90.64 | 88.14 | 35.66 | 37.12 | 6.49 | 2.87
|  | 50 Plus | 462 | 462 | 11.06 | 98.48 | 6.64 | 74.67 | 6.68 | 90.21 | 88.57 | 29.66 | 33.1 | 8.4 | 6.97 | 2.81 | 5.07 | 5.58 | 45.63 | 4.72 | 2.25 | 8.89 | 90.85 | 89.36 | 21.02 | 23.75 | 6.78 | 2.37
| COMB. CYCLE (BLOCK REPORTED UNITS ONLY | All Sizes | 277 | 276.75 | 86.38 | 98.63 | 56.2 | 80.59 | 58.03 | 87.82 | 85.24 | 3.72 | 4.69 | 3.72 | 9.94 | 2.24 | 3.87 | 4.61 | 7.43 | 8.31 | 1.63 | 69.73 | 88.37 | 85.34 | 2.06 | 3.13 | 10.16 | 1.47
| HYDRO | All Sizes | 1049 | 1040 | 25.61 | 99.95 | 40.41 | 64.33 | 62.99 | 80.76 | 80.41 | 8.65 | 8.77 | 7.34 | 13.11 | 6.12 | 8.02 | 8.12 | 11.17 | 11.22 | 1.89 | 62.82 | 82.56 | 82.24 | 4.32 | 4.41 | 14.52 | 2.92
|  | 1-29 | 393 | 384 | 102.89 | 99.85 | 35.74 | 54.23 | 61.33 | 75.05 | 74.77 | 15.59 | 15.75 | 13.79 | 13.43 | 11.51 | 13.51 | 13.68 | 18.03 | 11.43 | 2 | 65.91 | 82.38 | 82.07 | 6.1 | 6.33 | 13.24 | 4.38
|  | 30 Plus | 656 | 656 | 18.02 | 99.96 | 40.72 | 65.02 | 63.97 | 84.1 | 83.71 | 4.31 | 4.4 | 3.6 | 12.93 | 2.97 | 4.8 | 4.87 | 6.88 | 11.1 | 1.83 | 62.62 | 82.57 | 82.25 | 4.2 | 4.27 | 14.6 | 2.82
| PUMPED STORAGE | All Sizes | 109 | 109 | 8.85 | 99.92 | 7.85 | 44.66 | 26.91 | 80.38 | 80.24 | 8.67 | 8.67 | 6.11 | 15.64 | 3.98 | 6.15 | 6.15 | 12.8 | 13.47 | 2.17 | 17.58 | 79.33 | 78.98 | 9.64 | 9.65 | 16.97 | 3.7
| MULTIBOILER/MULTI-TURBINE | All Sizes | 22 | 22 | 314.96 | 98.51 | 33.81 | 65.37 | 66.03 | 86.12 | 78.92 | 2.53 | 8.88 | 7.25 | 12.17 | 1.72 | 3.93 | 9.16 | 12.97 | 9.96 | 2.21 | 51.73 | 80.86 | 77.27 | 3.26 | 6.94 | 17.4 | 1.74
| DIESEL** | All Sizes | 133 | 133 | 7.73 | 99.41 | 7.82 | 60.62 | 5 | 94.11 | 93.61 | 17.08 | 19.48 | 6.07 | 4.86 | 1.03 | 3.24 | 3.46 | 40.84 | 2.65 | 2.21 | 12.9 | 91.14 | 90.17 | 10.93 | 12.67 | 7.28 | 1.58
**Caution: EFOR and WEFOR values may be low since deratings during reserve shutdown periods may not have been reported for a large number of these units.
*** The two methods for calculating combined cycle units is not available at this time.
**** Less than three generating companies are reporting this type of unit. To retain confidentiality of the data, no data is reported here.