## Sheet1
2014 Generating Unit Statistical Brochure -- Five Years, 2010 - 2014, Units Reporting Events
NOTE: This brochure contains data on units reporting events only. For a review of statistics containing all units that reported, see the brochure "2010-2014 Generating Unit Statistical Brochure -- All Units Reporting".
(The differences between statistics with or with events will appear in equations needing derating information such as EAF, EFOR, and other equations. The equations are more accurate if events are reported.)
|  | MW Trb/Gen | # of | Unit-
| Unit Type | Nameplate | Units | Years | ART | SR | NCF | NOF | SF | AF | EAF | FOR | EFOR | EFORd | SOF | FOF | UOF | EUOF | EUOR | POF | MOF | WSF | WAF | WEAF | WFOR | WEFOR | WSOF | WFOF
| FOSSIL | All Sizes | 1391 | 5817.25 | 293.43 | 97.48 | 49.47 | 75.53 | 57.03 | 85.2 | 82.81 | 7.73 | 10.07 | 8.4 | 10.02 | 4.78 | 7.54 | 9.31 | 14.34 | 7.25 | 2.76 | 65.5 | 84.33 | 81.97 | 6.63 | 8.78 | 11.03 | 4.65
| All Fuel Types | 1-99 | 323 | 1221.92 | 188.09 | 98.46 | 27.06 | 64.36 | 40.74 | 86.48 | 84.13 | 13.05 | 15.97 | 11.19 | 7.37 | 6.12 | 8.85 | 10.45 | 20.84 | 4.63 | 2.73 | 42.04 | 87.17 | 84.94 | 11.27 | 14.08 | 7.47 | 5.34
|  | 100-199 | 356 | 1474.25 | 264.67 | 97.73 | 33.31 | 64.68 | 50.09 | 87.16 | 84.79 | 6.63 | 8.82 | 6.99 | 9.28 | 3.56 | 6.26 | 7.79 | 13.72 | 6.58 | 2.7 | 51.49 | 86.98 | 84.53 | 6.41 | 8.66 | 9.49 | 3.53
|  | 200-299 | 163 | 698.17 | 310.04 | 97.37 | 41.13 | 67.32 | 60.71 | 83.08 | 80.28 | 8.24 | 10.87 | 9.28 | 11.47 | 5.45 | 8.52 | 10.75 | 15.47 | 8.4 | 3.06 | 61.09 | 83.24 | 80.44 | 8.03 | 10.64 | 11.42 | 5.33
|  | 300-399 | 121 | 533 | 251.54 | 97.52 | 38.5 | 67.63 | 57.21 | 84.49 | 82.51 | 6.64 | 8.75 | 7.32 | 11.44 | 4.07 | 6.59 | 8.13 | 12.71 | 8.92 | 2.52 | 56.93 | 84.47 | 82.52 | 6.57 | 8.63 | 11.53 | 4
|  | 400-599 | 223 | 969.25 | 328.89 | 96.54 | 51.25 | 74.81 | 68.25 | 83.92 | 81.4 | 6.85 | 9.24 | 8.27 | 11.06 | 5.02 | 7.92 | 9.94 | 13 | 8.16 | 2.9 | 68.51 | 83.82 | 81.28 | 6.95 | 9.33 | 11.06 | 5.11
|  | 600-799 | 139 | 608.58 | 569.09 | 96.68 | 59.99 | 80.95 | 74.26 | 84.06 | 81.66 | 6.44 | 8.43 | 7.94 | 10.84 | 5.11 | 7.84 | 9.78 | 11.89 | 8.1 | 2.73 | 74.1 | 84.09 | 81.69 | 6.36 | 8.37 | 10.88 | 5.03
|  | 800-999 | 54 | 254.08 | 387.47 | 97.47 | 57.18 | 82.49 | 68.98 | 84.67 | 82.9 | 4.53 | 6.22 | 5.6 | 12.06 | 3.27 | 5.54 | 7.13 | 9.56 | 9.8 | 2.26 | 69.31 | 84.79 | 83.05 | 4.48 | 6.14 | 11.95 | 3.25
|  | 1000 Plus | 13 | 58 | 757.27 | 92.53 | 63.92 | 85.38 | 73.87 | 79.98 | 77.38 | 7.4 | 9.03 | 8.63 | 14.12 | 5.9 | 9.49 | 11.47 | 13.74 | 10.54 | 3.58 | 74.86 | 80.09 | 77.55 | 7.33 | 8.91 | 13.99 | 5.93
| Coal | All Sizes | 892 | 3781.67 | 476.11 | 96.71 | 61.1 | 80.08 | 69.05 | 85.87 | 83.22 | 6.1 | 8.25 | 7.43 | 9.64 | 4.48 | 7.4 | 9.38 | 12.22 | 6.73 | 2.92 | 76.3 | 85.08 | 82.57 | 5.57 | 7.47 | 10.42 | 4.5
| Primary | 1-99 | 153 | 570.75 | 238.61 | 97.87 | 36.67 | 71.25 | 50.51 | 87.24 | 84.97 | 9.71 | 12.55 | 9.76 | 7.33 | 5.43 | 8.64 | 10.54 | 17.63 | 4.12 | 3.21 | 51.46 | 88.24 | 85.98 | 7.91 | 10.78 | 7.34 | 4.42
|  | 100-199 | 240 | 987.67 | 433.35 | 97 | 43.95 | 70.3 | 61.47 | 88.2 | 85.26 | 5.06 | 7.21 | 6.18 | 8.52 | 3.28 | 6.3 | 8.12 | 11.9 | 5.5 | 3.02 | 62.52 | 88.05 | 85.08 | 5.01 | 7.19 | 8.65 | 3.29
|  | 200-299 | 118 | 519.5 | 486.54 | 96.58 | 48.92 | 72.17 | 67.4 | 83.43 | 80.11 | 7.63 | 10.41 | 9.36 | 11 | 5.57 | 8.87 | 11.49 | 15.01 | 7.7 | 3.3 | 67.78 | 83.67 | 80.35 | 7.38 | 10.14 | 10.93 | 5.4
|  | 300-399 | 70 | 313.92 | 532.51 | 96.02 | 57.54 | 76.29 | 75.16 | 85.36 | 82.72 | 5.52 | 7.69 | 7.17 | 10.25 | 4.39 | 7.1 | 9.18 | 11.15 | 7.54 | 2.71 | 75.43 | 85.48 | 82.86 | 5.47 | 7.6 | 10.16 | 4.36
|  | 400-599 | 151 | 664.75 | 555.83 | 95.81 | 65.25 | 81.29 | 80.23 | 85 | 82.46 | 5.24 | 7.25 | 6.99 | 10.57 | 4.44 | 7.11 | 9.06 | 10.36 | 7.9 | 2.67 | 80.27 | 84.96 | 82.41 | 5.26 | 7.28 | 10.59 | 4.45
|  | 600-799 | 113 | 498.58 | 717.32 | 96.49 | 66.97 | 82.43 | 81.12 | 84.86 | 82.52 | 5.57 | 7.26 | 7.04 | 10.36 | 4.79 | 7.43 | 9.25 | 10.45 | 7.72 | 2.64 | 81.24 | 84.92 | 82.58 | 5.55 | 7.24 | 10.3 | 4.78
|  | 800-999 | 36 | 173.5 | 892.95 | 96.2 | 68.58 | 84.98 | 80.69 | 85.19 | 83.51 | 4.52 | 5.76 | 5.57 | 10.99 | 3.82 | 6.18 | 7.74 | 8.91 | 8.62 | 2.36 | 80.7 | 85.32 | 83.68 | 4.46 | 5.66 | 10.91 | 3.77
|  | 1000 Plus | 12 | 53 | 818.89 | 91.97 | 67.75 | 86.58 | 78.1 | 80.4 | 77.73 | 7.01 | 8.57 | 8.4 | 13.72 | 5.89 | 9.02 | 11 | 12.63 | 10.58 | 3.14 | 78.25 | 80.42 | 77.84 | 7.03 | 8.55 | 13.67 | 5.91
| Oil | All Sizes | 113 | 362.58 | 99.33 | 98.51 | 9.01 | 41.37 | 26.25 | 84.25 | 83.28 | 13.03 | 15.24 | 10.4 | 11.69 | 3.93 | 6.8 | 7.63 | 22.78 | 8.82 | 2.87 | 21.78 | 79.82 | 78.75 | 16.94 | 19.63 | 15.73 | 4.44
| Primary | 1-99 | 34 | 116.42 | 91.59 | 99.1 | 21.11 | 45.82 | 40.7 | 89.01 | 88.2 | 5.79 | 7.02 | 4.59 | 8.06 | 2.5 | 5.26 | 5.87 | 12.76 | 5.3 | 2.76 | 46.07 | 89.1 | 88.18 | 5.43 | 6.95 | 8.14 | 2.64
|  | 100-199 | 23 | 75.25 | 85.72 | 98.59 | 7.75 | 49.95 | 14.39 | 85.63 | 84.34 | 29.45 | 33.51 | 15.15 | 8.36 | 6.01 | 8.32 | 9.53 | 40.22 | 6.05 | 2.31 | 15.52 | 85.45 | 83.99 | 25.3 | 29.87 | 9.3 | 5.26
|  | 200-299 | 7 | 15.92 | 41.27 | 94.99 | 2.81 | 43.13 | 6.25 | 91.08 | 90.19 | 31.91 | 37.89 | 16.96 | 5.99 | 2.93 | 5.04 | 5.93 | 47.89 | 3.89 | 2.11 | 6.51 | 90.19 | 89.18 | 33.91 | 40.21 | 6.47 | 3.34
|  | 300-399 | 17 | 71.33 | 186.14 | 97.02 | 12.86 | 42.68 | 29.43 | 80.94 | 80.3 | 5.81 | 7.37 | 5.33 | 17.25 | 1.81 | 4.16 | 4.73 | 13.99 | 14.9 | 2.34 | 30.13 | 80.64 | 79.99 | 5.84 | 7.38 | 17.49 | 1.87
|  | 400-599 | 15 | 38.75 | 173.45 | 98.44 | 8.47 | 30.99 | 26.2 | 85.2 | 84.05 | 16.45 | 18.2 | 12.41 | 9.64 | 5.16 | 9.08 | 9.96 | 27.94 | 5.71 | 3.93 | 27.34 | 84.63 | 83.44 | 17.67 | 19.36 | 9.5 | 5.87
|  | 600-799 | 9 | 24.08 | 31.1 | 98.61 | 6.83 | 49.62 | 13.66 | 73.4 | 71.99 | 43.99 | 47.29 | 36.23 | 15.87 | 10.73 | 15.08 | 16.47 | 54.94 | 11.52 | 4.35 | 13.77 | 73.34 | 71.88 | 41.44 | 45.06 | 16.92 | 9.74
|  | 800-999 | 7 | 15.83 | 36.91 | 92.58 | 0.74 | 36.86 | 2 | 68.64 | 67.98 | 29.88 | 39.92 | 15.98 | 30.51 | 0.85 | 3.5 | 3.93 | 66.96 | 27.87 | 2.64 | 2 | 69.17 | 68.52 | 29.7 | 39.67 | 29.98 | 0.84
| Gas | All Sizes | 396 | 1441.92 | 90.86 | 98.22 | 11.83 | 35.69 | 28.61 | 83.65 | 82.16 | 15.98 | 18.62 | 10.89 | 10.91 | 5.44 | 7.87 | 8.98 | 24.3 | 8.48 | 2.43 | 33.14 | 82.23 | 80.35 | 13.57 | 16.91 | 12.57 | 5.2
| Primary | 1-99 | 126 | 420.42 | 113.17 | 98.53 | 8.97 | 46.23 | 16.64 | 85.73 | 84.47 | 30.24 | 32.24 | 14.96 | 7.06 | 7.21 | 9.27 | 9.88 | 37.61 | 5 | 2.06 | 19.4 | 85.5 | 84.08 | 26.61 | 28.6 | 7.47 | 7.03
|  | 100-199 | 102 | 409.5 | 93.67 | 98.58 | 10.95 | 36.15 | 29.07 | 84.87 | 83.7 | 11.54 | 13.59 | 8.26 | 11.34 | 3.79 | 5.77 | 6.68 | 19 | 9.36 | 1.98 | 30.28 | 84.48 | 83.18 | 11.12 | 13.26 | 11.73 | 3.79
|  | 200-299 | 40 | 150.08 | 100.26 | 98.67 | 15.35 | 36.77 | 41.39 | 80.63 | 79.45 | 11.96 | 13.65 | 9.39 | 13.75 | 5.62 | 8.03 | 9.04 | 18.18 | 11.34 | 2.4 | 41.75 | 80.6 | 79.43 | 11.85 | 13.52 | 13.79 | 5.61
|  | 300-399 | 39 | 147.75 | 63.88 | 98.72 | 9.55 | 31.99 | 29.65 | 84.3 | 83.15 | 13.12 | 15.09 | 9.08 | 11.22 | 4.48 | 6.65 | 7.43 | 20.19 | 9.05 | 2.17 | 29.86 | 84.31 | 83.18 | 12.74 | 14.67 | 11.33 | 4.36
|  | 400-599 | 60 | 236.08 | 89.6 | 97.2 | 12.93 | 34.53 | 37.57 | 80.21 | 77.64 | 15.37 | 19.49 | 12.84 | 12.96 | 6.82 | 10.36 | 12.61 | 25.78 | 9.42 | 3.54 | 37.45 | 79.9 | 77.27 | 15.97 | 20.14 | 12.99 | 7.12
|  | 600-799 | 19 | 45.92 | 194.71 | 93.45 | 11.87 | 38.21 | 30.33 | 80.45 | 77.53 | 12.92 | 20.04 | 13.4 | 15.05 | 4.5 | 8.46 | 11.34 | 28.54 | 11.1 | 3.96 | 31.06 | 80.65 | 77.69 | 12.4 | 19.49 | 14.96 | 4.39
|  | 800-999 | 10 | 32.17 | 44.38 | 98.71 | 10.67 | 37.03 | 28.75 | 85.47 | 84.34 | 1.64 | 3.88 | 2.09 | 14.05 | 0.48 | 3.52 | 4.21 | 12.77 | 11.01 | 3.03 | 28.81 | 85.43 | 84.27 | 1.62 | 3.82 | 14.1 | 0.47
| Lignite Primary | All Sizes | 23 | 112.5 | 773.38 | 95.59 | 73.05 | 85.93 | 85.19 | 87.7 | 84.02 | 4.25 | 7.41 | 7.25 | 8.52 | 3.78 | 5.42 | 8.44 | 9.31 | 6.88 | 1.64 | 85.01 | 87.82 | 84.15 | 4.57 | 8.01 | 8.11 | 4.07
| Oil/Gas | All Sizes | 477 | 1804.5 | 92.43 | 98.27 | 11.15 | 36.67 | 28.11 | 83.78 | 82.4 | 15.41 | 17.96 | 10.88 | 11.08 | 5.12 | 7.64 | 8.7 | 24 | 8.56 | 2.52 | 30.42 | 81.65 | 79.97 | 14.17 | 17.39 | 13.33 | 5.02
| Primary | 1-99 | 156 | 536.83 | 102.57 | 98.8 | 11.88 | 46.06 | 22.48 | 86.52 | 85.37 | 21.25 | 23.06 | 11.4 | 7.31 | 6.07 | 8.3 | 8.91 | 28.68 | 5.08 | 2.23 | 25.8 | 86.36 | 85.06 | 18.81 | 20.71 | 7.63 | 5.98
|  | 100-199 | 119 | 484.75 | 92.94 | 98.56 | 10.41 | 37.43 | 26.73 | 84.99 | 83.8 | 13.42 | 15.75 | 9.17 | 10.87 | 4.14 | 6.18 | 7.13 | 21.4 | 8.84 | 2.03 | 27.82 | 84.64 | 83.32 | 12.67 | 15.14 | 11.32 | 4.03
|  | 200-299 | 45 | 166 | 97.96 | 98.53 | 14.08 | 36.88 | 37.9 | 81.67 | 80.51 | 12.38 | 14.2 | 9.44 | 12.98 | 5.36 | 7.73 | 8.73 | 18.97 | 10.6 | 2.37 | 38.17 | 81.57 | 80.42 | 12.35 | 14.18 | 13.05 | 5.38
|  | 300-399 | 52 | 219.08 | 82.01 | 98.45 | 10.73 | 35.83 | 29.58 | 83.16 | 82.19 | 10.79 | 12.64 | 7.99 | 13.26 | 3.58 | 5.81 | 6.52 | 18.21 | 11.03 | 2.23 | 29.96 | 83 | 82.04 | 10.38 | 12.19 | 13.53 | 3.47
|  | 400-599 | 67 | 274.83 | 94.59 | 97.28 | 12.26 | 34.13 | 35.88 | 80.96 | 78.6 | 15.49 | 19.35 | 12.59 | 12.47 | 6.58 | 10.17 | 12.22 | 26.02 | 8.87 | 3.6 | 35.93 | 80.61 | 78.2 | 16.17 | 20.05 | 12.46 | 6.93
|  | 600-799 | 25 | 70 | 95.72 | 96.5 | 10.19 | 40.27 | 24.46 | 77.97 | 75.58 | 21.48 | 27.72 | 20.58 | 15.34 | 6.69 | 10.79 | 13.14 | 36.21 | 11.25 | 4.09 | 25.31 | 78.22 | 75.76 | 19.6 | 26 | 15.61 | 6.17
|  | 800-999 | 12 | 48 | 44.08 | 98.44 | 7.27 | 37.03 | 19.77 | 79.82 | 78.85 | 2.97 | 5.75 | 2.86 | 19.57 | 0.61 | 3.51 | 4.12 | 17.25 | 16.67 | 2.9 | 19.62 | 79.86 | 78.87 | 2.97 | 5.73 | 19.54 | 0.6
| NUCLEAR | All Sizes | 102 | 482.75 | 3779.18 | 97.62 | 88.03 | 98.47 | 88.88 | 88.88 | 87.11 | 3.61 | 4.3 | 4.3 | 7.79 | 3.33 | 3.67 | 4.56 | 4.93 | 7.45 | 0.35 | 89.4 | 89.4 | 87.64 | 3.39 | 4.06 | 7.47 | 3.14
| All Types | 400-799 | 14 | 69 | 2931.65 | 98.78 | 80.27 | 97.28 | 82.05 | 82.05 | 79.49 | 5.46 | 6.62 | 6.62 | 13.2 | 4.74 | 5.06 | 6.39 | 7.33 | 12.89 | 0.32 | 82.51 | 82.51 | 79.93 | 4.82 | 6.03 | 13.31 | 4.18
|  | 800-999 | 35 | 169.75 | 4325.71 | 95.74 | 88.9 | 99.53 | 89.29 | 89.29 | 88 | 3.79 | 4.27 | 4.27 | 7.2 | 3.52 | 3.84 | 4.53 | 4.86 | 6.87 | 0.33 | 89.32 | 89.32 | 88.06 | 3.78 | 4.25 | 7.17 | 3.51
|  | 1000 Plus | 53 | 244 | 3742.42 | 98.6 | 88.74 | 98.08 | 90.52 | 90.52 | 88.64 | 3 | 3.71 | 3.71 | 6.68 | 2.8 | 3.17 | 4.07 | 4.35 | 6.32 | 0.37 | 90.47 | 90.47 | 88.57 | 2.98 | 3.69 | 6.75 | 2.78
| PWR | All Sizes | 65 | 307.75 | 3923.98 | 97.99 | 87.27 | 98.61 | 87.87 | 87.87 | 86.48 | 4.75 | 5.25 | 5.25 | 7.75 | 4.38 | 4.55 | 5.13 | 5.55 | 7.58 | 0.17 | 88.49 | 88.49 | 87.1 | 4.35 | 4.87 | 7.48 | 4.03
|  | 400-799 | 7 | 35 | 2806.65 | 98.82 | 80.09 | 98.22 | 80.37 | 80.37 | 78.33 | 8.56 | 9.02 | 9.02 | 12.1 | 7.53 | 7.91 | 8.55 | 9.69 | 11.71 | 0.39 | 81.54 | 81.54 | 79.46 | 7.27 | 7.8 | 12.07 | 6.39
|  | 800-999 | 23 | 109.75 | 4243.74 | 96.24 | 87.22 | 99.79 | 87.35 | 87.35 | 86.34 | 5.21 | 5.61 | 5.61 | 7.85 | 4.8 | 4.94 | 5.43 | 5.89 | 7.71 | 0.13 | 87.4 | 87.4 | 86.4 | 5.19 | 5.58 | 7.81 | 4.78
|  | 1000 Plus | 35 | 163 | 4051.54 | 98.97 | 88.12 | 98.07 | 89.84 | 89.84 | 88.34 | 3.66 | 4.25 | 4.25 | 6.74 | 3.42 | 3.56 | 4.19 | 4.48 | 6.59 | 0.15 | 89.86 | 89.86 | 88.34 | 3.62 | 4.2 | 6.77 | 3.37
| BWR | All Sizes | 34 | 161 | 3598.11 | 96.98 | 90.63 | 98.29 | 92.37 | 92.37 | 89.91 | 1.5 | 2.41 | 2.41 | 6.23 | 1.41 | 2.04 | 3.42 | 3.62 | 5.6 | 0.63 | 92.22 | 92.22 | 89.77 | 1.54 | 2.43 | 6.34 | 1.44
|  | 400-799 | 5 | 25 | 3001.38 | 98.53 | 88.75 | 96.61 | 91.77 | 91.77 | 88.65 | 2.23 | 3.58 | 3.58 | 6.13 | 2.1 | 2.42 | 4.25 | 4.51 | 5.81 | 0.32 | 91.86 | 91.86 | 88.79 | 2.25 | 3.58 | 6.02 | 2.11
|  | 800-999 | 11 | 55 | 4786.29 | 93.96 | 92.53 | 99.12 | 93.38 | 93.38 | 91.51 | 0.92 | 1.56 | 1.56 | 5.76 | 0.86 | 1.37 | 2.41 | 2.55 | 5.25 | 0.51 | 93.35 | 93.35 | 91.54 | 0.94 | 1.58 | 5.76 | 0.89
|  | 1000 Plus | 18 | 81 | 3246.58 | 98.02 | 89.96 | 98.12 | 91.86 | 91.86 | 89.22 | 1.68 | 2.63 | 2.63 | 6.58 | 1.57 | 2.37 | 3.85 | 4.08 | 5.77 | 0.81 | 91.69 | 91.69 | 89.02 | 1.73 | 2.68 | 6.7 | 1.61
| CANDU | All Sizes | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | ****
| JET | All Sizes | 342 | 1550 | 4.5 | 98.51 | 3.75 | 80.05 | 3.42 | 90.28 | 88.79 | 45.02 | 46.12 | 11.22 | 5.74 | 4.03 | 7.06 | 7.52 | 58.14 | 2.71 | 3.03 | 4.68 | 89.83 | 88.02 | 40.16 | 41.86 | 5.95 | 4.27
| ENGINE** | 1-19 | 41 | 189.08 | 7.74 | 96.07 | 0.25 | 25.89 | 0.98 | 92.83 | 91.23 | 73.86 | 75.43 | 21.57 | 4.39 | 2.78 | 5.41 | 5.64 | 85.19 | 1.77 | 2.63 | 0.96 | 92.61 | 90.95 | 75.68 | 76.93 | 4.41 | 2.98
|  | 20 Plus | 301 | 1360.92 | 4.43 | 98.57 | 3.93 | 80.62 | 3.75 | 89.94 | 88.47 | 43.51 | 44.57 | 11.11 | 5.92 | 4.2 | 7.28 | 7.78 | 56.39 | 2.83 | 3.08 | 4.88 | 89.68 | 87.87 | 39.48 | 41.2 | 6.03 | 4.34
| GAS | All Sizes | 928 | 3907.42 | 7.09 | 97.6 | 3.55 | 71.09 | 3.07 | 89.89 | 87.32 | 59.46 | 59.76 | 11.77 | 5.57 | 4.54 | 6.57 | 6.64 | 68.09 | 3.54 | 2.03 | 5 | 90.81 | 88.76 | 39.88 | 40.25 | 5.85 | 3.33
| TURBINE** | 1-19 | 174 | 718 | 4.24 | 94.96 | 0.72 | 65.66 | 1.07 | 85.6 | 83.28 | 88.42 | 88.57 | 20.81 | 6.23 | 8.19 | 10.78 | 10.88 | 91.05 | 3.64 | 2.59 | 1.09 | 86.03 | 83.38 | 88.16 | 88.29 | 5.86 | 8.14
|  | 20-49 | 241 | 916.67 | 4.82 | 96.87 | 1.5 | 69.74 | 1.47 | 90.47 | 85.4 | 79.49 | 79.54 | 15.28 | 3.83 | 5.7 | 7.07 | 7.14 | 82.76 | 2.45 | 1.37 | 2.15 | 90.5 | 84.87 | 70.85 | 71.09 | 4.27 | 5.23
|  | 50 Plus | 509 | 2260.75 | 7.29 | 98.11 | 2.92 | 65.84 | 3.91 | 90.98 | 89.3 | 43.07 | 43.48 | 8.81 | 6.02 | 2.99 | 5.09 | 5.15 | 56.47 | 3.92 | 2.1 | 4.44 | 91.13 | 89.5 | 39.38 | 39.76 | 5.95 | 2.9
| COMB. CYCLE (BLOCK REPORTED UNITS ONLY | All Sizes | 179 | 775.17 | 77.6 | 98.89 | 51.34 | 79.13 | 53 | 87.4 | 84.36 | 5.02 | 6.27 | 4.78 | 9.8 | 2.8 | 4.66 | 5.6 | 9.63 | 7.94 | 1.86 | 64.88 | 88.77 | 85.86 | 2.97 | 3.97 | 9.24 | 1.98
| HYDRO | All Sizes | 1074 | 4795.5 | 47.05 | 99.9 | 40.05 | 66.32 | 59.02 | 82.89 | 82.55 | 6.87 | 7.05 | 6.32 | 12.24 | 4.88 | 6.81 | 6.94 | 9.51 | 10.31 | 1.93 | 60.39 | 82.88 | 82.59 | 3.72 | 3.82 | 14.63 | 2.5
|  | 1-29 | 472 | 2107.58 | 137.84 | 99.78 | 38.16 | 66.17 | 57.22 | 80.74 | 80.36 | 10.28 | 10.58 | 10.2 | 11.65 | 7.61 | 9.52 | 9.74 | 12.83 | 9.74 | 1.91 | 57.68 | 84.87 | 84.33 | 5.06 | 5.53 | 11.41 | 3.72
|  | 30 Plus | 602 | 2687.92 | 31.66 | 99.91 | 40.2 | 66.33 | 60.43 | 84.56 | 84.26 | 3.99 | 4.08 | 3.5 | 12.7 | 2.74 | 4.69 | 4.75 | 6.73 | 10.75 | 1.95 | 60.61 | 82.72 | 82.45 | 3.6 | 3.67 | 14.89 | 2.4
| PUMPED STORAGE | All Sizes | 114 | 493.25 | 8.24 | 99.75 | 8.87 | 42.78 | 28.95 | 83.78 | 83.58 | 8.24 | 8.29 | 6.02 | 12.2 | 4.02 | 5.8 | 5.83 | 11.52 | 10.42 | 1.78 | 20.73 | 82.39 | 81.88 | 9.16 | 9.28 | 13.84 | 3.77
| MULTIBOILER/MULTI-TURBINE | All Sizes | 24 | 84.17 | 886.5 | 98.67 | 56.32 | 66.68 | 81.5 | 90.14 | 82.63 | 3.8 | 8.43 | 7.86 | 6.65 | 3.22 | 4.44 | 9.77 | 11.31 | 5.43 | 1.22 | 84.47 | 89.95 | 84.67 | 2.22 | 5.4 | 8.13 | 1.92
| DIESEL** | All Sizes | 203 | 583.92 | 28.02 | 99.24 | 13.06 | 71.51 | 13.99 | 94.43 | 92.98 | 18.63 | 20.29 | 12.31 | 2.37 | 3.2 | 5.15 | 5.55 | 28.71 | 0.42 | 1.95 | 18.26 | 95.6 | 94.71 | 10.74 | 12.34 | 2.2 | 2.2
**Caution: EFOR and WEFOR values may be low since deratings during reserve shutdown periods may not have been reported for a large number of these units.
*** The two methods for calculating combined cycle units is not available at this time.
**** Less than three generating companies are reporting this type of unit. To retain confidentiality of the data, no data is reported here.