## 2020-4
Generator Catagory/Classification | Start | End | # Units | Unit-Years | NMC | NDC | Attempts | Actual | SH | RSH | # RSH | Pump Hr | SCH | AH | FOH | # FOH | POH | # POH | SEPO | # SEPO | MOH | # MOH | SEMO | # SEMO | UAH | PH | EFDH | ESDH | EFDHRS | EDOH | POF | MOF | ART | SR | NCF | NOF | SF | AF | EAF | FOR | EFOR | EFORd | SOF | FOF | UOF | EUOF | EUOR | WSF | WAF | WEAF | WFOR | WEFOR | WSOF | WFOF
FOSSIL All Fuel Types All Sizes | 2016 | 2020 | 1192 | 4994.08 | 325 | 324 | 29.03 | 28.71 | 4214.78 | 2428.87 | 13.76 | 0 | 0 | 6643.65 | 424.73 | 5.32 | 679.13 | 1.32 | 37.06 | 0.13 | 308.34 | 2.49 | 6.16 | 0.05 | 1455.42 | 8099.07 | 143.22 | 50.66 | 36.72 | 193.88 | 8.84 | 3.88 | 146.81 | 98.9 | 40.56 | 69.64 | 52.04 | 82.03 | 79.23 | 9.15 | 12.15 | 9.31 | 12.73 | 5.24 | 9.13 | 11.14 | 18.05 | 58.24 | 81.06 | 78.39 | 8.31 | 11.14 | 13.66 | 5.28
FOSSIL All Fuel Types 001-099 | 2016 | 2020 | 253 | 1046.92 | 52 | 51 | 32.31 | 32.14 | 3502.62 | 3073.8 | 16.78 | 0 | 0 | 6576.43 | 414.26 | 4.34 | 475.35 | 1.15 | 34.09 | 0.08 | 288.89 | 1.65 | 1.97 | 0.01 | 1214.56 | 7790.98 | 128.33 | 57.41 | 38.28 | 185.74 | 6.54 | 3.73 | 108.98 | 99.47 | 29.52 | 63.4 | 44.96 | 84.41 | 81.2 | 10.58 | 13.72 | 9.41 | 10.27 | 5.32 | 9.05 | 11 | 20.16 | 46.56 | 84.55 | 81.49 | 9.95 | 13.11 | 10.3 | 5.15
FOSSIL All Fuel Types 100-199 | 2016 | 2020 | 272 | 1070.17 | 137 | 136 | 61.65 | 61.39 | 3027.44 | 3223.1 | 16.44 | 0 | 0 | 6250.54 | 373.65 | 4.02 | 634.77 | 1.24 | 29.65 | 0.1 | 285 | 2.07 | 4.67 | 0.03 | 1327.74 | 7578.28 | 120.07 | 58.84 | 52.08 | 178.91 | 8.77 | 3.82 | 49.31 | 99.58 | 24.97 | 60.12 | 39.95 | 82.48 | 79.61 | 10.99 | 14.3 | 8.64 | 12.59 | 4.93 | 8.75 | 10.55 | 21.29 | 41.54 | 82.3 | 79.35 | 10.79 | 14.06 | 12.68 | 5.02
FOSSIL All Fuel Types 200-299 | 2016 | 2020 | 137 | 552.67 | 229 | 228 | 16.39 | 15.99 | 4483.34 | 2126.88 | 13.79 | 0 | 0 | 6610.22 | 387.39 | 5.38 | 639.44 | 1.27 | 19.45 | 0.11 | 311.12 | 3.14 | 8.69 | 0.08 | 1366.08 | 7976.3 | 128.45 | 38.65 | 36 | 167.1 | 8.26 | 4.01 | 280.38 | 97.56 | 36.31 | 65.02 | 56.21 | 82.87 | 80.46 | 7.95 | 10.51 | 8.71 | 12.27 | 4.86 | 8.87 | 10.71 | 16.32 | 55.84 | 83.13 | 80.75 | 7.85 | 10.37 | 12.11 | 4.76
FOSSIL All Fuel Types 300-399 | 2016 | 2020 | 112 | 481 | 336 | 335 | 20.31 | 19.91 | 4167.94 | 2722.22 | 17.75 | 0 | 0 | 6890.15 | 397.73 | 5.91 | 844.06 | 1.6 | 55.5 | 0.17 | 299.26 | 3.02 | 12.96 | 0.07 | 1609.5 | 8499.66 | 157.23 | 44.29 | 33.34 | 201.53 | 10.58 | 3.67 | 209.34 | 98.03 | 29.63 | 61.14 | 49.04 | 81.06 | 78.53 | 8.71 | 12.07 | 9.4 | 14.26 | 4.68 | 8.35 | 10.38 | 17.94 | 48.47 | 81.02 | 78.55 | 8.73 | 12.06 | 14.35 | 4.64
FOSSIL All Fuel Types 400-599 | 2016 | 2020 | 198 | 884.83 | 482 | 480 | 15.35 | 14.97 | 5031.55 | 1747.41 | 10.39 | 0 | 0 | 6778.96 | 549.33 | 7.04 | 765.82 | 1.45 | 49.05 | 0.17 | 327.42 | 2.88 | 5.75 | 0.08 | 1697.37 | 8476.33 | 176.38 | 46.1 | 30.91 | 222.48 | 9.61 | 3.93 | 336.11 | 97.52 | 40.97 | 68.77 | 59.36 | 79.98 | 77.1 | 9.84 | 12.93 | 11.13 | 13.54 | 6.48 | 10.41 | 12.71 | 18.1 | 59.57 | 80.1 | 77.25 | 9.74 | 12.79 | 13.47 | 6.43
FOSSIL All Fuel Types 600-799 | 2016 | 2020 | 145 | 622.5 | 662 | 659 | 11.31 | 10.93 | 5472.59 | 1428.26 | 6.33 | 0 | 0 | 6900.85 | 414.36 | 6.28 | 792.21 | 1.35 | 36.91 | 0.14 | 315.36 | 2.82 | 9.13 | 0.06 | 1567.98 | 8468.83 | 165.52 | 43.4 | 27.9 | 208.92 | 9.79 | 3.83 | 500.69 | 96.64 | 48.62 | 75.09 | 64.62 | 81.49 | 78.75 | 7.04 | 9.8 | 8.76 | 13.62 | 4.89 | 8.72 | 10.91 | 14.8 | 64.75 | 81.4 | 78.68 | 7.06 | 9.81 | 13.68 | 4.92
FOSSIL All Fuel Types 800-999 | 2016 | 2020 | 59 | 276 | 827 | 827 | 18.54 | 18.17 | 5418.66 | 1665.35 | 14.33 | 0 | 0 | 7084 | 388.5 | 5.38 | 788.29 | 1.33 | 48.34 | 0.23 | 329.59 | 2.83 | 6.87 | 0.07 | 1561.59 | 8645.6 | 138.43 | 44.94 | 22.16 | 183.37 | 9.68 | 3.89 | 298.22 | 98 | 44.85 | 71.09 | 62.68 | 81.94 | 79.79 | 6.69 | 9.04 | 7.78 | 13.57 | 4.49 | 8.39 | 10.38 | 14.53 | 63.09 | 82.05 | 79.91 | 6.58 | 8.91 | 13.5 | 4.44
FOSSIL All Fuel Types 1000 Plus | 2016 | 2020 | 16 | 55 | 1234 | 1231 | 9.53 | 9.16 | 5489.23 | 919.86 | 4.69 | 0 | 0 | 6409.09 | 529.62 | 5.15 | 1122.74 | 1.35 | 9.43 | 0.05 | 698.28 | 3.76 | 0 | 0 | 2360.07 | 8769.16 | 148.1 | 125.73 | 12.04 | 273.83 | 12.91 | 7.96 | 599.26 | 96.12 | 47.38 | 74.31 | 62.6 | 73.09 | 69.72 | 8.8 | 11.24 | 10.3 | 20.87 | 6.04 | 14 | 16.15 | 21.01 | 63.76 | 73.24 | 70 | 8.82 | 11.19 | 20.59 | 6.17
FOSSIL Coal Primary All Sizes | 2016 | 2020 | 731 | 2883.58 | 394 | 392 | 20.92 | 20.61 | 5100.6 | 1504.47 | 6.31 | 0 | 0 | 6605.07 | 422.27 | 5.92 | 653.28 | 1.15 | 35.7 | 0.13 | 303.44 | 2.66 | 7.06 | 0.07 | 1421.74 | 8026.8 | 139.57 | 58.93 | 20.58 | 198.5 | 8.58 | 3.87 | 247.48 | 98.52 | 49.73 | 73.04 | 63.54 | 82.29 | 79.47 | 7.65 | 10.14 | 8.71 | 12.45 | 5.26 | 9.13 | 11.14 | 15.26 | 68.09 | 81.39 | 78.69 | 7.31 | 9.71 | 13.24 | 5.37
FOSSIL Coal Primary 001-099 | 2016 | 2020 | 101 | 334 | 56 | 56 | 13.99 | 13.78 | 3507.75 | 3070.45 | 11.52 | 0 | 0 | 6578.2 | 301.03 | 4.65 | 487.24 | 1.1 | 26.91 | 0.08 | 181.23 | 1.43 | 1.06 | 0.02 | 997.47 | 7575.66 | 93.48 | 72.54 | 37.32 | 166.02 | 6.79 | 2.41 | 254.55 | 98.5 | 35.75 | 72.94 | 46.3 | 86.83 | 84.14 | 7.9 | 10.26 | 8.02 | 9.19 | 3.97 | 6.38 | 8 | 14.98 | 49.02 | 87.45 | 84.77 | 7.08 | 9.4 | 8.81 | 3.73
FOSSIL Coal Primary 100-199 | 2016 | 2020 | 162 | 542.83 | 143 | 142 | 60.64 | 60.43 | 3775.63 | 1945.98 | 6.16 | 0 | 0 | 5721.62 | 359.02 | 4.17 | 496.03 | 0.92 | 23.49 | 0.09 | 277.9 | 2 | 5.95 | 0.04 | 1162.38 | 6883.99 | 119 | 82.16 | 35.37 | 201.17 | 7.55 | 4.12 | 62.48 | 99.65 | 36.34 | 66.06 | 54.85 | 83.11 | 79.65 | 8.68 | 11.46 | 8.42 | 11.67 | 5.22 | 9.34 | 11.29 | 17.43 | 55.01 | 82.94 | 79.5 | 8.92 | 11.81 | 11.67 | 5.39
FOSSIL Coal Primary 200-299 | 2016 | 2020 | 91 | 358.42 | 229 | 227 | 11.1 | 10.72 | 4925.69 | 1532.69 | 6.88 | 0 | 0 | 6458.39 | 428.77 | 5.88 | 588.52 | 1.16 | 17.98 | 0.13 | 346.77 | 3.48 | 13.4 | 0.12 | 1395.44 | 7853.82 | 108.71 | 46.07 | 12.44 | 154.78 | 7.72 | 4.59 | 459.49 | 96.58 | 43.95 | 70.9 | 62.72 | 82.23 | 79.8 | 8.01 | 10.01 | 8.87 | 12.31 | 5.46 | 10.05 | 11.64 | 15.96 | 62 | 82.7 | 80.25 | 7.98 | 9.99 | 11.93 | 5.37
FOSSIL Coal Primary 300-399 | 2016 | 2020 | 65 | 271 | 328 | 327 | 13.49 | 13.1 | 5230.31 | 1682.98 | 7.89 | 0 | 0 | 6913.29 | 457.65 | 7.02 | 744.14 | 1.11 | 60.52 | 0.18 | 355.07 | 3.24 | 10.79 | 0.09 | 1628.17 | 8541.46 | 201.15 | 62.42 | 23.68 | 263.56 | 9.42 | 4.28 | 399.26 | 97.11 | 42.24 | 69.07 | 61.23 | 80.94 | 77.7 | 8.05 | 11.53 | 10.02 | 13.7 | 5.36 | 9.64 | 12.25 | 17.18 | 61.16 | 81.01 | 77.81 | 8.02 | 11.5 | 13.66 | 5.33
FOSSIL Coal Primary 400-599 | 2016 | 2020 | 138 | 607.25 | 485 | 484 | 11.89 | 11.55 | 6024.08 | 862.18 | 5 | 0 | 0 | 6886.26 | 519.93 | 7.37 | 722.7 | 1.24 | 51.98 | 0.17 | 291.44 | 2.8 | 7.51 | 0.09 | 1593.57 | 8479.83 | 172.52 | 43.66 | 14.49 | 216.18 | 9.14 | 3.53 | 521.57 | 97.14 | 51.14 | 71.84 | 71.04 | 81.21 | 78.36 | 7.95 | 10.56 | 9.79 | 12.66 | 6.13 | 9.66 | 11.93 | 14.75 | 71.19 | 81.27 | 78.45 | 7.87 | 10.46 | 12.65 | 6.08
FOSSIL Coal Primary 600-799 | 2016 | 2020 | 118 | 516.17 | 662 | 660 | 10.6 | 10.26 | 6100.38 | 932.35 | 4.53 | 0 | 0 | 7032.73 | 402.37 | 6.4 | 730.7 | 1.21 | 31.3 | 0.13 | 312.39 | 2.89 | 5.95 | 0.06 | 1482.72 | 8515.45 | 144.42 | 48.11 | 6.81 | 192.53 | 8.95 | 3.74 | 594.58 | 96.79 | 54.66 | 76.25 | 71.64 | 82.59 | 80.03 | 6.19 | 8.4 | 7.78 | 12.69 | 4.73 | 8.46 | 10.41 | 12.99 | 71.68 | 82.55 | 79.98 | 6.2 | 8.41 | 12.71 | 4.73
FOSSIL Coal Primary 800-999 | 2016 | 2020 | 42 | 197.92 | 835 | 834 | 9.44 | 9.03 | 6061.13 | 918.97 | 3.77 | 0 | 0 | 6980.09 | 455.9 | 5.84 | 811.47 | 1.37 | 51.19 | 0.23 | 351 | 2.91 | 7.08 | 0.06 | 1676.63 | 8656.73 | 136.32 | 51.11 | 21.8 | 187.43 | 9.97 | 4.14 | 671.22 | 95.66 | 50.92 | 72.58 | 70.02 | 80.63 | 78.44 | 7 | 9.06 | 8.42 | 14.1 | 5.27 | 9.4 | 11.42 | 14.33 | 70.16 | 80.86 | 78.69 | 6.85 | 8.89 | 13.98 | 5.16
FOSSIL Coal Primary 1000 Plus | 2016 | 2020 | 14 | 51 | 1255 | 1251 | 9.76 | 9.39 | 5767.2 | 625.6 | 4.41 | 0 | 0 | 6392.8 | 569.62 | 5.43 | 1124.73 | 1.39 | 10.17 | 0.06 | 671.61 | 3.88 | 0 | 0 | 2376.14 | 8768.94 | 128.29 | 119.58 | 0.85 | 247.87 | 12.94 | 7.66 | 614.19 | 96.21 | 49.76 | 75.05 | 65.77 | 72.9 | 69.82 | 8.99 | 11.01 | 10.33 | 20.6 | 6.5 | 14.15 | 16.01 | 20.03 | 66.3 | 73.11 | 70.09 | 8.96 | 11.01 | 20.36 | 6.53
FOSSIL Oil Primary All Sizes | 2016 | 2020 | 73 | 238.17 | 292 | 292 | 21.33 | 21.14 | 1903.55 | 4589.88 | 19.14 | 0 | 0 | 6493.43 | 368.02 | 2.55 | 614.57 | 1.02 | 18.1 | 0.08 | 427.89 | 1.79 | 7.85 | 0.04 | 1436.43 | 7929.86 | 158.32 | 19.77 | 62.28 | 178.1 | 7.98 | 5.49 | 90.04 | 99.11 | 5.74 | 42.74 | 24 | 81.89 | 79.57 | 16.2 | 22.55 | 11.2 | 13.47 | 4.64 | 10.14 | 12.29 | 35.14 | 13.44 | 82.14 | 80.48 | 15.07 | 22.06 | 15.48 | 2.39
FOSSIL Oil Primary 001-099 | 2016 | 2020 | 16 | 76.75 | 65 | 65 | 48.35 | 48.21 | 3626.52 | 2045.57 | 34.48 | 0 | 0 | 5672.09 | 516.09 | 3.02 | 279.68 | 0.23 | 0 | 0 | 645.19 | 1.77 | 0 | 0 | 1440.96 | 7113.06 | 327.87 | 28.69 | 106.54 | 356.56 | 3.93 | 9.07 | 75.22 | 99.71 | 28.98 | 48.42 | 50.98 | 79.74 | 74.73 | 12.46 | 19.86 | 14.2 | 13 | 7.26 | 16.33 | 21.34 | 31.01 | 59.85 | 80.38 | 74.99 | 8.27 | 15.45 | 14.23 | 5.4
FOSSIL Oil Primary 100-199 | 2016 | 2020 | 17 | 47.75 | 123 | 123 | 6.39 | 6.16 | 1541.2 | 5179.09 | 8.21 | 0 | 0 | 6720.3 | 548.74 | 1.82 | 536.76 | 0.8 | 2.16 | 0.02 | 352.96 | 1.59 | 0 | 0 | 1440.62 | 8160.92 | 115.37 | 9.01 | 43.79 | 124.38 | 6.6 | 4.33 | 250.19 | 96.4 | 13 | 59.73 | 18.89 | 82.35 | 80.82 | 26.26 | 31.12 | 17.38 | 10.93 | 6.72 | 11.05 | 12.53 | 41.04 | 21.76 | 82.25 | 80.61 | 22.08 | 27.03 | 11.59 | 6.17
FOSSIL Oil Primary 200-299 | 2016 | 2020 | **** | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [10 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: POF to FOR
FOSSIL Oil Primary 300-399 | 2016 | 2020 | 11 | 43 | 367 | 367 | 8.56 | 8.44 | 1792.65 | 4547.39 | 12.47 | 0 | 0 | 6340.04 | 283.09 | 2.56 | 886.55 | 1.81 | 27.17 | 0.09 | 213.34 | 1.58 | 0.13 | 0.02 | 1410.29 | 7750.33 | 22.31 | 15.38 | 5.91 | 37.69 | 11.79 | 2.75 | 212.4 | 98.6 | 8.35 | 35.28 | 23.13 | 81.8 | 81.32 | 13.64 | 14.67 | 10.25 | 14.54 | 3.65 | 6.41 | 6.71 | 22.66 | 23.67 | 82.04 | 81.54 | 12.62 | 13.65 | 14.54 | 3.42
FOSSIL Oil Primary 400-599 | 2016 | 2020 | 10 | 29.17 | 453 | 452 | 8.26 | 8.16 | 163.3 | 7394.65 | 12.62 | 0 | 0 | 7557.95 | 242.75 | 2.74 | 743.65 | 1.61 | 44.07 | 0.1 | 182.44 | 1.99 | 0 | 0 | 1212.92 | 8770.87 | 49.05 | 12.54 | 31.47 | 61.59 | 8.98 | 2.08 | 20.01 | 98.79 | 0.51 | 28.29 | 1.86 | 86.17 | 85.22 | 59.78 | 66.69 | 23.32 | 11.06 | 2.77 | 4.85 | 5.42 | 76.41 | 1.8 | 86.17 | 85.24 | 60.63 | 67.28 | 11.07 | 2.77
FOSSIL Oil Primary 600-799 | 2016 | 2020 | 9 | 24.33 | 627 | 625 | 15.41 | 15.21 | 425.92 | 6943.15 | 20.05 | 0 | 0 | 7369.07 | 91.67 | 2.92 | 730.98 | 1.56 | 23.39 | 0.21 | 487.26 | 2.14 | 65.89 | 0.21 | 1399.19 | 8768.26 | 84.99 | 9.6 | 74.82 | 94.59 | 8.6 | 6.31 | 28 | 98.7 | 1.88 | 40.01 | 4.86 | 84.04 | 82.74 | 17.71 | 29.82 | 10.55 | 14.91 | 1.05 | 7.35 | 8.35 | 63.65 | 4.7 | 83 | 81.6 | 17.77 | 31.35 | 15.98 | 1.02
FOSSIL Oil Primary 800-999 | 2016 | 2020 | 7 | 12.92 | 814 | 812 | 3.79 | 3.25 | 108.91 | 6809.84 | 6.89 | 0 | 0 | 6918.75 | 17.33 | 1.39 | 1338.28 | 1.55 | 91.8 | 0.54 | 385.61 | 1.94 | 20.23 | 0.23 | 1853.25 | 8772 | 75.35 | 0 | 73.86 | 75.35 | 16.3 | 4.63 | 33.51 | 85.75 | 0.51 | 41.41 | 1.24 | 78.87 | 77.81 | 13.73 | 46.32 | 11.39 | 20.93 | 0.2 | 4.82 | 5.68 | 82.27 | 1.22 | 79.01 | 77.94 | 13.73 | 46.78 | 20.8 | 0.19
FOSSIL Gas Primary All Sizes | 2016 | 2020 | 373 | 1461.08 | 232 | 232 | 37.81 | 37.47 | 2264.33 | 4274.72 | 27.15 | 0 | 0 | 6539.06 | 445.38 | 4.23 | 777.3 | 1.64 | 43.46 | 0.11 | 340.74 | 2.45 | 5 | 0.04 | 1611.88 | 8150.94 | 129.82 | 26.22 | 72.06 | 156.04 | 10.07 | 4.24 | 60.43 | 99.1 | 12.77 | 42.72 | 27.78 | 80.22 | 77.94 | 16.44 | 20.68 | 11.17 | 14.31 | 5.46 | 9.71 | 11.45 | 29.72 | 29.9 | 78.32 | 75.82 | 16.16 | 20.83 | 15.92 | 5.76
FOSSIL Gas Primary 001-099 | 2016 | 2020 | 100 | 379.08 | 53 | 52 | 31.79 | 31.62 | 1684 | 4495.09 | 17.14 | 0 | 0 | 6179.09 | 521.22 | 2.65 | 452.46 | 1.03 | 44.73 | 0.07 | 385.47 | 1.53 | 1.27 | 0.01 | 1405.15 | 7584.23 | 70.74 | 2.46 | 44.02 | 73.2 | 6.56 | 5.1 | 53.26 | 99.47 | 12.33 | 44.73 | 22.2 | 81.47 | 79.76 | 23.64 | 26.32 | 11.87 | 11.65 | 6.87 | 11.97 | 12.93 | 37.19 | 27.57 | 81.46 | 79.64 | 20.57 | 23 | 11.41 | 7.14
FOSSIL Gas Primary 100-199 | 2016 | 2020 | 113 | 456.25 | 130 | 130 | 53.15 | 52.82 | 2145.29 | 4635.39 | 29.93 | 0 | 0 | 6780.67 | 343.67 | 4.06 | 819.07 | 1.67 | 40.89 | 0.12 | 294.05 | 2.21 | 3.86 | 0.03 | 1501.53 | 8282.21 | 124.37 | 33.9 | 75.47 | 158.27 | 10.38 | 3.6 | 40.62 | 99.38 | 12.19 | 45.31 | 25.9 | 81.87 | 79.52 | 13.81 | 18.25 | 8.92 | 13.98 | 4.15 | 7.75 | 9.46 | 27.18 | 26.89 | 81.59 | 79.07 | 13.49 | 17.76 | 14.22 | 4.2
FOSSIL Gas Primary 200-299 | 2016 | 2020 | 43 | 168 | 231 | 231 | 26.34 | 26.02 | 3216.19 | 3567.62 | 27.75 | 0 | 0 | 6783.82 | 279.33 | 3.84 | 763.31 | 1.5 | 20.71 | 0.08 | 266.32 | 2.62 | 0 | 0 | 1329.66 | 8113.48 | 164.26 | 22.93 | 89.97 | 187.18 | 9.66 | 3.28 | 123.6 | 98.79 | 17.52 | 43.7 | 39.64 | 83.61 | 81.28 | 7.99 | 12.37 | 8.19 | 12.95 | 3.44 | 6.73 | 9.02 | 18.92 | 40.08 | 83.5 | 81.27 | 7.64 | 11.82 | 13.19 | 3.31
FOSSIL Gas Primary 300-399 | 2016 | 2020 | 39 | 153.5 | 344 | 343 | 32.64 | 32.18 | 2668.25 | 4234.67 | 34.14 | 0 | 0 | 6902.92 | 353.84 | 4.98 | 1033.45 | 2.35 | 57.3 | 0.17 | 244.37 | 3.17 | 21.53 | 0.06 | 1710.5 | 8613.42 | 128.95 | 24.12 | 60.88 | 153.06 | 12.66 | 3.09 | 82.92 | 98.59 | 11.54 | 37.28 | 30.98 | 80.14 | 78.15 | 11.71 | 15.66 | 9.59 | 15.75 | 4.11 | 7.2 | 8.8 | 22.59 | 30.95 | 79.9 | 77.99 | 11.74 | 15.58 | 15.98 | 4.12
FOSSIL Gas Primary 400-599 | 2016 | 2020 | 51 | 217.33 | 481 | 481 | 26.47 | 25.99 | 2567.05 | 3700.21 | 26.42 | 0 | 0 | 6267.26 | 698.11 | 6.52 | 909.52 | 2.02 | 38.38 | 0.14 | 469.44 | 3.41 | 2.34 | 0.06 | 2117.79 | 8385.05 | 185.88 | 56.29 | 81.15 | 242.17 | 11.3 | 5.63 | 98.77 | 98.19 | 13.26 | 43.27 | 30.61 | 74.74 | 71.74 | 21.38 | 26.42 | 16.96 | 16.93 | 8.33 | 13.95 | 16.31 | 35.68 | 30.64 | 75.17 | 72.15 | 21.11 | 26.11 | 16.63 | 8.2
FOSSIL Gas Primary 600-799 | 2016 | 2020 | 17 | 53.75 | 695 | 695 | 16.07 | 15.11 | 2148.06 | 3661.77 | 16.19 | 0 | 0 | 5809.83 | 651.99 | 7.14 | 1523 | 2.75 | 116.33 | 0.32 | 382.54 | 3.27 | 18.77 | 0.11 | 2692.63 | 8502.46 | 314.6 | 22.91 | 210.94 | 337.51 | 19.28 | 4.72 | 142.16 | 94.03 | 13.32 | 49.92 | 25.26 | 68.33 | 64.36 | 23.28 | 32.1 | 21.71 | 24 | 7.67 | 12.39 | 16.23 | 40.23 | 26.69 | 69.02 | 65.3 | 22.29 | 30.52 | 23.33 | 7.65
FOSSIL Gas Primary 800-999 | 2016 | 2020 | 10 | 33.17 | 787 | 787 | 87.26 | 86.92 | 2048.88 | 5319.79 | 90.42 | 0 | 0 | 7368.67 | 251.39 | 3.38 | 726.21 | 1.36 | 30.87 | 0.06 | 383.87 | 4.28 | 7.05 | 0.15 | 1399.39 | 8768.05 | 42.98 | 26.95 | 22.02 | 69.93 | 8.63 | 4.46 | 23.57 | 99.61 | 7.57 | 32.46 | 23.37 | 84.04 | 83.24 | 10.93 | 12.68 | 5.37 | 13.09 | 2.87 | 7.33 | 8.09 | 25.79 | 23.34 | 83.79 | 82.97 | 11.13 | 12.88 | 13.29 | 2.92
FOSSIL Lignite Primary All Sizes | 2016 | 2020 | 34 | 110.75 | 499 | 499 | 83.04 | 82.41 | 6911.43 | 366.12 | 1.58 | 0 | 0 | 7277.56 | 352.77 | 6.55 | 485.18 | 1.03 | 41.19 | 0.23 | 115.18 | 1.35 | 10.85 | 0.05 | 1005.18 | 8282.74 | 272.67 | 39.19 | 0.89 | 311.87 | 6.36 | 1.52 | 83.87 | 99.24 | 65.84 | 78.11 | 83.44 | 87.86 | 83.32 | 4.86 | 8.61 | 8.21 | 7.88 | 4.26 | 5.78 | 9.33 | 10.45 | 84.29 | 88.52 | 84.3 | 4.68 | 8.71 | 7.35 | 4.13
FOSSIL Oil/Gas Primary 001-099 | 2016 | 2020 | 115 | 455.83 | 55 | 55 | 34.58 | 34.41 | 2011.07 | 4082.66 | 20.06 | 0 | 0 | 6093.72 | 520.36 | 2.71 | 423.37 | 0.89 | 37.2 | 0.05 | 429.2 | 1.57 | 1.05 | 0.01 | 1411.18 | 7504.9 | 114.04 | 6.87 | 54.55 | 120.91 | 6.14 | 5.73 | 58.44 | 99.51 | 15.54 | 45.99 | 26.8 | 81.2 | 78.96 | 20.56 | 24.53 | 12 | 11.87 | 6.93 | 12.67 | 14.27 | 35.5 | 33.78 | 81.25 | 78.74 | 16.76 | 20.66 | 11.95 | 6.8
FOSSIL Oil/Gas Primary 100-199 | 2016 | 2020 | 122 | 504 | 130 | 129 | 48.72 | 48.4 | 2088.06 | 4686.9 | 27.87 | 0 | 0 | 6774.95 | 363.1 | 3.85 | 792.32 | 1.59 | 37.22 | 0.11 | 299.63 | 2.15 | 3.5 | 0.03 | 1495.76 | 8270.72 | 123.52 | 31.54 | 72.47 | 155.06 | 10.03 | 3.67 | 43.14 | 99.34 | 12.26 | 46.35 | 25.25 | 81.91 | 79.64 | 14.81 | 19.28 | 9.32 | 13.69 | 4.39 | 8.06 | 9.74 | 28.33 | 26.45 | 81.65 | 79.2 | 14.17 | 18.48 | 13.99 | 4.37
FOSSIL Oil/Gas Primary 200-299 | 2016 | 2020 | 43 | 168.25 | 231 | 231 | 26.32 | 26 | 3211.63 | 3574.48 | 27.75 | 0 | 0 | 6786.1 | 279.22 | 3.86 | 762.17 | 1.5 | 20.68 | 0.08 | 266.22 | 2.63 | 0 | 0 | 1328.29 | 8114.4 | 164.01 | 22.89 | 89.83 | 186.91 | 9.65 | 3.28 | 123.52 | 98.78 | 17.49 | 43.7 | 39.58 | 83.63 | 81.3 | 8 | 12.38 | 8.19 | 12.93 | 3.44 | 6.72 | 9.01 | 18.94 | 40.01 | 83.52 | 81.3 | 7.64 | 11.82 | 13.17 | 3.31
FOSSIL Oil/Gas Primary 300-399 | 2016 | 2020 | 50 | 196.5 | 349 | 348 | 27.37 | 26.98 | 2476.64 | 4303.1 | 29.39 | 0 | 0 | 6779.74 | 338.36 | 4.45 | 1001.3 | 2.23 | 50.71 | 0.15 | 237.58 | 2.82 | 16.85 | 0.05 | 1644.81 | 8424.55 | 105.61 | 22.2 | 48.85 | 127.82 | 12.49 | 3.02 | 91.8 | 98.58 | 10.87 | 36.94 | 29.4 | 80.48 | 78.79 | 12.02 | 15.5 | 9.5 | 15.51 | 4.02 | 7.04 | 8.38 | 22.6 | 29.42 | 80.35 | 78.74 | 11.89 | 15.25 | 15.68 | 3.97
FOSSIL Oil/Gas Primary 400-599 | 2016 | 2020 | 60 | 246.5 | 478 | 477 | 24.31 | 23.88 | 2282.64 | 4137.34 | 24.79 | 0 | 0 | 6419.98 | 644.23 | 6.07 | 889.89 | 1.97 | 39.06 | 0.14 | 435.49 | 3.25 | 2.06 | 0.05 | 2010.72 | 8430.7 | 169.69 | 51.11 | 75.27 | 220.8 | 11.02 | 5.19 | 95.59 | 98.23 | 11.77 | 43.16 | 27.08 | 76.15 | 73.4 | 22.01 | 27.11 | 16.62 | 16.21 | 7.64 | 12.83 | 14.97 | 36.55 | 27.27 | 76.45 | 73.68 | 21.71 | 26.77 | 15.98 | 7.56
FOSSIL Oil/Gas Primary 600-799 | 2016 | 2020 | 22 | 78.08 | 674 | 673 | 15.87 | 15.14 | 1611.38 | 4684.36 | 17.39 | 0 | 0 | 6295.74 | 477.37 | 5.83 | 1276.19 | 2.38 | 87.36 | 0.28 | 415.17 | 2.92 | 33.45 | 0.14 | 2289.55 | 8585.29 | 243.05 | 18.76 | 168.52 | 261.81 | 15.88 | 5.23 | 106.43 | 95.4 | 9.93 | 49.24 | 18.77 | 73.33 | 70.21 | 22.85 | 31.92 | 18.86 | 21.11 | 5.56 | 10.79 | 13.72 | 43.32 | 20.18 | 73.16 | 70.13 | 21.99 | 30.58 | 21.15 | 5.69
FOSSIL Oil/Gas Primary 800-999 | 2016 | 2020 | 12 | 46.08 | 794 | 794 | 63.86 | 63.47 | 1505.13 | 5737.43 | 67.01 | 0 | 0 | 7242.56 | 185.78 | 2.82 | 897.77 | 1.41 | 47.95 | 0.2 | 384.36 | 3.62 | 10.74 | 0.17 | 1526.6 | 8769.16 | 52.05 | 19.4 | 36.55 | 71.45 | 10.78 | 4.51 | 23.71 | 99.39 | 5.54 | 32.64 | 17.16 | 82.59 | 81.72 | 10.99 | 13.77 | 5.21 | 15.29 | 2.12 | 6.62 | 7.41 | 30.25 | 16.98 | 82.41 | 81.53 | 11.19 | 14.01 | 15.45 | 2.14
FOSSIL Oil/Gas Primary All Sizes | 2016 | 2020 | 426 | 1699.25 | 241 | 240 | 35.5 | 35.18 | 2213.76 | 4318.9 | 26.03 | 0 | 0 | 6532.66 | 434.53 | 3.99 | 754.49 | 1.55 | 39.91 | 0.11 | 352.96 | 2.36 | 5.4 | 0.04 | 1587.29 | 8119.95 | 133.82 | 25.32 | 70.69 | 159.14 | 9.78 | 4.41 | 62.93 | 99.1 | 11.58 | 42.72 | 27.26 | 80.45 | 78.17 | 16.41 | 20.9 | 11.17 | 14.2 | 5.35 | 9.76 | 11.56 | 30.4 | 27.1 | 78.97 | 76.61 | 16.07 | 20.93 | 15.84 | 5.19
NUCLEAR All Types All Sizes | 2016 | 2020 | 102 | 471.75 | 1013 | 1009 | 1.59 | 1.55 | 8094.49 | 0.09 | 0 | 0 | 0 | 8094.58 | 142.36 | 0.86 | 455.08 | 0.92 | 18.93 | 0.09 | 19.3 | 0.16 | 0.29 | 0.01 | 635.96 | 8730.54 | 44.06 | 80.18 | 0 | 124.24 | 5.43 | 0.22 | 5222.25 | 97.48 | 91.71 | 99.11 | 92.71 | 92.72 | 90.88 | 1.73 | 2.26 | 2.26 | 5.65 | 1.63 | 1.85 | 2.72 | 2.87 | 92.53 | 92.53 | 90.7 | 1.81 | 2.34 | 5.76 | 1.71
NUCLEAR All Types 400-799 | 2016 | 2020 | 13 | 56 | 621 | 616 | 1.36 | 1.3 | 8029.41 | 0 | 0 | 0 | 0 | 8029.41 | 132.57 | 1.02 | 376.41 | 0.8 | 22.57 | 0.09 | 32.19 | 0.2 | 0.21 | 0.02 | 563.95 | 8593.36 | 57.39 | 75.28 | 0 | 132.67 | 4.64 | 0.38 | 6176.47 | 95.59 | 91.03 | 97.56 | 93.44 | 93.44 | 90.98 | 1.62 | 2.33 | 2.33 | 5.02 | 1.54 | 1.92 | 2.85 | 2.99 | 93.31 | 93.31 | 90.89 | 1.67 | 2.39 | 5.11 | 1.58
NUCLEAR All Types 800-999 | 2016 | 2020 | 35 | 161.75 | 887 | 885 | 1.59 | 1.55 | 8184.08 | 0 | 0 | 0 | 0 | 8184.08 | 113.46 | 0.82 | 413.36 | 0.88 | 23.87 | 0.09 | 19.25 | 0.16 | 0.01 | 0.01 | 569.95 | 8754.03 | 44.86 | 70.86 | 0 | 115.72 | 4.99 | 0.22 | 5280.05 | 97.48 | 93.08 | 99.63 | 93.49 | 93.49 | 91.93 | 1.37 | 1.91 | 1.91 | 5.21 | 1.3 | 1.52 | 2.43 | 2.56 | 93.42 | 93.42 | 91.87 | 1.4 | 1.94 | 5.25 | 1.33
NUCLEAR All Types 1000 Plus | 2016 | 2020 | 54 | 254 | 1180 | 1174 | 1.63 | 1.61 | 8051.78 | 0.16 | 0.01 | 0 | 0 | 8051.95 | 162.93 | 0.86 | 498.99 | 0.96 | 14.98 | 0.1 | 16.49 | 0.16 | 0.49 | 0 | 693.88 | 8745.82 | 40.61 | 87.2 | 0 | 127.81 | 5.88 | 0.19 | 5001.11 | 98.77 | 91.14 | 99.04 | 92.06 | 92.07 | 90.18 | 1.98 | 2.48 | 2.48 | 6.07 | 1.86 | 2.06 | 2.87 | 3.04 | 92.02 | 92.02 | 90.13 | 2.03 | 2.53 | 6.07 | 1.91
NUCLEAR PWR All Sizes | 2016 | 2020 | 62 | 289 | 1031 | 1027 | 1.51 | 1.47 | 8077.6 | 0 | 0 | 0 | 0 | 8077.6 | 126.25 | 0.83 | 497.82 | 0.88 | 24.49 | 0.11 | 11.41 | 0.1 | 0.04 | 0 | 660.01 | 8737.62 | 31.23 | 55.76 | 0 | 86.99 | 5.98 | 0.13 | 5494.97 | 97.35 | 92.04 | 99.65 | 92.45 | 92.45 | 91.06 | 1.54 | 1.92 | 1.92 | 6.11 | 1.44 | 1.58 | 2.12 | 2.25 | 92.37 | 92.37 | 90.97 | 1.55 | 1.94 | 6.18 | 1.45
NUCLEAR PWR 400-799 | 2016 | 2020 | 5 | 20 | 600 | 594 | 1.3 | 1.3 | 8118.85 | 0 | 0 | 0 | 0 | 8118.85 | 115.03 | 1.3 | 436.27 | 0.95 | 40.48 | 0.15 | 22.38 | 0.15 | 0.6 | 0.05 | 614.75 | 8733.6 | 12.44 | 80.12 | 0 | 92.56 | 5.46 | 0.26 | 6245.27 | 100 | 92.02 | 99.21 | 92.96 | 92.96 | 90.78 | 1.4 | 1.55 | 1.55 | 5.72 | 1.32 | 1.58 | 1.92 | 2.03 | 92.75 | 92.75 | 90.69 | 1.41 | 1.55 | 5.93 | 1.32
NUCLEAR PWR 800-999 | 2016 | 2020 | 22 | 103 | 887 | 886 | 1.5 | 1.43 | 8145.73 | 0 | 0 | 0 | 0 | 8145.73 | 105.69 | 0.77 | 453.88 | 0.86 | 26.98 | 0.08 | 12.46 | 0.11 | 0 | 0 | 599.01 | 8744.74 | 29.38 | 42.84 | 0 | 72.22 | 5.5 | 0.14 | 5696.31 | 95.33 | 93.23 | 100.19 | 93.15 | 93.15 | 92.16 | 1.28 | 1.64 | 1.64 | 5.64 | 1.21 | 1.35 | 1.86 | 1.97 | 93.05 | 93.05 | 92.05 | 1.32 | 1.68 | 5.7 | 1.24
NUCLEAR PWR 1000 Plus | 2016 | 2020 | 35 | 166 | 1173 | 1167 | 1.54 | 1.51 | 8030.36 | 0 | 0.01 | 0 | 0 | 8030.36 | 140.36 | 0.81 | 532.5 | 0.88 | 21.03 | 0.13 | 9.43 | 0.09 | 0 | 0 | 703.32 | 8733.68 | 34.64 | 60.85 | 0 | 95.49 | 6.34 | 0.11 | 5318.12 | 98.05 | 91.48 | 99.42 | 91.95 | 91.95 | 90.41 | 1.72 | 2.14 | 2.14 | 6.45 | 1.61 | 1.72 | 2.3 | 2.46 | 92.02 | 92.02 | 90.48 | 1.67 | 2.09 | 6.42 | 1.56
NUCLEAR BWR All Sizes | 2016 | 2020 | 32 | 147 | 1037 | 1033 | 1.67 | 1.64 | 8172.49 | 0.28 | 0.01 | 0 | 0 | 8172.77 | 143.75 | 0.86 | 358.26 | 0.96 | 8.42 | 0.06 | 33.05 | 0.3 | 0.85 | 0.01 | 544.33 | 8717.1 | 63.89 | 123.59 | 0 | 187.48 | 4.21 | 0.39 | 4983.23 | 98.2 | 92.03 | 98.58 | 93.75 | 93.76 | 91.17 | 1.73 | 2.5 | 2.5 | 4.6 | 1.65 | 2.04 | 3.43 | 3.58 | 93.35 | 93.36 | 90.81 | 1.93 | 2.66 | 4.81 | 1.84
NUCLEAR BWR 400-799 | 2016 | 2020 | 4 | 16 | 644 | 639 | 1.63 | 1.44 | 7927.52 | 0 | 0 | 0 | 0 | 7927.52 | 152.46 | 1.19 | 140.32 | 0.38 | 28.4 | 0.13 | 40.61 | 0.38 | 0 | 0 | 361.79 | 8289.31 | 109.09 | 95.49 | 0 | 204.58 | 2.04 | 0.49 | 5505.22 | 88.34 | 91.9 | 96.2 | 95.64 | 95.64 | 92.4 | 1.89 | 3.24 | 3.24 | 2.53 | 1.84 | 2.33 | 4.27 | 4.36 | 95.53 | 95.53 | 92.27 | 1.99 | 3.36 | 2.54 | 1.93
NUCLEAR BWR 800-999 | 2016 | 2020 | 10 | 46 | 889 | 885 | 1.54 | 1.54 | 8326.99 | 0 | 0 | 0 | 0 | 8326.99 | 97.64 | 0.74 | 299.58 | 0.89 | 11.2 | 0.09 | 34.45 | 0.28 | 0.05 | 0.02 | 442.92 | 8769.91 | 74.75 | 102.89 | 0 | 177.64 | 3.54 | 0.39 | 5407.14 | 100 | 94.42 | 99.43 | 94.95 | 94.95 | 92.47 | 1.16 | 2.05 | 2.05 | 3.94 | 1.11 | 1.51 | 3.02 | 3.13 | 94.97 | 94.97 | 92.54 | 1.16 | 2.04 | 3.92 | 1.12
NUCLEAR BWR 1000 Plus | 2016 | 2020 | 18 | 85 | 1192 | 1187 | 1.74 | 1.73 | 8134.98 | 0.49 | 0.01 | 0 | 0 | 8135.47 | 167.06 | 0.87 | 431.03 | 1.11 | 3.16 | 0.04 | 30.86 | 0.29 | 1.45 | 0.01 | 633.57 | 8769.04 | 49.51 | 140.09 | 0 | 189.59 | 4.95 | 0.37 | 4702.3 | 99.43 | 91.07 | 98.47 | 92.77 | 92.77 | 90.25 | 2.01 | 2.61 | 2.61 | 5.32 | 1.91 | 2.27 | 3.5 | 3.68 | 92.49 | 92.5 | 89.96 | 2.24 | 2.85 | 5.38 | 2.12
NUCLEAR CANDU All Sizes | 2016 | 2020 | **** | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [10 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: POF to FOR
JET ENGINE All Sizes | 2016 | 2020 | 267 | 1088.25 | 39 | 38 | 81.32 | 80.47 | 392.91 | 7211.96 | 85.12 | 0 | 120.03 | 7724.89 | 257.08 | 5.98 | 322.69 | 1.86 | 14.57 | 0.08 | 248.59 | 4.4 | 12.51 | 0.05 | 855.45 | 8580.34 | 29.4 | 25.59 | 27.66 | 54.99 | 3.93 | 3.04 | 4.88 | 98.95 | 4.95 | 79.37 | 4.58 | 90.03 | 87.64 | 33.39 | 35.91 | 8.97 | 6.97 | 3 | 6.04 | 6.57 | 51.84 | 6.23 | 89.67 | 86.25 | 29.4 | 32.61 | 7.09 | 3.24
JET ENGINE 001-019 | 2016 | 2020 | 27 | 121 | 15 | 15 | 14.66 | 14.3 | 104.22 | 7939.47 | 19.33 | 0 | 0 | 8043.69 | 192.84 | 3.3 | 307.28 | 1.18 | 6.02 | 0.07 | 168.85 | 3.67 | 20.68 | 0.11 | 695.67 | 8739.36 | 0.13 | 2.68 | 0 | 2.81 | 3.58 | 2.17 | 7.29 | 97.54 | 0.2 | 18.89 | 1.19 | 92.04 | 92 | 64.92 | 64.96 | 18.31 | 5.75 | 2.21 | 4.38 | 4.41 | 78.4 | 1.07 | 91.73 | 91.69 | 66.44 | 66.49 | 6.15 | 2.12
JET ENGINE 20 Plus | 2016 | 2020 | 240 | 967.25 | 42 | 41 | 89.66 | 88.74 | 429.02 | 7120.95 | 93.35 | 0 | 135.04 | 7685.01 | 265.12 | 6.31 | 324.62 | 1.94 | 15.64 | 0.08 | 258.57 | 4.49 | 11.49 | 0.04 | 875.44 | 8560.45 | 33.06 | 28.46 | 31.12 | 61.52 | 3.97 | 3.15 | 4.83 | 98.97 | 5.16 | 79.82 | 5.01 | 89.77 | 87.08 | 31.97 | 34.66 | 8.86 | 7.13 | 3.1 | 6.25 | 6.84 | 50.43 | 6.46 | 89.58 | 86 | 28.93 | 32.2 | 7.13 | 3.3
GAS TURBINE All Sizes | 2016 | 2020 | 709 | 3109 | 66 | 64 | 52.72 | 51.95 | 433.78 | 7175.32 | 54.98 | 0 | 0 | 7609.1 | 359.84 | 4.02 | 346.96 | 1.7 | 19.47 | 0.07 | 195.99 | 3.07 | 19.6 | 0.08 | 941.86 | 8550.97 | 19.8 | 7.03 | 17.59 | 26.83 | 4.29 | 2.52 | 8.35 | 98.54 | 5 | 70.5 | 5.07 | 88.99 | 86.57 | 45.34 | 46.8 | 10.22 | 6.81 | 4.21 | 6.73 | 6.99 | 57.99 | 7.1 | 89.66 | 87 | 31.01 | 32.53 | 7.15 | 3.19
GAS TURBINE 001-019 | 2016 | 2020 | 107 | 446.75 | 15 | 15 | 27.22 | 26.13 | 87.47 | 7024.28 | 33.13 | 0 | 0 | 7111.75 | 475.97 | 3.75 | 205.44 | 0.84 | 25.66 | 0.05 | 191.28 | 2.55 | 62.6 | 0.17 | 960.95 | 8072.7 | 10.07 | 4.73 | 9.76 | 14.8 | 2.86 | 3.14 | 3.35 | 96 | 0.71 | 66.16 | 1.08 | 88.1 | 87.21 | 84.48 | 84.79 | 17.2 | 6.01 | 5.9 | 9.04 | 9.17 | 89.45 | 1.07 | 88.09 | 87.2 | 84.75 | 85.04 | 5.98 | 5.93
GAS TURBINE 020-049 | 2016 | 2020 | 143 | 603.25 | 29 | 28 | 65.66 | 65.1 | 347.58 | 7138.4 | 59.73 | 0 | 0 | 7485.98 | 477.95 | 3.7 | 269.81 | 1.47 | 16.33 | 0.04 | 178.46 | 3.05 | 6.18 | 0.03 | 948.73 | 8434.72 | 12.28 | 0.45 | 10.59 | 12.74 | 3.39 | 2.19 | 5.34 | 99.15 | 4.71 | 79.08 | 4.12 | 88.75 | 86.09 | 57.9 | 58.63 | 10.4 | 5.58 | 5.67 | 7.86 | 8.01 | 66.13 | 5.96 | 89.03 | 86.31 | 44.3 | 45.24 | 6.24 | 4.74
GAS TURBINE 50 Plus | 2016 | 2020 | 459 | 2059 | 88 | 86 | 54.46 | 53.7 | 534.17 | 7218.91 | 58.34 | 0 | 0 | 7753.09 | 300.04 | 4.17 | 400.26 | 1.96 | 19.05 | 0.09 | 202.15 | 3.19 | 14.21 | 0.08 | 935.71 | 8688.79 | 24.11 | 9.46 | 21.34 | 33.57 | 4.83 | 2.49 | 9.95 | 98.6 | 5.18 | 69.88 | 6.15 | 89.23 | 86.58 | 35.97 | 37.89 | 9.27 | 7.32 | 3.45 | 5.94 | 6.26 | 50.48 | 7.42 | 89.78 | 87.05 | 28.45 | 30.08 | 7.27 | 2.95
COMBINED CYCLE All Sizes | 2016 | 2020 | 345 | 1420.08 | 298 | 291 | 61.73 | 61.02 | 4833.52 | 2822.55 | 54.43 | 0 | 0 | 7656.08 | 204.94 | 5.51 | 653.34 | 2.49 | 31.81 | 0.19 | 148.84 | 2.18 | 1.51 | 0.03 | 1040.45 | 8696.53 | 48.23 | 49.01 | 12.89 | 97.24 | 7.88 | 1.73 | 79.21 | 98.85 | 54.25 | 80.81 | 55.58 | 88.04 | 84.92 | 4.07 | 5.01 | 3.87 | 9.61 | 2.36 | 4.09 | 4.84 | 8.08 | 67.12 | 88.4 | 84.95 | 2.55 | 3.54 | 9.85 | 1.76
HYDRO All Sizes | 2016 | 2020 | 1060 | 4432 | 67 | 67 | 158.99 | 158.89 | 5518.63 | 1322.16 | 37.75 | 5.94 | 130.98 | 6977.71 | 579.52 | 3.5 | 983.34 | 2.82 | 14.22 | 0.03 | 151.39 | 2.62 | 7.86 | 0.01 | 1736.33 | 8714.04 | 12.53 | 7.34 | 2.04 | 19.86 | 11.45 | 1.83 | 34.73 | 99.94 | 36.23 | 57.22 | 63.33 | 80.07 | 79.55 | 9.29 | 9.49 | 8.04 | 13.28 | 6.65 | 8.48 | 8.64 | 11.77 | 63.32 | 81.56 | 81.13 | 4.68 | 4.8 | 15.26 | 3.18
HYDRO 001-029 | 2016 | 2020 | 402 | 1676 | 11 | 11 | 44.64 | 44.58 | 5318.99 | 1039.68 | 14.78 | 13.11 | 116.87 | 6488.65 | 1021.87 | 4.98 | 930.88 | 1.83 | 14.6 | 0.03 | 164.94 | 2.39 | 2.9 | 0.01 | 2135.19 | 8623.83 | 23.85 | 7.44 | 3.71 | 31.29 | 10.96 | 1.95 | 119.31 | 99.87 | 34.52 | 52.29 | 61.68 | 75.24 | 74.76 | 15.79 | 16.15 | 14.37 | 12.91 | 11.85 | 13.8 | 14.09 | 18.29 | 66.02 | 80.66 | 80.25 | 8.83 | 9.23 | 12.74 | 6.6
HYDRO 30 Plus | 2016 | 2020 | 658 | 2756 | 101 | 100 | 228.53 | 228.4 | 5640.04 | 1493.94 | 51.72 | 1.57 | 139.56 | 7275.12 | 310.52 | 2.6 | 1015.25 | 3.43 | 13.99 | 0.03 | 143.14 | 2.75 | 10.88 | 0.01 | 1493.78 | 8768.9 | 5.64 | 7.27 | 1.03 | 12.91 | 11.74 | 1.76 | 24.69 | 99.94 | 36.35 | 57.58 | 64.32 | 82.97 | 82.42 | 5.1 | 5.19 | 4.29 | 13.49 | 3.54 | 5.3 | 5.38 | 7.55 | 63.13 | 81.62 | 81.2 | 4.37 | 4.46 | 15.44 | 2.95
PUMPED STORAGE All Sizes | 2016 | 2020 | 111 | 544 | 130 | 129 | 252.27 | 252.08 | 2593.47 | 3327.86 | 209.84 | 1008.97 | 240.74 | 7171.04 | 269.56 | 2.81 | 1103.7 | 3.14 | 35.72 | 0.1 | 188.68 | 4.6 | 0.69 | 0.01 | 1598.35 | 8769.39 | 2.35 | 1.96 | 0.7 | 4.3 | 12.99 | 2.16 | 10.29 | 99.92 | 8 | 45.26 | 29.57 | 81.77 | 81.57 | 6.55 | 6.61 | 4.69 | 15.15 | 3.07 | 5.23 | 5.27 | 10.73 | 17.68 | 79.41 | 78.89 | 7.77 | 7.98 | 17.73 | 2.86
MULTIBOILER/MULTI-TURBINE All Sizes | 2016 | 2020 | 24 | 102 | 315 | 313 | 14.76 | 14.49 | 4988.94 | 2271.32 | 12.18 | 0 | 0 | 7260.26 | 260.17 | 4.58 | 791.71 | 1.49 | 29.58 | 0.1 | 271.82 | 2.15 | 0.34 | 0.01 | 1353.61 | 8613.87 | 417.08 | 172.82 | 20.89 | 589.9 | 9.53 | 3.16 | 344.3 | 98.17 | 26.23 | 58.16 | 57.92 | 84.29 | 76.45 | 4.96 | 12.85 | 9.94 | 12.69 | 3.02 | 6.18 | 11.73 | 18.13 | 45.11 | 81.25 | 77.3 | 4.2 | 8.85 | 16.77 | 1.98
DIESEL All Sizes | 2016 | 2020 | 151 | 657.17 | 8 | 8 | 78.54 | 78.01 | 724.41 | 7340.59 | 80.12 | 0 | 0 | 8065 | 225.89 | 6.48 | 213.13 | 0.81 | 0.62 | 0 | 145.34 | 3.07 | 3.62 | 0.05 | 588.59 | 8653.59 | 18.23 | 13.44 | 14.71 | 31.67 | 2.47 | 1.72 | 9.29 | 99.33 | 11 | 65.86 | 8.37 | 93.2 | 92.6 | 23.77 | 25.3 | 7.92 | 4.19 | 2.61 | 4.33 | 4.6 | 35.56 | 16.7 | 93.77 | 92.22 | 12.82 | 15.81 | 3.78 | 2.46
* Column title definitions and calculations can be found in the GADS Data Reporting Instructsions - Appendix F Equations
**Caution: EFOR and WEFOR values may be low since deratings during reserve shutdown periods may not have been reported for a large number of these units.
*** The two methods for calculating combined cycle units is not available at this time.
**** Less than three generating companies are reporting this type of unit. To retain confidentiality of the data, no data is reported here.