## Sheet1
Generator Catagory/Classification | Start | End | # Units | Unit-Years | NMC | NDC | Attempts | Actual | SH | RSH | # RSH | Pump Hr | SCH | AH | FOH | # FOH | POH | # POH | SEPO | # SEPO | MOH | # MOH | SEMO | # SEMO | UAH | PH | EFDH | ESDH | EFDHRS | EDOH | POF | MOF | ART | SR | NCF | NOF | SF | AF | EAF | FOR | EFOR | EFORd | SOF | FOF | UOF | EUOF | EUOR | WSF | WAF | WEAF | WFOR | WEFOR | WSOF | WFOF
FOSSIL All Fuel Types All Sizes | 2017 | 2021 | 1144 | 4644.58 | 333 | 332 | 29.94 | 29.61 | 4205.71 | 2410.31 | 13.65 | 0 | 0 | 6616.02 | 460.77 | 5.38 | 695.96 | 1.31 | 36.62 | 0.13 | 329.44 | 2.57 | 6.53 | 0.05 | 1529.33 | 8145.35 | 153.51 | 51.98 | 39.55 | 205.49 | 8.99 | 4.12 | 142.04 | 98.9 | 39.94 | 69.72 | 51.63 | 81.22 | 78.29 | 9.87 | 13.05 | 9.95 | 13.12 | 5.66 | 9.78 | 11.93 | 19.24 | 57.29 | 80.32 | 77.51 | 8.88 | 11.93 | 14.09 | 5.59
FOSSIL All Fuel Types 001-099 | 2017 | 2021 | 236 | 953 | 52 | 52 | 34.25 | 34.09 | 3450.11 | 2924.43 | 17.2 | 0 | 0 | 6374.54 | 490.34 | 4.38 | 484.89 | 1.1 | 31.45 | 0.07 | 305.86 | 1.72 | 0.87 | 0.01 | 1313.4 | 7687.94 | 130.55 | 59.16 | 38.55 | 189.71 | 6.72 | 3.99 | 101.21 | 99.53 | 29.77 | 64.83 | 44.88 | 82.92 | 79.61 | 12.44 | 15.6 | 10.64 | 10.71 | 6.38 | 10.37 | 12.37 | 22.18 | 45.92 | 83.24 | 80.07 | 11.91 | 15.19 | 10.55 | 6.21
FOSSIL All Fuel Types 100-199 | 2017 | 2021 | 261 | 956.83 | 136 | 136 | 66.96 | 66.68 | 3094.85 | 3248.85 | 16.51 | 0 | 0 | 6343.7 | 433.18 | 4.07 | 640.02 | 1.19 | 27.62 | 0.09 | 299.85 | 2.05 | 4.5 | 0.03 | 1405.16 | 7748.85 | 131.06 | 56.17 | 56.63 | 187.23 | 8.62 | 3.93 | 46.41 | 99.58 | 24.88 | 60.36 | 39.94 | 81.87 | 78.92 | 12.28 | 15.74 | 9.44 | 12.54 | 5.59 | 9.52 | 11.45 | 22.72 | 41.21 | 81.65 | 78.63 | 12.15 | 15.59 | 12.65 | 5.7
FOSSIL All Fuel Types 200-299 | 2017 | 2021 | 130 | 511 | 231 | 230 | 15.75 | 15.34 | 4560.93 | 2179.64 | 12.77 | 0 | 0 | 6740.58 | 371.44 | 5.46 | 655.08 | 1.35 | 20.35 | 0.13 | 350.52 | 3.26 | 10.06 | 0.09 | 1407.45 | 8148.03 | 140.88 | 41.89 | 36.96 | 182.77 | 8.29 | 4.43 | 297.32 | 97.4 | 36.92 | 66.22 | 55.98 | 82.73 | 80.13 | 7.53 | 10.31 | 8.55 | 12.71 | 4.56 | 8.98 | 10.96 | 16.73 | 55.75 | 83.05 | 80.49 | 7.35 | 10.09 | 12.53 | 4.42
FOSSIL All Fuel Types 300-399 | 2017 | 2021 | 108 | 447.25 | 337 | 336 | 20.76 | 20.32 | 4013.2 | 2777.2 | 18.21 | 0 | 0 | 6790.4 | 385.06 | 6.02 | 879.57 | 1.66 | 47.44 | 0.17 | 334.85 | 3.18 | 16.7 | 0.1 | 1663.62 | 8454.02 | 175.05 | 45.5 | 39.13 | 220.56 | 10.97 | 4.16 | 197.5 | 97.88 | 28.78 | 61.37 | 47.47 | 80.32 | 77.54 | 8.75 | 12.62 | 9.69 | 15.12 | 4.55 | 8.71 | 11.02 | 19.41 | 46.9 | 80.25 | 77.55 | 8.82 | 12.65 | 15.21 | 4.54
FOSSIL All Fuel Types 400-599 | 2017 | 2021 | 192 | 848 | 482 | 480 | 15.21 | 14.8 | 4987.86 | 1796.45 | 10.34 | 0 | 0 | 6784.31 | 560.25 | 6.89 | 773.81 | 1.47 | 57.08 | 0.18 | 342.73 | 2.94 | 4.27 | 0.07 | 1738.14 | 8522.45 | 188.59 | 52.64 | 35.25 | 241.23 | 9.75 | 4.07 | 337.02 | 97.3 | 40.03 | 68.2 | 58.53 | 79.61 | 76.54 | 10.1 | 13.41 | 11.48 | 13.82 | 6.57 | 10.65 | 13.06 | 18.75 | 58.69 | 79.7 | 76.67 | 9.95 | 13.22 | 13.81 | 6.49
FOSSIL All Fuel Types 600-799 | 2017 | 2021 | 144 | 601.5 | 661 | 659 | 11.44 | 11.05 | 5390.44 | 1405.79 | 6.37 | 0 | 0 | 6796.23 | 449.57 | 6.43 | 828.55 | 1.36 | 35.63 | 0.14 | 338.82 | 2.92 | 12.07 | 0.07 | 1664.64 | 8460.87 | 172.09 | 43.75 | 30.2 | 215.84 | 10.21 | 4.15 | 487.82 | 96.59 | 48.08 | 75.19 | 63.71 | 80.33 | 77.5 | 7.7 | 10.59 | 9.45 | 14.36 | 5.31 | 9.46 | 11.75 | 15.97 | 63.94 | 80.26 | 77.45 | 7.7 | 10.56 | 14.41 | 5.33
FOSSIL All Fuel Types 800-999 | 2017 | 2021 | 60 | 268 | 828 | 828 | 17.48 | 17.07 | 5229.67 | 1829.46 | 13.66 | 0 | 0 | 7059.13 | 425.76 | 5.32 | 780.48 | 1.22 | 42.93 | 0.21 | 334.18 | 2.83 | 6.38 | 0.06 | 1589.73 | 8648.86 | 141.99 | 46.53 | 27.75 | 188.52 | 9.52 | 3.94 | 306.37 | 97.65 | 43.24 | 71.05 | 60.47 | 81.62 | 79.41 | 7.53 | 9.99 | 8.5 | 13.46 | 4.92 | 8.86 | 10.91 | 15.65 | 60.85 | 81.72 | 79.53 | 7.41 | 9.84 | 13.41 | 4.87
FOSSIL All Fuel Types 1000 Plus | 2017 | 2021 | 13 | 54 | 1239 | 1235 | 9.48 | 9.04 | 5219.66 | 1033.46 | 4.52 | 0 | 0 | 6253.12 | 655.1 | 5.46 | 1149.32 | 1.35 | 13.96 | 0.09 | 692.06 | 3.7 | 0 | 0 | 2510.43 | 8763.56 | 202.21 | 112.14 | 13.75 | 314.35 | 13.27 | 7.9 | 577.4 | 95.36 | 44.86 | 73.81 | 59.56 | 71.35 | 67.56 | 11.15 | 14.56 | 13.15 | 21.17 | 7.48 | 15.37 | 18.2 | 24.19 | 60.77 | 71.27 | 67.52 | 11.22 | 14.59 | 21.06 | 7.68
FOSSIL Coal Primary All Sizes | 2017 | 2021 | 695 | 2668.75 | 405 | 404 | 24.72 | 24.4 | 5139.86 | 1466.69 | 6.12 | 0 | 0 | 6606.55 | 453.38 | 5.97 | 667.61 | 1.16 | 34.33 | 0.13 | 323.44 | 2.72 | 8 | 0.07 | 1486.76 | 8093.31 | 150.56 | 59.59 | 21.94 | 210.15 | 8.67 | 4.1 | 210.65 | 98.71 | 48.95 | 73.09 | 63.51 | 81.63 | 78.66 | 8.11 | 10.76 | 9.2 | 12.77 | 5.6 | 9.7 | 11.85 | 16.11 | 66.98 | 80.61 | 77.78 | 7.91 | 10.5 | 13.64 | 5.75
FOSSIL Coal Primary 001-099 | 2017 | 2021 | 96 | 286.58 | 57 | 57 | 12.59 | 12.44 | 3580.89 | 2793.65 | 9.9 | 0 | 0 | 6374.54 | 321.48 | 4.55 | 481.58 | 0.99 | 27.95 | 0.07 | 197.69 | 1.57 | 1.23 | 0.02 | 1029.94 | 7404.48 | 95.3 | 70.04 | 38.63 | 165.34 | 6.88 | 2.69 | 287.85 | 98.81 | 36.42 | 73.13 | 48.36 | 86.09 | 83.37 | 8.24 | 10.58 | 8.43 | 9.57 | 4.34 | 7.03 | 8.68 | 15.5 | 49.81 | 87.14 | 84.39 | 7.59 | 9.93 | 8.77 | 4.09
FOSSIL Coal Primary 100-199 | 2017 | 2021 | 144 | 472.92 | 143 | 142 | 85.43 | 85.23 | 3993.18 | 1876.42 | 5.73 | 0 | 0 | 5869.6 | 430.97 | 4.4 | 515.89 | 0.97 | 20.31 | 0.1 | 266.49 | 1.83 | 6.51 | 0.03 | 1240.17 | 7109.78 | 130.56 | 80.53 | 36.37 | 211.1 | 7.54 | 3.84 | 46.85 | 99.77 | 37.73 | 67.31 | 56.16 | 82.56 | 78.85 | 9.74 | 12.59 | 9.3 | 11.38 | 6.06 | 9.9 | 11.96 | 17.95 | 56.05 | 82.19 | 78.57 | 10.11 | 13.03 | 11.5 | 6.31
FOSSIL Coal Primary 200-299 | 2017 | 2021 | 84 | 333.75 | 229 | 228 | 11.15 | 10.79 | 5073.2 | 1537.66 | 6.34 | 0 | 0 | 6610.86 | 405.02 | 5.94 | 582.14 | 1.23 | 16.64 | 0.13 | 402.09 | 3.6 | 15.4 | 0.14 | 1421.29 | 8032.15 | 121.63 | 50.33 | 13.19 | 171.96 | 7.45 | 5.2 | 470.18 | 96.77 | 44.64 | 71.25 | 63.16 | 82.3 | 79.68 | 7.39 | 9.59 | 8.5 | 12.65 | 5.04 | 10.24 | 11.99 | 16.29 | 62.65 | 82.76 | 80.13 | 7.28 | 9.49 | 12.32 | 4.92
FOSSIL Coal Primary 300-399 | 2017 | 2021 | 64 | 248.17 | 330 | 329 | 13.97 | 13.53 | 5051.46 | 1764.84 | 8.47 | 0 | 0 | 6816.3 | 451.65 | 7.1 | 727.63 | 1.11 | 42.67 | 0.17 | 400.47 | 3.43 | 16.69 | 0.14 | 1639.11 | 8455.41 | 224.9 | 65.67 | 29.6 | 290.57 | 9.11 | 4.93 | 373.35 | 96.85 | 40.89 | 68.6 | 59.74 | 80.61 | 77.01 | 8.21 | 12.23 | 10.49 | 14.04 | 5.34 | 10.28 | 13.27 | 18.82 | 59.61 | 80.63 | 77.07 | 8.27 | 12.28 | 13.99 | 5.37
FOSSIL Coal Primary 400-599 | 2017 | 2021 | 134 | 574.33 | 486 | 484 | 12.02 | 11.68 | 5969.71 | 898.95 | 5.29 | 0 | 0 | 6868.65 | 547.08 | 7.11 | 726.87 | 1.26 | 59.65 | 0.17 | 306.53 | 2.82 | 5.4 | 0.07 | 1645.54 | 8514.19 | 180.75 | 47.83 | 16.9 | 228.58 | 9.24 | 3.66 | 511.11 | 97.17 | 50.29 | 71.59 | 70.11 | 80.67 | 77.71 | 8.39 | 11.14 | 10.29 | 12.9 | 6.43 | 10.09 | 12.45 | 15.48 | 70.24 | 80.71 | 77.77 | 8.28 | 11 | 12.95 | 6.34
FOSSIL Coal Primary 600-799 | 2017 | 2021 | 118 | 505.08 | 662 | 660 | 11.04 | 10.68 | 5994.5 | 955.39 | 4.93 | 0 | 0 | 6949.89 | 436.19 | 6.6 | 757.55 | 1.23 | 28.44 | 0.12 | 333.53 | 2.98 | 8.32 | 0.07 | 1564.02 | 8513.91 | 148.26 | 49.38 | 6.53 | 197.64 | 9.23 | 4.02 | 561.28 | 96.74 | 53.86 | 76.47 | 70.41 | 81.63 | 79.01 | 6.78 | 9.08 | 8.38 | 13.25 | 5.12 | 9.14 | 11.17 | 14.02 | 70.44 | 81.63 | 79 | 6.78 | 9.08 | 13.25 | 5.13
FOSSIL Coal Primary 800-999 | 2017 | 2021 | 43 | 192.92 | 836 | 835 | 9.23 | 8.8 | 5792.87 | 1125.04 | 4.15 | 0 | 0 | 6917.91 | 496.9 | 5.67 | 825.44 | 1.23 | 43.93 | 0.19 | 357.83 | 2.99 | 6.94 | 0.06 | 1731.04 | 8648.95 | 143.14 | 50.01 | 27.5 | 193.15 | 10.05 | 4.22 | 658.28 | 95.34 | 48.68 | 72.51 | 66.98 | 79.99 | 77.73 | 7.9 | 10.13 | 9.29 | 14.27 | 5.75 | 9.96 | 12.07 | 15.61 | 67.13 | 80.22 | 78 | 7.74 | 9.93 | 14.16 | 5.63
FOSSIL Coal Primary 1000 Plus | 2017 | 2021 | 12 | 50 | 1260 | 1256 | 9.62 | 9.16 | 5562.67 | 616.98 | 3.98 | 0 | 0 | 6179.65 | 701.87 | 5.74 | 1229.26 | 1.44 | 15.08 | 0.1 | 637.5 | 3.74 | 0 | 0 | 2583.71 | 8763.36 | 191.12 | 113.41 | 1.75 | 304.53 | 14.2 | 7.27 | 607.28 | 95.22 | 47.45 | 74.26 | 63.48 | 70.52 | 66.82 | 11.2 | 14.25 | 13.32 | 21.47 | 8.01 | 15.28 | 17.94 | 22.77 | 63.89 | 70.61 | 66.94 | 11.26 | 14.35 | 21.28 | 8.11
FOSSIL Oil Primary All Sizes | 2017 | 2021 | 64 | 225.5 | 300 | 299 | 21.11 | 20.95 | 1811.89 | 4610.02 | 22.22 | 0 | 0 | 6421.91 | 430.36 | 2.39 | 624.1 | 1.02 | 19.34 | 0.09 | 447.28 | 1.77 | 8.07 | 0.03 | 1529.15 | 7951.06 | 187.38 | 17.62 | 74.59 | 205 | 8.09 | 5.73 | 86.49 | 99.24 | 5.07 | 42.66 | 22.79 | 80.77 | 78.09 | 19.19 | 26.66 | 12.61 | 13.82 | 5.41 | 11.14 | 13.65 | 39.02 | 11.89 | 82.44 | 80.69 | 16.94 | 25.04 | 15.14 | 2.42
FOSSIL Oil Primary 001-099 | 2017 | 2021 | 16 | 73.5 | 66 | 66 | 48.73 | 48.53 | 3403.29 | 1980.9 | 44.61 | 0 | 0 | 5384.19 | 713.26 | 3.18 | 273.12 | 0.18 | 0 | 0 | 660.59 | 1.73 | 0 | 0 | 1646.97 | 7031.16 | 394.81 | 21.04 | 136.9 | 415.85 | 3.88 | 9.4 | 70.13 | 99.59 | 29.25 | 50.48 | 48.4 | 76.58 | 70.66 | 17.33 | 26.05 | 18.75 | 13.28 | 10.14 | 19.54 | 25.43 | 36.38 | 57.93 | 78.23 | 71.89 | 11.41 | 20.06 | 14.31 | 7.46
FOSSIL Oil Primary 100-199 | 2017 | 2021 | 14 | 40.08 | 121 | 121 | 5.49 | 5.34 | 1811.23 | 5042.13 | 7.51 | 0 | 0 | 6853.36 | 656.36 | 1.55 | 557.49 | 0.82 | 0 | 0 | 390.67 | 1.57 | 0 | 0 | 1604.52 | 8457.88 | 159.9 | 11.05 | 52.82 | 170.96 | 6.59 | 4.62 | 339.18 | 97.27 | 14.48 | 58.64 | 21.41 | 81.03 | 79.01 | 26.6 | 32.39 | 18.27 | 11.21 | 7.76 | 12.38 | 14.35 | 41.6 | 24.7 | 81.05 | 78.86 | 22.45 | 28.38 | 11.8 | 7.15
FOSSIL Oil Primary 200-299 | 2017 | 2021 | 1 | 0.08 | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | [10 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * | * | bar: POF to FOR
FOSSIL Oil Primary 300-399 | 2017 | 2021 | 9 | 42.92 | 366 | 366 | 7.95 | 7.85 | 1598.92 | 4663.64 | 12.37 | 0 | 0 | 6262.55 | 220.64 | 2.17 | 1002.04 | 1.91 | 32.1 | 0.12 | 226.66 | 1.65 | 0.13 | 0.02 | 1481.57 | 7744.12 | 23.08 | 8.16 | 5.51 | 31.25 | 13.35 | 2.93 | 203.68 | 98.74 | 6.89 | 32.78 | 20.65 | 80.87 | 80.46 | 12.13 | 13.35 | 9.16 | 16.28 | 2.85 | 5.78 | 6.1 | 23.02 | 21.02 | 81.16 | 80.75 | 11.44 | 12.66 | 16.13 | 2.71
FOSSIL Oil Primary 400-599 | 2017 | 2021 | 9 | 28 | 455 | 453 | 8.32 | 8.25 | 157.69 | 7378.39 | 12.43 | 0 | 0 | 7536.08 | 165.73 | 2.29 | 814.62 | 1.68 | 49.71 | 0.18 | 199.01 | 2 | 0 | 0 | 1229.06 | 8765.14 | 43.7 | 36.83 | 26.62 | 80.53 | 9.86 | 2.27 | 19.11 | 99.16 | 0.48 | 27.84 | 1.8 | 85.98 | 84.72 | 51.24 | 59.83 | 19.35 | 12.13 | 1.89 | 4.16 | 4.91 | 72.64 | 1.72 | 85.91 | 84.65 | 52.82 | 61.24 | 12.16 | 1.93
FOSSIL Oil Primary 600-799 | 2017 | 2021 | 9 | 23.33 | 621 | 618 | 13.03 | 12.94 | 316.22 | 7060.13 | 17.31 | 0 | 0 | 7376.35 | 150.34 | 2.53 | 726.37 | 1.41 | 14.39 | 0.13 | 422.41 | 1.71 | 73.61 | 0.21 | 1387.12 | 8763.47 | 82.11 | 9.26 | 72.88 | 91.37 | 8.45 | 5.66 | 24.44 | 99.31 | 1.54 | 43.52 | 3.61 | 84.17 | 82.81 | 32.22 | 43.09 | 13.93 | 14.11 | 1.72 | 7.38 | 8.34 | 70.27 | 3.54 | 83.4 | 81.94 | 32.17 | 44.2 | 14.92 | 1.68
FOSSIL Oil Primary 800-999 | 2017 | 2021 | 5 | 13.58 | 812 | 810 | 3.46 | 3.02 | 113.33 | 6989.6 | 7.14 | 0 | 0 | 7102.93 | 30.42 | 1.47 | 1100.77 | 1.55 | 92.44 | 0.52 | 433.67 | 2.13 | 7.07 | 0.07 | 1664.36 | 8767.29 | 98.13 | 0 | 95.83 | 98.13 | 13.61 | 5.03 | 37.53 | 87.28 | 0.51 | 40.04 | 1.29 | 81.02 | 79.64 | 21.16 | 53.66 | 15.97 | 18.64 | 0.35 | 5.37 | 6.49 | 83.68 | 1.27 | 81.12 | 79.75 | 20.98 | 53.86 | 18.54 | 0.34
FOSSIL Gas Primary All Sizes | 2017 | 2021 | 362 | 1370.25 | 236 | 236 | 38.36 | 37.96 | 2231.83 | 4265.04 | 26.47 | 0 | 0 | 6496.88 | 484.9 | 4.37 | 795.89 | 1.61 | 44.27 | 0.12 | 363.55 | 2.56 | 5.15 | 0.04 | 1693.77 | 8190.64 | 140.65 | 27.81 | 77.32 | 168.47 | 10.26 | 4.5 | 58.79 | 98.96 | 13.03 | 43.61 | 27.25 | 79.32 | 76.93 | 17.85 | 22.39 | 12 | 14.76 | 5.92 | 10.42 | 12.3 | 31.71 | 29.88 | 77.74 | 75.06 | 16.28 | 21.36 | 16.45 | 5.81
FOSSIL Gas Primary 001-099 | 2017 | 2021 | 91 | 343.42 | 53 | 52 | 34.32 | 34.13 | 1513.52 | 4403.69 | 16.57 | 0 | 0 | 5917.21 | 642.31 | 2.84 | 465.51 | 1.04 | 39.33 | 0.05 | 404.14 | 1.51 | 1.29 | 0.01 | 1552.58 | 7469.79 | 72.07 | 2.64 | 41.73 | 74.71 | 6.76 | 5.43 | 44.35 | 99.45 | 12.19 | 49.04 | 20.26 | 79.22 | 77.43 | 29.79 | 32.51 | 14.05 | 12.19 | 8.6 | 14.03 | 15.02 | 43.08 | 24.85 | 79.43 | 77.47 | 26.37 | 29.07 | 11.67 | 8.9
FOSSIL Gas Primary 100-199 | 2017 | 2021 | 113 | 432.5 | 131 | 130 | 54.06 | 53.68 | 2156.76 | 4650.28 | 29.44 | 0 | 0 | 6807.05 | 383.28 | 4.01 | 794.01 | 1.49 | 38.89 | 0.09 | 329.26 | 2.34 | 2.84 | 0.04 | 1548.28 | 8355.32 | 130.32 | 30.82 | 80.63 | 161.14 | 9.97 | 3.97 | 40.18 | 99.3 | 12.21 | 45.95 | 25.81 | 81.47 | 79.19 | 15.09 | 19.6 | 9.48 | 13.94 | 4.59 | 8.56 | 10.39 | 29.11 | 26.57 | 81.35 | 78.88 | 14.68 | 19.1 | 14.08 | 4.57
FOSSIL Gas Primary 200-299 | 2017 | 2021 | 44 | 151.17 | 234 | 234 | 25.04 | 24.66 | 3077.39 | 3857.74 | 26.73 | 0 | 0 | 6935.13 | 271.56 | 3.86 | 804.48 | 1.55 | 26.62 | 0.12 | 259.47 | 2.76 | 0 | 0 | 1362.12 | 8297.25 | 174.65 | 24.39 | 93.33 | 199.04 | 10.02 | 3.13 | 124.79 | 98.48 | 17.36 | 45.81 | 37.09 | 83.58 | 81.15 | 8.11 | 12.96 | 8.35 | 13.14 | 3.27 | 6.4 | 8.79 | 19.61 | 37.9 | 83.64 | 81.34 | 7.6 | 12.16 | 13.25 | 3.12
FOSSIL Gas Primary 300-399 | 2017 | 2021 | 38 | 144.67 | 344 | 343 | 33.33 | 32.77 | 2676.28 | 4129.63 | 34.13 | 0 | 0 | 6805.91 | 345.49 | 5.47 | 1130.95 | 2.51 | 61.82 | 0.19 | 271.85 | 3.3 | 22.97 | 0.06 | 1833.08 | 8638.99 | 146.79 | 25.42 | 68.54 | 172.21 | 13.81 | 3.41 | 81.67 | 98.32 | 13.06 | 42.12 | 30.98 | 78.78 | 76.57 | 11.43 | 15.93 | 9.85 | 17.22 | 4 | 7.41 | 9.25 | 23.56 | 31 | 78.58 | 76.47 | 11.37 | 15.7 | 17.44 | 3.98
FOSSIL Gas Primary 400-599 | 2017 | 2021 | 50 | 214.25 | 479 | 479 | 24.9 | 24.34 | 2639.79 | 3720.49 | 24.77 | 0 | 0 | 6360.29 | 669.7 | 6.57 | 914.78 | 2.01 | 46.13 | 0.17 | 484.25 | 3.58 | 2.11 | 0.05 | 2116.97 | 8477.26 | 205.43 | 69.22 | 90.68 | 274.65 | 11.34 | 5.74 | 108.45 | 97.75 | 13.1 | 42.28 | 31.14 | 75.03 | 71.69 | 20.24 | 25.74 | 16.78 | 17.07 | 7.9 | 13.64 | 16.15 | 35.13 | 30.98 | 75.39 | 72.1 | 19.96 | 25.42 | 16.89 | 7.73
FOSSIL Gas Primary 600-799 | 2017 | 2021 | 16 | 51.75 | 685 | 685 | 16.43 | 15.46 | 2260.92 | 3325.54 | 16.93 | 0 | 0 | 5586.46 | 653.21 | 7.03 | 1654.57 | 2.69 | 124.87 | 0.37 | 441.94 | 3.59 | 25.88 | 0.1 | 2900.48 | 8486.94 | 351.53 | 15.77 | 241.35 | 367.3 | 20.97 | 5.51 | 146.24 | 94.1 | 14.06 | 49.21 | 26.64 | 65.82 | 61.5 | 22.42 | 31.84 | 21.99 | 26.48 | 7.7 | 13.21 | 17.39 | 40.68 | 28.57 | 66.08 | 61.97 | 21.34 | 30.11 | 26.17 | 7.75
FOSSIL Gas Primary 800-999 | 2017 | 2021 | 10 | 32.5 | 790 | 790 | 80.09 | 79.6 | 2174.06 | 5256.36 | 82.8 | 0 | 0 | 7430.42 | 300.54 | 4 | 629.56 | 1.23 | 31.5 | 0.06 | 362.84 | 3.97 | 8.43 | 0.12 | 1332.87 | 8763.29 | 54.71 | 26.59 | 24.55 | 81.3 | 7.54 | 4.24 | 27.31 | 99.39 | 7.87 | 31.91 | 24.81 | 84.79 | 83.86 | 12.14 | 14.21 | 6.4 | 11.78 | 3.43 | 7.67 | 8.56 | 25.8 | 24.67 | 84.46 | 83.52 | 12.56 | 14.6 | 12 | 3.54
FOSSIL Lignite Primary All Sizes | 2017 | 2021 | 25 | 96.92 | 520 | 519 | 9.45 | 8.93 | 6834.96 | 264.11 | 1.71 | 0 | 0 | 7099.07 | 405.61 | 6.88 | 492.84 | 1.1 | 51.27 | 0.31 | 122.33 | 1.32 | 0.67 | 0.06 | 1072.72 | 8171.79 | 314.46 | 40.51 | 1.31 | 354.97 | 6.66 | 1.51 | 765.39 | 94.5 | 65.49 | 77.95 | 83.64 | 86.87 | 81.53 | 5.6 | 9.94 | 9.66 | 8.16 | 4.96 | 6.47 | 10.58 | 11.74 | 84.01 | 87.58 | 82.97 | 5.33 | 9.72 | 7.69 | 4.73
FOSSIL Oil/Gas Primary 001-099 | 2017 | 2021 | 106 | 416.92 | 55 | 55 | 36.86 | 36.67 | 1846.68 | 3976.56 | 21.51 | 0 | 0 | 5823.24 | 654.82 | 2.9 | 431.6 | 0.89 | 32.39 | 0.04 | 449.35 | 1.54 | 1.06 | 0.01 | 1569.22 | 7392.46 | 128.97 | 5.88 | 58.51 | 134.85 | 6.28 | 6.09 | 50.36 | 99.48 | 15.67 | 49.58 | 24.98 | 78.77 | 76.29 | 26.18 | 30.62 | 14.58 | 12.37 | 8.86 | 14.95 | 16.76 | 41.15 | 31.6 | 79.18 | 76.33 | 21.41 | 26.07 | 12.21 | 8.61
FOSSIL Oil/Gas Primary 100-199 | 2017 | 2021 | 120 | 472.58 | 130 | 129 | 49.94 | 49.58 | 2127.46 | 4683.52 | 27.58 | 0 | 0 | 6810.97 | 406.44 | 3.8 | 773.95 | 1.43 | 35.59 | 0.08 | 334.47 | 2.27 | 2.6 | 0.03 | 1553.05 | 8364.02 | 132.82 | 29.15 | 78.27 | 161.97 | 9.68 | 4.03 | 42.91 | 99.28 | 12.39 | 46.89 | 25.44 | 81.43 | 79.17 | 16.04 | 20.64 | 9.9 | 13.71 | 4.86 | 8.89 | 10.73 | 30.15 | 26.42 | 81.32 | 78.88 | 15.31 | 19.85 | 13.9 | 4.78
FOSSIL Oil/Gas Primary 200-299 | 2017 | 2021 | 44 | 151.25 | 234 | 234 | 25.04 | 24.67 | 3076.74 | 3858.79 | 26.75 | 0 | 0 | 6935.52 | 271.41 | 3.86 | 804.03 | 1.55 | 26.6 | 0.12 | 260.03 | 2.76 | 0 | 0 | 1362.08 | 8297.6 | 174.55 | 24.37 | 93.28 | 198.93 | 10.01 | 3.13 | 124.72 | 98.52 | 17.36 | 45.81 | 37.08 | 83.58 | 81.16 | 8.11 | 12.96 | 8.35 | 13.14 | 3.27 | 6.4 | 8.79 | 19.62 | 37.88 | 83.64 | 81.34 | 7.59 | 12.16 | 13.25 | 3.11
FOSSIL Oil/Gas Primary 300-399 | 2017 | 2021 | 46 | 187.58 | 349 | 348 | 27.52 | 27.07 | 2429.79 | 4251.8 | 29.16 | 0 | 0 | 6681.59 | 316.93 | 4.71 | 1101.46 | 2.37 | 55.02 | 0.17 | 261.51 | 2.93 | 17.75 | 0.05 | 1752.66 | 8434.26 | 118.49 | 21.47 | 54.12 | 139.96 | 13.71 | 3.31 | 89.76 | 98.36 | 11.71 | 40.63 | 28.81 | 79.22 | 77.39 | 11.54 | 15.55 | 9.53 | 17.02 | 3.76 | 7.07 | 8.59 | 23.48 | 28.81 | 79.14 | 77.41 | 11.38 | 15.22 | 17.16 | 3.7
FOSSIL Oil/Gas Primary 400-599 | 2017 | 2021 | 59 | 242.25 | 477 | 476 | 22.98 | 22.48 | 2352.9 | 4143.29 | 23.34 | 0 | 0 | 6496.19 | 611.45 | 6.07 | 903.2 | 1.97 | 46.55 | 0.17 | 451.28 | 3.4 | 1.87 | 0.05 | 2014.35 | 8510.53 | 186.73 | 65.48 | 83.28 | 252.21 | 11.16 | 5.32 | 104.67 | 97.82 | 11.67 | 42.18 | 27.65 | 76.33 | 73.24 | 20.63 | 26.19 | 16.32 | 16.48 | 7.18 | 12.51 | 14.81 | 35.86 | 27.66 | 76.58 | 73.52 | 20.35 | 25.87 | 16.35 | 7.07
FOSSIL Oil/Gas Primary 600-799 | 2017 | 2021 | 21 | 75.08 | 665 | 664 | 15.37 | 14.68 | 1656.58 | 4486.12 | 17.05 | 0 | 0 | 6142.7 | 496.93 | 5.63 | 1366.12 | 2.29 | 90.54 | 0.29 | 435.87 | 3.01 | 40.71 | 0.13 | 2430.18 | 8572.87 | 267.8 | 13.75 | 189 | 281.55 | 16.99 | 5.56 | 112.85 | 95.51 | 10.34 | 48.93 | 19.32 | 71.65 | 68.27 | 23.08 | 32.65 | 19.46 | 22.55 | 5.8 | 11.36 | 14.51 | 44.06 | 21.14 | 71.22 | 67.9 | 21.96 | 30.99 | 22.83 | 5.95
FOSSIL Oil/Gas Primary 800-999 | 2017 | 2021 | 12 | 46.08 | 797 | 796 | 57.5 | 57.03 | 1566.64 | 5767.24 | 60.5 | 0 | 0 | 7333.89 | 220.92 | 3.25 | 768.46 | 1.32 | 49.46 | 0.2 | 383.72 | 3.43 | 8.03 | 0.11 | 1430.58 | 8764.47 | 67.51 | 18.75 | 45.56 | 86.26 | 9.33 | 4.47 | 27.47 | 99.18 | 5.66 | 32.09 | 17.87 | 83.68 | 82.62 | 12.36 | 15.73 | 6.26 | 13.8 | 2.52 | 6.99 | 7.95 | 30.96 | 17.64 | 83.45 | 82.39 | 12.76 | 16.13 | 13.97 | 2.58
FOSSIL Oil/Gas Primary All Sizes | 2017 | 2021 | 409 | 1595.75 | 245 | 245 | 35.92 | 35.55 | 2172.49 | 4313.79 | 25.87 | 0 | 0 | 6486.28 | 477.19 | 4.09 | 771.62 | 1.53 | 40.75 | 0.11 | 375.38 | 2.45 | 5.57 | 0.03 | 1670.51 | 8156.79 | 147.26 | 26.37 | 76.93 | 173.63 | 9.96 | 4.67 | 61.11 | 98.97 | 11.66 | 43.54 | 26.63 | 79.52 | 77.09 | 18.01 | 22.9 | 12.08 | 14.63 | 5.85 | 10.52 | 12.49 | 32.63 | 26.79 | 78.55 | 76.02 | 16.33 | 21.65 | 16.22 | 5.23
NUCLEAR All Types All Sizes | 2017 | 2021 | 104 | 463.75 | 1020 | 1016 | 1.57 | 1.54 | 8085.68 | 0.09 | 0 | 0 | 0 | 8085.77 | 135.99 | 0.82 | 458.82 | 0.92 | 17.37 | 0.09 | 15.72 | 0.13 | 0.27 | 0 | 628.17 | 8713.93 | 43.02 | 84.48 | 0 | 127.51 | 5.46 | 0.18 | 5250.44 | 98.09 | 91.79 | 99.11 | 92.79 | 92.79 | 90.93 | 1.65 | 2.18 | 2.18 | 5.65 | 1.56 | 1.74 | 2.63 | 2.79 | 92.61 | 92.61 | 90.74 | 1.73 | 2.25 | 5.76 | 1.63
NUCLEAR All Types 400-799 | 2017 | 2021 | 12 | 49 | 626 | 620 | 1.35 | 1.31 | 8034.04 | 0 | 0 | 0 | 0 | 8034.04 | 139.37 | 0.69 | 359.16 | 0.84 | 24.97 | 0.08 | 20.83 | 0.1 | 0 | 0 | 544.33 | 8578.37 | 57.95 | 83.43 | 0 | 141.38 | 4.48 | 0.24 | 6132.85 | 97.04 | 91.16 | 97.54 | 93.65 | 93.65 | 91.15 | 1.71 | 2.41 | 2.41 | 4.72 | 1.62 | 1.87 | 2.81 | 2.94 | 93.46 | 93.46 | 90.99 | 1.81 | 2.54 | 4.81 | 1.73
NUCLEAR All Types 800-999 | 2017 | 2021 | 37 | 162.75 | 889 | 887 | 1.56 | 1.52 | 8184.06 | 0 | 0 | 0 | 0 | 8184.06 | 106.31 | 0.82 | 424.46 | 0.87 | 21.14 | 0.08 | 13.37 | 0.12 | 0.01 | 0.01 | 565.29 | 8749.35 | 42.11 | 69.27 | 0 | 111.39 | 5.09 | 0.15 | 5384.25 | 97.44 | 93.11 | 99.63 | 93.54 | 93.54 | 92.01 | 1.28 | 1.79 | 1.79 | 5.25 | 1.22 | 1.37 | 2.26 | 2.38 | 93.46 | 93.46 | 91.92 | 1.31 | 1.83 | 5.3 | 1.24
NUCLEAR All Types 1000 Plus | 2017 | 2021 | 55 | 252 | 1182 | 1177 | 1.63 | 1.6 | 8032.18 | 0.16 | 0 | 0 | 0 | 8032.34 | 154.5 | 0.85 | 500.39 | 0.96 | 13.47 | 0.1 | 16.23 | 0.15 | 0.49 | 0 | 685.08 | 8717.42 | 40.7 | 94.51 | 0 | 135.22 | 5.89 | 0.19 | 5020.11 | 98.16 | 91.2 | 99.01 | 92.14 | 92.14 | 90.18 | 1.89 | 2.38 | 2.38 | 6.09 | 1.77 | 1.96 | 2.84 | 3.02 | 92.12 | 92.12 | 90.15 | 1.92 | 2.43 | 6.08 | 1.8
NUCLEAR PWR All Sizes | 2017 | 2021 | 61 | 280 | 1040 | 1036 | 1.52 | 1.48 | 8045.89 | 0 | 0 | 0 | 0 | 8045.89 | 124.84 | 0.76 | 509.23 | 0.9 | 22.38 | 0.11 | 10.81 | 0.08 | 0 | 0 | 667.26 | 8713.15 | 32 | 57.61 | 0 | 89.61 | 6.1 | 0.12 | 5436.41 | 97.37 | 91.82 | 99.58 | 92.34 | 92.34 | 90.94 | 1.53 | 1.92 | 1.92 | 6.23 | 1.43 | 1.56 | 2.13 | 2.26 | 92.21 | 92.21 | 90.79 | 1.59 | 1.99 | 6.3 | 1.49
NUCLEAR PWR 400-799 | 2017 | 2021 | 4 | 17 | 614 | 607 | 1.41 | 1.41 | 8201.46 | 0 | 0 | 0 | 0 | 8201.46 | 65.01 | 0.41 | 439.41 | 1.12 | 45.25 | 0.12 | 14.53 | 0.12 | 0 | 0 | 564.19 | 8765.65 | 19.03 | 91.13 | 0 | 110.16 | 5.53 | 0.17 | 5816.64 | 100 | 92.4 | 99.11 | 93.56 | 93.56 | 91.26 | 0.79 | 1.02 | 1.02 | 5.69 | 0.74 | 0.91 | 1.36 | 1.44 | 93.22 | 93.22 | 91.06 | 0.92 | 1.16 | 5.91 | 0.87
NUCLEAR PWR 800-999 | 2017 | 2021 | 22 | 98 | 888 | 887 | 1.44 | 1.37 | 8131.85 | 0 | 0 | 0 | 0 | 8131.85 | 98.19 | 0.71 | 479.19 | 0.86 | 23.67 | 0.07 | 5.42 | 0.06 | 0 | 0 | 606.48 | 8738.33 | 31.47 | 43.53 | 0 | 75.01 | 5.75 | 0.06 | 5935.66 | 95.14 | 93 | 100.07 | 93.06 | 93.06 | 92.04 | 1.19 | 1.58 | 1.58 | 5.82 | 1.12 | 1.19 | 1.72 | 1.82 | 92.94 | 92.94 | 91.92 | 1.23 | 1.62 | 5.9 | 1.16
NUCLEAR PWR 1000 Plus | 2017 | 2021 | 35 | 165 | 1174 | 1169 | 1.58 | 1.55 | 7978.81 | 0 | 0 | 0 | 0 | 7978.81 | 146.84 | 0.82 | 534.26 | 0.9 | 19.25 | 0.13 | 13.63 | 0.09 | 0 | 0 | 713.98 | 8692.79 | 33.66 | 62.51 | 0 | 96.16 | 6.37 | 0.16 | 5147.62 | 98.1 | 91.25 | 99.38 | 91.79 | 91.79 | 90.24 | 1.81 | 2.22 | 2.22 | 6.52 | 1.69 | 1.85 | 2.45 | 2.61 | 91.82 | 91.82 | 90.27 | 1.79 | 2.21 | 6.51 | 1.67
NUCLEAR BWR All Sizes | 2017 | 2021 | 31 | 139 | 1044 | 1040 | 1.6 | 1.58 | 8190.87 | 0.3 | 0.01 | 0 | 0 | 8191.17 | 127.75 | 0.86 | 358.13 | 0.93 | 7.32 | 0.05 | 23.82 | 0.24 | 0.9 | 0.01 | 517.94 | 8709.1 | 56.54 | 132.68 | 0 | 189.21 | 4.2 | 0.28 | 5184.09 | 98.75 | 92.69 | 98.86 | 94.05 | 94.05 | 91.49 | 1.54 | 2.22 | 2.22 | 4.48 | 1.47 | 1.75 | 3.15 | 3.28 | 93.76 | 93.76 | 91.2 | 1.65 | 2.32 | 4.67 | 1.57
NUCLEAR BWR 400-799 | 2017 | 2021 | 4 | 13 | 644 | 639 | 1.15 | 1 | 7845.36 | 0 | 0 | 0 | 0 | 7845.36 | 137.07 | 0.92 | 150.63 | 0.38 | 34.95 | 0.15 | 5.3 | 0.08 | 0 | 0 | 327.95 | 8173.31 | 107.17 | 131.33 | 0 | 238.49 | 2.27 | 0.06 | 7845.36 | 86.96 | 91.98 | 95.98 | 95.99 | 95.99 | 92.33 | 1.72 | 3.06 | 3.06 | 2.34 | 1.68 | 1.74 | 3.71 | 3.79 | 95.83 | 95.83 | 92.13 | 1.82 | 3.19 | 2.4 | 1.77
NUCLEAR BWR 800-999 | 2017 | 2021 | 9 | 45 | 889 | 885 | 1.62 | 1.62 | 8323.58 | 0 | 0 | 0 | 0 | 8323.58 | 115.37 | 0.89 | 285.97 | 0.87 | 8.71 | 0.07 | 31.12 | 0.24 | 0.05 | 0.02 | 441.22 | 8764.8 | 49.56 | 95.84 | 0 | 145.4 | 3.36 | 0.36 | 5138.01 | 100 | 95.01 | 100.07 | 94.97 | 94.97 | 92.82 | 1.37 | 1.95 | 1.95 | 3.72 | 1.32 | 1.67 | 2.88 | 2.98 | 94.95 | 94.95 | 92.84 | 1.38 | 1.98 | 3.72 | 1.33
NUCLEAR BWR 1000 Plus | 2017 | 2021 | 18 | 81 | 1194 | 1190 | 1.65 | 1.64 | 8172.59 | 0.51 | 0.01 | 0 | 0 | 8173.1 | 133.14 | 0.83 | 431.53 | 1.05 | 2.12 | 0.02 | 22.75 | 0.27 | 1.52 | 0.01 | 591.05 | 8764.15 | 52.29 | 153.36 | 0 | 205.64 | 4.95 | 0.28 | 4983.29 | 99.39 | 91.79 | 98.59 | 93.25 | 93.26 | 90.62 | 1.6 | 2.23 | 2.23 | 5.22 | 1.52 | 1.8 | 3.21 | 3.38 | 93.1 | 93.11 | 90.45 | 1.74 | 2.39 | 5.24 | 1.65
NUCLEAR CANDU All Sizes | 2017 | 2021 | 1 | 5 | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | [10 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * | * | bar: POF to FOR
JET ENGINE All Sizes | 2017 | 2021 | 218 | 1011.5 | 40 | 39 | 83.05 | 82.19 | 382.73 | 7262.01 | 86.75 | 0 | 109.16 | 7753.91 | 278.08 | 5.73 | 350.01 | 2.3 | 13.29 | 0.07 | 238.34 | 4.25 | 5.93 | 0.04 | 885.64 | 8639.55 | 29.37 | 27.88 | 27.84 | 57.25 | 4.21 | 2.83 | 4.66 | 98.96 | 5.03 | 81.57 | 4.43 | 89.75 | 86.96 | 36.12 | 38.54 | 8.96 | 7.03 | 3.22 | 6.05 | 6.56 | 53.08 | 6.17 | 89.38 | 85.45 | 31.36 | 34.29 | 7.17 | 3.45
JET ENGINE 001-019 | 2017 | 2021 | 26 | 116 | 15 | 15 | 14.92 | 14.56 | 138.16 | 8020.15 | 19.61 | 0 | 0 | 8158.31 | 197 | 3.34 | 262.04 | 1.34 | 0.72 | 0.03 | 129.1 | 3.35 | 16.97 | 0.03 | 605.83 | 8764.14 | 0.12 | 2.82 | 0 | 2.93 | 3 | 1.67 | 9.49 | 97.59 | 0.19 | 13.51 | 1.58 | 93.09 | 92.98 | 58.78 | 58.81 | 17.73 | 4.66 | 2.25 | 3.91 | 3.95 | 71.15 | 1.43 | 93.05 | 92.97 | 60.49 | 60.53 | 4.76 | 2.19
JET ENGINE 20 Plus | 2017 | 2021 | 192 | 895.5 | 43 | 42 | 91.87 | 90.95 | 414.41 | 7163.81 | 95.45 | 0 | 123.31 | 7701.53 | 288.58 | 6.04 | 361.4 | 2.42 | 14.92 | 0.07 | 252.49 | 4.37 | 4.5 | 0.04 | 921.88 | 8623.41 | 33.16 | 31.13 | 31.45 | 64.28 | 4.36 | 2.98 | 4.56 | 99 | 5.25 | 82.26 | 4.81 | 89.31 | 86.17 | 34.92 | 37.51 | 8.89 | 7.34 | 3.35 | 6.33 | 6.91 | 52.09 | 6.38 | 89.21 | 85.11 | 30.94 | 33.93 | 7.28 | 3.51
GAS TURBINE All Sizes | 2017 | 2021 | 680 | 2942 | 67 | 65 | 55.72 | 54.96 | 445.46 | 7152.89 | 56.88 | 0 | 0 | 7598.35 | 368.94 | 4.06 | 361.62 | 1.75 | 19.12 | 0.05 | 199.86 | 3.04 | 15.23 | 0.05 | 964.76 | 8563.11 | 18.84 | 4.85 | 16.59 | 23.7 | 4.45 | 2.51 | 8.11 | 98.64 | 5 | 70.31 | 5.2 | 88.73 | 86.06 | 45.3 | 46.66 | 10.08 | 6.96 | 4.31 | 6.82 | 7.06 | 57.65 | 7.11 | 89.4 | 86.37 | 31.43 | 32.83 | 7.34 | 3.26
GAS TURBINE 001-019 | 2017 | 2021 | 99 | 405 | 15 | 15 | 26.24 | 25.16 | 86.35 | 6995.55 | 32.18 | 0 | 0 | 7081.9 | 497.08 | 3.66 | 215.67 | 0.78 | 27.34 | 0.04 | 190.09 | 2.49 | 44.44 | 0.07 | 974.62 | 8056.52 | 10.76 | 4.38 | 10.45 | 15.14 | 3.02 | 2.91 | 3.43 | 95.88 | 0.65 | 61.66 | 1.07 | 87.9 | 86.9 | 85.2 | 85.51 | 17.58 | 5.93 | 6.17 | 9.08 | 9.22 | 89.57 | 1.06 | 88 | 86.97 | 85.27 | 85.56 | 5.88 | 6.12
GAS TURBINE 020-049 | 2017 | 2021 | 136 | 575 | 29 | 28 | 75.66 | 75.06 | 386.44 | 7086.91 | 64.29 | 0 | 0 | 7473.35 | 488.73 | 3.9 | 280.75 | 1.57 | 10.13 | 0.03 | 187.26 | 3.4 | 5.12 | 0.03 | 972 | 8445.35 | 13.73 | 0.44 | 11.62 | 14.17 | 3.44 | 2.28 | 5.15 | 99.21 | 5.08 | 78.28 | 4.58 | 88.49 | 85.72 | 55.84 | 56.66 | 10.15 | 5.72 | 5.79 | 8.06 | 8.23 | 64.4 | 6.49 | 88.69 | 85.87 | 42.79 | 43.81 | 6.46 | 4.86
GAS TURBINE 50 Plus | 2017 | 2021 | 445 | 1962 | 89 | 86 | 55.96 | 55.22 | 536.88 | 7204.7 | 59.81 | 0 | 0 | 7741.59 | 307.37 | 4.19 | 415.45 | 2 | 20.05 | 0.07 | 205.56 | 3.05 | 12.16 | 0.05 | 960.6 | 8702.19 | 22.01 | 6.25 | 19.31 | 28.26 | 5 | 2.5 | 9.72 | 98.68 | 5.13 | 69.69 | 6.17 | 88.96 | 85.99 | 36.41 | 38.14 | 9.23 | 7.51 | 3.53 | 6.03 | 6.32 | 50.65 | 7.37 | 89.51 | 86.39 | 29.04 | 30.5 | 7.48 | 3.01
COMBINED CYCLE All Sizes | 2017 | 2021 | 342 | 1454.25 | 308 | 301 | 63.42 | 62.73 | 4801.03 | 2811.93 | 56.68 | 0 | 0 | 7612.96 | 219.54 | 5.43 | 659.59 | 2.47 | 29.55 | 0.16 | 161.77 | 2.18 | 1.67 | 0.03 | 1072.12 | 8685.08 | 47.71 | 53.56 | 14.52 | 101.27 | 7.93 | 1.88 | 76.53 | 98.91 | 54.21 | 80.88 | 55.28 | 87.66 | 84.41 | 4.37 | 5.31 | 4.06 | 9.82 | 2.53 | 4.41 | 5.17 | 8.63 | 67.02 | 88.1 | 84.5 | 2.75 | 3.78 | 10 | 1.9
HYDRO All Sizes | 2017 | 2021 | 909 | 4256 | 68 | 68 | 142.79 | 142.68 | 5423.93 | 1336.68 | 36.99 | 5.97 | 134.88 | 6901.46 | 592.62 | 3.55 | 1012.6 | 2.84 | 19.89 | 0.03 | 149.07 | 2.54 | 10.65 | 0.01 | 1784.82 | 8686.28 | 12.81 | 8.99 | 1.97 | 21.8 | 11.89 | 1.84 | 38.01 | 99.92 | 33.58 | 53.86 | 62.44 | 79.45 | 78.89 | 9.62 | 9.83 | 8.31 | 13.73 | 6.82 | 8.66 | 8.82 | 12.13 | 62.35 | 80.72 | 80.27 | 4.89 | 5.01 | 16 | 3.28
HYDRO 001-029 | 2017 | 2021 | 336 | 1599 | 12 | 12 | 41.91 | 41.85 | 5240.78 | 1021.59 | 13.82 | 13.42 | 128.07 | 6403.86 | 1034.33 | 5.13 | 923.04 | 1.75 | 17.05 | 0.04 | 175.3 | 2.41 | 4.85 | 0.01 | 2154.56 | 8558.42 | 24.96 | 8.04 | 3.89 | 33 | 10.98 | 2.1 | 125.23 | 99.86 | 33.52 | 51.56 | 61.24 | 74.83 | 74.32 | 16.12 | 16.5 | 14.73 | 13.09 | 12.09 | 14.19 | 14.49 | 18.78 | 65.02 | 79.65 | 79.24 | 10.11 | 10.52 | 12.77 | 7.58
HYDRO 30 Plus | 2017 | 2021 | 573 | 2657 | 102 | 102 | 203.5 | 203.35 | 5534.15 | 1526.31 | 50.93 | 1.49 | 138.97 | 7200.92 | 326.8 | 2.59 | 1066.5 | 3.5 | 21.6 | 0.03 | 133.28 | 2.61 | 14.14 | 0.01 | 1562.31 | 8763.23 | 5.51 | 9.56 | 0.82 | 15.07 | 12.42 | 1.68 | 27.21 | 99.93 | 33.58 | 54.02 | 63.15 | 82.17 | 81.57 | 5.45 | 5.54 | 4.55 | 14.1 | 3.73 | 5.41 | 5.49 | 7.83 | 62.17 | 80.8 | 80.34 | 4.48 | 4.58 | 16.23 | 2.98
PUMPED STORAGE All Sizes | 2017 | 2021 | 111 | 533 | 131 | 131 | 248.39 | 248.21 | 2507.91 | 3351.26 | 208.89 | 991.38 | 238.37 | 7088.92 | 343.13 | 2.83 | 1108.7 | 3.02 | 32.15 | 0.11 | 190.94 | 4.67 | 0.71 | 0.01 | 1675.62 | 8764.54 | 2.6 | 2.24 | 0.84 | 4.83 | 13.02 | 2.19 | 10.1 | 99.93 | 7.79 | 45.4 | 28.61 | 80.88 | 80.67 | 8.41 | 8.47 | 5.88 | 15.2 | 3.91 | 6.1 | 6.14 | 12.59 | 17.15 | 78.56 | 78.03 | 10.92 | 11.14 | 17.37 | 4.07
MULTIBOILER/MULTI-TURBINE All Sizes | 2017 | 2021 | 23 | 97 | 328 | 326 | 14.35 | 14.01 | 4663.62 | 2451.14 | 11.91 | 0 | 0 | 7114.76 | 328.61 | 4.86 | 810.51 | 1.51 | 32.37 | 0.11 | 373.29 | 2.69 | 5.67 | 0.02 | 1550.46 | 8665.23 | 439.56 | 165.85 | 30.14 | 605.42 | 9.73 | 4.37 | 332.88 | 97.63 | 23.72 | 56.38 | 53.82 | 82.11 | 74.05 | 6.58 | 15.29 | 11.61 | 14.1 | 3.79 | 8.17 | 13.87 | 22.13 | 42.08 | 79.16 | 74.61 | 5.48 | 11.5 | 18.4 | 2.44
DIESEL All Sizes | 2017 | 2021 | 209 | 739.17 | 10 | 10 | 129.48 | 128.48 | 1171.69 | 6914.36 | 117.45 | 0 | 0 | 8086.05 | 243.95 | 8.17 | 211.67 | 1.14 | 1.81 | 0.01 | 140.69 | 4.01 | 2.48 | 0.03 | 600.6 | 8686.65 | 24.45 | 12.91 | 18.63 | 37.36 | 2.46 | 1.65 | 9.12 | 99.23 | 15.14 | 66.11 | 13.49 | 93.09 | 92.46 | 17.23 | 18.71 | 6.58 | 4.11 | 2.81 | 4.46 | 4.79 | 26.33 | 22.91 | 94.5 | 92.95 | 9.33 | 12.02 | 3.14 | 2.36