## OC
| Standard Number | Requirement Number | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Supports a Reliability Objective (as defined by the Reliability Principles) (Yes/No/Maybe) | Meets the Paragraph 81 criteria? (Mark only if Yes) | Appropriate as a guide rather than a standard? (Mark only if Yes) | C1 | C2 | C3 | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | Q9 | Q10 | Q11 | Q12 | Q13 | OC Content Score 0-3 | OC Quality Score 0-13 | Comment/Rationale
Standard and Requirement | [6 empty] | Is the content of the requirement technically correct, including identifying who does what and when? | Are the correct functional entities identified? | Are the appropriate actions, for which there should be accountability, included or is there a gap? | Should the requirement stand alone as is or should it be consolidated with other standards? | Is it drafted as a results-based standard (RBS) requirement (performance, risk (prevention) or capability) and does it follow the RBS format (e.g., sub-requirement structure)? | Is it technologically neutral? | Are the expectations for each function clear? | Does the requirement align with the purpose? | Is it a higher solution than the lowest common denominator? | Is it measureable? | Does it have a technical basis in engineering and operations? | Is it complete and self-contained? | Is the language clear and does not contain ambiguous or outdated terms? | Can it be practically implemented? | Does it use consistent terminology? | Is the Standard cost effective in achieving the reliability purpose or objective of the Standard and mitigating the risk to the BES?
BAL-001-2 , R1 | BAL-001-2 | R1 | R1. The Responsible Entity shall operate such that the Control Performance Standard 1 (CPS1), calculated in accordance with Attachment 1, is greater than or equal to 100 percent for the applicable Interconnection in which it operates for each preceding 12 consecutive calendar month period, evaluated monthly. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | No | 3 | 12
BAL-001-2 , R2 | BAL-001-2 | R2 | R2. Each Balancing Authority shall operate such that its clock-minute average of Reporting ACE does not exceed its clock-minute Balancing Authority ACE Limit (BAAL) for more than 30 consecutive clock-minutes, calculated in accordance with Attachment 2, for the applicable Interconnection in which the Balancing Authority operates.[Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | No | 3 | 12
EOP-010-1 , R1 | EOP-010-1 | R1 | R1. Each Reliability Coordinator shall develop, maintain, and implement a GMD Operating Plan that coordinates GMD Operating Procedures or Operating Processes within its Reliability Coordinator Area. At a minimum, the GMD Operating Plan shall include: 1.1 A description of activities designed to mitigate the effects of GMD events on the reliable operation of the interconnected transmission system within the Reliability Coordinator Area. 1.2 A process for the Reliability Coordinator to review the GMD Operating Procedures or Operating Processes of Transmission Operators within its Reliability Coordinator Area. | yes | yes |  | yes | yes | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
EOP-010-1 , R2 | EOP-010-1 | R2 | R2. Each Reliability Coordinator shall disseminate forecasted and current space weather information to functional entities identified as recipients in the Reliability Coordinator's GMD Operating Plan. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
EOP-010-1 , R3. | EOP-010-1 | R3. | R3. Each Transmission Operator shall develop, maintain, and implement a GMD Operating Procedure or Operating Process to mitigate the effects of GMD events on the reliable operation of its respective system. At a minimum, the Operating Procedure or Operating Process shall include: 3.1. Steps or tasks to receive space weather information. 3.2. System Operator actions to be initiated based on predetermined conditions. 3.3. The conditions for terminating the Operating Procedure or Operating Process. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
EOP-011-1 , R1. | EOP-011-1 | R1. | R1. Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] 1.1. Roles and responsibilities for activating the Operating Plan(s); 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.1. Notification to its Reliability Coordinator, to include current and projected conditions, when experiencing an operating Emergency; 1.2.2. Cancellation or recall of Transmission and generation outages; 1.2.3. Transmission system reconfiguration; 1.2.4. Redispatch of generation request; 1.2.5. Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and 1.2.6. Reliability impacts of extreme weather conditions. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
EOP-011-1 , R2. | EOP-011-1 | R2. | R2. Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] 2.1. Roles and responsibilities for activating the Operating Plan(s); 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.1. Notification to its Reliability Coordinator, to include current and projected conditions when experiencing a Capacity Emergency or Energy Emergency; 2.2.2. Requesting an Energy Emergency Alert, per Attachment 1; 2.2.3. Managing generating resources in its Balancing Authority Area to address: 2.2.3.1. capability and availability; 2.2.3.2. fuel supply and inventory concerns; 2.2.3.3. fuel switching capabilities; and 2.2.3.4. environmental constraints. 2.2.4. Public appeals for voluntary Load reductions; 2.2.5. Requests to government agencies to implement their programs to achieve necessary energy reductions; 2.2.6. Reduction of internal utility energy use; 2.2.7. Use of Interruptible Load, curtailable Load and demand response; 2.2.8. Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and 2.2.9. Reliability impacts of extreme weather conditions. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
EOP-011-1 , R3. | EOP-011-1 | R3. | R3. The Reliability Coordinator shall review the Operating Plan(s) to mitigate operating Emergencies submitted by a Transmission Operator or a Balancing Authority regarding any reliability risks that are identified between Operating Plans. [Violation Risk Factor: High] [Time Horizon: Operations Planning] 3.1. Within 30 calendar days of receipt, the Reliability Coordinator shall: 3.1.1. Review each submitted Operating Plan(s) on the basis of compatibility and inter-dependency with other Balancing Authorities’ and Transmission Operators’ Operating Plans; 3.1.2. Review each submitted Operating Plan(s) for coordination to avoid risk to Wide Area reliability; and 3.1.3. Notify each Balancing Authority and Transmission Operator of the results of its review, specifying any time frame for resubmittal of its Operating Plan(s) if revisions are identified. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
EOP-011-1 , R4. | EOP-011-1 | R4. | R4. Each Transmission Operator and Balancing Authority shall address any reliability risks identified by its Reliability Coordinator pursuant to Requirement R3 and resubmit its Operating Plan(s) to its Reliability Coordinator within a time period specified by its Reliability Coordinator. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
EOP-011-1 , R5. | EOP-011-1 | R5. | R5. Each Reliability Coordinator that receives an Emergency notification from a Transmission Operator or Balancing Authority within its Reliability Coordinator Area shall notify, within 30 minutes from the time of receiving notification, other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators. [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
EOP-011-1 , R6. | EOP-011-1 | R6. | R6. Each Reliability Coordinator that has a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area shall declare an Energy Emergency Alert, as detailed in Attachment 1. [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
FAC-008-3 , R1 | FAC-008-3 | R1 | R1. Each Generator Owner shall have documentation for determining the Facility Ratings of its solely and jointly owned generator Facility(ies) up to the low side terminals of the main step up transformer if the Generator Owner does not own the main step up transformer and the high side terminals of the main step up transformer if the Generator Owner owns the main step up transformer. 1.1. The documentation shall contain assumptions used to rate the generator and at least one of the following: • Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis. • Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. 1.2. The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
FAC-008-3 , R2. | FAC-008-3 | R2. | Each Generator Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned equipment connected between the location specified in R1 and the point of interconnection with the Transmission Owner that contains all of the following. 1.1. The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. 1.2. The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: 1.2.1. Equipment Rating standard(s) used in development of this methodology. 1.2.2. Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. 1.2.3. Ambient conditions (for particular or average conditions or as they vary in real-time). 1.2.4. Operating limitations. 1.3. A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. 1.4. The process by which the Rating of equipment that comprises a Facility is determined. 1.4.1. The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. 1.4.2. The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | [19 empty] | 3 | 12
FAC-008-3 , R3. | FAC-008-3 | R3. | R3. Each Transmission Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned Facilities (except for those generating unit Facilities addressed in R1 and R2) that contains all of the following: [Violation Risk Factor: Medium] [ Time Horizon: Long-term Planning] 3.1. The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. 3.2. The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: 3.2.1. Equipment Rating standard(s) used in development of this methodology. 3.2.2. Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. 3.2.3. Ambient conditions (for particular or average conditions or as they vary in real-time). 3.2.4. Operating limitations. 3.3. A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. 3.4. The process by which the Rating of equipment that comprises a Facility is determined. 3.4.1. The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. 3.4.2. The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
FAC-008-3 , R4. | FAC-008-3 | R4. | R4. Each Transmission Owner shall make its Facility Ratings methodology and each Generator Owner shall each make its documentation for determining its Facility Ratings and its Facility Ratings methodology available for inspection and technical review by those Reliability Coordinators, Transmission Operators, Transmission Planners and Planning Coordinators that have responsibility for the area in which the associated Facilities are located, within 21 calendar days of receipt of a request. (Retirement approved by FERC effective January 21, 2014.) | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
FAC-008-3 , R5. | FAC-008-3 | R5. | R5. If a Reliability Coordinator, Transmission Operator, Transmission Planner or Planning Coordinator provides documented comments on its technical review of a Transmission Owner’s Facility Ratings methodology or Generator Owner’s documentation for determining its Facility Ratings and its Facility Rating methodology, the Transmission Owner or Generator Owner shall provide a response to that commenting entity within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Facility Ratings methodology and, if no change will be made to that Facility Ratings methodology, the reason why. (Retirement approved by FERC effective January 21, 2014.) | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
FAC-008-3 , R6. | FAC-008-3 | R6. | R6. Each Transmission Owner and Generator Owner shall have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology or documentation for determining its Facility Ratings. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
FAC-008-3 , R7. | FAC-008-3 | R7. | R7. Each Generator Owner shall provide Facility Ratings (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) as scheduled by such requesting entities | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
FAC-008-3 , R8. | FAC-008-3 | R8. | R8. Each Transmission Owner (and each Generator Owner subject to Requirement R2) shall provide requested information as specified below (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s): [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] 8.1. As scheduled by the requesting entities: 8.1.1. Facility Ratings 8.1.2. Identity of the most limiting equipment of the Facilities 8.2. Within 30 calendar days (or a later date if specified by the requester), for any requested Facility with a Thermal Rating that limits the use of Facilities under the requester’s authority by causing any of the following: 1) An Interconnection Reliability Operating Limit, 2) A limitation of Total Transfer Capability, 3) An impediment to generator deliverability, or 4) An impediment to service to a major load center: 8.2.1. Identity of the existing next most limiting equipment of the Facility 8.2.2. The Thermal Rating for the next most limiting equipment identified in Requirement R8, Part 8.2.1. | maybe | yes | yes | yes | yes | yes | yes | no | yes | yes | yes | yes | yes | no | yes | yes | yes | yes | yes | 3 | 10 | What reliabillity purpose is knowing the next higher limit? Seems to me that this is a tariff issue, not a reliability issue.
INT-004-3.1 , R1 | INT-004-3.1 | R1 | R1. Each Purchasing-Selling Entity that secures energy to serve Load via a Dynamic Schedule or Pseudo-Tie shall ensure that a Request for Interchange is submitted as an on-time Arranged Interchange to the Sink Balancing Authority for that Dynamic Schedule or Pseudo-Tie, unless the information about the Pseudo-Tie is included in congestion management procedure(s) via an alternate method. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | no | yes | yes | yes | yes | yes | yes | yes | 3 | 11 | Haven't all the INT standards been superseded by NAESB standards?
INT-004-3.1 , R2 | INT-004-3.1 | R2 | R2. The Purchasing-Selling Entity that submits a Request for Interchange in accordance with Requirement R1 shall ensure the Confirmed Interchange associated with that Dynamic Schedule or Pseudo-Tie is updated for future hours in order to support congestion management procedures if any one of the following occurs: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning, Same Day Operations, Real Time Operations] 2.1. For Confirmed Interchange greater than 250 MW for the last hour, the actual hourly integrated energy deviates from the Confirmed Interchange by more than 10% for that hour and that deviation is expected to persist. 2.2. For Confirmed Interchange less than or equal to 250 MW for the last hour, the actual hourly integrated energy deviates from the Confirmed Interchange by more than 25 MW for that hour and that deviation is expected to persist. 2.3. The Purchasing-Selling Entity receives notification from a Reliability Coordinator or Transmission Operator to update the Confirmed Interchange. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
INT-004-3.1 , R3. | INT-004-3.1 | R3. | R3. Each Balancing Authority shall only implement or operate a Pseudo-Tie that is included in the NAESB Electric Industry Registry publication in order to support congestion management procedures. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
INT-006-4 , R1 | INT-006-4 | R1 | R1. Each Balancing Authority shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B. 1.1. Each Source and Sink Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if it does not expect to be capable of supporting the magnitude of the Interchange, including ramping, throughout the duration of the Arranged Interchange. 1.2. Each Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if the Scheduling Path (proper connectivity of Adjacent Balancing Authorities) between it and its Adjacent Balancing Authorities is invalid. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
INT-006-4 , R2 | INT-006-4 | R2 | R2. Each Transmission Service Provider shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B. 2.1. Each Transmission Service Provider shall deny the Arranged Interchange or curtail Confirmed Interchange if the transmission path (proper connectivity of adjacent Transmission Service Providers) between it and its adjacent Transmission Service Providers is invalid. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
INT-006-4 , R3. | INT-006-4 | R3. | R3. The Source Balancing Authority and the Sink Balancing Authority receiving a Reliability Adjustment Arranged Interchange shall approve or deny it prior to the expiration of the time period defined in Attachment 1, Column B. 3.1. If a Balancing Authority denies a Reliability Adjustment Arranged Interchange, the Balancing Authority must communicate that fact to its Reliability Coordinator no more than 10 minutes after the denial. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
INT-006-4 , R4 | INT-006-4 | R4 | R4. Each Sink Balancing Authority shall confirm that none of the following conditions exist prior to transitioning an Arranged Interchange to Confirmed Interchange: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning, Same-day Operations, Real-time Operations] • It is a Reliability Adjustment Arranged Interchange, the time period specified in Attachment 1, Column B has elapsed, and the Source Balancing Authority or the Sink Balancing Authority associated with the Arranged Interchange has not communicated its approval of the transition. • It is not a Reliability Adjustment Arranged Interchange, the time period specified in Attachment 1, Column B, has elapsed, and not all Balancing Authorities and Transmission Service Providers associated with the Arranged Interchange have communicated their approval of the transition. • It is not a Reliability Adjustment Arranged Interchange, the time period specified in Attachment 1, Column B, has elapsed, and any entity associated with the Arranged Interchange has communicated its denial of the transition. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
INT-006-4 , R5 | INT-006-4 | R5 | R5. For each Arranged Interchange that is transitioned to Confirmed Interchange, the Sink Balancing Authority shall notify the following entities of the on-time Confirmed Interchange such that the notification is delivered in time to be incorporated into scheduling systems prior to ramp start as specified in Attachment 1, Column D: 5.1. The Source Balancing Authority, 5.2. Each Intermediate Balancing Authority, 5.3. Each Reliability Coordinator associated with each Balancing Authority included in the Arranged Interchange, | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
INT-009-2.1 , R1 | INT-009-2.1 | R1 | R1. Each Balancing Authority shall agree with each of its Adjacent Balancing Authorities that its Composite Confirmed Interchange with that Adjacent Balancing Authority, at mutually agreed upon time intervals, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange per INT-010-2 not yet captured in the Composite Confirmed Interchange, is: 1.1. Identical in magnitude to that of the Adjacent Balancing Authority, and 1.2. Opposite in sign or direction to that of the Adjacent Balancing Authority. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
INT-009-2.1 , R2 | INT-009-2.1 | R2 | R2. The Attaining Balancing Authority and the Native Balancing Authority shall use a dynamic value emanating from an agreed upon common source to account for the Pseudo-Tie in the Actual Net Interchange (NIA) term of their respective control ACE (or alternate control process). | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
INT-009-2.1 , R3. | INT-009-2.1 | R3. | R3. Each Balancing Authority in whose area the high-voltage direct current tie is controlled shall coordinate the Confirmed Interchange prior to its implementation with the Transmission Operator of the high-voltage direct current tie. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
INT-010-2.1 , R1 | INT-010-2.1 | R1 | R1. The Balancing Authority that experiences a loss of resources covered by an energy sharing agreement or other reliability needs covered by an energy sharing agreement shall ensure that a Request for Interchange (RFI) is submitted with a start time no more than 60 minutes beyond the resource loss. If the use of the energy sharing agreement does not exceed 60 minutes from the time of the resource loss, no RFI is required. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
INT-010-2.1 , R2 | INT-010-2.1 | R2 | R2. Each Sink Balancing Authority shall ensure that a Reliability Adjustment Arranged Interchange reflecting a modification is submitted within 60 minutes of the start of the modification if a Reliability Coordinator directs the modification of a Confirmed Interchange or Implemented Interchange for actual or anticipated reliability-related reasons. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
INT-010-2.1 , R3. | INT-010-2.1 | R3. | R3. Each Sink Balancing Authority shall ensure that a Request for Interchange is submitted reflecting that Interchange Schedule within 60 minutes of the start of the scheduled Interchange if a Reliability Coordinator directs the scheduling of Interchange for actual or anticipated reliability-related reasons. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
NUC-001-3 , R1 | NUC-001-3 | R1 | R1. The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
NUC-001-3 , R2. | NUC-001-3 | R2. | R2. The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
NUC-001-3 , R3. | NUC-001-3 | R3. | R3. Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
NUC-001-3 , R4. | NUC-001-3 | R4. | R4. Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall 4.1. Incorporate the NPIRs into their operating analyses of the electric system. 4.2. Operate the electric system to meet the NPIRs. 4.3. Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
NUC-001-3 , R5. | NUC-001-3 | R5. | R5. Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall operate the nuclear plant to meet the NPIRs | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
NUC-001-3 , R6. | NUC-001-3 | R6. | R6. Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
NUC-001-3 , R7. | NUC-001-3 | R7. | R7. Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
NUC-001-3 , R8. | NUC-001-3 | R8. | R8. Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
NUC-001-3 , R9 | NUC-001-3 | R9 | R9. The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include the following elements in aggregate within the Agreement(s) identified in R2. • Where multiple Agreements with a single Transmission Entity are put into effect, the R9 elements must be addressed in aggregate within the Agreements; however, each Agreement does not have to contain each element. The Nuclear Plant Generator Operator and the Transmission Entity are responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements. • Where Agreements with multiple Transmission Entities are required, the Nuclear Plant Generator Operator is responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements with the Transmission Entities. The Agreements with each Transmission Entity do not have to contain each element; however, the Agreements with the multiple Transmission Entities, in the aggregate, must address all R9 elements. For each Agreement(s), the Nuclear Plant Generator Operator and the Transmission Entity are responsible to ensure the Agreement(s) contain(s) the elements of R9 applicable to that Transmission Entity9.1. Retired. [Note: Part 9.1 was retired under the Paragraph 81 project. The NUC SDT proposes to leave this Part blank to avoid renumbering Requirement parts that would impact existing agreements throughout the industry.] 9.2. Technical requirements and analysis: 9.2.1. Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the Agreement. 9.2.2. Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. 9.2.3. Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. 9.3. Operations and maintenance coordination 9.3.1. Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. 9.3.2. Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. 9.3.3. Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. 9.3.4. Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. 9.3.5. Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. 9.3.6. Coordination of physical and cyber security protection at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. 9.3.7. Coordination of the NPIRs with transmission system Remedial Action Schemes and any programs that reduce or shed load based on underfrequency or undervoltage. 9.4. Communications and training Administrative elements: 9.4.1. Provisions for communications affecting the NPIRs between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of applicable unique terms. 9.4.2. Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. 9.4.3. Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. 9.4.4. Provisions for supplying information necessary to report to government agencies, as related to NPIRs. 9.4.5. Provisions for personnel training, as related to NPIRs. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PER-001-0.2 , R1. | PER-001-0.2 | R1. | R1. Each Transmission Operator and Balancing Authority shall provide operating personnel with the responsibility and authority to implement real-time actions to ensure the stable and reliable operation of the Bulk Electric System. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PER-003-1 , R1. | PER-003-1 | R1. | R1. Each Reliability Coordinator shall staff its Real-time operating positions performing Reliability Coordinator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining a valid NERC Reliability Operator certificate ( ) : [Risk Factor: High][Time Horizon: Real-time Operations] 1.1. Areas of Competency 1.1.1. Resource and demand balancing 1.1.2. Transmission operations 1.1.3. Emergency preparedness and operations 1.1.4. System operations 1.1.5. Protection and control 1.1.6. Voltage and reactive 1.1.7. Interchange scheduling and coordination 1.1.8. Interconnection reliability operations and coordination | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PER-003-1 , R2. | PER-003-1 | R2. | R2. Each Transmission Operator shall staff its Real-time operating positions performing Transmission Operator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates ( ) : [Risk Factor: High][Time Horizon: Real-time Operations]: 2.1. Areas of Competency 2.1.1. Transmission operations 2.1.2. Emergency preparedness and operations 2.1.3. System operations 2.1.4. Protection and control 2.1.5. Voltage and reactive 2.2. Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Transmission Operator | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PER-003-1 , R3. | PER-003-1 | R3. | R3. Each Balancing Authority shall staff its Real-time operating positions performing Balancing Authority reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates (1) : [Risk Factor: High][Time Horizon: Real-time Operations]: 3.1. Areas of Competency 3.1.1. Resources and demand balancing 3.1.2. Emergency preparedness and operations 3.1.3. System operations 3.1.4. Interchange scheduling and coordination 3.2. Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Balancing and Interchange Operator | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PER-004-2 , R1. | PER-004-2 | R1. | R1. Each Reliability Coordinator shall be staffed with adequately trained and NERC-certified Reliability Coordinator operators, 24 hours per day, seven days per week. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PER-004-2 , R2. | PER-004-2 | R2. | R2. Reliability Coordinator operating personnel shall place particular attention on SOLs and IROLs and inter-tie facility limits. The Reliability Coordinator shall ensure protocols are in place to allow Reliability Coordinator operating personnel to have the best available information at all times. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | yes |  | yes | yes | yes | yes | no | no | yes | no | yes | yes | no | yes | yes | no | yes | yes | yes | 3 | 7 | This seems to be saying "do your job". We already have requirement to do these actions - this is redundant to the TOP and IRO family of standards.
PRC-004-5(i) , R1. | PRC-004-5(i) | R1. | R1. Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] 1.1 The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and 1.2 The BES interrupting device owner owns all or part of the Composite Protection System; and 1.3 The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-004-5(i) , R2. | PRC-004-5(i) | R2. | R2. Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] 2.1 For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: 2.1.1 The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and 2.1.2 The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and 2.1.3 The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. 2.2 For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-004-5(i) , R3. | PRC-004-5(i) | R3. | R3. Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-004-5(i) , R4. | PRC-004-5(i) | R4. | R4. Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: [Violation Risk Factor: High] [Time Horizon: Operations Assessment, Operations Planning] • The identification of the cause(s) of the Misoperation; or • A declaration that no cause was identified. | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12 | Not sure you need a requirement to keep looking for the root cause? This seems like more of a procedure than a reliability requirement.
PRC-004-5(i) , R5. | PRC-004-5(i) | R5. | R5. Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: [Violation Risk Factor: High] [Time Horizon: Operations Planning, Long-Term Planning] • Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or • Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-004-5(i) , R6. | PRC-004-5(i) | R6. | R6. Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. [Violation Risk Factor: High][Time Horizon: Operations Planning, Long-Term Planning] | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12 | Also looks like a procedure, not a reliability requirement.
PRC-005-6 , R1. | PRC-005-6 | R1. | R1. Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems, Automatic Reclosing, and Sudden Pressure Relaying identified in Section 4.2, Facilities. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] The PSMP shall: 1.1. Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. 1.2. Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-3, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-005-6 , R2. | PRC-005-6 | R2. | R2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-005-6 , R3. | PRC-005-6 | R3. | R3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-3, and Table 5. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-005-6 , R4. | PRC-005-6 | R4. | R4. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the performance-based program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-005-6 , R5. | PRC-005-6 | R5. | R5. Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12 | Also looks like a procedure, not a reliability requirement.
PRC-006-2 , R1. | PRC-006-2 | R1. | R1. Each Planning Coordinator shall develop and document criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES), including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12 |  | 17400
PRC-006-2 , R2. | PRC-006-2 | R2. | R2. Each Planning Coordinator shall identify one or more islands to serve as a basis for designing its UFLS program including: [VRF: Medium][Time Horizon: Long-term Planning] 2.1. Those islands selected by applying the criteria in Requirement R1, and 2.2. Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and 2.3. A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. | yes | yes |  | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 2 | 12
PRC-006-2 , R3. | PRC-006-2 | R3. | R3. Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). [VRF: High][Time Horizon: Long-term Planning] 3.1. Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and 3.2. Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and 3.3. Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: • Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES • Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES • Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-006-2 , R4. | PRC-006-2 | R4. | R4. Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2. The simulation shall model each of the following: [VRF: High][Time Horizon: Long-term Planning] 4.1. Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. 4.2. Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. 4.3. Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. 4.4. Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. 4.5. Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. 4.6. Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. 4.7. Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-006-2 , R5. | PRC-006-2 | R5. | R5. Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall coordinate its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island through one of the following: [VRF: High][Time Horizon: Long-term Planning] • Develop a common UFLS program design and schedule for implementation per Requirement R3 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct a joint UFLS design assessment per Requirement R4 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct an independent UFLS design assessment per Requirement R4 for the identified island, and in the event the UFLS design assessment fails to meet Requirement R3, identify modifications to the UFLS program(s) to meet Requirement R3 and report these modifications as recommendations to the other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island and the ERO. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-006-2 , R6. | PRC-006-2 | R6. | R6. Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-006-2 , R7. | PRC-006-2 | R7. | R7. Each Planning Coordinator shall provide its UFLS database containing data necessary to model its UFLS program to other Planning Coordinators within its Interconnection within 30 calendar days of a request. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-006-2 , R8. | PRC-006-2 | R8. | R8. Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-006-2 , R9. | PRC-006-2 | R9. | R9. Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-006-2 , R10. | PRC-006-2 | R10. | R10. Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-006-2 , R11. | PRC-006-2 | R11. | R11. Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall conduct and document an assessment of the event within one year of event actuation to evaluate: [VRF: Medium][Time Horizon: Operations Assessment] 11.1. The performance of the UFLS equipment, 11.2. The effectiveness of the UFLS program. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12 | Also looks like a procedure, not a reliability requirement.
PRC-006-2 , R12. | PRC-006-2 | R12. | R12. Each Planning Coordinator, in whose islanding event assessment (per R11) UFLS program deficiencies are identified, shall conduct and document a UFLS design assessment to consider the identified deficiencies within two years of event actuation. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12 | Also looks like a procedure, not a reliability requirement.
PRC-006-2 , R13. | PRC-006-2 | R13. | R13. Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall coordinate its event assessment (in accordance with Requirement R11) with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event through one of the following: [VRF: Medium][Time Horizon: Operations Assessment] • Conduct a joint event assessment per Requirement R11 among the Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 that reaches conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 and where the assessment fails to reach conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, identify differences in the assessments that likely resulted in the differences in the conclusions and recommendations and report these differences to the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event and the ERO. | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12 | Also looks like a procedure, not a reliability requirement.
PRC-010-2 , R1. | PRC-010-2 | R1. | R1. Each Planning Coordinator or Transmission Planner that is developing a UVLS Program shall evaluate its effectiveness and subsequently provide the UVLS Program’s specifications and implementation schedule to the UVLS entities responsible for implementing the UVLS Program. The evaluation shall include, but is not limited to, studies and analyses that show: [Violation Risk Factor: High] [Time Horizon: Long‐term Planning] 1.1. The implementation of the UVLS Program resolves the identified undervoltage issues that led to its development and design. 1.2. The UVLS Program is integrated through coordination with generator voltage ride‐through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage‐based load shedding programs. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-010-2 , R2. | PRC-010-2 | R2. | R2. Each UVLS entity shall adhere to the UVLS Program specifications and implementation schedule determined by its Planning Coordinator or Transmission Planner associated with UVLS Program development per Requirement R1 or with any Corrective Action Plans per Requirement R5. [Violation Risk Factor: High] [Time Horizon: Long‐term Planning] | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-010-2 , R3. | PRC-010-2 | R3. | R3. Each Planning Coordinator or Transmission Planner shall perform a comprehensive assessment to evaluate the effectiveness of each of its UVLS Programs at least once every 60 calendar months. Each assessment shall include, but is not limited to, studies and analyses that evaluate whether: [Violation Risk Factor: Medium] [Time Horizon: Long‐term Planning] 3.1. The UVLS Program resolves the identified undervoltage issues for which the UVLS Program is designed. 3.2. The UVLS Program is integrated through coordination with generator voltage ride‐through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage‐based load shedding programs. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-010-2 , R4. | PRC-010-2 | R4. | R4. Each Planning Coordinator or Transmission Planner shall, within 12 calendar months of an event that resulted in a voltage excursion for which its UVLS Program was designed to operate, perform an assessment to evaluate: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] 4.1. Whether its UVLS Program resolved the undervoltage issues associated with the event, and 4.2. The performance (i.e., operation and non-operation) of the UVLS Program equipment. | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12 | Also looks like a procedure, not a reliability requirement.
PRC-010-2 , R5. | PRC-010-2 | R5. | R5. Each Planning Coordinator or Transmission Planner that identifies deficiencies during an assessment performed in either Requirement R3 or R4 shall develop a Corrective Action Plan to address the deficiencies and subsequently provide the Corrective Action Plan, including an implementation schedule, to UVLS entities within three calendar months of completing the assessment. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12 | Also looks like a procedure, not a reliability requirement.
PRC-010-2 , R6. | PRC-010-2 | R6. | R6. Each Planning Coordinator that has a UVLS Program in its area shall update a database containing data necessary to model the UVLS Program(s) in its area for use in event analyses and assessments of the UVLS Program at least once each calendar year. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12 | Also looks like a procedure, not a reliability requirement.
PRC-010-2 , R7. | PRC-010-2 | R7. | R7. Each UVLS entity shall provide data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of a UVLS Program database. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-010-2 , R8. | PRC-010-2 | R8. | R8. Each Planning Coordinator that has a UVLS Program in its area shall provide its UVLS Program database to other Planning Coordinators and Transmission Planners within its Interconnection, and other functional entities with a reliability need, within 30 calendar days of a written request. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12 | Also looks like a procedure, not a reliability requirement.
PRC-018-1 , R1. | PRC-018-1 | R1. | R1. Each Transmission Owner and Generator Owner required to install DMEs by its Regional Reliability Organization (reliability standard PRC-002 Requirements 1-3) shall have DMEs installed that meet the following requirements: R1.1. Internal Clocks in DME devices shall be synchronized to within 2 milliseconds or less of Universal Coordinated Time scale (UTC) R1.2. Recorded data from each Disturbance shall be retrievable for ten calendar days.. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12 | May stray into capacity - this gets close to being a materials standard.
PRC-018-1 , R2. | PRC-018-1 | R2. | R2. The Transmission Owner and Generator Owner shall each install DMEs in accordance with its Regional Reliability Organization’s installation requirements (reliability standard PRC-002 Requirements 1 through 3). | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12 | May stray into capacity - this gets close to being a materials standard.
PRC-018-1 , R3. | PRC-018-1 | R3. | R3. The Transmission Owner and Generator Owner shall each maintain, and report to its Regional Reliability Organization on request, the following data on the DMEs installed to meet that region’s installation requirements (reliability standard PRC-002 Requirements1.1, 2.1 and 3.1): R3.1. Type of DME (sequence of event recorder, fault recorder, or dynamic disturbance recorder). R3.2. Make and model of equipment. R3.3. Installation location. R3.4. Operational status. R3.5. Date last tested. R3.6. Monitored elements, such as transmission circuit, bus section, etc. R3.7. Monitored devices, such as circuit breaker, disconnect status, alarms, etc. R3.8. Monitored electrical quantities, such as voltage, current, etc. | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12 | Also looks like a procedure, not a reliability requirement.
PRC-018-1 , R4. | PRC-018-1 | R4. | R4. The Transmission Owner and Generator Owner shall each provide Disturbance data (recorded by DMEs) in accordance with its Regional Reliability Organization’s requirements (reliability standard PRC-002 Requirement 4). | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-018-1 , R5. | PRC-018-1 | R5. | R5. The Transmission Owner and Generator Owner shall each archive all data recorded by DMEs for Regional Reliability Organization-identified events for at least three years. | yes |  |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12 | Isn't this really just data retention? Seems out of place as a requirement.
PRC-018-1 , R6. | PRC-018-1 | R6. | R6. Each Transmission Owner and Generator Owner that is required by its Regional Reliability Organization to have DMEs shall have a maintenance and testing program for those DMEs that includes: R6.1. Maintenance and testing intervals and their basis. R6.2. Summary of maintenance and testing procedures. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-019-2 , R1. | PRC-019-2 | R1. | R1. At a maximum of every five calendar years, each Generator Owner and Transmission Owner with applicable Facilities shall coordinate the voltage regulating system controls, (including in-service limiters and protection functions) with the applicable equipment capabilities and settings of the applicable Protection System devices and functions. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] 1.1. Assuming the normal automatic voltage regulator control loop and steady-state system operating conditions, verify the following coordination items for each applicable Facility: 1.1.1. The in-service limiters are set to operate before the Protection System of the applicable Facility in order to avoid disconnecting the generator unnecessarily. 1.1.2. The applicable in-service Protection System devices are set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-019-2 , R2. | PRC-019-2 | R2. | R2. Within 90 calendar days following the identification or implementation of systems, equipment or setting changes that will affect the coordination described in Requirement R1, each Generator Owner and Transmission Owner with applicable Facilities shall perform the coordination as described in Requirement R1. These possible systems, equipment or settings changes include, but are not limited to the following [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning]: • Voltage regulating settings or equipment changes; • Protection System settings or component changes; • Generating or synchronous condenser equipment capability changes; or • Generator or synchronous condenser step-up transformer changes. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-023-4 , R1. | PRC-023-4 | R1. | R1. Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees (see Standard for criteria). | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-023-4 , R2. | PRC-023-4 | R2. | R2. Each Transmission Owner, Generator Owner, and Distribution Provider shall set its out-of-step blocking elements to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-023-4 , R3. | PRC-023-4 | R3. | R3. Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning] | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-023-4 , R4. | PRC-023-4 | R4. | R4. Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-023-4 , R5. | PRC-023-4 | R5. | R5. Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that have protective relay settings that limit circuit capability. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-023-4 , R6. | PRC-023-4 | R6. | R6. Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in PRC-023-4, Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5. The Planning Coordinator shall: [Violation Risk Factor: High] [Time Horizon: Long Term Planning] 6.1 Maintain a list of circuits subject to PRC-023-4 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023-4, Attachment B applies. 6.2 Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-024-2 , R1. | PRC-024-2 | R1. | R1. Each Generator Owner that has generator frequency protective relaying activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1, subject to the following exceptions: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] • Generating unit(s) may trip if the protective functions (such as out-of-step functions or loss-of-field functions) operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 1 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-024-2 , R2. | PRC-024-2 | R2. | R2. Each Generator Owner that has generator voltage protective relaying1 activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating unit(s) as a result of a voltage excursion (at the point of interconnection ) caused by an event on the transmission system external to the generating plant that remains within the “no trip zone” of PRC-024 Attachment 2. If the Transmission Planner allows less stringent voltage relay settings than those required to meet PRC-024 Attachment 2, then the Generator Owner shall set its protective relaying within the voltage recovery characteristics of a location-specific Transmission Planner’s study. Requirement R2 is subject to the following exceptions: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] • Generating unit(s) may trip in accordance with a Special Protection System (SPS) or Remedial Action Scheme (RAS). • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip by action of protective functions (such as out-of-step functions or loss-of-field functions) that operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 2 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-024-2 , R3. | PRC-024-2 | R3. | R3. Each Generator Owner shall document each known regulatory or equipment limitation that prevents an applicable generating unit with generator frequency or voltage protective relays from meeting the relay setting criteria in Requirements R1 or R2 including (but not limited to) study results, experience from an actual event, or manufacturer’s advice. [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] 3.1. The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following: • Identification of a regulatory or equipment limitation. • Repair of the equipment causing the limitation that removes the limitation. • Replacement of the equipment causing the limitation with equipment that removes the limitation. • Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-024-2 , R4. | PRC-024-2 | R4. | R4. Each Generator Owner shall provide its applicable generator protection trip settings associated with Requirements R1 and R2 to the Planning Coordinator or Transmission Planner that models the associated unit within 60 calendar days of receipt of a written request for the data and within 60 calendar days of any change to those previously requested trip settings unless directed by the requesting Planning Coordinator or Transmission Planner that the reporting of relay setting changes is not required. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-025-1 , R1. | PRC-025-1 | R1. | R1. Each Generator Owner, Transmission Owner, and Distribution Provider shall apply settings that are in accordance with PRC-025-1 – Attachment 1: Relay Settings, on each load-responsive protective relay while maintaining reliable fault protection. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-026-1 , R1. | PRC-026-1 | R1. | R1. Each Planning Coordinator shall, at least once each calendar year, provide notification of each generator, transformer, and transmission line BES Element in its area that meets one or more of the following criteria, if any, to the respective Generator Owner and Transmission Owner: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] Criteria: 1. Generator(s) where an angular stability constraint exists that is addressed by a System Operating Limit (SOL) or a Remedial Action Scheme (RAS) and those Elements terminating at the Transmission station associated with the generator(s). 2. An Element that is monitored as part of an SOL identified by the Planning Coordinator’s methodology based on an angular stability constraint. 3. An Element that forms the boundary of an island in the most recent underfrequency load shedding (UFLS) design assessment based on application of the Planning Coordinator’s criteria for identifying islands, only if the island is formed by tripping the Element due to angular instability. 4. An Element identified in the most recent annual Planning Assessment where relay tripping occurs due to a stable or unstable power swing during a simulated disturbance. | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12 | Also looks like a procedure, not a reliability requirement.
PRC-026-1 , R2. | PRC-026-1 | R2. | R2. Each Generator Owner and Transmission Owner shall: [Violation Risk Factor: High] [Time Horizon: Operations Planning] 2.1 Within 12 full calendar months of notification of a BES Element pursuant to Requirement R1, determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B where an evaluation of that Element’s load-responsive protective relay(s) based on PRC-026-1 – Attachment B criteria has not been performed in the last five calendar years. 2.2 Within 12 full calendar months of becoming aware of a generator, transformer, or transmission line BES Element that tripped in response to a stable or unstable power swing due to the operation of its protective relay(s), determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-026-1 , R3. | PRC-026-1 | R3. | R3. Each Generator Owner and Transmission Owner shall, within six full calendar months of determining a load-responsive protective relay does not meet the PRC-026-1 – Attachment B criteria pursuant to Requirement R2, develop a Corrective Action Plan (CAP) to meet one of the following: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] • The Protection System meets the PRC-026-1 – Attachment B criteria, while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element); or • The Protection System is excluded under the PRC-026-1 – Attachment A criteria (e.g., modifying the Protection System so that relay functions are supervised by power swing blocking or using relay systems that are immune to power swings), while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element). | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-026-1 , R4. | PRC-026-1 | R4. | R4. Each Generator Owner and Transmission Owner shall implement each CAP developed pursuant to Requirement R3 and update each CAP if actions or timetables change until all actions are complete. [Violation Risk Factor: Medium][Time Horizon: Long-Term Planning] | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12 | Also looks like a procedure, not a reliability requirement.
VAR-001-4.1 , R1. | VAR-001-4.1 | R1. | R1. Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. [Violation Risk Factor: High] [Time Horizon: Operational Planning] 1.1. Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
VAR-001-4.1 , R2. | VAR-001-4.1 | R2. | R2. Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
VAR-001-4.1 , R3. | VAR-001-4.1 | R3. | R3. Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
VAR-001-4.1 , R4. | VAR-001-4.1 | R4. | R4. The Transmission Operator shall specify the criteria that will exempt generators from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] 4.1 If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12 | More procedure than requirement.
VAR-001-4.1 , R5. | VAR-001-4.1 | R5. | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] 5.1. The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). 5.2. The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). 5.3. The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
VAR-001-4.1 , R6. | VAR-001-4.1 | R6. | R6. After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
VAR-002-4 , R1. | VAR-002-4 | R1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] • That the generator is being operated in start-up,1 shutdown,2 or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
VAR-002-4 , R2. | VAR-002-4 | R2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule3 (within each generating Facility’s capabilities4) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] 2.1. When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. 2.2. When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. 2.3. Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
VAR-002-4 , R3. | VAR-002-4 | R3. | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
VAR-002-4 , R4. | VAR-002-4 | R4. | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] • Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
VAR-002-4 , R5. | VAR-002-4 | R5. | . The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. [Violation Risk Factor: Lower] [Time Horizon: Real-time Operations] 5.1. For generator step-up and auxiliary transformers5 with primary voltages equal to or greater than the generator terminal voltage: 5.1.1. Tap settings. 5.1.2. Available fixed tap ranges. 5.1.3. Impedance data. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12 | This seems to be redundant to the TOP standards. The TOP can ask for any data it wants for reliability purposes.
VAR-002-4 , R6. | VAR-002-4 | R6. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. [Violation Risk Factor: Lower] [Time Horizon: Real-time Operations] 6.1. If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. | yes | yes |  | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12 | This one is more of an official excuse than a requirement. As such, it seems redundant to the TOP standards.

## PC
| Standard and Requirement | Requirement Number | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Supports a Reliability Objective (as defined by the Reliability Principles) (Yes/No/Maybe) | Meets the Paragraph 81 criteria? (Mark only if Yes) | Appropriate as a guide rather than a standard? (Mark only if Yes) | C1 | C2 | C3 | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | Q9 | Q10 | Q11 | Q12 | Q13 | PC Content Score 0-3 | PC Quality Score 0-13 | Comment/Rationale
Standard and Requirement | [6 empty] | Is the content of the requirement technically correct, including identifying who does what and when? | Are the correct functional entities identified? | Are the appropriate actions, for which there should be accountability, included or is there a gap? | Should the requirement stand alone as is or should it be consolidated with other standards? | Is it drafted as a results-based standard (RBS) requirement (performance, risk (prevention) or capability) and does it follow the RBS format (e.g., sub-requirement structure)? | Is it technologically neutral? | Are the expectations for each function clear? | Does the requirement align with the purpose? | Is it a higher solution than the lowest common denominator? | Is it measureable? | Does it have a technical basis in engineering and operations? | Is it complete and self-contained? | Is the language clear and does not contain ambiguous or outdated terms? | Can it be practically implemented? | Does it use consistent terminology? | Is the Standard cost effective in achieving the reliability purpose or objective of the Standard and mitigating the risk to the BES?
BAL-001-2 , R1 | BAL-001-2 | R1 | R1. The Responsible Entity shall operate such that the Control Performance Standard 1 (CPS1), calculated in accordance with Attachment 1, is greater than or equal to 100 percent for the applicable Interconnection in which it operates for each preceding 12 consecutive calendar month period, evaluated monthly. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | 3 | 11 | I scored column T as a "no" because the requirement is not self-contained, it refers to an Attachment. I think that this is an acceptable way to handle the calculation method, but I wasn't sure if the question was focused on the requirement or the entire standard.
BAL-001-2 , R2 | BAL-001-2 | R2 | R2. Each Balancing Authority shall operate such that its clock-minute average of Reporting ACE does not exceed its clock-minute Balancing Authority ACE Limit (BAAL) for more than 30 consecutive clock-minutes, calculated in accordance with Attachment 2, for the applicable Interconnection in which the Balancing Authority operates.[Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | 3 | 11 | I scored column T as a "no" because the requirement is not self-contained, it refers to an Attachment. I think that this is an acceptable way to handle the calculation method, but I wasn't sure if the question was focused on the requirement or the entire standard.
EOP-010-1, R1 | EOP-010-1 | R1 | R1. Each Reliability Coordinator shall develop, maintain, and implement a GMD Operating Plan that coordinates GMD Operating Procedures or Operating Processes within its Reliability Coordinator Area. At a minimum, the GMD Operating Plan shall include: 1.1 A description of activities designed to mitigate the effects of GMD events on the reliable operation of the interconnected transmission system within the Reliability Coordinator Area. 1.2 A process for the Reliability Coordinator to review the GMD Operating Procedures or Operating Processes of Transmission Operators within its Reliability Coordinator Area. | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12
EOP-010-1, R2 | EOP-010-1 | R2 | R2. Each Reliability Coordinator shall disseminate forecasted and current space weather information to functional entities identified as recipients in the Reliability Coordinator's GMD Operating Plan. | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12
EOP-010-1, R3. | EOP-010-1 | R3. | R3. Each Transmission Operator shall develop, maintain, and implement a GMD Operating Procedure or Operating Process to mitigate the effects of GMD events on the reliable operation of its respective system. At a minimum, the Operating Procedure or Operating Process shall include: 3.1. Steps or tasks to receive space weather information. 3.2. System Operator actions to be initiated based on predetermined conditions. 3.3. The conditions for terminating the Operating Procedure or Operating Process. | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12
EOP-011-1, R1. | EOP-011-1 | R1. | R1. Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] 1.1. Roles and responsibilities for activating the Operating Plan(s); 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.1. Notification to its Reliability Coordinator, to include current and projected conditions, when experiencing an operating Emergency; 1.2.2. Cancellation or recall of Transmission and generation outages; 1.2.3. Transmission system reconfiguration; 1.2.4. Redispatch of generation request; 1.2.5. Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and 1.2.6. Reliability impacts of extreme weather conditions. | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12
EOP-011-1, R2. | EOP-011-1 | R2. | R2. Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] 2.1. Roles and responsibilities for activating the Operating Plan(s); 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.1. Notification to its Reliability Coordinator, to include current and projected conditions when experiencing a Capacity Emergency or Energy Emergency; 2.2.2. Requesting an Energy Emergency Alert, per Attachment 1; 2.2.3. Managing generating resources in its Balancing Authority Area to address: 2.2.3.1. capability and availability; 2.2.3.2. fuel supply and inventory concerns; 2.2.3.3. fuel switching capabilities; and 2.2.3.4. environmental constraints. 2.2.4. Public appeals for voluntary Load reductions; 2.2.5. Requests to government agencies to implement their programs to achieve necessary energy reductions; 2.2.6. Reduction of internal utility energy use; 2.2.7. Use of Interruptible Load, curtailable Load and demand response; 2.2.8. Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and 2.2.9. Reliability impacts of extreme weather conditions. | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12
EOP-011-1, R3. | EOP-011-1 | R3. | R3. The Reliability Coordinator shall review the Operating Plan(s) to mitigate operating Emergencies submitted by a Transmission Operator or a Balancing Authority regarding any reliability risks that are identified between Operating Plans. [Violation Risk Factor: High] [Time Horizon: Operations Planning] 3.1. Within 30 calendar days of receipt, the Reliability Coordinator shall: 3.1.1. Review each submitted Operating Plan(s) on the basis of compatibility and inter-dependency with other Balancing Authorities’ and Transmission Operators’ Operating Plans; 3.1.2. Review each submitted Operating Plan(s) for coordination to avoid risk to Wide Area reliability; and 3.1.3. Notify each Balancing Authority and Transmission Operator of the results of its review, specifying any time frame for resubmittal of its Operating Plan(s) if revisions are identified. | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12
EOP-011-1, R4. | EOP-011-1 | R4. | R4. Each Transmission Operator and Balancing Authority shall address any reliability risks identified by its Reliability Coordinator pursuant to Requirement R3 and resubmit its Operating Plan(s) to its Reliability Coordinator within a time period specified by its Reliability Coordinator. | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12
EOP-011-1, R5. | EOP-011-1 | R5. | R5. Each Reliability Coordinator that receives an Emergency notification from a Transmission Operator or Balancing Authority within its Reliability Coordinator Area shall notify, within 30 minutes from the time of receiving notification, other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators. [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12
EOP-011-1, R6. | EOP-011-1 | R6. | R6. Each Reliability Coordinator that has a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area shall declare an Energy Emergency Alert, as detailed in Attachment 1. [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12
FAC-008-3, R1 | FAC-008-3 | R1 | R1. Each Generator Owner shall have documentation for determining the Facility Ratings of its solely and jointly owned generator Facility(ies) up to the low side terminals of the main step up transformer if the Generator Owner does not own the main step up transformer and the high side terminals of the main step up transformer if the Generator Owner owns the main step up transformer. 1.1. The documentation shall contain assumptions used to rate the generator and at least one of the following: • Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis. • Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. 1.2. The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | Yes |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11
FAC-008-3, R2. | FAC-008-3 | R2. | Each Generator Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned equipment connected between the location specified in R1 and the point of interconnection with the Transmission Owner that contains all of the following. 1.1. The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. 1.2. The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: 1.2.1. Equipment Rating standard(s) used in development of this methodology. 1.2.2. Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. 1.2.3. Ambient conditions (for particular or average conditions or as they vary in real-time). 1.2.4. Operating limitations. 1.3. A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. 1.4. The process by which the Rating of equipment that comprises a Facility is determined. 1.4.1. The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. 1.4.2. The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | Yes |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11
FAC-008-3, R3. | FAC-008-3 | R3. | R3. Each Transmission Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned Facilities (except for those generating unit Facilities addressed in R1 and R2) that contains all of the following: [Violation Risk Factor: Medium] [ Time Horizon: Long-term Planning] 3.1. The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. 3.2. The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: 3.2.1. Equipment Rating standard(s) used in development of this methodology. 3.2.2. Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. 3.2.3. Ambient conditions (for particular or average conditions or as they vary in real-time). 3.2.4. Operating limitations. 3.3. A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. 3.4. The process by which the Rating of equipment that comprises a Facility is determined. 3.4.1. The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. 3.4.2. The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | Yes |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11
FAC-008-3, R4. | FAC-008-3 | R4. | R4. Each Transmission Owner shall make its Facility Ratings methodology and each Generator Owner shall each make its documentation for determining its Facility Ratings and its Facility Ratings methodology available for inspection and technical review by those Reliability Coordinators, Transmission Operators, Transmission Planners and Planning Coordinators that have responsibility for the area in which the associated Facilities are located, within 21 calendar days of receipt of a request. (Retirement approved by FERC effective January 21, 2014.) | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | While not technically incorrect, really nothing technical about standard.
FAC-008-3, R5. | FAC-008-3 | R5. | R5. If a Reliability Coordinator, Transmission Operator, Transmission Planner or Planning Coordinator provides documented comments on its technical review of a Transmission Owner’s Facility Ratings methodology or Generator Owner’s documentation for determining its Facility Ratings and its Facility Rating methodology, the Transmission Owner or Generator Owner shall provide a response to that commenting entity within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Facility Ratings methodology and, if no change will be made to that Facility Ratings methodology, the reason why. (Retirement approved by FERC effective January 21, 2014.) | Maybe | Yes | Yes |  | Yes | Yes | No | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | This looks administrative to me but it is measurable and I suppose it reduces risk if the inquiry is what is used to check the ratings, but if there is a disagreement the entity only needs to explain why. Not sure how that reduces risk unless there is a new round of response and comment ad-infinitum. While not technically incorrect, really nothing technical about standard.
FAC-008-3, R6. | FAC-008-3 | R6. | R6. Each Transmission Owner and Generator Owner shall have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology or documentation for determining its Facility Ratings. | Yes |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | While not technically incorrect, really nothing technical about standard.
FAC-008-3, R7. | FAC-008-3 | R7. | R7. Each Generator Owner shall provide Facility Ratings (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) as scheduled by such requesting entities | Yes |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11
FAC-008-3, R8. | FAC-008-3 | R8. | R8. Each Transmission Owner (and each Generator Owner subject to Requirement R2) shall provide requested information as specified below (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s): [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] 8.1. As scheduled by the requesting entities: 8.1.1. Facility Ratings 8.1.2. Identity of the most limiting equipment of the Facilities 8.2. Within 30 calendar days (or a later date if specified by the requester), for any requested Facility with a Thermal Rating that limits the use of Facilities under the requester’s authority by causing any of the following: 1) An Interconnection Reliability Operating Limit, 2) A limitation of Total Transfer Capability, 3) An impediment to generator deliverability, or 4) An impediment to service to a major load center: 8.2.1. Identity of the existing next most limiting equipment of the Facility 8.2.2. The Thermal Rating for the next most limiting equipment identified in Requirement R8, Part 8.2.1. | Yes |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11
INT-004-3.1 , R1 | INT-004-3.1 | R1 | R1. Each Purchasing-Selling Entity that secures energy to serve Load via a Dynamic Schedule or Pseudo-Tie shall ensure that a Request for Interchange is submitted as an on-time Arranged Interchange to the Sink Balancing Authority for that Dynamic Schedule or Pseudo-Tie, unless the information about the Pseudo-Tie is included in congestion management procedure(s) via an alternate method. | [6 empty] | No | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No | Yes | No | 3 | 9
INT-004-3.1 , R2 | INT-004-3.1 | R2 | R2. The Purchasing-Selling Entity that submits a Request for Interchange in accordance with Requirement R1 shall ensure the Confirmed Interchange associated with that Dynamic Schedule or Pseudo-Tie is updated for future hours in order to support congestion management procedures if any one of the following occurs: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning, Same Day Operations, Real Time Operations] 2.1. For Confirmed Interchange greater than 250 MW for the last hour, the actual hourly integrated energy deviates from the Confirmed Interchange by more than 10% for that hour and that deviation is expected to persist. 2.2. For Confirmed Interchange less than or equal to 250 MW for the last hour, the actual hourly integrated energy deviates from the Confirmed Interchange by more than 25 MW for that hour and that deviation is expected to persist. 2.3. The Purchasing-Selling Entity receives notification from a Reliability Coordinator or Transmission Operator to update the Confirmed Interchange. | [6 empty] | No | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No | Yes | No | 3 | 9
INT-004-3.1 , R3. | INT-004-3.1 | R3. | R3. Each Balancing Authority shall only implement or operate a Pseudo-Tie that is included in the NAESB Electric Industry Registry publication in order to support congestion management procedures. | Maybe | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | Yes | Yes | Yes | 3 | 10 | . I have never seen another requirement where an external entities process is the heart of the requirement. What happens if NAESB changes their Registry, who monitors that? Changes to the standard may or may not be able to be made at the same pace as the NAESB process. I have not managed schedules since 2002 when ComEd came into PJM but this requirement looks administrative to me.
INT-006-4, R1 | INT-006-4 | R1 | R1. Each Balancing Authority shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B. 1.1. Each Source and Sink Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if it does not expect to be capable of supporting the magnitude of the Interchange, including ramping, throughout the duration of the Arranged Interchange. 1.2. Each Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if the Scheduling Path (proper connectivity of Adjacent Balancing Authorities) between it and its Adjacent Balancing Authorities is invalid. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes |  | 3 | 10 | I would like this standard to be a guide, but setting out the responsibilities of each party with respect to interchange is important to balancing and controlling ACE, so I think it has to stay a standard. I said that the requirement is not entirely self-contained because it references an Attachment to the standard, but the entire standard appears to be self-contained. I indicated that it is not a higher solution than the lowest common denominator because it identifies criteria for denying the Arranged Interchange. It does not fully describe the reliability evaluation of the arranged interchange, just two trigger points for denial. I think that is adequate, but might be considered "lowest common denominator.
INT-006-4, R2 | INT-006-4 | R2 | R2. Each Transmission Service Provider shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B. 2.1. Each Transmission Service Provider shall deny the Arranged Interchange or curtail Confirmed Interchange if the transmission path (proper connectivity of adjacent Transmission Service Providers) between it and its adjacent Transmission Service Providers is invalid. | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes |  | 3 | 10 | I would like this standard to be a guide, but setting out the responsibilities of each party with respect to interchange is important to balancing and controlling ACE, so I think it has to stay a standard. I said that the requirement is not entirely self-contained because it references an Attachment to the standard, but the entire standard appears to be self-contained. I indicated that it is not a higher solution than the lowest common denominator because it identifies criteria for denying the Arranged Interchange. It does not fully describe the reliability evaluation of the arranged interchange, just two trigger points for denial. I think that is adequate, but might be considered "lowest common denominator."
INT-006-4, R3. | INT-006-4 | R3. | R3. The Source Balancing Authority and the Sink Balancing Authority receiving a Reliability Adjustment Arranged Interchange shall approve or deny it prior to the expiration of the time period defined in Attachment 1, Column B. 3.1. If a Balancing Authority denies a Reliability Adjustment Arranged Interchange, the Balancing Authority must communicate that fact to its Reliability Coordinator no more than 10 minutes after the denial. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes |  | 3 | 11 | I said that the requirement is not entirely self-contained because it references an Attachment to the standard, but the entire standard appears to be self-contained.
INT-006-4, R4 | INT-006-4 | R4 | R4. Each Sink Balancing Authority shall confirm that none of the following conditions exist prior to transitioning an Arranged Interchange to Confirmed Interchange: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning, Same-day Operations, Real-time Operations] • It is a Reliability Adjustment Arranged Interchange, the time period specified in Attachment 1, Column B has elapsed, and the Source Balancing Authority or the Sink Balancing Authority associated with the Arranged Interchange has not communicated its approval of the transition. • It is not a Reliability Adjustment Arranged Interchange, the time period specified in Attachment 1, Column B, has elapsed, and not all Balancing Authorities and Transmission Service Providers associated with the Arranged Interchange have communicated their approval of the transition. • It is not a Reliability Adjustment Arranged Interchange, the time period specified in Attachment 1, Column B, has elapsed, and any entity associated with the Arranged Interchange has communicated its denial of the transition. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes |  | 3 | 11 | I said that the requirement is not entirely self-contained because it references an Attachment to the standard, but the entire standard appears to be self-contained.
INT-006-4, R5 | INT-006-4 | R5 | R5. For each Arranged Interchange that is transitioned to Confirmed Interchange, the Sink Balancing Authority shall notify the following entities of the on-time Confirmed Interchange such that the notification is delivered in time to be incorporated into scheduling systems prior to ramp start as specified in Attachment 1, Column D: 5.1. The Source Balancing Authority, 5.2. Each Intermediate Balancing Authority, 5.3. Each Reliability Coordinator associated with each Balancing Authority included in the Arranged Interchange, | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes |  | 3 | 11 | I said that the requirement is not entirely self-contained because it references an Attachment to the standard, but the entire standard appears to be self-contained.
INT-009-2.1, R1 | INT-009-2.1 | R1 | R1. Each Balancing Authority shall agree with each of its Adjacent Balancing Authorities that its Composite Confirmed Interchange with that Adjacent Balancing Authority, at mutually agreed upon time intervals, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange per INT-010-2 not yet captured in the Composite Confirmed Interchange, is: 1.1. Identical in magnitude to that of the Adjacent Balancing Authority, and 1.2. Opposite in sign or direction to that of the Adjacent Balancing Authority. | Yes |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
INT-009-2.1, R2 | INT-009-2.1 | R2 | R2. The Attaining Balancing Authority and the Native Balancing Authority shall use a dynamic value emanating from an agreed upon common source to account for the Pseudo-Tie in the Actual Net Interchange (NIA) term of their respective control ACE (or alternate control process). | Yes |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
INT-009-2.1, R3. | INT-009-2.1 | R3. | R3. Each Balancing Authority in whose area the high-voltage direct current tie is controlled shall coordinate the Confirmed Interchange prior to its implementation with the Transmission Operator of the high-voltage direct current tie. | Yes |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
INT-010-2.1, R1 | INT-010-2.1 | R1 | R1. The Balancing Authority that experiences a loss of resources covered by an energy sharing agreement or other reliability needs covered by an energy sharing agreement shall ensure that a Request for Interchange (RFI) is submitted with a start time no more than 60 minutes beyond the resource loss. If the use of the energy sharing agreement does not exceed 60 minutes from the time of the resource loss, no RFI is required. | Maybe | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 3 | 8 | My concern is that the I think the RFI is post event to create the record, i.e. the interchange occurs immediately when the emergency is declared and the “schedule” is made after the fact to balance the interchange record keeping. I don’t know how this “reduces BES risk” The INT standards are all intended to ensure that BAs "do the right thing" regarding interchange. I wish that these could be relegated to guidelines, but I think that this one should stay as a standard. I’m not sure if it has a technical basis in engineering or operations. The 60 minutes was just to ensure that if emergency energy sharing was implemented, that the interchange was entered within a reasonable amount of time. Not sure 60 minutes is the right number. It might be a "lowest common denominator" kind of provision.
INT-010-2.1, R2 | INT-010-2.1 | R2 | R2. Each Sink Balancing Authority shall ensure that a Reliability Adjustment Arranged Interchange reflecting a modification is submitted within 60 minutes of the start of the modification if a Reliability Coordinator directs the modification of a Confirmed Interchange or Implemented Interchange for actual or anticipated reliability-related reasons. | Maybe |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 3 | 8 | My concern is that the I think the RFI is post event to create the record, i.e. the interchange occurs immediately when the emergency is declared and the “schedule” is made after the fact to balance the interchange record keeping. I don’t know how this “reduces BES risk” The INT standards are all intended to ensure that BAs "do the right thing" regarding interchange. I wish that these could be relegated to guidelines, but I think that this one should stay as a standard. I’m not sure if it has a technical basis in engineering or operations. The 60 minutes was just to ensure that if emergency energy sharing was implemented, that the interchange was entered within a reasonable amount of time. Not sure 60 minutes is the right number. It might be a "lowest common denominator" kind of provision.
INT-010-2.1, R3. | INT-010-2.1 | R3. | R3. Each Sink Balancing Authority shall ensure that a Request for Interchange is submitted reflecting that Interchange Schedule within 60 minutes of the start of the scheduled Interchange if a Reliability Coordinator directs the scheduling of Interchange for actual or anticipated reliability-related reasons. | Maybe |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 3 | 8 | My concern is that the I think the RFI is post event to create the record, i.e. the interchange occurs immediately when the emergency is declared and the “schedule” is made after the fact to balance the interchange record keeping. I don’t know how this “reduces BES risk” The INT standards are all intended to ensure that BAs "do the right thing" regarding interchange. I wish that these could be relegated to guidelines, but I think that this one should stay as a standard. I’m not sure if it has a technical basis in engineering or operations. The 60 minutes was just to ensure that if emergency energy sharing was implemented, that the interchange was entered within a reasonable amount of time. Not sure 60 minutes is the right number. It might be a "lowest common denominator" kind of provision.
NUC-001-3, R1 | NUC-001-3 | R1 | R1. The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt. | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
NUC-001-3, R2. | NUC-001-3 | R2. | R2. The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs. | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
NUC-001-3, R3. | NUC-001-3 | R3. | R3. Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
NUC-001-3, R4. | NUC-001-3 | R4. | R4. Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall 4.1. Incorporate the NPIRs into their operating analyses of the electric system. 4.2. Operate the electric system to meet the NPIRs. 4.3. Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
NUC-001-3, R5. | NUC-001-3 | R5. | R5. Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall operate the nuclear plant to meet the NPIRs | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
NUC-001-3, R6. | NUC-001-3 | R6. | R6. Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
NUC-001-3, R7. | NUC-001-3 | R7. | R7. Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
NUC-001-3, R8. | NUC-001-3 | R8. | R8. Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
NUC-001-3, R9 | NUC-001-3 | R9 | R9. The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include the following elements in aggregate within the Agreement(s) identified in R2. • Where multiple Agreements with a single Transmission Entity are put into effect, the R9 elements must be addressed in aggregate within the Agreements; however, each Agreement does not have to contain each element. The Nuclear Plant Generator Operator and the Transmission Entity are responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements. • Where Agreements with multiple Transmission Entities are required, the Nuclear Plant Generator Operator is responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements with the Transmission Entities. The Agreements with each Transmission Entity do not have to contain each element; however, the Agreements with the multiple Transmission Entities, in the aggregate, must address all R9 elements. For each Agreement(s), the Nuclear Plant Generator Operator and the Transmission Entity are responsible to ensure the Agreement(s) contain(s) the elements of R9 applicable to that Transmission Entity9.1. Retired. [Note: Part 9.1 was retired under the Paragraph 81 project. The NUC SDT proposes to leave this Part blank to avoid renumbering Requirement parts that would impact existing agreements throughout the industry.] 9.2. Technical requirements and analysis: 9.2.1. Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the Agreement. 9.2.2. Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. 9.2.3. Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. 9.3. Operations and maintenance coordination 9.3.1. Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. 9.3.2. Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. 9.3.3. Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. 9.3.4. Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. 9.3.5. Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. 9.3.6. Coordination of physical and cyber security protection at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. 9.3.7. Coordination of the NPIRs with transmission system Remedial Action Schemes and any programs that reduce or shed load based on underfrequency or undervoltage. 9.4. Communications and training Administrative elements: 9.4.1. Provisions for communications affecting the NPIRs between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of applicable unique terms. 9.4.2. Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. 9.4.3. Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. 9.4.4. Provisions for supplying information necessary to report to government agencies, as related to NPIRs. 9.4.5. Provisions for personnel training, as related to NPIRs. | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PER-001-0.2, R1. | PER-001-0.2 | R1. | R1. Each Transmission Operator and Balancing Authority shall provide operating personnel with the responsibility and authority to implement real-time actions to ensure the stable and reliable operation of the Bulk Electric System. | Yes |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11
PER-003-1, R1. | PER-003-1 | R1. | R1. Each Reliability Coordinator shall staff its Real-time operating positions performing Reliability Coordinator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining a valid NERC Reliability Operator certificate ( ) : [Risk Factor: High][Time Horizon: Real-time Operations] 1.1. Areas of Competency 1.1.1. Resource and demand balancing 1.1.2. Transmission operations 1.1.3. Emergency preparedness and operations 1.1.4. System operations 1.1.5. Protection and control 1.1.6. Voltage and reactive 1.1.7. Interchange scheduling and coordination 1.1.8. Interconnection reliability operations and coordination | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PER-003-1, R2. | PER-003-1 | R2. | R2. Each Transmission Operator shall staff its Real-time operating positions performing Transmission Operator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates ( ) : [Risk Factor: High][Time Horizon: Real-time Operations]: 2.1. Areas of Competency 2.1.1. Transmission operations 2.1.2. Emergency preparedness and operations 2.1.3. System operations 2.1.4. Protection and control 2.1.5. Voltage and reactive 2.2. Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Transmission Operator | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PER-003-1, R3. | PER-003-1 | R3. | R3. Each Balancing Authority shall staff its Real-time operating positions performing Balancing Authority reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates (1) : [Risk Factor: High][Time Horizon: Real-time Operations]: 3.1. Areas of Competency 3.1.1. Resources and demand balancing 3.1.2. Emergency preparedness and operations 3.1.3. System operations 3.1.4. Interchange scheduling and coordination 3.2. Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Balancing and Interchange Operator | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PER-004-2, R1. | PER-004-2 | R1. | R1. Each Reliability Coordinator shall be staffed with adequately trained and NERC-certified Reliability Coordinator operators, 24 hours per day, seven days per week. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | Yes |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11
PER-004-2, R2. | PER-004-2 | R2. | R2. Reliability Coordinator operating personnel shall place particular attention on SOLs and IROLs and inter-tie facility limits. The Reliability Coordinator shall ensure protocols are in place to allow Reliability Coordinator operating personnel to have the best available information at all times. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | Yes |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | No | No | No | No | Yes | Yes | 3 | 7
PRC-004-5(i), R1. | PRC-004-5(i) | R1. | R1. Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] 1.1 The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and 1.2 The BES interrupting device owner owns all or part of the Composite Protection System; and 1.3 The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-004-5(i), R2. | PRC-004-5(i) | R2. | R2. Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] 2.1 For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: 2.1.1 The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and 2.1.2 The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and 2.1.3 The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. 2.2 For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-004-5(i), R3. | PRC-004-5(i) | R3. | R3. Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-004-5(i), R4. | PRC-004-5(i) | R4. | R4. Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: [Violation Risk Factor: High] [Time Horizon: Operations Assessment, Operations Planning] • The identification of the cause(s) of the Misoperation; or • A declaration that no cause was identified. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-004-5(i), R5. | PRC-004-5(i) | R5. | R5. Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: [Violation Risk Factor: High] [Time Horizon: Operations Planning, Long-Term Planning] • Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or • Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-004-5(i), R6. | PRC-004-5(i) | R6. | R6. Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. [Violation Risk Factor: High][Time Horizon: Operations Planning, Long-Term Planning] | Maybe | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | My reason is based on where does compliance oversight stop and what is the reduction in risk. A CAP is a Corrective Action Plan; by definition, it must be implemented to correct the identified failure. If it changes due to exigent circumstances, it will be updated, the record / evidence of completion will show that, I don’t think there needs to be a requirement to implement and update the plan.
PRC-005-6, R1. | PRC-005-6 | R1. | R1. Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems, Automatic Reclosing, and Sudden Pressure Relaying identified in Section 4.2, Facilities. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] The PSMP shall: 1.1. Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. 1.2. Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-3, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-005-6, R2. | PRC-005-6 | R2. | R2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-005-6, R3. | PRC-005-6 | R3. | R3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-3, and Table 5. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-005-6, R4. | PRC-005-6 | R4. | R4. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the performance-based program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-005-6, R5. | PRC-005-6 | R5. | R5. Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | Maybe | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes |  | Yes | No | No | No | No | Yes | No | 2 | 6 | I think this administrative but I am in the minority. I also wonder what would happen if I “demonstrated efforts” that were a failure, would that meet the requirement?
PRC-006-2 , R1. | PRC-006-2 | R1. | R1. Each Planning Coordinator shall develop and document criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES), including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-006-2 , R2. | PRC-006-2 | R2. | R2. Each Planning Coordinator shall identify one or more islands to serve as a basis for designing its UFLS program including: [VRF: Medium][Time Horizon: Long-term Planning] 2.1. Those islands selected by applying the criteria in Requirement R1, and 2.2. Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and 2.3. A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. | Yes |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12
PRC-006-2 , R3. | PRC-006-2 | R3. | R3. Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). [VRF: High][Time Horizon: Long-term Planning] 3.1. Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and 3.2. Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and 3.3. Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: • Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES • Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES • Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-006-2 , R4. | PRC-006-2 | R4. | R4. Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2. The simulation shall model each of the following: [VRF: High][Time Horizon: Long-term Planning] 4.1. Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. 4.2. Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. 4.3. Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. 4.4. Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. 4.5. Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. 4.6. Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. 4.7. Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-006-2 , R5. | PRC-006-2 | R5. | R5. Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall coordinate its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island through one of the following: [VRF: High][Time Horizon: Long-term Planning] • Develop a common UFLS program design and schedule for implementation per Requirement R3 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct a joint UFLS design assessment per Requirement R4 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct an independent UFLS design assessment per Requirement R4 for the identified island, and in the event the UFLS design assessment fails to meet Requirement R3, identify modifications to the UFLS program(s) to meet Requirement R3 and report these modifications as recommendations to the other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island and the ERO. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-006-2 , R6. | PRC-006-2 | R6. | R6. Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-006-2 , R7. | PRC-006-2 | R7. | R7. Each Planning Coordinator shall provide its UFLS database containing data necessary to model its UFLS program to other Planning Coordinators within its Interconnection within 30 calendar days of a request. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-006-2 , R8. | PRC-006-2 | R8. | R8. Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-006-2 , R9. | PRC-006-2 | R9. | R9. Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-006-2 , R10. | PRC-006-2 | R10. | R10. Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-006-2 , R11. | PRC-006-2 | R11. | R11. Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall conduct and document an assessment of the event within one year of event actuation to evaluate: [VRF: Medium][Time Horizon: Operations Assessment] 11.1. The performance of the UFLS equipment, 11.2. The effectiveness of the UFLS program. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-006-2 , R12. | PRC-006-2 | R12. | R12. Each Planning Coordinator, in whose islanding event assessment (per R11) UFLS program deficiencies are identified, shall conduct and document a UFLS design assessment to consider the identified deficiencies within two years of event actuation. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-006-2 , R13. | PRC-006-2 | R13. | R13. Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall coordinate its event assessment (in accordance with Requirement R11) with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event through one of the following: [VRF: Medium][Time Horizon: Operations Assessment] • Conduct a joint event assessment per Requirement R11 among the Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 that reaches conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 and where the assessment fails to reach conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, identify differences in the assessments that likely resulted in the differences in the conclusions and recommendations and report these differences to the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event and the ERO. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-010-2, R1. | PRC-010-2 | R1. | R1. Each Planning Coordinator or Transmission Planner that is developing a UVLS Program shall evaluate its effectiveness and subsequently provide the UVLS Program’s specifications and implementation schedule to the UVLS entities responsible for implementing the UVLS Program. The evaluation shall include, but is not limited to, studies and analyses that show: [Violation Risk Factor: High] [Time Horizon: Long‐term Planning] 1.1. The implementation of the UVLS Program resolves the identified undervoltage issues that led to its development and design. 1.2. The UVLS Program is integrated through coordination with generator voltage ride‐through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage‐based load shedding programs. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-010-2, R2. | PRC-010-2 | R2. | R2. Each UVLS entity shall adhere to the UVLS Program specifications and implementation schedule determined by its Planning Coordinator or Transmission Planner associated with UVLS Program development per Requirement R1 or with any Corrective Action Plans per Requirement R5. [Violation Risk Factor: High] [Time Horizon: Long‐term Planning] | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-010-2, R3. | PRC-010-2 | R3. | R3. Each Planning Coordinator or Transmission Planner shall perform a comprehensive assessment to evaluate the effectiveness of each of its UVLS Programs at least once every 60 calendar months. Each assessment shall include, but is not limited to, studies and analyses that evaluate whether: [Violation Risk Factor: Medium] [Time Horizon: Long‐term Planning] 3.1. The UVLS Program resolves the identified undervoltage issues for which the UVLS Program is designed. 3.2. The UVLS Program is integrated through coordination with generator voltage ride‐through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage‐based load shedding programs. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-010-2, R4. | PRC-010-2 | R4. | R4. Each Planning Coordinator or Transmission Planner shall, within 12 calendar months of an event that resulted in a voltage excursion for which its UVLS Program was designed to operate, perform an assessment to evaluate: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] 4.1. Whether its UVLS Program resolved the undervoltage issues associated with the event, and 4.2. The performance (i.e., operation and non-operation) of the UVLS Program equipment. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-010-2, R5. | PRC-010-2 | R5. | R5. Each Planning Coordinator or Transmission Planner that identifies deficiencies during an assessment performed in either Requirement R3 or R4 shall develop a Corrective Action Plan to address the deficiencies and subsequently provide the Corrective Action Plan, including an implementation schedule, to UVLS entities within three calendar months of completing the assessment. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-010-2, R6. | PRC-010-2 | R6. | R6. Each Planning Coordinator that has a UVLS Program in its area shall update a database containing data necessary to model the UVLS Program(s) in its area for use in event analyses and assessments of the UVLS Program at least once each calendar year. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-010-2, R7. | PRC-010-2 | R7. | R7. Each UVLS entity shall provide data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of a UVLS Program database. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-010-2, R8. | PRC-010-2 | R8. | R8. Each Planning Coordinator that has a UVLS Program in its area shall provide its UVLS Program database to other Planning Coordinators and Transmission Planners within its Interconnection, and other functional entities with a reliability need, within 30 calendar days of a written request. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-018-1, R1. | PRC-018-1 | R1. | R1. Each Transmission Owner and Generator Owner required to install DMEs by its Regional Reliability Organization (reliability standard PRC-002 Requirements 1-3) shall have DMEs installed that meet the following requirements: R1.1. Internal Clocks in DME devices shall be synchronized to within 2 milliseconds or less of Universal Coordinated Time scale (UTC) R1.2. Recorded data from each Disturbance shall be retrievable for ten calendar days.. | Yes |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 | 10
PRC-018-1, R2. | PRC-018-1 | R2. | R2. The Transmission Owner and Generator Owner shall each install DMEs in accordance with its Regional Reliability Organization’s installation requirements (reliability standard PRC-002 Requirements 1 through 3). | Yes |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | No | Yes | Yes | 3 | 9
PRC-018-1, R3. | PRC-018-1 | R3. | R3. The Transmission Owner and Generator Owner shall each maintain, and report to its Regional Reliability Organization on request, the following data on the DMEs installed to meet that region’s installation requirements (reliability standard PRC-002 Requirements1.1, 2.1 and 3.1): R3.1. Type of DME (sequence of event recorder, fault recorder, or dynamic disturbance recorder). R3.2. Make and model of equipment. R3.3. Installation location. R3.4. Operational status. R3.5. Date last tested. R3.6. Monitored elements, such as transmission circuit, bus section, etc. R3.7. Monitored devices, such as circuit breaker, disconnect status, alarms, etc. R3.8. Monitored electrical quantities, such as voltage, current, etc. | Yes |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 | 10
PRC-018-1, R4. | PRC-018-1 | R4. | R4. The Transmission Owner and Generator Owner shall each provide Disturbance data (recorded by DMEs) in accordance with its Regional Reliability Organization’s requirements (reliability standard PRC-002 Requirement 4). | Yes |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | No | Yes | Yes | 3 | 9
PRC-018-1, R5. | PRC-018-1 | R5. | R5. The Transmission Owner and Generator Owner shall each archive all data recorded by DMEs for Regional Reliability Organization-identified events for at least three years. | Maybe | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | No | Yes | No | 3 | 9 | A SDT is told to follow the FFT and P81 order, paraphrased, “avoid requirements that only support documenting and reporting” . There is a place for data collection for post event analysis but I don’t think it is a standard. See below also.
PRC-018-1, R6. | PRC-018-1 | R6. | R6. Each Transmission Owner and Generator Owner that is required by its Regional Reliability Organization to have DMEs shall have a maintenance and testing program for those DMEs that includes: R6.1. Maintenance and testing intervals and their basis. R6.2. Summary of maintenance and testing procedures. | Maybe | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes |  | Yes | No | Yes | Yes | Yes | Yes | No | 3 | 9 | See my comments about PRC-018 in the word doc. This standard is in effect de jure across the country but de facto, only in NPCC. Only NPCC has a Regional DME standard. This is scheduled to go way when the new PRC-002 standard is fully implemented, starting in July 2017. I just think assessing this is a waste of time. It’s not going to be modified, there is no sense in grading it.
PRC-019-2, R1. | PRC-019-2 | R1. | R1. At a maximum of every five calendar years, each Generator Owner and Transmission Owner with applicable Facilities shall coordinate the voltage regulating system controls, (including in-service limiters and protection functions) with the applicable equipment capabilities and settings of the applicable Protection System devices and functions. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] 1.1. Assuming the normal automatic voltage regulator control loop and steady-state system operating conditions, verify the following coordination items for each applicable Facility: 1.1.1. The in-service limiters are set to operate before the Protection System of the applicable Facility in order to avoid disconnecting the generator unnecessarily. 1.1.2. The applicable in-service Protection System devices are set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-019-2, R2. | PRC-019-2 | R2. | R2. Within 90 calendar days following the identification or implementation of systems, equipment or setting changes that will affect the coordination described in Requirement R1, each Generator Owner and Transmission Owner with applicable Facilities shall perform the coordination as described in Requirement R1. These possible systems, equipment or settings changes include, but are not limited to the following [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning]: • Voltage regulating settings or equipment changes; • Protection System settings or component changes; • Generating or synchronous condenser equipment capability changes; or • Generator or synchronous condenser step-up transformer changes. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-023-4, R1. | PRC-023-4 | R1. | R1. Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees (see Standard for criteria). | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-023-4, R2. | PRC-023-4 | R2. | R2. Each Transmission Owner, Generator Owner, and Distribution Provider shall set its out-of-step blocking elements to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-023-4, R3. | PRC-023-4 | R3. | R3. Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning] | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-023-4, R4. | PRC-023-4 | R4. | R4. Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-023-4, R5. | PRC-023-4 | R5. | R5. Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that have protective relay settings that limit circuit capability. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-023-4, R6. | PRC-023-4 | R6. | R6. Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in PRC-023-4, Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5. The Planning Coordinator shall: [Violation Risk Factor: High] [Time Horizon: Long Term Planning] 6.1 Maintain a list of circuits subject to PRC-023-4 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023-4, Attachment B applies. 6.2 Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-024-2, R1. | PRC-024-2 | R1. | R1. Each Generator Owner that has generator frequency protective relaying activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1, subject to the following exceptions: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] • Generating unit(s) may trip if the protective functions (such as out-of-step functions or loss-of-field functions) operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 1 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-024-2, R2. | PRC-024-2 | R2. | R2. Each Generator Owner that has generator voltage protective relaying1 activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating unit(s) as a result of a voltage excursion (at the point of interconnection ) caused by an event on the transmission system external to the generating plant that remains within the “no trip zone” of PRC-024 Attachment 2. If the Transmission Planner allows less stringent voltage relay settings than those required to meet PRC-024 Attachment 2, then the Generator Owner shall set its protective relaying within the voltage recovery characteristics of a location-specific Transmission Planner’s study. Requirement R2 is subject to the following exceptions: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] • Generating unit(s) may trip in accordance with a Special Protection System (SPS) or Remedial Action Scheme (RAS). • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip by action of protective functions (such as out-of-step functions or loss-of-field functions) that operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 2 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-024-2, R3. | PRC-024-2 | R3. | R3. Each Generator Owner shall document each known regulatory or equipment limitation that prevents an applicable generating unit with generator frequency or voltage protective relays from meeting the relay setting criteria in Requirements R1 or R2 including (but not limited to) study results, experience from an actual event, or manufacturer’s advice. [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] 3.1. The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following: • Identification of a regulatory or equipment limitation. • Repair of the equipment causing the limitation that removes the limitation. • Replacement of the equipment causing the limitation with equipment that removes the limitation. • Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-024-2, R4. | PRC-024-2 | R4. | R4. Each Generator Owner shall provide its applicable generator protection trip settings associated with Requirements R1 and R2 to the Planning Coordinator or Transmission Planner that models the associated unit within 60 calendar days of receipt of a written request for the data and within 60 calendar days of any change to those previously requested trip settings unless directed by the requesting Planning Coordinator or Transmission Planner that the reporting of relay setting changes is not required. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-025-1, R1. | PRC-025-1 | R1. | R1. Each Generator Owner, Transmission Owner, and Distribution Provider shall apply settings that are in accordance with PRC-025-1 – Attachment 1: Relay Settings, on each load-responsive protective relay while maintaining reliable fault protection. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-026-1, R1. | PRC-026-1 | R1. | R1. Each Planning Coordinator shall, at least once each calendar year, provide notification of each generator, transformer, and transmission line BES Element in its area that meets one or more of the following criteria, if any, to the respective Generator Owner and Transmission Owner: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] Criteria: 1. Generator(s) where an angular stability constraint exists that is addressed by a System Operating Limit (SOL) or a Remedial Action Scheme (RAS) and those Elements terminating at the Transmission station associated with the generator(s). 2. An Element that is monitored as part of an SOL identified by the Planning Coordinator’s methodology based on an angular stability constraint. 3. An Element that forms the boundary of an island in the most recent underfrequency load shedding (UFLS) design assessment based on application of the Planning Coordinator’s criteria for identifying islands, only if the island is formed by tripping the Element due to angular instability. 4. An Element identified in the most recent annual Planning Assessment where relay tripping occurs due to a stable or unstable power swing during a simulated disturbance. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-026-1, R2. | PRC-026-1 | R2. | R2. Each Generator Owner and Transmission Owner shall: [Violation Risk Factor: High] [Time Horizon: Operations Planning] 2.1 Within 12 full calendar months of notification of a BES Element pursuant to Requirement R1, determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B where an evaluation of that Element’s load-responsive protective relay(s) based on PRC-026-1 – Attachment B criteria has not been performed in the last five calendar years. 2.2 Within 12 full calendar months of becoming aware of a generator, transformer, or transmission line BES Element that tripped in response to a stable or unstable power swing due to the operation of its protective relay(s), determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-026-1, R3. | PRC-026-1 | R3. | R3. Each Generator Owner and Transmission Owner shall, within six full calendar months of determining a load-responsive protective relay does not meet the PRC-026-1 – Attachment B criteria pursuant to Requirement R2, develop a Corrective Action Plan (CAP) to meet one of the following: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] • The Protection System meets the PRC-026-1 – Attachment B criteria, while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element); or • The Protection System is excluded under the PRC-026-1 – Attachment A criteria (e.g., modifying the Protection System so that relay functions are supervised by power swing blocking or using relay systems that are immune to power swings), while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element). | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-026-1, R4. | PRC-026-1 | R4. | R4. Each Generator Owner and Transmission Owner shall implement each CAP developed pursuant to Requirement R3 and update each CAP if actions or timetables change until all actions are complete. [Violation Risk Factor: Medium][Time Horizon: Long-Term Planning] | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
VAR-001-4.1, R1. | VAR-001-4.1 | R1. | R1. Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. [Violation Risk Factor: High] [Time Horizon: Operational Planning] 1.1. Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
VAR-001-4.1, R2. | VAR-001-4.1 | R2. | R2. Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
VAR-001-4.1, R3. | VAR-001-4.1 | R3. | R3. Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
VAR-001-4.1, R4. | VAR-001-4.1 | R4. | R4. The Transmission Operator shall specify the criteria that will exempt generators from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] 4.1 If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
VAR-001-4.1, R5. | VAR-001-4.1 | R5. | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] 5.1. The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). 5.2. The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). 5.3. The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
VAR-001-4.1, R6. | VAR-001-4.1 | R6. | R6. After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
VAR-002-4, R1. | VAR-002-4 | R1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] • That the generator is being operated in start-up,1 shutdown,2 or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
VAR-002-4, R2. | VAR-002-4 | R2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule3 (within each generating Facility’s capabilities4) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] 2.1. When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. 2.2. When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. 2.3. Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
VAR-002-4, R3. | VAR-002-4 | R3. | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
VAR-002-4, R4. | VAR-002-4 | R4. | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] • Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
VAR-002-4, R5. | VAR-002-4 | R5. | . The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. [Violation Risk Factor: Lower] [Time Horizon: Real-time Operations] 5.1. For generator step-up and auxiliary transformers5 with primary voltages equal to or greater than the generator terminal voltage: 5.1.1. Tap settings. 5.1.2. Available fixed tap ranges. 5.1.3. Impedance data. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
VAR-002-4, R6. | VAR-002-4 | R6. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. [Violation Risk Factor: Lower] [Time Horizon: Real-time Operations] 6.1. If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12

## RE
| Standard Number | Requirement Number | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Supports a Reliability Objective (as defined by the Reliability Principles) (Yes/No/Maybe) | Meets the Paragraph 81 criteria? (Mark only if Yes) | Appropriate as a guide rather than a standard? (Mark only if Yes) | C1 | C2 | C3 | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | Q9 | Q10 | Q11 | Q12 | Q13 | RE Content Score 0-3 | RE Quality Score 0-13 | Comment/Rationale
Standard and Requirement | [6 empty] | Is the content of the requirement technically correct, including identifying who does what and when? | Are the correct functional entities identified? | Are the appropriate actions, for which there should be accountability, included or is there a gap? | Should the requirement stand alone as is or should it be consolidated with other standards? | Is it drafted as a results-based standard (RBS) requirement (performance, risk (prevention) or capability) and does it follow the RBS format (e.g., sub-requirement structure)? | Is it technologically neutral? | Are the expectations for each function clear? | Does the requirement align with the purpose? | Is it a higher solution than the lowest common denominator? | Is it measureable? | Does it have a technical basis in engineering and operations? | Is it complete and self-contained? | Is the language clear and does not contain ambiguous or outdated terms? | Can it be practically implemented? | Does it use consistent terminology? | Is the Standard cost effective in achieving the reliability purpose or objective of the Standard and mitigating the risk to the BES?
BAL-001-2 , R1 | BAL-001-2 | R1 | R1. The Responsible Entity shall operate such that the Control Performance Standard 1 (CPS1), calculated in accordance with Attachment 1, is greater than or equal to 100 percent for the applicable Interconnection in which it operates for each preceding 12 consecutive calendar month period, evaluated monthly. | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes |  | 3 | 11 | Question validity of the 12 month averaged period meeting the reliabiliy intent of the Standard. Clarity needed to define Responsible Entity (Should be a defined entity in the Applicability based use in requirement.). Standard does not use the most recent Results-Based Standard template.
BAL-001-2 , R2 | BAL-001-2 | R2 | R2. Each Balancing Authority shall operate such that its clock-minute average of Reporting ACE does not exceed its clock-minute Balancing Authority ACE Limit (BAAL) for more than 30 consecutive clock-minutes, calculated in accordance with Attachment 2, for the applicable Interconnection in which the Balancing Authority operates.[Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes |  | 3 | 11 | Standard does not use the most recent Results-Based Standard template.
EOP-010-1, R1 | EOP-010-1 | R1 | R1. Each Reliability Coordinator shall develop, maintain, and implement a GMD Operating Plan that coordinates GMD Operating Procedures or Operating Processes within its Reliability Coordinator Area. At a minimum, the GMD Operating Plan shall include: 1.1 A description of activities designed to mitigate the effects of GMD events on the reliable operation of the interconnected transmission system within the Reliability Coordinator Area. 1.2 A process for the Reliability Coordinator to review the GMD Operating Procedures or Operating Processes of Transmission Operators within its Reliability Coordinator Area. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
EOP-010-1, R2 | EOP-010-1 | R2 | R2. Each Reliability Coordinator shall disseminate forecasted and current space weather information to functional entities identified as recipients in the Reliability Coordinator's GMD Operating Plan. | Yes |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes |  | Yes | Yes | No | No | Yes | No | Yes | 2 | 8 | Requirement does not establish a peridicity of disseminating information to entities. Clarity needed on timing of reports and how entity defines 'current'. Requirement points to GMD Operating Plan as process for disseminating weather information, however R1 does not require inclusion of such information in Plan. Consider requirement establishing confirmation of receipt of information from the RC.
EOP-010-1, R3. | EOP-010-1 | R3. | R3. Each Transmission Operator shall develop, maintain, and implement a GMD Operating Procedure or Operating Process to mitigate the effects of GMD events on the reliable operation of its respective system. At a minimum, the Operating Procedure or Operating Process shall include: 3.1. Steps or tasks to receive space weather information. 3.2. System Operator actions to be initiated based on predetermined conditions. 3.3. The conditions for terminating the Operating Procedure or Operating Process. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
EOP-011-1, R1. | EOP-011-1 | R1. | R1. Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] 1.1. Roles and responsibilities for activating the Operating Plan(s); 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.1. Notification to its Reliability Coordinator, to include current and projected conditions, when experiencing an operating Emergency; 1.2.2. Cancellation or recall of Transmission and generation outages; 1.2.3. Transmission system reconfiguration; 1.2.4. Redispatch of generation request; 1.2.5. Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and 1.2.6. Reliability impacts of extreme weather conditions. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | 3 | 11 | In reference to self-contained, the standard does not provide direction to curtail transmission service.
EOP-011-1, R2. | EOP-011-1 | R2. | R2. Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] 2.1. Roles and responsibilities for activating the Operating Plan(s); 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.1. Notification to its Reliability Coordinator, to include current and projected conditions when experiencing a Capacity Emergency or Energy Emergency; 2.2.2. Requesting an Energy Emergency Alert, per Attachment 1; 2.2.3. Managing generating resources in its Balancing Authority Area to address: 2.2.3.1. capability and availability; 2.2.3.2. fuel supply and inventory concerns; 2.2.3.3. fuel switching capabilities; and 2.2.3.4. environmental constraints. 2.2.4. Public appeals for voluntary Load reductions; 2.2.5. Requests to government agencies to implement their programs to achieve necessary energy reductions; 2.2.6. Reduction of internal utility energy use; 2.2.7. Use of Interruptible Load, curtailable Load and demand response; 2.2.8. Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and 2.2.9. Reliability impacts of extreme weather conditions. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
EOP-011-1, R3. | EOP-011-1 | R3. | R3. The Reliability Coordinator shall review the Operating Plan(s) to mitigate operating Emergencies submitted by a Transmission Operator or a Balancing Authority regarding any reliability risks that are identified between Operating Plans. [Violation Risk Factor: High] [Time Horizon: Operations Planning] 3.1. Within 30 calendar days of receipt, the Reliability Coordinator shall: 3.1.1. Review each submitted Operating Plan(s) on the basis of compatibility and inter-dependency with other Balancing Authorities’ and Transmission Operators’ Operating Plans; 3.1.2. Review each submitted Operating Plan(s) for coordination to avoid risk to Wide Area reliability; and 3.1.3. Notify each Balancing Authority and Transmission Operator of the results of its review, specifying any time frame for resubmittal of its Operating Plan(s) if revisions are identified. | Yes |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | No | Yes | 1 | 11 | The RC reviews Operating Plans submitted by the TOP and BA. The BA Plan addresses capacity and energy emergencies and should be identified as such in requirement. RC mandated resubmittal times not identified. Consider establishing a time frame requirement.
EOP-011-1, R4. | EOP-011-1 | R4. | R4. Each Transmission Operator and Balancing Authority shall address any reliability risks identified by its Reliability Coordinator pursuant to Requirement R3 and resubmit its Operating Plan(s) to its Reliability Coordinator within a time period specified by its Reliability Coordinator. | Yes |  |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes |  | 1 | 12 | Consider adding requirement to require TOP/BA to submit updated Plan to RC for review. Currently language only supports initial submittal of Plans to the RC. When would the TOP/BA be requried by the Standard to resubmit a revised Plan and under what circumstances would re-submittal be required? RC resubmittal times not identified. Consider establishing a time frame requirement.
EOP-011-1, R5. | EOP-011-1 | R5. | R5. Each Reliability Coordinator that receives an Emergency notification from a Transmission Operator or Balancing Authority within its Reliability Coordinator Area shall notify, within 30 minutes from the time of receiving notification, other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators. [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | Yes |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | No | Yes | 2 | 11 | Use of term 'neighboring' vs. 'adjacent' should be evaluated. Inconsistencies currently exist in Reliability Standards in regards to these terms. 30 minute time frame is potentially a significant amount of time which could result in a reliability concern. Consider shorting timeframe to ensure timely notifications.
EOP-011-1, R6. | EOP-011-1 | R6. | R6. Each Reliability Coordinator that has a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area shall declare an Energy Emergency Alert, as detailed in Attachment 1. [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | Yes |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | Considering including a time limit for the RC to declare an EEA.
FAC-008-3, R1 | FAC-008-3 | R1 | R1. Each Generator Owner shall have documentation for determining the Facility Ratings of its solely and jointly owned generator Facility(ies) up to the low side terminals of the main step up transformer if the Generator Owner does not own the main step up transformer and the high side terminals of the main step up transformer if the Generator Owner owns the main step up transformer. 1.1. The documentation shall contain assumptions used to rate the generator and at least one of the following: • Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis. • Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. 1.2. The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | No | Yes | No |  | 3 | 9 | The term 'Facility Ratings' does not provide clarity on the need for identifying 'normal' and 'emergency' ratings. Are both the 'normal' and 'emergency' ratings required for R1? Standard does not use the most recent Results-Based Standard template.
FAC-008-3, R2. | FAC-008-3 | R2. | Each Generator Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned equipment connected between the location specified in R1 and the point of interconnection with the Transmission Owner that contains all of the following. 1.1. The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. 1.2. The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: 1.2.1. Equipment Rating standard(s) used in development of this methodology. 1.2.2. Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. 1.2.3. Ambient conditions (for particular or average conditions or as they vary in real-time). 1.2.4. Operating limitations. 1.3. A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. 1.4. The process by which the Rating of equipment that comprises a Facility is determined. 1.4.1. The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. 1.4.2. The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes |  | 3 | 11 | Jointly Owned Facilities up to the point of interconnection; Facility Rating methodologies may not be appropriate for the Generator Interconnection Facilities.Standard does not use the most recent Results-Based Standard template.
FAC-008-3, R3. | FAC-008-3 | R3. | R3. Each Transmission Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned Facilities (except for those generating unit Facilities addressed in R1 and R2) that contains all of the following: [Violation Risk Factor: Medium] [ Time Horizon: Long-term Planning] 3.1. The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. 3.2. The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: 3.2.1. Equipment Rating standard(s) used in development of this methodology. 3.2.2. Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. 3.2.3. Ambient conditions (for particular or average conditions or as they vary in real-time). 3.2.4. Operating limitations. 3.3. A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. 3.4. The process by which the Rating of equipment that comprises a Facility is determined. 3.4.1. The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. 3.4.2. The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Standard does not use the most recent Results-Based Standard template. Ambient is defined as "of or related to immediate surroundings". Use of this term may need to be revisited- is it approapriate. Ratings methodologies have been established and implemented for many years. Has the industry matured enough that this should be a guideline document?
FAC-008-3, R4. | FAC-008-3 | R4. | R4. Each Transmission Owner shall make its Facility Ratings methodology and each Generator Owner shall each make its documentation for determining its Facility Ratings and its Facility Ratings methodology available for inspection and technical review by those Reliability Coordinators, Transmission Operators, Transmission Planners and Planning Coordinators that have responsibility for the area in which the associated Facilities are located, within 21 calendar days of receipt of a request. (Retirement approved by FERC effective January 21, 2014.) |  | Yes | [17 empty] | 3 | 11 | Standard requirement is retired | bar: Q2
FAC-008-3, R5. | FAC-008-3 | R5. | R5. If a Reliability Coordinator, Transmission Operator, Transmission Planner or Planning Coordinator provides documented comments on its technical review of a Transmission Owner’s Facility Ratings methodology or Generator Owner’s documentation for determining its Facility Ratings and its Facility Rating methodology, the Transmission Owner or Generator Owner shall provide a response to that commenting entity within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Facility Ratings methodology and, if no change will be made to that Facility Ratings methodology, the reason why. (Retirement approved by FERC effective January 21, 2014.) |  | Yes | [17 empty] | 3 | 11 | Standard requirement is retired | bar: Q2
FAC-008-3, R6. | FAC-008-3 | R6. | R6. Each Transmission Owner and Generator Owner shall have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology or documentation for determining its Facility Ratings. | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | No | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Standard does not use the most recent Results-Based Standard template. There seems to be a need for clarity regarding jointly owned facilities and whose methodology needs to be used when evaluating ratings for consistency.
FAC-008-3, R7. | FAC-008-3 | R7. | R7. Each Generator Owner shall provide Facility Ratings (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) as scheduled by such requesting entities | Yes | Yes |  | No | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | No | Yes | Yes | Yes | 2 | 10 | As scheduled' language could be potentially unreasonable to comply with. Alternative language should consider the use of 'mutualy agreeable' or a timeframe of 30 daysor similar for compliance. What is meant by the term 'associated'? Consider 'respective' to identify the appropriate entity. Standard does not use the most recent Results-Based Standard template. R7 seems to be duplicative with R8-P81?
FAC-008-3, R8. | FAC-008-3 | R8. | R8. Each Transmission Owner (and each Generator Owner subject to Requirement R2) shall provide requested information as specified below (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s): [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] 8.1. As scheduled by the requesting entities: 8.1.1. Facility Ratings 8.1.2. Identity of the most limiting equipment of the Facilities 8.2. Within 30 calendar days (or a later date if specified by the requester), for any requested Facility with a Thermal Rating that limits the use of Facilities under the requester’s authority by causing any of the following: 1) An Interconnection Reliability Operating Limit, 2) A limitation of Total Transfer Capability, 3) An impediment to generator deliverability, or 4) An impediment to service to a major load center: 8.2.1. Identity of the existing next most limiting equipment of the Facility 8.2.2. The Thermal Rating for the next most limiting equipment identified in Requirement R8, Part 8.2.1. | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | No | Yes | Yes |  | 3 | 10 | What is meant by the term 'associated'? Consider 'respective' to identify the appropriate entity. 8.2.1 Specifies the 'identity…'; suggest considering 'Identifying the existing…'. Standard does not use the most recent Results-Based Standard template.
INT-004-3.1 , R1 | INT-004-3.1 | R1 | R1. Each Purchasing-Selling Entity that secures energy to serve Load via a Dynamic Schedule or Pseudo-Tie shall ensure that a Request for Interchange is submitted as an on-time Arranged Interchange to the Sink Balancing Authority for that Dynamic Schedule or Pseudo-Tie, unless the information about the Pseudo-Tie is included in congestion management procedure(s) via an alternate method. | No |  | Yes | [16 empty] | 3 | 12 | Purchase Selling Entity (PSE) function has been removed from the Registry Criteira and all previously registered PSEs have been de-registered or de-activated. Requirements with the sole applicablity of PSE and market-based in nature, will be migrated over to the NAESB requirements.
INT-004-3.1 , R2 | INT-004-3.1 | R2 | R2. The Purchasing-Selling Entity that submits a Request for Interchange in accordance with Requirement R1 shall ensure the Confirmed Interchange associated with that Dynamic Schedule or Pseudo-Tie is updated for future hours in order to support congestion management procedures if any one of the following occurs: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning, Same Day Operations, Real Time Operations] 2.1. For Confirmed Interchange greater than 250 MW for the last hour, the actual hourly integrated energy deviates from the Confirmed Interchange by more than 10% for that hour and that deviation is expected to persist. 2.2. For Confirmed Interchange less than or equal to 250 MW for the last hour, the actual hourly integrated energy deviates from the Confirmed Interchange by more than 25 MW for that hour and that deviation is expected to persist. 2.3. The Purchasing-Selling Entity receives notification from a Reliability Coordinator or Transmission Operator to update the Confirmed Interchange. |  |  | Yes | [16 empty] | 3 | 12 | Purchase Selling Entity (PSE) function has been removed from the Registry Criteira and all previously registered PSEs have been de-registered or de-activated. Requirements with the sole applicablity of PSE and market-based in nature, will be migrated over to the NAESB requirements.
INT-004-3.1 , R3. | INT-004-3.1 | R3. | R3. Each Balancing Authority shall only implement or operate a Pseudo-Tie that is included in the NAESB Electric Industry Registry publication in order to support congestion management procedures. | No | Yes | Yes | [16 empty] | 3 | 12 | This requirement may be considered administrative in nature since it is registering the pseudo-tie with NAESB, although it is critical to identify pseudo-ties for the IDC calculator. Perhaps this should identification should be in a guideline document as opposed to a standard.
INT-006-4, R1 | INT-006-4 | R1 | R1. Each Balancing Authority shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B. 1.1. Each Source and Sink Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if it does not expect to be capable of supporting the magnitude of the Interchange, including ramping, throughout the duration of the Arranged Interchange. 1.2. Each Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if the Scheduling Path (proper connectivity of Adjacent Balancing Authorities) between it and its Adjacent Balancing Authorities is invalid. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 11 | Suggest clarafication to the defintion of 'Arranged Interchange' to indicate it is 'the request for interchange at the time of it's submittal until the time it is confirmed (approved). Native, Source and Sending BAs and Attaining, Sink and Receiving BAs are identified in several Standards. Standards should be consistent in the identification of the BAs. Recommend the use of 'sink' and 'source' to establish consistency.
INT-006-4, R2 | INT-006-4 | R2 | R2. Each Transmission Service Provider shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B. 2.1. Each Transmission Service Provider shall deny the Arranged Interchange or curtail Confirmed Interchange if the transmission path (proper connectivity of adjacent Transmission Service Providers) between it and its adjacent Transmission Service Providers is invalid. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 11 | Suggest clarafication to the defintion of 'Arranged Interchange' to indicate it is 'the request for interchange at the time of it's submittal until the time it is confirmed (approved).
INT-006-4, R3. | INT-006-4 | R3. | R3. The Source Balancing Authority and the Sink Balancing Authority receiving a Reliability Adjustment Arranged Interchange shall approve or deny it prior to the expiration of the time period defined in Attachment 1, Column B. 3.1. If a Balancing Authority denies a Reliability Adjustment Arranged Interchange, the Balancing Authority must communicate that fact to its Reliability Coordinator no more than 10 minutes after the denial. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 11 | Suggest clarafication to the defintion of 'Arranged Interchange' to indicate it is 'the request for interchange at the time of it's submittal until the time it is confirmed (approved).
INT-006-4, R4 | INT-006-4 | R4 | R4. Each Sink Balancing Authority shall confirm that none of the following conditions exist prior to transitioning an Arranged Interchange to Confirmed Interchange: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning, Same-day Operations, Real-time Operations] • It is a Reliability Adjustment Arranged Interchange, the time period specified in Attachment 1, Column B has elapsed, and the Source Balancing Authority or the Sink Balancing Authority associated with the Arranged Interchange has not communicated its approval of the transition. • It is not a Reliability Adjustment Arranged Interchange, the time period specified in Attachment 1, Column B, has elapsed, and not all Balancing Authorities and Transmission Service Providers associated with the Arranged Interchange have communicated their approval of the transition. • It is not a Reliability Adjustment Arranged Interchange, the time period specified in Attachment 1, Column B, has elapsed, and any entity associated with the Arranged Interchange has communicated its denial of the transition. | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 10 | Requirement is confusing based on the 'none' statement followed by a bulleted set of critieria. Suggest requirement be reworded for clarity.
INT-006-4, R5 | INT-006-4 | R5 | R5. For each Arranged Interchange that is transitioned to Confirmed Interchange, the Sink Balancing Authority shall notify the following entities of the on-time Confirmed Interchange such that the notification is delivered in time to be incorporated into scheduling systems prior to ramp start as specified in Attachment 1, Column D: 5.1. The Source Balancing Authority, 5.2. Each Intermediate Balancing Authority, 5.3. Each Reliability Coordinator associated with each Balancing Authority included in the Arranged Interchange, | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
INT-009-2.1, R1 | INT-009-2.1 | R1 | R1. Each Balancing Authority shall agree with each of its Adjacent Balancing Authorities that its Composite Confirmed Interchange with that Adjacent Balancing Authority, at mutually agreed upon time intervals, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange per INT-010-2 not yet captured in the Composite Confirmed Interchange, is: 1.1. Identical in magnitude to that of the Adjacent Balancing Authority, and 1.2. Opposite in sign or direction to that of the Adjacent Balancing Authority. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
INT-009-2.1, R2 | INT-009-2.1 | R2 | R2. The Attaining Balancing Authority and the Native Balancing Authority shall use a dynamic value emanating from an agreed upon common source to account for the Pseudo-Tie in the Actual Net Interchange (NIA) term of their respective control ACE (or alternate control process). | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
INT-009-2.1, R3. | INT-009-2.1 | R3. | R3. Each Balancing Authority in whose area the high-voltage direct current tie is controlled shall coordinate the Confirmed Interchange prior to its implementation with the Transmission Operator of the high-voltage direct current tie. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
INT-010-2.1, R1 | INT-010-2.1 | R1 | R1. The Balancing Authority that experiences a loss of resources covered by an energy sharing agreement or other reliability needs covered by an energy sharing agreement shall ensure that a Request for Interchange (RFI) is submitted with a start time no more than 60 minutes beyond the resource loss. If the use of the energy sharing agreement does not exceed 60 minutes from the time of the resource loss, no RFI is required. | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | No | Yes | Yes |  | 3 | 10 | R1 should be separated into two (2) parts to clarify the criteira for when and if an RFI is required to be submitted. The requirement has two separate criteria which should be identified as R1.1 and 1.2.
INT-010-2.1, R2 | INT-010-2.1 | R2 | R2. Each Sink Balancing Authority shall ensure that a Reliability Adjustment Arranged Interchange reflecting a modification is submitted within 60 minutes of the start of the modification if a Reliability Coordinator directs the modification of a Confirmed Interchange or Implemented Interchange for actual or anticipated reliability-related reasons. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
INT-010-2.1, R3. | INT-010-2.1 | R3. | R3. Each Sink Balancing Authority shall ensure that a Request for Interchange is submitted reflecting that Interchange Schedule within 60 minutes of the start of the scheduled Interchange if a Reliability Coordinator directs the scheduling of Interchange for actual or anticipated reliability-related reasons. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
NUC-001-3, R1 | NUC-001-3 | R1 | R1. The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
NUC-001-3, R2. | NUC-001-3 | R2. | R2. The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
NUC-001-3, R3. | NUC-001-3 | R3. | R3. Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. | Yes |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | When does the Transmission Entity incorporate the NPIR into their analysis and communicate it to the Nuclear Plant Operator. Should this be two requirements? Perhaps this should be a guide rather than a requirement.
NUC-001-3, R4. | NUC-001-3 | R4. | R4. Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall 4.1. Incorporate the NPIRs into their operating analyses of the electric system. 4.2. Operate the electric system to meet the NPIRs. 4.3. Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
NUC-001-3, R5. | NUC-001-3 | R5. | R5. Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall operate the nuclear plant to meet the NPIRs | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
NUC-001-3, R6. | NUC-001-3 | R6. | R6. Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
NUC-001-3, R7. | NUC-001-3 | R7. | R7. Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
NUC-001-3, R8. | NUC-001-3 | R8. | R8. Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
NUC-001-3, R9 | NUC-001-3 | R9 | R9. The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include the following elements in aggregate within the Agreement(s) identified in R2. • Where multiple Agreements with a single Transmission Entity are put into effect, the R9 elements must be addressed in aggregate within the Agreements; however, each Agreement does not have to contain each element. The Nuclear Plant Generator Operator and the Transmission Entity are responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements. • Where Agreements with multiple Transmission Entities are required, the Nuclear Plant Generator Operator is responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements with the Transmission Entities. The Agreements with each Transmission Entity do not have to contain each element; however, the Agreements with the multiple Transmission Entities, in the aggregate, must address all R9 elements. For each Agreement(s), the Nuclear Plant Generator Operator and the Transmission Entity are responsible to ensure the Agreement(s) contain(s) the elements of R9 applicable to that Transmission Entity9.1. Retired. [Note: Part 9.1 was retired under the Paragraph 81 project. The NUC SDT proposes to leave this Part blank to avoid renumbering Requirement parts that would impact existing agreements throughout the industry.] 9.2. Technical requirements and analysis: 9.2.1. Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the Agreement. 9.2.2. Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. 9.2.3. Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. 9.3. Operations and maintenance coordination 9.3.1. Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. 9.3.2. Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. 9.3.3. Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. 9.3.4. Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. 9.3.5. Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. 9.3.6. Coordination of physical and cyber security protection at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. 9.3.7. Coordination of the NPIRs with transmission system Remedial Action Schemes and any programs that reduce or shed load based on underfrequency or undervoltage. 9.4. Communications and training Administrative elements: 9.4.1. Provisions for communications affecting the NPIRs between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of applicable unique terms. 9.4.2. Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. 9.4.3. Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. 9.4.4. Provisions for supplying information necessary to report to government agencies, as related to NPIRs. 9.4.5. Provisions for personnel training, as related to NPIRs. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PER-001-0.2, R1. | PER-001-0.2 | R1. | R1. Each Transmission Operator and Balancing Authority shall provide operating personnel with the responsibility and authority to implement real-time actions to ensure the stable and reliable operation of the Bulk Electric System. | Yes |  |  | Yes | No | Yes | No | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes |  | 2 | 10 | Retirement date: March 31, 2017. Replaced by the TOP Suite of Standards. Per Mapping Document (TOP/IRO Project) states:'In FERC Order 693a, paragraph 112, the Commission clarifies that a Reliability Coordinator’s authority to issue directives arises out of the Commission’s approval of Reliability Standards that mandate compliance with such directives. The SDT reasonably applied this same logic to Transmission Operators and Balancing Authorities and that makes this requirement superfluous and thus it can be deleted.' Standard does not use the most recent Standard template.
PER-003-1, R1. | PER-003-1 | R1. | R1. Each Reliability Coordinator shall staff its Real-time operating positions performing Reliability Coordinator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining a valid NERC Reliability Operator certificate ( ) : [Risk Factor: High][Time Horizon: Real-time Operations] 1.1. Areas of Competency 1.1.1. Resource and demand balancing 1.1.2. Transmission operations 1.1.3. Emergency preparedness and operations 1.1.4. System operations 1.1.5. Protection and control 1.1.6. Voltage and reactive 1.1.7. Interchange scheduling and coordination 1.1.8. Interconnection reliability operations and coordination | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Standard does not use the most recent Results-Based Standard template.
PER-003-1, R2. | PER-003-1 | R2. | R2. Each Transmission Operator shall staff its Real-time operating positions performing Transmission Operator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates ( ) : [Risk Factor: High][Time Horizon: Real-time Operations]: 2.1. Areas of Competency 2.1.1. Transmission operations 2.1.2. Emergency preparedness and operations 2.1.3. System operations 2.1.4. Protection and control 2.1.5. Voltage and reactive 2.2. Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Transmission Operator | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Standard does not use the most recent Results-Based Standard template.
PER-003-1, R3. | PER-003-1 | R3. | R3. Each Balancing Authority shall staff its Real-time operating positions performing Balancing Authority reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates (1) : [Risk Factor: High][Time Horizon: Real-time Operations]: 3.1. Areas of Competency 3.1.1. Resources and demand balancing 3.1.2. Emergency preparedness and operations 3.1.3. System operations 3.1.4. Interchange scheduling and coordination 3.2. Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Balancing and Interchange Operator | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Standard does not use the most recent Results-Based Standard template.
PER-004-2, R1. | PER-004-2 | R1. | R1. Each Reliability Coordinator shall be staffed with adequately trained and NERC-certified Reliability Coordinator operators, 24 hours per day, seven days per week. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | Yes |  |  | No | Yes | Yes | No | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 10 | Requirement could be incorporated into the IRO Standards. Remove the 'adequately trained' phrase, as this covered by PER-005 Systematic Approach to Training, Standards lacks associated Measures (Standard does not use the most recent Results-Based Standard template.).
PER-004-2, R2. | PER-004-2 | R2. | R2. Reliability Coordinator operating personnel shall place particular attention on SOLs and IROLs and inter-tie facility limits. The Reliability Coordinator shall ensure protocols are in place to allow Reliability Coordinator operating personnel to have the best available information at all times. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] |  | Yes | [17 empty] | 3 | 12 | Requirement 2 will be retired when PER-005-1 Requirement 3 becomes effective on July 1, 2016.
PRC-004-5(i), R1. | PRC-004-5(i) | R1. | R1. Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] 1.1 The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and 1.2 The BES interrupting device owner owns all or part of the Composite Protection System; and 1.3 The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | Yes |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | Standard no longer has a reporting requirement to require notification to the Regional Entities of mis-operations. Currently relying on Section 1600 Data Request which is not enforcable on Canadian and Mexican entities. Enforcement date of 4/2/2017 should this be graded? Also the reporting requirment -is to whom? The misoperations are being reported to the Regions currently and NERC is installing the MIDAS system but there is no specific requirement. Data is envisioned to be collected using the Data 1600 Data Request of the NERC ROP.
PRC-004-5(i), R2. | PRC-004-5(i) | R2. | R2. Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] 2.1 For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: 2.1.1 The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and 2.1.2 The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and 2.1.3 The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. 2.2 For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Is the 120 day reporting period appropriate? Consider reducing the number of days for time requirement.
PRC-004-5(i), R3. | PRC-004-5(i) | R3. | R3. Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 11 | Recommend revising requirement to clarify timeframes.
PRC-004-5(i), R4. | PRC-004-5(i) | R4. | R4. Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: [Violation Risk Factor: High] [Time Horizon: Operations Assessment, Operations Planning] • The identification of the cause(s) of the Misoperation; or • A declaration that no cause was identified. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-004-5(i), R5. | PRC-004-5(i) | R5. | R5. Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: [Violation Risk Factor: High] [Time Horizon: Operations Planning, Long-Term Planning] • Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or • Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-004-5(i), R6. | PRC-004-5(i) | R6. | R6. Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. [Violation Risk Factor: High][Time Horizon: Operations Planning, Long-Term Planning] | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-005-6, R1. | PRC-005-6 | R1. | R1. Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems, Automatic Reclosing, and Sudden Pressure Relaying identified in Section 4.2, Facilities. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] The PSMP shall: 1.1. Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. 1.2. Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-3, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. | Yes |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | Applying PRC-005-6 maintenance requirements to limited impact RAS (as defined by PRC-012-2) protection system components is not needed because their Misoperations have limited impact by definition. Pending FERC approval of PRC-012-2, PRC-005-6 should be revised to exclude the standard's applicability to limited impact RAS protection system components. .Also while performing routine maintenance on sudden pressure relays that trip may reduce misoperations, members removing sudden pressure relay trips may result in reduction in fault detecting capability of the composite transformer protection. In addition, misoperations of sudden pressure relays are not reportable per Section 1600 Misoperation Data Request, and thus there will be no visibility to provide evidence that increased maintenance requirements are providing reliability benefits.
PRC-005-6, R2. | PRC-005-6 | R2. | R2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-005-6, R3. | PRC-005-6 | R3. | R3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-3, and Table 5. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-005-6, R4. | PRC-005-6 | R4. | R4. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the performance-based program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-005-6, R5. | PRC-005-6 | R5. | R5. Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-006-2 , R1. | PRC-006-2 | R1. | R1. Each Planning Coordinator shall develop and document criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES), including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-006-2 , R2. | PRC-006-2 | R2. | R2. Each Planning Coordinator shall identify one or more islands to serve as a basis for designing its UFLS program including: [VRF: Medium][Time Horizon: Long-term Planning] 2.1. Those islands selected by applying the criteria in Requirement R1, and 2.2. Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and 2.3. A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. | Yes |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | Yes | Yes | Yes | 2 | 11 | Requirement 2.3 mentions 'mutual consent' but it is unclear which parties must demonstrate 'consent'. The current RSAW indicates consent is between the PC and the ajoining Regional Entity.
PRC-006-2 , R3. | PRC-006-2 | R3. | R3. Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). [VRF: High][Time Horizon: Long-term Planning] 3.1. Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and 3.2. Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and 3.3. Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: • Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES • Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES • Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-006-2 , R4. | PRC-006-2 | R4. | R4. Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2. The simulation shall model each of the following: [VRF: High][Time Horizon: Long-term Planning] 4.1. Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. 4.2. Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. 4.3. Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. 4.4. Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. 4.5. Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. 4.6. Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. 4.7. Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-006-2 , R5. | PRC-006-2 | R5. | R5. Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall coordinate its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island through one of the following: [VRF: High][Time Horizon: Long-term Planning] • Develop a common UFLS program design and schedule for implementation per Requirement R3 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct a joint UFLS design assessment per Requirement R4 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct an independent UFLS design assessment per Requirement R4 for the identified island, and in the event the UFLS design assessment fails to meet Requirement R3, identify modifications to the UFLS program(s) to meet Requirement R3 and report these modifications as recommendations to the other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island and the ERO. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-006-2 , R6. | PRC-006-2 | R6. | R6. Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-006-2 , R7. | PRC-006-2 | R7. | R7. Each Planning Coordinator shall provide its UFLS database containing data necessary to model its UFLS program to other Planning Coordinators within its Interconnection within 30 calendar days of a request. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-006-2 , R8. | PRC-006-2 | R8. | R8. Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 11 | Inconsistent use of 'UFLS Entity' in M8-“the “e” in entity is capitalized in the measure and it is not capitalized in the requirement” The UFLS entity's may not know who their PC is n in some regions so there could be some opportunity for PCs to coordinate this data to ensure all that need the data have it.
PRC-006-2 , R9. | PRC-006-2 | R9. | R9. Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 11 | Inconsistent use of 'UFLS Entity' in M9-“the “e” in entity is capitalized in the measure and it is not capitalized in the requirement”The UFLS entity's may not know who their PC is n in some regions so there could be some opportunity for PCs to coordinate this data to ensure all that need the data have it.
PRC-006-2 , R10. | PRC-006-2 | R10. | R10. Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-006-2 , R11. | PRC-006-2 | R11. | R11. Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall conduct and document an assessment of the event within one year of event actuation to evaluate: [VRF: Medium][Time Horizon: Operations Assessment] 11.1. The performance of the UFLS equipment, 11.2. The effectiveness of the UFLS program. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-006-2 , R12. | PRC-006-2 | R12. | R12. Each Planning Coordinator, in whose islanding event assessment (per R11) UFLS program deficiencies are identified, shall conduct and document a UFLS design assessment to consider the identified deficiencies within two years of event actuation. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-006-2 , R13. | PRC-006-2 | R13. | R13. Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall coordinate its event assessment (in accordance with Requirement R11) with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event through one of the following: [VRF: Medium][Time Horizon: Operations Assessment] • Conduct a joint event assessment per Requirement R11 among the Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 that reaches conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 and where the assessment fails to reach conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, identify differences in the assessments that likely resulted in the differences in the conclusions and recommendations and report these differences to the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event and the ERO. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-010-2, R1. | PRC-010-2 | R1. | R1. Each Planning Coordinator or Transmission Planner that is developing a UVLS Program shall evaluate its effectiveness and subsequently provide the UVLS Program’s specifications and implementation schedule to the UVLS entities responsible for implementing the UVLS Program. The evaluation shall include, but is not limited to, studies and analyses that show: [Violation Risk Factor: High] [Time Horizon: Long‐term Planning] 1.1. The implementation of the UVLS Program resolves the identified undervoltage issues that led to its development and design. 1.2. The UVLS Program is integrated through coordination with generator voltage ride‐through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage‐based load shedding programs. | Yes |  |  | No | No | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 12 | In general, the PRC Standards that identify the 'PC' or the 'TP' tend to cause confusion on who the actual responsible entity is.
PRC-010-2, R2. | PRC-010-2 | R2. | R2. Each UVLS entity shall adhere to the UVLS Program specifications and implementation schedule determined by its Planning Coordinator or Transmission Planner associated with UVLS Program development per Requirement R1 or with any Corrective Action Plans per Requirement R5. [Violation Risk Factor: High] [Time Horizon: Long‐term Planning] | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | No | 3 | 11 | R2 does not facilitate input from the UVLS entities in the development of the implementation schedule yet the UVLS entities have the compliance burden. The implementation plan is dictated by Planning Coordinators or Transmission Planners and must be adhered to by the UVLS entities. This is not always practical as the planning groups may not have information and experience necessary to develop a realistic implementation timeframe. The UFLS entity's may not know who their PC is n in some regions so there could be some opportunity for PCs to coordinate this data to ensure all that need the data have it.
PRC-010-2, R3. | PRC-010-2 | R3. | R3. Each Planning Coordinator or Transmission Planner shall perform a comprehensive assessment to evaluate the effectiveness of each of its UVLS Programs at least once every 60 calendar months. Each assessment shall include, but is not limited to, studies and analyses that evaluate whether: [Violation Risk Factor: Medium] [Time Horizon: Long‐term Planning] 3.1. The UVLS Program resolves the identified undervoltage issues for which the UVLS Program is designed. 3.2. The UVLS Program is integrated through coordination with generator voltage ride‐through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage‐based load shedding programs. | Yes |  |  | No | No | Yes | Yes | Yes | Yes | Yes | Yes |  | No | Yes | Yes | Yes | No | No | Yes | 1 | 9 | In general, the PRC Standards that identify the 'PC' or the 'TP' tend to cause confusion on who the actual responsible entity is.
PRC-010-2, R4. | PRC-010-2 | R4. | R4. Each Planning Coordinator or Transmission Planner shall, within 12 calendar months of an event that resulted in a voltage excursion for which its UVLS Program was designed to operate, perform an assessment to evaluate: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] 4.1. Whether its UVLS Program resolved the undervoltage issues associated with the event, and 4.2. The performance (i.e., operation and non-operation) of the UVLS Program equipment. | Yes |  |  | No | No | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 12 | In general, the PRC Standards that identify the 'PC' or the 'TP' tend to cause confusion on who the actual responsible entity is.
PRC-010-2, R5. | PRC-010-2 | R5. | R5. Each Planning Coordinator or Transmission Planner that identifies deficiencies during an assessment performed in either Requirement R3 or R4 shall develop a Corrective Action Plan to address the deficiencies and subsequently provide the Corrective Action Plan, including an implementation schedule, to UVLS entities within three calendar months of completing the assessment. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | Yes |  |  | No | No | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 12 | In general, the PRC Standards that identify the 'PC' or the 'TP' tend to cause confusion on who the actual responsible entity is.
PRC-010-2, R6. | PRC-010-2 | R6. | R6. Each Planning Coordinator that has a UVLS Program in its area shall update a database containing data necessary to model the UVLS Program(s) in its area for use in event analyses and assessments of the UVLS Program at least once each calendar year. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-010-2, R7. | PRC-010-2 | R7. | R7. Each UVLS entity shall provide data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of a UVLS Program database. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-010-2, R8. | PRC-010-2 | R8. | R8. Each Planning Coordinator that has a UVLS Program in its area shall provide its UVLS Program database to other Planning Coordinators and Transmission Planners within its Interconnection, and other functional entities with a reliability need, within 30 calendar days of a written request. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
PRC-018-1, R1. | PRC-018-1 | R1. | R1. Each Transmission Owner and Generator Owner required to install DMEs by its Regional Reliability Organization (reliability standard PRC-002 Requirements 1-3) shall have DMEs installed that meet the following requirements: R1.1. Internal Clocks in DME devices shall be synchronized to within 2 milliseconds or less of Universal Coordinated Time scale (UTC) R1.2. Recorded data from each Disturbance shall be retrievable for ten calendar days.. | [19 empty] | 3 | 12 | PRC-018-1 Is scheduled to be retired midnight of the day immediately prior to six (6) years after the effective date of the approved PRC-002-2 in the particular jurisdiction in which the new standard is becoming effective. No need to review this standard.
PRC-018-1, R2. | PRC-018-1 | R2. | R2. The Transmission Owner and Generator Owner shall each install DMEs in accordance with its Regional Reliability Organization’s installation requirements (reliability standard PRC-002 Requirements 1 through 3). | [19 empty] | 3 | 12 | PRC-018-1 Is scheduled to be retired midnight of the day immediately prior to six (6) years after the effective date of the approved PRC-002-2 in the particular jurisdiction in which the new standard is becoming effective. No need to review this standard.
PRC-018-1, R3. | PRC-018-1 | R3. | R3. The Transmission Owner and Generator Owner shall each maintain, and report to its Regional Reliability Organization on request, the following data on the DMEs installed to meet that region’s installation requirements (reliability standard PRC-002 Requirements1.1, 2.1 and 3.1): R3.1. Type of DME (sequence of event recorder, fault recorder, or dynamic disturbance recorder). R3.2. Make and model of equipment. R3.3. Installation location. R3.4. Operational status. R3.5. Date last tested. R3.6. Monitored elements, such as transmission circuit, bus section, etc. R3.7. Monitored devices, such as circuit breaker, disconnect status, alarms, etc. R3.8. Monitored electrical quantities, such as voltage, current, etc. |  | Yes | [17 empty] | 3 | 12 | PRC-018-1 Is scheduled to be retired midnight of the day immediately prior to six (6) years after the effective date of the approved PRC-002-2 in the particular jurisdiction in which the new standard is becoming effective. No need to review this standard.
PRC-018-1, R4. | PRC-018-1 | R4. | R4. The Transmission Owner and Generator Owner shall each provide Disturbance data (recorded by DMEs) in accordance with its Regional Reliability Organization’s requirements (reliability standard PRC-002 Requirement 4). | [19 empty] | 3 | 12 | PRC-018 will be retired in the evening before July 1, 2016. Replaced by requirements in PRC-002-2 Disturbance Monitoring
PRC-018-1, R5. | PRC-018-1 | R5. | R5. The Transmission Owner and Generator Owner shall each archive all data recorded by DMEs for Regional Reliability Organization-identified events for at least three years. | [19 empty] | 3 | 12 | PRC-018 will be retired in the evening before July 1, 2016. Replaced by requirements in PRC-002-2 Disturbance Monitoring
PRC-018-1, R6. | PRC-018-1 | R6. | R6. Each Transmission Owner and Generator Owner that is required by its Regional Reliability Organization to have DMEs shall have a maintenance and testing program for those DMEs that includes: R6.1. Maintenance and testing intervals and their basis. R6.2. Summary of maintenance and testing procedures. | [19 empty] | 3 | 12 | PRC-018 will be retired in the evening before July 1, 2016. Replaced by requirements in PRC-002-2 Disturbance Monitoring
PRC-019-2, R1. | PRC-019-2 | R1. | R1. At a maximum of every five calendar years, each Generator Owner and Transmission Owner with applicable Facilities shall coordinate the voltage regulating system controls, (including in-service limiters and protection functions) with the applicable equipment capabilities and settings of the applicable Protection System devices and functions. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] 1.1. Assuming the normal automatic voltage regulator control loop and steady-state system operating conditions, verify the following coordination items for each applicable Facility: 1.1.1. The in-service limiters are set to operate before the Protection System of the applicable Facility in order to avoid disconnecting the generator unnecessarily. 1.1.2. The applicable in-service Protection System devices are set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Standard does not use the most recent Results-Based Standard template.
PRC-019-2, R2. | PRC-019-2 | R2. | R2. Within 90 calendar days following the identification or implementation of systems, equipment or setting changes that will affect the coordination described in Requirement R1, each Generator Owner and Transmission Owner with applicable Facilities shall perform the coordination as described in Requirement R1. These possible systems, equipment or settings changes include, but are not limited to the following [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning]: • Voltage regulating settings or equipment changes; • Protection System settings or component changes; • Generating or synchronous condenser equipment capability changes; or • Generator or synchronous condenser step-up transformer changes. | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Standard does not use the most recent Results-Based Standard template.
PRC-023-4, R1. | PRC-023-4 | R1. | R1. Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees (see Standard for criteria). | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | No | Yes | Yes | No | Yes | Yes | Yes | 3 | 9 | Review terms 'transmission' and 'faults' for verification of correct usage. Defined terms in the Glossary. Standard does not use the most recent Results-Based Standard template. Under Applicability, Section 4.2-Circuits Subject to Requirements, additional language should be added to clarify that the standard ONLY applies to BES elements. Attachement B - "Circuits to Evaluate" should only be BES elements. Some entities including auditors misinterpreted the standard to apply to all elements 100 kV and above. Some entities have classified elements connected 100 kV and above as non-BES, and as written the standard also would apply to these non-BES elements.
PRC-023-4, R2. | PRC-023-4 | R2. | R2. Each Transmission Owner, Generator Owner, and Distribution Provider shall set its out-of-step blocking elements to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | Maybe |  |  | No | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | No | Yes | No | Yes | Yes | No | 2 | 9 | OOS blocking schemes will never impact the loadability of a transmission element, since they are just that, systems that block tripping. PRC-026 is a standard governing relay performance during STABLE swings. OOS blocking elements are a basic tool in avoiding operation on stable swings. Stable swinging systems are a bit of an oxymoron, they have the ability to go unstable, and they occur at times when faults are more likely than normal. Anyone using OOS blocking elements has the responsibility to ensure they will operate for faults. This has absolutely nothing to do with loadability. A standard promoting the use of these elements for any reason is the place where reliability of fault clearing when these elements are deployed needs to address this. PRC-026-1 is the proper location, and it is important that it be addressed there. Standard does not use the most recent Results-Based Standard template.
PRC-023-4, R3. | PRC-023-4 | R3. | R3. Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning] | Yes |  |  | No | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | Standard does not use the most recent Results-Based Standard template. The UFLS entity's may not know who their PC is n in some regions so there could be some opportunity for PCs to coordinate this data to ensure all that need the data have it.
PRC-023-4, R4. | PRC-023-4 | R4. | R4. Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | Yes |  |  | No | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | No | Yes | Yes |  | 2 | 10 | Review the term 'transmission' for verification of correct usage. Defined terms in the Glossary. Standard does not use the most recent Results-Based Standard template. The UFLS entity's may not know who their PC is n in some regions so there could be some opportunity for PCs to coordinate this data to ensure all that need the data have it.
PRC-023-4, R5. | PRC-023-4 | R5. | R5. Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that have protective relay settings that limit circuit capability. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Review the term 'transmission' for verification of correct usage. Defined terms in the Glossary. Potentially R5 could be a P81 requirement. NERC Legal should verify if this requirement is in response to a FERC Directive. If this data for list, a ROP Section 1600 Data Request would be appropriate. Standard does not use the most recent Results-Based Standard template.
PRC-023-4, R6. | PRC-023-4 | R6. | R6. Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in PRC-023-4, Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5. The Planning Coordinator shall: [Violation Risk Factor: High] [Time Horizon: Long Term Planning] 6.1 Maintain a list of circuits subject to PRC-023-4 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023-4, Attachment B applies. 6.2 Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Potentially 6.1 and 6.2 could be P81 requirements. NERC Legal should verify if this requirement is in response to a FERC Directive. If this data for list, a ROP Section 1600 Data Request would be appropriate. Standard does not use the most recent Results-Based Standard template.
PRC-024-2, R1. | PRC-024-2 | R1. | R1. Each Generator Owner that has generator frequency protective relaying activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1, subject to the following exceptions: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] • Generating unit(s) may trip if the protective functions (such as out-of-step functions or loss-of-field functions) operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 1 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Standard does not use the most recent Results-Based Standard template.
PRC-024-2, R2. | PRC-024-2 | R2. | R2. Each Generator Owner that has generator voltage protective relaying1 activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating unit(s) as a result of a voltage excursion (at the point of interconnection ) caused by an event on the transmission system external to the generating plant that remains within the “no trip zone” of PRC-024 Attachment 2. If the Transmission Planner allows less stringent voltage relay settings than those required to meet PRC-024 Attachment 2, then the Generator Owner shall set its protective relaying within the voltage recovery characteristics of a location-specific Transmission Planner’s study. Requirement R2 is subject to the following exceptions: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] • Generating unit(s) may trip in accordance with a Special Protection System (SPS) or Remedial Action Scheme (RAS). • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip by action of protective functions (such as out-of-step functions or loss-of-field functions) that operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 2 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Standard does not use the most recent Results-Based Standard template.
PRC-024-2, R3. | PRC-024-2 | R3. | R3. Each Generator Owner shall document each known regulatory or equipment limitation that prevents an applicable generating unit with generator frequency or voltage protective relays from meeting the relay setting criteria in Requirements R1 or R2 including (but not limited to) study results, experience from an actual event, or manufacturer’s advice. [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] 3.1. The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following: • Identification of a regulatory or equipment limitation. • Repair of the equipment causing the limitation that removes the limitation. • Replacement of the equipment causing the limitation with equipment that removes the limitation. • Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. | Yes |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes |  | 3 | 10 | R3 is a requirement to address non-compliance with R1 & R2. Recommend R3 be combined with R1 & R2 to support documentation justifying potential non-compliance with R1 and/or R2. Standard does not use the most recent Results-Based Standard template.
PRC-024-2, R4. | PRC-024-2 | R4. | R4. Each Generator Owner shall provide its applicable generator protection trip settings associated with Requirements R1 and R2 to the Planning Coordinator or Transmission Planner that models the associated unit within 60 calendar days of receipt of a written request for the data and within 60 calendar days of any change to those previously requested trip settings unless directed by the requesting Planning Coordinator or Transmission Planner that the reporting of relay setting changes is not required. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | Yes | Yes |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Requirement is duplicative in nature, as this data will be captured by MOD-032-1. SStandard does not use the most recent Results-Based Standard template.
PRC-025-1, R1. | PRC-025-1 | R1. | R1. Each Generator Owner, Transmission Owner, and Distribution Provider shall apply settings that are in accordance with PRC-025-1 – Attachment 1: Relay Settings, on each load-responsive protective relay while maintaining reliable fault protection. | Yes |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | No | Yes | Yes | No | Yes | Yes | 2 | 10 | It may not feasible to perform testing of this standard at .85 pu at generating station radially connected to a load center via a transmission topology with high Source Impedance Ratio (TBD) because doing so would result in unsustainable system voltage much lower than .85 pu. Also, the standard does not address manufacture ratings on equipment that may be more restrictive and affect the ability to comply with the standard
PRC-026-1, R1. | PRC-026-1 | R1. | R1. Each Planning Coordinator shall, at least once each calendar year, provide notification of each generator, transformer, and transmission line BES Element in its area that meets one or more of the following criteria, if any, to the respective Generator Owner and Transmission Owner: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] Criteria: 1. Generator(s) where an angular stability constraint exists that is addressed by a System Operating Limit (SOL) or a Remedial Action Scheme (RAS) and those Elements terminating at the Transmission station associated with the generator(s). 2. An Element that is monitored as part of an SOL identified by the Planning Coordinator’s methodology based on an angular stability constraint. 3. An Element that forms the boundary of an island in the most recent underfrequency load shedding (UFLS) design assessment based on application of the Planning Coordinator’s criteria for identifying islands, only if the island is formed by tripping the Element due to angular instability. 4. An Element identified in the most recent annual Planning Assessment where relay tripping occurs due to a stable or unstable power swing during a simulated disturbance. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 11 | Review the term 'transmission' for verification of correct usage. Defined terms in the Glossary. Enforcement Date of 1/1/2018, should we be grading this?
PRC-026-1, R2. | PRC-026-1 | R2. | R2. Each Generator Owner and Transmission Owner shall: [Violation Risk Factor: High] [Time Horizon: Operations Planning] 2.1 Within 12 full calendar months of notification of a BES Element pursuant to Requirement R1, determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B where an evaluation of that Element’s load-responsive protective relay(s) based on PRC-026-1 – Attachment B criteria has not been performed in the last five calendar years. 2.2 Within 12 full calendar months of becoming aware of a generator, transformer, or transmission line BES Element that tripped in response to a stable or unstable power swing due to the operation of its protective relay(s), determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 11 | Review the term 'transmission' for verification of correct usage. Defined terms in the Glossary.
PRC-026-1, R3. | PRC-026-1 | R3. | R3. Each Generator Owner and Transmission Owner shall, within six full calendar months of determining a load-responsive protective relay does not meet the PRC-026-1 – Attachment B criteria pursuant to Requirement R2, develop a Corrective Action Plan (CAP) to meet one of the following: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] • The Protection System meets the PRC-026-1 – Attachment B criteria, while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element); or • The Protection System is excluded under the PRC-026-1 – Attachment A criteria (e.g., modifying the Protection System so that relay functions are supervised by power swing blocking or using relay systems that are immune to power swings), while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element). | Yes |  |  | No | Yes | No | Yes | Yes | Yes | No | Yes |  | Yes | Yes | No | No | Yes | Yes | Yes | 1 | 9 | Review the term 'fault' for verification of correct usage. Defined terms in the Glossary. Consider requiring the GO and TO to provide a copy of the CAP to the PC.
PRC-026-1, R4. | PRC-026-1 | R4. | R4. Each Generator Owner and Transmission Owner shall implement each CAP developed pursuant to Requirement R3 and update each CAP if actions or timetables change until all actions are complete. [Violation Risk Factor: Medium][Time Horizon: Long-Term Planning] | Yes |  |  | No | Yes | No | Yes | Yes | Yes | No | Yes |  | Yes | Yes | No | Yes | Yes | Yes | Yes | 1 | 10 | Consider requiring the GO and TO to provide a copy of the revised CAP to the PC.
VAR-001-4.1, R1. | VAR-001-4.1 | R1. | R1. Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. [Violation Risk Factor: High] [Time Horizon: Operational Planning] 1.1. Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. | Yes |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Consider making R1.1 a stand alone/separate requirement.
VAR-001-4.1, R2. | VAR-001-4.1 | R2. | R2. Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 11 | Consider removal of the term 'sufficeint' from the requirement to improve clarity of the requirement.
VAR-001-4.1, R3. | VAR-001-4.1 | R3. | R3. Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 11 | Review the term 'transmission' for verification of correct usage. Defined terms in the Glossary.
VAR-001-4.1, R4. | VAR-001-4.1 | R4. | R4. The Transmission Operator shall specify the criteria that will exempt generators from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] 4.1 If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. | Yes |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes |  | Yes | Yes | No | Yes | Yes | Yes |  | 3 | 9 | Suggest combining R4 and R4.1 into a single requirement. Suggest establishing a timeframe associated with the notification.
VAR-001-4.1, R5. | VAR-001-4.1 | R5. | R5. Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] 5.1. The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). 5.2. The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). 5.3. The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
VAR-001-4.1, R6. | VAR-001-4.1 | R6. | R6. After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. | Yes |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes |  | 2 | 12 | Consider establishing a timeframe after cosolitation with GO, that TOP provides documentation.
VAR-002-4, R1. | VAR-002-4 | R1. | R1. The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] • That the generator is being operated in start-up,1 shutdown,2 or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes |  | Yes | No | Yes | Yes | Yes | No | Yes | 3 | 9 | Second bullet in R1 provides a provision for a generator AVR to be operated in other than the directed mode of operation by the TOP. What is the technical basis and under what conditions would this apply? And is this potentially a detriment to reliability? The phrase 'connected to the interconnected transmission system' should be reviewed based on the revised BES defintion to ensure the appropriate applicability for the Standard.
VAR-002-4, R2. | VAR-002-4 | R2. | R2. Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule3 (within each generating Facility’s capabilities4) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] 2.1. When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. 2.2. When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. 2.3. Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
VAR-002-4, R3. | VAR-002-4 | R3. | R3. Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
VAR-002-4, R4. | VAR-002-4 | R4. | R4. Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] • Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. | Yes |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Consider combining bulleted provision with the parent requirement (R4) or identify the Disperesed Generation Resources in the Applicability for specific applicable requirements.
VAR-002-4, R5. | VAR-002-4 | R5. | R5. The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. [Violation Risk Factor: Lower] [Time Horizon: Real-time Operations] 5.1. For generator step-up and auxiliary transformers5 with primary voltages equal to or greater than the generator terminal voltage: 5.1.1. Tap settings. 5.1.2. Available fixed tap ranges. 5.1.3. Impedance data. | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12
VAR-002-4, R6. | VAR-002-4 | R6. | R6. After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. [Violation Risk Factor: Lower] [Time Horizon: Real-time Operations] 6.1. If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. | Yes |  |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Consider combining R6.1 into the parent requirement (R6).

## NERC
| Standard Number | Requirement Number | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Previously Graded Standard (From 2013 Grading) | Requirement Text Change? (From 2013 Grading) | Supports a Reliability Objective (as defined by the Reliability Principles) (Yes/No/Maybe) | Meets the Paragraph 81 criteria? (Mark only if Yes) | Appropriate as a guide rather than a standard? (Mark only if Yes) | C1 | C2 | C3 | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | Q9 | Q10 | Q11 | Q12 | Q13 | Content Score 0-3 | Quality Score 0-13 | Comment/Rationale
[9 empty] | Is the content of the requirement technically correct, including identifying who does what and when? | Are the correct functional entities identified? | Are the appropriate actions, for which there should be accountability, included or is there a gap? | Should the requirement stand alone as is or should it be consolidated with other standards? | Is it drafted as a results-based standard (RBS) requirement (performance, risk (prevention) or capability) and does it follow the RBS format (e.g., sub-requirement structure)? | Is it technologically neutral? | Are the expectations for each function clear? | Does the requirement align with the purpose? | Is it a higher solution than the lowest common denominator? | Is it measureable? | Does it have a technical basis in engineering and operations? | Is it complete and self-contained? | Is the language clear and does not contain ambiguous or outdated terms? | Can it be practically implemented? | Does it use consistent terminology? | Is the Standard cost effective in achieving the reliability purpose or objective of the Standard and mitigating the risk to the BES?
BAL-001-2 , R1 | BAL-001-2 | R1 | R1. The Responsible Entity shall operate such that the Control Performance Standard 1 (CPS1), calculated in accordance with Attachment 1, is greater than or equal to 100 percent for the applicable Interconnection in which it operates for each preceding 12 consecutive calendar month period, evaluated monthly. | BAL-001-1 | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 1
BAL-001-2 , R2 | BAL-001-2 | R2 | R2. Each Balancing Authority shall operate such that its clock-minute average of Reporting ACE does not exceed its clock-minute Balancing Authority ACE Limit (BAAL) for more than 30 consecutive clock-minutes, calculated in accordance with Attachment 2, for the applicable Interconnection in which the Balancing Authority operates.[Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | BAL-001-1 | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | 3 | 10 |  | 2
EOP-010-1, R1 | EOP-010-1 | R1 | R1. Each Reliability Coordinator shall develop, maintain, and implement a GMD Operating Plan that coordinates GMD Operating Procedures or Operating Processes within its Reliability Coordinator Area. At a minimum, the GMD Operating Plan shall include: 1.1 A description of activities designed to mitigate the effects of GMD events on the reliable operation of the interconnected transmission system within the Reliability Coordinator Area. 1.2 A process for the Reliability Coordinator to review the GMD Operating Procedures or Operating Processes of Transmission Operators within its Reliability Coordinator Area. | No | N/A |  |  |  | YES | YES | YES | YES |  | YES | YES | YES |  | YES | YES | YES | YES | YES | YES | YES | 3 | 12 |  | 3
EOP-010-1, R2 | EOP-010-1 | R2 | R2. Each Reliability Coordinator shall disseminate forecasted and current space weather information to functional entities identified as recipients in the Reliability Coordinator's GMD Operating Plan. | No | N/A |  |  |  | YES | YES | YES | YES |  | YES | YES | YES |  | YES | YES | YES | NO | YES | YES | YES | 3 | 11 |  | 4
EOP-010-1, R3. | EOP-010-1 | R3. | R3. Each Transmission Operator shall develop, maintain, and implement a GMD Operating Procedure or Operating Process to mitigate the effects of GMD events on the reliable operation of its respective system. At a minimum, the Operating Procedure or Operating Process shall include: 3.1. Steps or tasks to receive space weather information. 3.2. System Operator actions to be initiated based on predetermined conditions. 3.3. The conditions for terminating the Operating Procedure or Operating Process. | No | N/A |  |  |  | YES | YES | YES | YES |  | YES | YES | YES |  | YES | YES | YES | YES | YES | YES | YES | 3 | 11 |  | 5
EOP-011-1, R1. | EOP-011-1 | R1. | R1. Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] 1.1. Roles and responsibilities for activating the Operating Plan(s); 1.2. Processes to prepare for and mitigate Emergencies including: 1.2.1. Notification to its Reliability Coordinator, to include current and projected conditions, when experiencing an operating Emergency; 1.2.2. Cancellation or recall of Transmission and generation outages; 1.2.3. Transmission system reconfiguration; 1.2.4. Redispatch of generation request; 1.2.5. Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and 1.2.6. Reliability impacts of extreme weather conditions. | EOP-011-1 Merged EOP-0003, EOP-004, and EOP-005 |  | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | 3 | 11 |  | 6
EOP-011-1, R2. | EOP-011-1 | R2. | R2. Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: [Violation Risk Factor: High] [Time Horizon: Real-Time Operations, Operations Planning, Long-term Planning] 2.1. Roles and responsibilities for activating the Operating Plan(s); 2.2. Processes to prepare for and mitigate Emergencies including: 2.2.1. Notification to its Reliability Coordinator, to include current and projected conditions when experiencing a Capacity Emergency or Energy Emergency; 2.2.2. Requesting an Energy Emergency Alert, per Attachment 1; 2.2.3. Managing generating resources in its Balancing Authority Area to address: 2.2.3.1. capability and availability; 2.2.3.2. fuel supply and inventory concerns; 2.2.3.3. fuel switching capabilities; and 2.2.3.4. environmental constraints. 2.2.4. Public appeals for voluntary Load reductions; 2.2.5. Requests to government agencies to implement their programs to achieve necessary energy reductions; 2.2.6. Reduction of internal utility energy use; 2.2.7. Use of Interruptible Load, curtailable Load and demand response; 2.2.8. Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and 2.2.9. Reliability impacts of extreme weather conditions. | EOP-011-1 Merged EOP-0003, EOP-004, and EOP-005 |  | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 12 |  | 7
EOP-011-1, R3. | EOP-011-1 | R3. | R3. The Reliability Coordinator shall review the Operating Plan(s) to mitigate operating Emergencies submitted by a Transmission Operator or a Balancing Authority regarding any reliability risks that are identified between Operating Plans. [Violation Risk Factor: High] [Time Horizon: Operations Planning] 3.1. Within 30 calendar days of receipt, the Reliability Coordinator shall: 3.1.1. Review each submitted Operating Plan(s) on the basis of compatibility and inter-dependency with other Balancing Authorities’ and Transmission Operators’ Operating Plans; 3.1.2. Review each submitted Operating Plan(s) for coordination to avoid risk to Wide Area reliability; and 3.1.3. Notify each Balancing Authority and Transmission Operator of the results of its review, specifying any time frame for resubmittal of its Operating Plan(s) if revisions are identified. | EOP-011-1 Merged EOP-0003, EOP-004, and EOP-005 |  | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | YES | 3 | 10 |  | 8
EOP-011-1, R4. | EOP-011-1 | R4. | R4. Each Transmission Operator and Balancing Authority shall address any reliability risks identified by its Reliability Coordinator pursuant to Requirement R3 and resubmit its Operating Plan(s) to its Reliability Coordinator within a time period specified by its Reliability Coordinator. | EOP-011-1 Merged EOP-0003, EOP-004, and EOP-005 |  | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | YES | 3 | 10 |  | 9
EOP-011-1, R5. | EOP-011-1 | R5. | R5. Each Reliability Coordinator that receives an Emergency notification from a Transmission Operator or Balancing Authority within its Reliability Coordinator Area shall notify, within 30 minutes from the time of receiving notification, other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators. [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | EOP-011-1 Merged EOP-0003, EOP-004, and EOP-005 |  | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 10
EOP-011-1, R6. | EOP-011-1 | R6. | R6. Each Reliability Coordinator that has a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area shall declare an Energy Emergency Alert, as detailed in Attachment 1. [Violation Risk Factor: High] [Time Horizon: Real-Time Operations] | EOP-011-1 Merged EOP-0003, EOP-004, and EOP-005 |  | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | YES | 3 | 10 |  | 11
FAC-008-3, R1 | FAC-008-3 | R1 | R1. Each Generator Owner shall have documentation for determining the Facility Ratings of its solely and jointly owned generator Facility(ies) up to the low side terminals of the main step up transformer if the Generator Owner does not own the main step up transformer and the high side terminals of the main step up transformer if the Generator Owner owns the main step up transformer. 1.1. The documentation shall contain assumptions used to rate the generator and at least one of the following: • Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis. • Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. 1.2. The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | FAC-008-3 | NO | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | 3 | 9 |  | 12
FAC-008-3, R2. | FAC-008-3 | R2. | Each Generator Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned equipment connected between the location specified in R1 and the point of interconnection with the Transmission Owner that contains all of the following. 1.1. The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. 1.2. The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: 1.2.1. Equipment Rating standard(s) used in development of this methodology. 1.2.2. Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. 1.2.3. Ambient conditions (for particular or average conditions or as they vary in real-time). 1.2.4. Operating limitations. 1.3. A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. 1.4. The process by which the Rating of equipment that comprises a Facility is determined. 1.4.1. The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. 1.4.2. The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | FAC-008-3 | NO | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 13
FAC-008-3, R3. | FAC-008-3 | R3. | R3. Each Transmission Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned Facilities (except for those generating unit Facilities addressed in R1 and R2) that contains all of the following: [Violation Risk Factor: Medium] [ Time Horizon: Long-term Planning] 3.1. The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. 3.2. The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: 3.2.1. Equipment Rating standard(s) used in development of this methodology. 3.2.2. Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. 3.2.3. Ambient conditions (for particular or average conditions or as they vary in real-time). 3.2.4. Operating limitations. 3.3. A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. 3.4. The process by which the Rating of equipment that comprises a Facility is determined. 3.4.1. The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. 3.4.2. The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | FAC-008-3 | NO | Yes - #3 | No |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 14
FAC-008-3, R4. | FAC-008-3 | R4. | R4. Each Transmission Owner shall make its Facility Ratings methodology and each Generator Owner shall each make its documentation for determining its Facility Ratings and its Facility Ratings methodology available for inspection and technical review by those Reliability Coordinators, Transmission Operators, Transmission Planners and Planning Coordinators that have responsibility for the area in which the associated Facilities are located, within 21 calendar days of receipt of a request. (Retirement approved by FERC effective January 21, 2014.) | FAC-008-3 | NO | No | Yes - Para 81 Phase 1 |  | Q4: No; Q13: Yes | 3 | 11 |  | 15
FAC-008-3, R5. | FAC-008-3 | R5. | R5. If a Reliability Coordinator, Transmission Operator, Transmission Planner or Planning Coordinator provides documented comments on its technical review of a Transmission Owner’s Facility Ratings methodology or Generator Owner’s documentation for determining its Facility Ratings and its Facility Rating methodology, the Transmission Owner or Generator Owner shall provide a response to that commenting entity within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Facility Ratings methodology and, if no change will be made to that Facility Ratings methodology, the reason why. (Retirement approved by FERC effective January 21, 2014.) | FAC-008-3 | NO | No | Yes - Para 81 Phase 1 |  | Q4: No; Q13: Yes | 3 | 11 |  | 16
FAC-008-3, R6. | FAC-008-3 | R6. | R6. Each Transmission Owner and Generator Owner shall have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology or documentation for determining its Facility Ratings. | FAC-008-3 | NO | Yes - #3 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 |  | 17
FAC-008-3, R7. | FAC-008-3 | R7. | R7. Each Generator Owner shall provide Facility Ratings (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) as scheduled by such requesting entities | FAC-008-3 | NO | Yes - #3, 10 |  |  | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 10 |  | 18
FAC-008-3, R8. | FAC-008-3 | R8. | R8. Each Transmission Owner (and each Generator Owner subject to Requirement R2) shall provide requested information as specified below (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s): [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] 8.1. As scheduled by the requesting entities: 8.1.1. Facility Ratings 8.1.2. Identity of the most limiting equipment of the Facilities 8.2. Within 30 calendar days (or a later date if specified by the requester), for any requested Facility with a Thermal Rating that limits the use of Facilities under the requester’s authority by causing any of the following: 1) An Interconnection Reliability Operating Limit, 2) A limitation of Total Transfer Capability, 3) An impediment to generator deliverability, or 4) An impediment to service to a major load center: 8.2.1. Identity of the existing next most limiting equipment of the Facility 8.2.2. The Thermal Rating for the next most limiting equipment identified in Requirement R8, Part 8.2.1. | FAC-008-3 | NO | Yes |  |  | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 10 |  | 19
INT-004-3.1 , R1 | INT-004-3.1 | R1 | R1. Each Purchasing-Selling Entity that secures energy to serve Load via a Dynamic Schedule or Pseudo-Tie shall ensure that a Request for Interchange is submitted as an on-time Arranged Interchange to the Sink Balancing Authority for that Dynamic Schedul | INT-004-2 | Yes | Yes |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | 2 | 9 |  | 20
INT-004-3.1 , R2 | INT-004-3.1 | R2 | R2. The Purchasing-Selling Entity that submits a Request for Interchange in accordance with Requirement R1 shall ensure the Confirmed Interchange associated with that Dynamic Schedule or Pseudo-Tie is updated for future hours in order to support congestion management procedures if any one of the following occurs: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning, Same Day Operations, Real Time Operations] 2.1. For Confirmed Interchange greater than 250 MW for the last hour, the actual hourly integrated energy deviates from the Confirmed Interchange by more than 10% for that hour and that deviation is expected to persist. 2.2. For Confirmed Interchange less than or equal to 250 MW for the last hour, the actual hourly integrated energy deviates from the Confirmed Interchange by more than 25 MW for that hour and that deviation is expected to persist. 2.3. The Purchasing-Selling Entity receives notification from a Reliability Coordinator or Transmission Operator to update the Confirmed Interchange. | INT-004-2 | Yes | Yes |  |  | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 |  | 21
INT-004-3.1 , R3. | INT-004-3.1 | R3. | R3. Each Balancing Authority shall only implement or operate a Pseudo-Tie that is included in the NAESB Electric Industry Registry publication in order to support congestion management procedures. | INT-004-2 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | 3 | 11 |  | 22
INT-006-4, R1 | INT-006-4 | R1 | R1. Each Balancing Authority shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B. 1.1. Each Source and Sink Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if it does not expect to be capable of supporting the magnitude of the Interchange, including ramping, throughout the duration of the Arranged Interchange. 1.2. Each Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if the Scheduling Path (proper connectivity of Adjacent Balancing Authorities) between it and its Adjacent Balancing Authorities is invalid. | INT-006-3 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | 3 | 11 |  | 23
INT-006-4, R2 | INT-006-4 | R2 | R2. Each Transmission Service Provider shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B. 2.1. Each Transmission Service Provider shall deny the Arranged Interchange or curtail Confirmed Interchange if the transmission path (proper connectivity of adjacent Transmission Service Providers) between it and its adjacent Transmission Service Providers is invalid. | INT-006-3 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 24
INT-006-4, R3. | INT-006-4 | R3. | R3. The Source Balancing Authority and the Sink Balancing Authority receiving a Reliability Adjustment Arranged Interchange shall approve or deny it prior to the expiration of the time period defined in Attachment 1, Column B. 3.1. If a Balancing Authority denies a Reliability Adjustment Arranged Interchange, the Balancing Authority must communicate that fact to its Reliability Coordinator no more than 10 minutes after the denial. | INT-006-3 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 25
INT-006-4, R4 | INT-006-4 | R4 | R4. Each Sink Balancing Authority shall confirm that none of the following conditions exist prior to transitioning an Arranged Interchange to Confirmed Interchange: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning, Same-day Operations, Real-time Operations] • It is a Reliability Adjustment Arranged Interchange, the time period specified in Attachment 1, Column B has elapsed, and the Source Balancing Authority or the Sink Balancing Authority associated with the Arranged Interchange has not communicated its approval of the transition. • It is not a Reliability Adjustment Arranged Interchange, the time period specified in Attachment 1, Column B, has elapsed, and not all Balancing Authorities and Transmission Service Providers associated with the Arranged Interchange have communicated their approval of the transition. • It is not a Reliability Adjustment Arranged Interchange, the time period specified in Attachment 1, Column B, has elapsed, and any entity associated with the Arranged Interchange has communicated its denial of the transition. | INT-006-3 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 26
INT-006-4, R5 | INT-006-4 | R5 | R5. For each Arranged Interchange that is transitioned to Confirmed Interchange, the Sink Balancing Authority shall notify the following entities of the on-time Confirmed Interchange such that the notification is delivered in time to be incorporated into scheduling systems prior to ramp start as specified in Attachment 1, Column D: 5.1. The Source Balancing Authority, 5.2. Each Intermediate Balancing Authority, 5.3. Each Reliability Coordinator associated with each Balancing Authority included in the Arranged Interchange, | INT-006-3 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 27
INT-009-2.1, R1 | INT-009-2.1 | R1 | R1. Each Balancing Authority shall agree with each of its Adjacent Balancing Authorities that its Composite Confirmed Interchange with that Adjacent Balancing Authority, at mutually agreed upon time intervals, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange per INT-010-2 not yet captured in the Composite Confirmed Interchange, is: 1.1. Identical in magnitude to that of the Adjacent Balancing Authority, and 1.2. Opposite in sign or direction to that of the Adjacent Balancing Authority. | INT-009-1 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 3 | 10 |  | 28
INT-009-2.1, R2 | INT-009-2.1 | R2 | R2. The Attaining Balancing Authority and the Native Balancing Authority shall use a dynamic value emanating from an agreed upon common source to account for the Pseudo-Tie in the Actual Net Interchange (NIA) term of their respective control ACE (or alternate control process). | INT-009-1 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 29
INT-009-2.1, R3. | INT-009-2.1 | R3. | R3. Each Balancing Authority in whose area the high-voltage direct current tie is controlled shall coordinate the Confirmed Interchange prior to its implementation with the Transmission Operator of the high-voltage direct current tie. | INT-009-1 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 30
INT-010-2.1, R1 | INT-010-2.1 | R1 | R1. The Balancing Authority that experiences a loss of resources covered by an energy sharing agreement or other reliability needs covered by an energy sharing agreement shall ensure that a Request for Interchange (RFI) is submitted with a start time no m | INT-010-1 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 31
INT-010-2.1, R2 | INT-010-2.1 | R2 | R2. Each Sink Balancing Authority shall ensure that a Reliability Adjustment Arranged Interchange reflecting a modification is submitted within 60 minutes of the start of the modification if a Reliability Coordinator directs the modification of a Confirmed Interchange or Implemented Interchange for actual or anticipated reliability-related reasons. | INT-010-1 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 32
INT-010-2.1, R3. | INT-010-2.1 | R3. | R3. Each Sink Balancing Authority shall ensure that a Request for Interchange is submitted reflecting that Interchange Schedule within 60 minutes of the start of the scheduled Interchange if a Reliability Coordinator directs the scheduling of Interchange for actual or anticipated reliability-related reasons. | INT-010-1 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 |  | 33
NUC-001-3, R1 | NUC-001-3 | R1 | R1. The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt. | NUC-001-2 | NO | Yes - #3 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 34
NUC-001-3, R2. | NUC-001-3 | R2. | R2. The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs. | NUC-001-2 | NO | Yes - #3, 4 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 35
NUC-001-3, R3. | NUC-001-3 | R3. | R3. Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. | NUC-001-2 | NO | Yes - #1 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 36
NUC-001-3, R4. | NUC-001-3 | R4. | R4. Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall 4.1. Incorporate the NPIRs into their operating analyses of the electric system. 4.2. Operate the electric system to meet the NPIRs. 4.3. Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. | NUC-001-2 | NO | Yes - #1 |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 |  | 37
NUC-001-3, R5. | NUC-001-3 | R5. | R5. Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall operate the nuclear plant to meet the NPIRs | NUC-001-2 | NO | Yes - #1 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 38
NUC-001-3, R6. | NUC-001-3 | R6. | R6. Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. | NUC-001-2 | NO | Yes - #1, 3 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 39
NUC-001-3, R7. | NUC-001-3 | R7. | R7. Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | NUC-001-2 | NO | Yes - #3 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 40
NUC-001-3, R8. | NUC-001-3 | R8. | R8. Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | NUC-001-2 | NO | Yes - #3 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 41
NUC-001-3, R9 | NUC-001-3 | R9 | R9. The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include the following elements in aggregate within the Agreement(s) identified in R2. • Where multiple Agreements with a single Transmission Entity are put into effect, the R9 elements must be addressed in aggregate within the Agreements; however, each Agreement does not have to contain each element. The Nuclear Plant Generator Operator and the Transmission Entity are responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements. • Where Agreements with multiple Transmission Entities are required, the Nuclear Plant Generator Operator is responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements with the Transmission Entities. The Agreements with each Transmission Entity do not have to contain each element; however, the Agreements with the multiple Transmission Entities, in the aggregate, must address all R9 elements. For each Agreement(s), the Nuclear Plant Generator Operator and the Transmission Entity are responsible to ensure the Agreement(s) contain(s) the elements of R9 applicable to that Transmission Entity9.1. Retired. [Note: Part 9.1 was retired under the Paragraph 81 project. The NUC SDT proposes to leave this Part blank to avoid renumbering Requirement parts that would impact existing agreements throughout the industry.] 9.2. Technical requirements and analysis: 9.2.1. Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the Agreement. 9.2.2. Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. 9.2.3. Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. 9.3. Operations and maintenance coordination 9.3.1. Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. 9.3.2. Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. 9.3.3. Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. 9.3.4. Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. 9.3.5. Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. 9.3.6. Coordination of physical and cyber security protection at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. 9.3.7. Coordination of the NPIRs with transmission system Remedial Action Schemes and any programs that reduce or shed load based on underfrequency or undervoltage. 9.4. Communications and training Administrative elements: 9.4.1. Provisions for communications affecting the NPIRs between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of applicable unique terms. 9.4.2. Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. 9.4.3. Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. 9.4.4. Provisions for supplying information necessary to report to government agencies, as related to NPIRs. 9.4.5. Provisions for personnel training, as related to NPIRs. | NUC-001-2 | NO | Yes - #3 |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 |  | 42
PER-001-0.2, R1. | PER-001-0.2 | R1. | R1. Each Transmission Operator and Balancing Authority shall provide operating personnel with the responsibility and authority to implement real-time actions to ensure the stable and reliable operation of the Bulk Electric System. | PER-001-0 | No | Yes - #6 |  |  | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 11 |  | 43
PER-003-1, R1. | PER-003-1 | R1. | R1. Each Reliability Coordinator shall staff its Real-time operating positions performing Reliability Coordinator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining a valid NERC Reliability Operator certificate ( ) : [Risk Factor: High][Time Horizon: Real-time Operations] 1.1. Areas of Competency 1.1.1. Resource and demand balancing 1.1.2. Transmission operations 1.1.3. Emergency preparedness and operations 1.1.4. System operations 1.1.5. Protection and control 1.1.6. Voltage and reactive 1.1.7. Interchange scheduling and coordination 1.1.8. Interconnection reliability operations and coordination | PER-003-1 | No | Yes - #6 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 11 |  | 44
PER-003-1, R2. | PER-003-1 | R2. | R2. Each Transmission Operator shall staff its Real-time operating positions performing Transmission Operator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates ( ) : [Risk Factor: High][Time Horizon: Real-time Operations]: 2.1. Areas of Competency 2.1.1. Transmission operations 2.1.2. Emergency preparedness and operations 2.1.3. System operations 2.1.4. Protection and control 2.1.5. Voltage and reactive 2.2. Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Transmission Operator | PER-003-1 | No | Yes - #6 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 11 |  | 45
PER-003-1, R3. | PER-003-1 | R3. | R3. Each Balancing Authority shall staff its Real-time operating positions performing Balancing Authority reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates (1) : [Risk Factor: High][Time Horizon: Real-time Operations]: 3.1. Areas of Competency 3.1.1. Resources and demand balancing 3.1.2. Emergency preparedness and operations 3.1.3. System operations 3.1.4. Interchange scheduling and coordination 3.2. Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Balancing and Interchange Operator | PER-003-1 | No | Yes - #6 | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 11 |  | 46
PER-004-2, R1. | PER-004-2 | R1. | R1. Each Reliability Coordinator shall be staffed with adequately trained and NERC-certified Reliability Coordinator operators, 24 hours per day, seven days per week. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | [5 empty] | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PER-004-2, R2. | PER-004-2 | R2. | R2. Reliability Coordinator operating personnel shall place particular attention on SOLs and IROLs and inter-tie facility limits. The Reliability Coordinator shall ensure protocols are in place to allow Reliability Coordinator operating personnel to have the best available information at all times. [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | [5 empty] | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 3 | 12
PRC-004-5(i), R1. | PRC-004-5(i) | R1. | R1. Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] 1.1 The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and 1.2 The BES interrupting device owner owns all or part of the Composite Protection System; and 1.3 The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | PRC-004-2a & PRC-004-2.1a | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | 3 | 11 |  | 1
PRC-004-5(i), R2. | PRC-004-5(i) | R2. | R2. Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] 2.1 For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: 2.1.1 The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and 2.1.2 The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and 2.1.3 The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. 2.2 For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. | PRC-004-2a & PRC-004-2.1a | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | 3 | 11 |  | 2
PRC-004-5(i), R3. | PRC-004-5(i) | R3. | R3. Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, id | PRC-004-2 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | 3 | 10 |  | 3
PRC-004-5(i), R4. | PRC-004-5(i) | R4. | R4. Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: [Violation Risk Factor: High] [Time Horizon: Operations Assessment, Operations Planning] • The identification of the cause(s) of the Misoperation; or • A declaration that no cause was identified. | PRC-004-2 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | 3 | 10 |  | 4
PRC-004-5(i), R5. | PRC-004-5(i) | R5. | R5. Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: [Violation Risk Factor: High] [Time Horizon: Operations Planning, Long-Term Planning] • Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or • Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | PRC-004-2 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | 3 | 10 |  | 5
PRC-004-5(i), R6. | PRC-004-5(i) | R6. | R6. Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. [Violation Risk Factor: High][Time Horizon: Operations Planning, Long-Term Planning] | PRC-004-2 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | 3 | 10 |  | 6
PRC-005-6, R1. | PRC-005-6 | R1. | R1. Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems, Automatic Reclosing, and Sudden Pressure Relaying identified in Section 4.2, Facilities. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] The PSMP shall: 1.1. Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. 1.2. Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-3, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. | PRC-005-1.1b, PRC-005-1b, PRC-005-2 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 |  | 7
PRC-005-6, R2. | PRC-005-6 | R2. | R2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | PRC-005-1.1b, PRC-005-1b, PRC-005-2 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 |  | 8
PRC-005-6, R3. | PRC-005-6 | R3. | R3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-3, and Table 5. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | PRC-005-1.1b, PRC-005-1b, PRC-005-2 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 |  | 9
PRC-005-6, R4. | PRC-005-6 | R4. | R4. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the performance-based program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | PRC-005-1.1b, PRC-005-1b, PRC-005-2 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 |  | 10
PRC-005-6, R5. | PRC-005-6 | R5. | R5. Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | PRC-005-1.1b, PRC-005-1b, PRC-005-2 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 |  | 11
PRC-006-2 , R1. | PRC-006-2 | R1. | R1. Each Planning Coordinator shall develop and document criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES), including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands | PRC-006-0, PRC-006-1 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 10 |  | 12
PRC-006-2 , R2. | PRC-006-2 | R2. | R2. Each Planning Coordinator shall identify one or more islands to serve as a basis for designing its UFLS program including: [VRF: Medium][Time Horizon: Long-term Planning] 2.1. Those islands selected by applying the criteria in Requirement R1, and 2.2. Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and 2.3. A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. | PRC-006-0, PRC-006-1 | Yes | Yes |  |  | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 |  | 13
PRC-006-2 , R3. | PRC-006-2 | R3. | R3. Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). [VRF: High][Time Horizon: Long-term Planning] 3.1. Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and 3.2. Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and 3.3. Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: • Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES • Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES • Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. | PRC-006-0, PRC-006-1 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 10 |  | 14
PRC-006-2 , R4. | PRC-006-2 | R4. | R4. Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2. The simulation shall model each of the following: [VRF: High][Time Horizon: Long-term Planning] 4.1. Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. 4.2. Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. 4.3. Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. 4.4. Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. 4.5. Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. 4.6. Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. 4.7. Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. | PRC-006-0, PRC-006-1 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 |  | 15
PRC-006-2 , R5. | PRC-006-2 | R5. | R5. Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall coordinate its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island through one of the following: [VRF: High][Time Horizon: Long-term Planning] • Develop a common UFLS program design and schedule for implementation per Requirement R3 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct a joint UFLS design assessment per Requirement R4 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct an independent UFLS design assessment per Requirement R4 for the identified island, and in the event the UFLS design assessment fails to meet Requirement R3, identify modifications to the UFLS program(s) to meet Requirement R3 and report these modifications as recommendations to the other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island and the ERO. | PRC-006-0, PRC-006-1 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 |  | 16
PRC-006-2 , R6. | PRC-006-2 | R6. | R6. Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | PRC-006-0, PRC-006-1 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 11 |  | 17
PRC-006-2 , R7. | PRC-006-2 | R7. | R7. Each Planning Coordinator shall provide its UFLS database containing data necessary to model its UFLS program to other Planning Coordinators within its Interconnection within 30 calendar days of a request. | PRC-006-0, PRC-006-1 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 18
PRC-006-2 , R8. | PRC-006-2 | R8. | R8. Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | PRC-006-0, PRC-006-1 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 19
PRC-006-2 , R9. | PRC-006-2 | R9. | R9. Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. | PRC-006-0, PRC-006-1 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 11 |  | 20
PRC-006-2 , R10. | PRC-006-2 | R10. | R10. Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | PRC-006-0, PRC-006-1 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 11 |  | 21
PRC-006-2 , R11. | PRC-006-2 | R11. | R11. Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall conduct and document an assessment of the event within one year of event actuation to evaluate: [VRF: Medium][Time Horizon: Operations Assessment] 11.1. The performance of the UFLS equipment, 11.2. The effectiveness of the UFLS program. | PRC-006-0, PRC-006-1 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 22
PRC-006-2 , R12. | PRC-006-2 | R12. | R12. Each Planning Coordinator, in whose islanding event assessment (per R11) UFLS program deficiencies are identified, shall conduct and document a UFLS design assessment to consider the identified deficiencies within two years of event actuation. | PRC-006-0, PRC-006-1 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | 3 | 11 |  | 23
PRC-006-2 , R13. | PRC-006-2 | R13. | R13. Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall coordinate its event assessment (in accordance with Requirement R11) with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event through one of the following: [VRF: Medium][Time Horizon: Operations Assessment] • Conduct a joint event assessment per Requirement R11 among the Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 that reaches conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 and where the assessment fails to reach conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, identify differences in the assessments that likely resulted in the differences in the conclusions and recommendations and report these differences to the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event and the ERO. | PRC-006-0, PRC-006-1 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 24
PRC-010-2, R1. | PRC-010-2 | R1. | R1. Each Planning Coordinator or Transmission Planner that is developing a UVLS Program shall evaluate its effectiveness and subsequently provide the UVLS Program’s specifications and implementation schedule to the UVLS entities responsible for implementing the UVLS Program. The evaluation shall include, but is not limited to, studies and analyses that show: [Violation Risk Factor: High] [Time Horizon: Long‐term Planning] 1.1. The implementation of the UVLS Program resolves the identified undervoltage issues that led to its development and design. 1.2. The UVLS Program is integrated through coordination with generator voltage ride‐through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage‐based load shedding programs. | PRC-010-0 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 10 |  | 25
PRC-010-2, R2. | PRC-010-2 | R2. | R2. Each UVLS entity shall adhere to the UVLS Program specifications and implementation schedule determined by its Planning Coordinator or Transmission Planner associated with UVLS Program development per Requirement R1 or with any Corrective Action Plans per Requirement R5. [Violation Risk Factor: High] [Time Horizon: Long‐term Planning] | PRC-010-0 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 |  | 26
PRC-010-2, R3. | PRC-010-2 | R3. | R3. Each Planning Coordinator or Transmission Planner shall perform a comprehensive assessment to evaluate the effectiveness of each of its UVLS Programs at least once every 60 calendar months. Each assessment shall include, but is not limited to, studies and analyses that evaluate whether: [Violation Risk Factor: Medium] [Time Horizon: Long‐term Planning] 3.1. The UVLS Program resolves the identified undervoltage issues for which the UVLS Program is designed. 3.2. The UVLS Program is integrated through coordination with generator voltage ride‐through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage‐based load shedding programs. | PRC-010-0 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 27
PRC-010-2, R4. | PRC-010-2 | R4. | R4. Each Planning Coordinator or Transmission Planner shall, within 12 calendar months of an event that resulted in a voltage excursion for which its UVLS Program was designed to operate, perform an assessment to evaluate: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] 4.1. Whether its UVLS Program resolved the undervoltage issues associated with the event, and 4.2. The performance (i.e., operation and non-operation) of the UVLS Program equipment. | PRC-010-0 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 28
PRC-010-2, R5. | PRC-010-2 | R5. | R5. Each Planning Coordinator or Transmission Planner that identifies deficiencies during an assessment performed in either Requirement R3 or R4 shall develop a Corrective Action Plan to address the deficiencies and subsequently provide the Corrective Action Plan, including an implementation schedule, to UVLS entities within three calendar months of completing the assessment. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | PRC-010-0 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 29
PRC-010-2, R6. | PRC-010-2 | R6. | R6. Each Planning Coordinator that has a UVLS Program in its area shall update a database containing data necessary to model the UVLS Program(s) in its area for use in event analyses and assessments of the UVLS Program at least once each calendar year. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | PRC-010-0 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | 3 | 10 |  | 30
PRC-010-2, R7. | PRC-010-2 | R7. | R7. Each UVLS entity shall provide data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of a UVLS Program database. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | PRC-010-0 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 31
PRC-010-2, R8. | PRC-010-2 | R8. | R8. Each Planning Coordinator that has a UVLS Program in its area shall provide its UVLS Program database to other Planning Coordinators and Transmission Planners within its Interconnection, and other functional entities with a reliability need, within 30 calendar days of a written request. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | PRC-010-0 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 32
PRC-018-1, R1. | PRC-018-1 | R1. | R1. Each Transmission Owner and Generator Owner required to install DMEs by its Regional Reliability Organization (reliability standard PRC-002 Requirements 1-3) shall have DMEs installed that meet the following requirements: R1.1. Internal Clocks in DME devices shall be synchronized to within 2 milliseconds or less of Universal Coordinated Time scale (UTC) R1.2. Recorded data from each Disturbance shall be retrievable for ten calendar days.. | PRC-018-1 | No | Yes |  |  | Yes | No | No | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | 1 | 7 |  | 33
PRC-018-1, R2. | PRC-018-1 | R2. | R2. The Transmission Owner and Generator Owner shall each install DMEs in accordance with its Regional Reliability Organization’s installation requirements (reliability standard PRC-002 Requirements 1 through 3). | PRC-018-1 | No | Yes - #5, 10 |  |  | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | No | No | No | No | Yes | 0 | 4 |  | 34
PRC-018-1, R3. | PRC-018-1 | R3. | R3. The Transmission Owner and Generator Owner shall each maintain, and report to its Regional Reliability Organization on request, the following data on the DMEs installed to meet that region’s installation requirements (reliability standard PRC-002 Requirements1.1, 2.1 and 3.1): R3.1. Type of DME (sequence of event recorder, fault recorder, or dynamic disturbance recorder). R3.2. Make and model of equipment. R3.3. Installation location. R3.4. Operational status. R3.5. Date last tested. R3.6. Monitored elements, such as transmission circuit, bus section, etc. R3.7. Monitored devices, such as circuit breaker, disconnect status, alarms, etc. R3.8. Monitored electrical quantities, such as voltage, current, etc. | PRC-018-1 | No | No - administrative | Yes - administrative | [17 empty] | 0 | 0 |  | 35
PRC-018-1, R4. | PRC-018-1 | R4. | R4. The Transmission Owner and Generator Owner shall each provide Disturbance data (recorded by DMEs) in accordance with its Regional Reliability Organization’s requirements (reliability standard PRC-002 Requirement 4). | PRC-018-1 | No | No |  |  | No | No | Yes | No | No | No | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | 1 | 5 |  | 36
PRC-018-1, R5. | PRC-018-1 | R5. | R5. The Transmission Owner and Generator Owner shall each archive all data recorded by DMEs for Regional Reliability Organization-identified events for at least three years. | PRC-018-1 | No | No |  |  | No | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | 1 | 6 |  | 37
PRC-018-1, R6. | PRC-018-1 | R6. | R6. Each Transmission Owner and Generator Owner that is required by its Regional Reliability Organization to have DMEs shall have a maintenance and testing program for those DMEs that includes: R6.1. Maintenance and testing intervals and their basis. R6.2. Summary of maintenance and testing procedures. | PRC-018-1 | No | No |  |  | No | No | Yes | No | No | No | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | 1 | 5 |  | 38
PRC-019-2, R1. | PRC-019-2 | R1. | R1. At a maximum of every five calendar years, each Generator Owner and Transmission Owner with applicable Facilities shall coordinate the voltage regulating system controls, (including in-service limiters and protection functions) with the applicable equipment capabilities and settings of the applicable Protection System devices and functions. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] 1.1. Assuming the normal automatic voltage regulator control loop and steady-state system operating conditions, verify the following coordination items for each applicable Facility: 1.1.1. The in-service limiters are set to operate before the Protection System of the applicable Facility in order to avoid disconnecting the generator unnecessarily. 1.1.2. The applicable in-service Protection System devices are set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. | PRC-019-1 | No | Yes - #1 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 39
PRC-019-2, R2. | PRC-019-2 | R2. | R2. Within 90 calendar days following the identification or implementation of systems, equipment or setting changes that will affect the coordination described in Requirement R1, each Generator Owner and Transmission Owner with applicable Facilities shall perform the coordination as described in Requirement R1. These possible systems, equipment or settings changes include, but are not limited to the following [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning]: • Voltage regulating settings or equipment changes; • Protection System settings or component changes; • Generating or synchronous condenser equipment capability changes; or • Generator or synchronous condenser step-up transformer changes. | PRC-019-1 | No | Yes - #1 | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 40
PRC-023-4, R1. | PRC-023-4 | R1. | R1. Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting tran | PRC-023-1, PRC-023-2 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 41
PRC-023-4, R2. | PRC-023-4 | R2. | R2. Each Transmission Owner, Generator Owner, and Distribution Provider shall set its out-of-step blocking elements to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | PRC-023-1, PRC-023-2 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 42
PRC-023-4, R3. | PRC-023-4 | R3. | R3. Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning] | PRC-023-1, PRC-023-2 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 43
PRC-023-4, R4. | PRC-023-4 | R4. | R4. Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | PRC-023-1, PRC-023-2 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 44
PRC-023-4, R5. | PRC-023-4 | R5. | R5. Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that have protective relay settings that limit circuit capability. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | PRC-023-1, PRC-023-2 | Yes | Yes |  |  | Yes | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | 3 | 8 |  | 45
PRC-023-4, R6. | PRC-023-4 | R6. | R6. Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in PRC-023-4, Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5. The Planning Coordinator shall: [Violation Risk Factor: High] [Time Horizon: Long Term Planning] 6.1 Maintain a list of circuits subject to PRC-023-4 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023-4, Attachment B applies. 6.2 Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. | PRC-023-1, PRC-023-2 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 46
PRC-024-2, R1. | PRC-024-2 | R1. | R1. Each Generator Owner that has generator frequency protective relaying activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1, subject to the following exceptions: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] • Generating unit(s) may trip if the protective functions (such as out-of-step functions or loss-of-field functions) operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 1 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | PRC-024-1 | NO | Yes - #5 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 47
PRC-024-2, R2. | PRC-024-2 | R2. | R2. Each Generator Owner that has generator voltage protective relaying1 activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating unit(s) as a result of a voltage excursion (at the point of interconnection ) caused by an event on the transmission system external to the generating plant that remains within the “no trip zone” of PRC-024 Attachment 2. If the Transmission Planner allows less stringent voltage relay settings than those required to meet PRC-024 Attachment 2, then the Generator Owner shall set its protective relaying within the voltage recovery characteristics of a location-specific Transmission Planner’s study. Requirement R2 is subject to the following exceptions: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] • Generating unit(s) may trip in accordance with a Special Protection System (SPS) or Remedial Action Scheme (RAS). • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip by action of protective functions (such as out-of-step functions or loss-of-field functions) that operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 2 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | PRC-024-1 | NO | Yes - #5 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 48
PRC-024-2, R3. | PRC-024-2 | R3. | R3. Each Generator Owner shall document each known regulatory or equipment limitation that prevents an applicable generating unit with generator frequency or voltage protective relays from meeting the relay setting criteria in Requirements R1 or R2 including (but not limited to) study results, experience from an actual event, or manufacturer’s advice. [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] 3.1. The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following: • Identification of a regulatory or equipment limitation. • Repair of the equipment causing the limitation that removes the limitation. • Replacement of the equipment causing the limitation with equipment that removes the limitation. • Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. | PRC-024-1 | NO | Yes - #1 |  |  | yes | yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 49
PRC-024-2, R4. | PRC-024-2 | R4. | R4. Each Generator Owner shall provide its applicable generator protection trip settings associated with Requirements R1 and R2 to the Planning Coordinator or Transmission Planner that models the associated unit within 60 calendar days of receipt of a written request for the data and within 60 calendar days of any change to those previously requested trip settings unless directed by the requesting Planning Coordinator or Transmission Planner that the reporting of relay setting changes is not required. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | PRC-024-1 | NO | Yes - #1 |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 50
PRC-025-1, R1. | PRC-025-1 | R1. | R1. Each Generator Owner, Transmission Owner, and Distribution Provider shall apply settings that are in accordance with PRC-025-1 – Attachment 1: Relay Settings, on each load-responsive protective relay while maintaining reliable fault protection. | N/A | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 51
PRC-026-1, R1. | PRC-026-1 | R1. | R1. Each Planning Coordinator shall, at least once each calendar year, provide notification of each generator, transformer, and transmission line BES Element in its area that meets one or more of the following criteria, if any, to the respective Generator Owner and Transmission Owner: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] Criteria: 1. Generator(s) where an angular stability constraint exists that is addressed by a System Operating Limit (SOL) or a Remedial Action Scheme (RAS) and those Elements terminating at the Transmission station associated with the generator(s). 2. An Element that is monitored as part of an SOL identified by the Planning Coordinator’s methodology based on an angular stability constraint. 3. An Element that forms the boundary of an island in the most recent underfrequency load shedding (UFLS) design assessment based on application of the Planning Coordinator’s criteria for identifying islands, only if the island is formed by tripping the Element due to angular instability. 4. An Element identified in the most recent annual Planning Assessment where relay tripping occurs due to a stable or unstable power swing during a simulated disturbance. | N/A | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 52
PRC-026-1, R2. | PRC-026-1 | R2. | R2. Each Generator Owner and Transmission Owner shall: [Violation Risk Factor: High] [Time Horizon: Operations Planning] 2.1 Within 12 full calendar months of notification of a BES Element pursuant to Requirement R1, determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B where an evaluation of that Element’s load-responsive protective relay(s) based on PRC-026-1 – Attachment B criteria has not been performed in the last five calendar years. 2.2 Within 12 full calendar months of becoming aware of a generator, transformer, or transmission line BES Element that tripped in response to a stable or unstable power swing due to the operation of its protective relay(s), determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B. | N/A | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 53
PRC-026-1, R3. | PRC-026-1 | R3. | R3. Each Generator Owner and Transmission Owner shall, within six full calendar months of determining a load-responsive protective relay does not meet the PRC-026-1 – Attachment B criteria pursuant to Requirement R2, develop a Corrective Action Plan (CAP) to meet one of the following: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] • The Protection System meets the PRC-026-1 – Attachment B criteria, while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element); or • The Protection System is excluded under the PRC-026-1 – Attachment A criteria (e.g., modifying the Protection System so that relay functions are supervised by power swing blocking or using relay systems that are immune to power swings), while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element). | N/A | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 54
PRC-026-1, R4. | PRC-026-1 | R4. | R4. Each Generator Owner and Transmission Owner shall implement each CAP developed pursuant to Requirement R3 and update each CAP if actions or timetables change until all actions are complete. [Violation Risk Factor: Medium][Time Horizon: Long-Term Planning] | N/A | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 55
VAR-001-4.1, R1. | VAR-001-4.1 | R1. | R1. Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. [Violation Risk Factor: High] [Time Horizon: Operational Planning] 1.1. Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. | VAR-001-2, VAR-001-3 | Yes | Yes |  |  | Yes | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 9 |  | 56
VAR-001-4.1, R2. | VAR-001-4.1 | R2. | R2. Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. | VAR-001-2, VAR-001-3 | Yes | Yes |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 |  | 57
VAR-001-4.1, R3. | VAR-001-4.1 | R3. | R3. Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. | VAR-001-2, VAR-001-3 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 |  | 58
VAR-001-4.1, R4. | VAR-001-4.1 | R4. | R4. The Transmission Operator shall specify the criteria that will exempt generators from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] 4.1 If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. | VAR-001-2, VAR-001-3 | Yes | Yes |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 |  | 59
VAR-001-4.1, R5. | VAR-001-4.1 | R5. | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] 5.1. The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). 5.2. The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). 5.3. The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. | VAR-001-2, VAR-001-3 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 |  | 60
VAR-001-4.1, R6. | VAR-001-4.1 | R6. | R6. After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. | VAR-001-2, VAR-001-3 | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 |  | 61
VAR-002-4, R1. | VAR-002-4 | R1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] • That the generator is being operated in start-up,1 shutdown,2 or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. | VAR-002-2b, VAR-002-1.1b | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 62
VAR-002-4, R2. | VAR-002-4 | R2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule3 (within each generating Facility’s capabilities4) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] 2.1. When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. 2.2. When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. 2.3. Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | VAR-002-2b, VAR-002-1.1b | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 63
VAR-002-4, R3. | VAR-002-4 | R3. | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | VAR-002-2b, VAR-002-1.1b | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 64
VAR-002-4, R4. | VAR-002-4 | R4. | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] • Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. | VAR-002-2b, VAR-002-1.1b | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 65
VAR-002-4, R5. | VAR-002-4 | R5. | . The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. [Violation Risk Factor: Lower] [Time Horizon: Real-time Operations] 5.1. For generator step-up and auxiliary transformers5 with primary voltages equal to or greater than the generator terminal voltage: 5.1.1. Tap settings. 5.1.2. Available fixed tap ranges. 5.1.3. Impedance data. | VAR-002-2b, VAR-002-1.1b | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 |  | 66
VAR-002-4, R6. | VAR-002-4 | R6. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. [Violation Risk Factor: Lower] [Time Horizon: Real-time Operations] 6.1. If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. | VAR-002-2b, VAR-002-1.1b | Yes | Yes |  |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 |  | 67